## Variables
CLUJ-NAPOCA |  |  | Standard climatic year | Anul climatic standard
Latitude ϕ [°] = | 46.778 |  |  | Latitudine (Paralela)
Longitude λ [°] = | 23.571 |  |  | Longitudine (Meridian)
λ = | 23.571 | [°] | longitude
Altitude [m] = | 410 |  |  | Altitudine
Building level | P+E
TZ = | 120 | [min] | Time zone (GMT + 2h / GMT + 120 min) | Fusul orar / Decalajul in timp fata de meridianul 0 / (GMT / UTC)
A = | 0.2 | [-] | Albedo (The extent to which the horizontal surface diffusely reflects the solar radiation | Albedo (Masura in care suprafata orizontala reflecta radiatia solara)
Symbol | Value | U.M. | Significance | Denumire
γt = | 45 | [°] | The angle of tilted sulface | Unghiul de inclinare a suprafetei colectorilor
αt = | 0 | [°] | The angle of solar azimuth of tilted surface | Unghiul azimutului (azimut) (al suprafetei colectorilor, fata de directia S) (0°=S; 90°=V; 180°=N; 270°=E)
NC = | 140 | [pcs] | Number of solar collectors | Numarul de colectori solari | [6 empty] | Tref | 301
Ap = | 3.23 | [m2] | Aperture area | Apertura (deschiderea / suprafata deschiderii) prin care intra radiatia solara in colector)
S = | 452.2 | [m2] | Total surface of the solar collectors | Suprafata totala a colectorilor solari | [6 empty] | ηTref | 0.11
η0 = | 0.804 | [%] | Optical efficiency of the considered thermal solar collectors | Randamentul optic al colectorilor solari considerati
k1 = | 1.33 | [W/(m2·K)] | Correction factor of the considered thermal solar collectors | Factor de corectie
k2 = | 0.0067 | [W/(m2·K2)] | Correction factor of the considered thermal solar collectors | Factor de corectie
tmw = | 85 | [°C] | Average temperature of the solar thermal agent | Temperatura medie a agentului termic
Tref = | 28 | [°C] | Reference temperature | Temperatura de referinta
| 301 | [K]
ηTref = | 0.11 | [%] | Electrical efficiency at the reference temperature |  | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF!
βref = | 0.004 | [-] | temperature coefficient | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
IgNOCT = | 800 | [W/m2] | the nominal global solar radiation
TNOCT = | 20 | [°C] | the normal operating cell temperature
| 293 | [K]
COPa = | 0.7 | [-] | coefficient of performance of the absorption chiller
Note on F10: Value that depends on the type of material. In this case it was chosen a concrete surface with a coefficient between 0.25 and 0.35.
Note on F19: Vacuum tube collector, Vitosol 300-T type SP3A, Viessmann
Note on F20: Vacuum tube collector, Vitosol 300-T type SP3A, Viessmann
Note on F21: Vacuum tube collector, Vitosol 300-T type SP3A, Viessmann

## Calculation
Month | Day of the year | Day of the month | Hour of the year | Hour of the day | text | IDir oriz | IDif oriz | ITot oriz | IDif oriz | IDif vert | Day | Hour | LT | y | δ(y) | EQT | MLT | ST | ω | γs, interm | γs | αs, interm | αs | θ | Idirt,int | Idirt | Idift=Idifti | Igt | ηinterm | η | P | QS | Q0,a | Q0,load | Q0,load | SFa | ηPV,interm | ηPV | ηDCAC | ηgPV | Pe | COPe,interm | COPe | Q0,PV | PPV1 | SFPV,interm | SFPV
[-] | [-] | [-] | [h] | [h] | [°C] | [W/m²] | [W/m²] | [W/m²] | [W/m²] | [W/m²] | [zi] | [h] | [min] | [°] | [°] | [min] | [min] | [h] | [°] | [°] | [°] | - | [°] | [°] | [W/m2] | [W/m2] | [W/m2] | [W/m2] | [%] | [%] | [kW] | [kW] | [kW] | [-] | [-] | [%] | [%] | [%] | [%] | [%] | [kW] | [-] | [-] | [kW] | [W/m2] | [%] | [%]
1 | 1 | 1 | 1 | 1 | -1.41 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 60 | 0.9863 | -22.8347 | -4.0384 | 34.284 | 0.50409 | 172.4386 | -65.2933 | 0 | 55.4814 | 124.5186 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.204 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7694 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 2 | 2 | -1.93 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 120 | 0.9863 | -22.8347 | -4.0384 | 94.284 | 1.5041 | 157.4386 | -59.9563 | 0 | 55.4814 | 124.5186 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9283 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9508 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 3 | 3 | -2.45 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 180 | 0.9863 | -22.8347 | -4.0384 | 154.284 | 2.5041 | 142.4386 | -51.5461 | 0 | 55.4814 | 124.5186 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6526 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1341 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 4 | 4 | -2.97 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 240 | 0.9863 | -22.8347 | -4.0384 | 214.284 | 3.5041 | 127.4386 | -41.7958 | 0 | 55.4814 | 124.5186 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.445 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3194 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 5 | 5 | -3.51 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 300 | 0.9863 | -22.8347 | -4.0384 | 274.284 | 4.5041 | 112.4386 | -31.5807 | 0 | 55.4814 | 124.5186 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.33 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5137 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 6 | 6 | -4.07 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 360 | 0.9863 | -22.8347 | -4.0384 | 334.284 | 5.5041 | 97.4386 | -21.377 | 0 | 55.4814 | 124.5186 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6166 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7174 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 7 | 7 | -4.66 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 420 | 0.9863 | -22.8347 | -4.0384 | 394.284 | 6.5041 | 82.4386 | -11.5217 | 0 | 55.4814 | 124.5186 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.5767 | 126.5767 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9344 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 8 | 8 | -5.29 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 480 | 0.9863 | -22.8347 | -4.0384 | 454.284 | 7.5041 | 67.4386 | -2.3288 | 0 | 55.4814 | 124.5186 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.8886 | 126.8886 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1687 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 9 | 9 | -6 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 1 | 9 | 540 | 0.9863 | -22.8347 | -4.0384 | 514.284 | 8.5041 | 52.4386 | 5.8525 | 5.8525 | 47.2568 | 132.7432 | 56.6656 | 0 | 0 | 1.6559 | 1.6559 | -105.7926 | 0% | 0.7488 | 0 | 0 | 105.0816 | 105.0816 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 10 | 10 | -6.6 | 0.28 | 20.83 | 21.11 | 20.83 | 10.42 | 1 | 10 | 600 | 0.9863 | -22.8347 | -4.0384 | 574.284 | 9.5041 | 37.4386 | 12.6121 | 12.6121 | 35.0381 | 144.9619 | 43.9963 | 0.9225 | 0.9225 | 17.7795 | 18.702 | -8.7161 | 0% | 8.4571 | 0 | 0 | 104.9086 | 104.9086 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.665 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 11 | 11 | -6.2 | 0.47 | 40.92 | 41.39 | 40.92 | 20.46 | 1 | 11 | 660 | 0.9863 | -22.8347 | -4.0384 | 634.284 | 10.5041 | 22.4386 | 17.4924 | 17.4924 | 21.6438 | 158.3562 | 32.9231 | 1.3125 | 1.3125 | 34.9274 | 36.2399 | -4.0807 | 0% | 16.3877 | 0 | 0 | 105.5764 | 105.5764 | 0% | 12.45% | 12.45% | 80% | 9.962% | 1.6326 | 12.5122 | 6 | 9.7953 | 3.6102 | 9.278% | 9.278%
1 | 1 | 1 | 12 | 12 | -6 | 0.75 | 65.64 | 66.39 | 65.64 | 32.82 | 1 | 12 | 720 | 0.9863 | -22.8347 | -4.0384 | 694.284 | 11.5041 | 7.4386 | 20.063 | 20.063 | 7.2978 | 172.7022 | 25.6584 | 1.9707 | 1.9707 | 56.0272 | 57.9979 | -2.2394 | 0% | 26.2267 | 0 | 0 | 105.6735 | 105.6735 | 0% | 12.41% | 12.41% | 80% | 9.93% | 2.6044 | 12.4362 | 6 | 15.6266 | 5.7595 | 14.79% | 14.79%
1 | 1 | 1 | 13 | 13 | -5.7 | 0.64 | 94.36 | 95 | 94.36 | 47.18 | 1 | 13 | 780 | 0.9863 | -22.8347 | -4.0384 | 754.284 | 12.5041 | -7.5614 | 20.0522 | 20.0522 | 7.4177 | 187.4177 | 25.6925 | 1.682 | 1.682 | 80.5413 | 82.2233 | -1.3335 | 0% | 37.1814 | 0 | 0 | 107.2586 | 107.2586 | 0% | 12.37% | 12.37% | 80% | 9.893% | 3.6785 | 12.3228 | 6 | 22.0707 | 8.1346 | 20.58% | 20.58%
1 | 1 | 1 | 14 | 14 | -5.8 | 1.39 | 114.25 | 115.64 | 114.25 | 57.13 | 1 | 14 | 840 | 0.9863 | -22.8347 | -4.0384 | 814.284 | 13.5041 | -22.5614 | 17.4613 | 17.4613 | 21.7579 | 201.7579 | 33.0027 | 3.8849 | 3.8849 | 97.5185 | 101.4034 | -0.93167 | 0% | 45.8546 | 0 | 0 | 107.8673 | 107.8673 | 0% | 12.34% | 12.34% | 80% | 9.875% | 4.528 | 12.3605 | 6 | 27.1679 | 10.0132 | 25.19% | 25.19%
1 | 1 | 1 | 15 | 15 | -6 | 0.75 | 84.36 | 85.11 | 84.36 | 42.18 | 1 | 15 | 900 | 0.9863 | -22.8347 | -4.0384 | 874.284 | 14.5041 | -37.5614 | 12.5638 | 12.5638 | 35.143 | 215.143 | 44.0953 | 2.4762 | 2.4762 | 72.0058 | 74.482 | -1.5659 | 0% | 33.6807 | 0 | 0 | 126.6045 | 126.6045 | 0% | 12.39% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 16 | 16 | -5.8 | 0.36 | 52.78 | 53.14 | 52.78 | 26.39 | 1 | 16 | 960 | 0.9863 | -22.8347 | -4.0384 | 934.284 | 15.5041 | -52.5614 | 5.7907 | 5.7907 | 47.3521 | 227.3521 | 56.773 | 0 | 0 | 45.0505 | 45.0505 | -3.1028 | 0% | 20.3719 | 0 | 0 | 125.0084 | 125.0084 | 0% | 12.42% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 17 | 17 | -7.1 | 0.19 | 23.97 | 24.16 | 23.97 | 11.99 | 1 | 17 | 1020 | 0.9863 | -22.8347 | -4.0384 | 994.284 | 16.5041 | -67.5614 | -2.4004 | 0 | 55.4814 | 235.4814 | 66.3781 | 0 | 0 | 20.4597 | 20.4597 | -7.9608 | 0% | 9.2519 | 0 | 0 | 121.1999 | 121.1999 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 18 | 18 | -8.1 | 0 | 0 | 0 | 0 | 0 | 1 | 18 | 1080 | 0.9863 | -22.8347 | -4.0384 | 1054.284 | 17.5041 | -82.5614 | -11.6001 | 0 | 55.4814 | 235.4814 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 117.9361 | 117.9361 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.248 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 19 | 19 | -8.8 | 0 | 0 | 0 | 0 | 0 | 1 | 19 | 1140 | 0.9863 | -22.8347 | -4.0384 | 1114.284 | 18.5041 | -97.5614 | -21.4595 | 0 | 55.4814 | 235.4814 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 116.0639 | 116.0639 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5254 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 20 | 20 | -10 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 1200 | 0.9863 | -22.8347 | -4.0384 | 1174.284 | 19.5041 | -112.5614 | -31.6648 | 0 | 55.4814 | 235.4814 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 113.0444 | 113.0444 | 0% | 12.67% | 0% | 80% | 0% | 0 | 14.009 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 21 | 21 | -11 | 0 | 0 | 0 | 0 | 0 | 1 | 21 | 1260 | 0.9863 | -22.8347 | -4.0384 | 1234.284 | 20.5041 | -127.5614 | -41.8783 | 0 | 55.4814 | 235.4814 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -34.7646 | 0 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4197 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 22 | 22 | -11 | 0 | 0 | 0 | 0 | 0 | 1 | 22 | 1320 | 0.9863 | -22.8347 | -4.0384 | 1294.284 | 21.5041 | -142.5614 | -51.622 | 0 | 55.4814 | 235.4814 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.0237 | 0 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4197 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 23 | 23 | -11.1 | 0 | 0 | 0 | 0 | 0 | 1 | 23 | 1380 | 0.9863 | -22.8347 | -4.0384 | 1354.284 | 22.5041 | -157.5614 | -60.0156 | 0 | 55.4814 | 235.4814 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.1079 | 0 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4612 | 6 | 0 | 0 | 0% | 0%
1 | 1 | 1 | 24 | 24 | -12.4 | 0 | 0 | 0 | 0 | 0 | 1 | 24 | 1440 | 0.9863 | -22.8347 | -4.0384 | 1414.284 | 23.5041 | -172.5614 | -65.3175 | 0 | 55.4814 | 235.4814 | 66.3781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -37.0209 | 0 | 0% | 12.78% | 0% | 80% | 0% | 0 | 15.0064 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 25 | 1 | -11.6 | 0 | 0 | 0 | 0 | 0 | 2 | 25 | 60 | 1.9726 | -22.7506 | -4.2459 | 34.284 | 0.50063 | 172.4905 | -65.2214 | 0 | 55.6186 | 124.3814 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.6664 | 0 | 0% | 12.74% | 0% | 80% | 0% | 0 | 14.6695 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 26 | 2 | -11.5 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 120 | 1.9726 | -22.7506 | -4.2459 | 94.284 | 1.5006 | 157.4905 | -59.9098 | 0 | 55.6186 | 124.3814 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.4484 | 0 | 0% | 12.74% | 0% | 80% | 0% | 0 | 14.6277 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 27 | 3 | -11.5 | 0 | 0 | 0 | 0 | 0 | 2 | 27 | 180 | 1.9726 | -22.7506 | -4.2459 | 154.284 | 2.5006 | 142.4905 | -51.5159 | 0 | 55.6186 | 124.3814 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.3827 | 0 | 0% | 12.74% | 0% | 80% | 0% | 0 | 14.6277 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 28 | 4 | -10.4 | 0 | 0 | 0 | 0 | 0 | 2 | 28 | 240 | 1.9726 | -22.7506 | -4.2459 | 214.284 | 3.5006 | 127.4905 | -41.7731 | 0 | 55.6186 | 124.3814 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -33.7063 | 0 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.1724 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 29 | 5 | -10.1 | 0 | 0 | 0 | 0 | 0 | 2 | 29 | 300 | 1.9726 | -22.7506 | -4.2459 | 274.284 | 4.5006 | 112.4905 | -31.56 | 0 | 55.6186 | 124.3814 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.3624 | 0 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.0498 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 30 | 6 | -9.5 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 360 | 1.9726 | -22.7506 | -4.2459 | 334.284 | 5.5006 | 97.4905 | -21.3544 | 0 | 55.6186 | 124.3814 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.9227 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8063 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 31 | 7 | -9.3 | 0 | 0 | 0 | 0 | 0 | 2 | 31 | 420 | 1.9726 | -22.7506 | -4.2459 | 394.284 | 6.5006 | 82.4905 | -11.4942 | 0 | 55.6186 | 124.3814 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 119.4205 | 119.4205 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.7257 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 32 | 8 | -8.9 | 0 | 0 | 0 | 0 | 0 | 2 | 32 | 480 | 1.9726 | -22.7506 | -4.2459 | 454.284 | 7.5006 | 67.4905 | -2.294 | 0 | 55.6186 | 124.3814 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.2686 | 121.2686 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5653 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 33 | 9 | -8.7 | 0 | 2.22 | 2.22 | 2.22 | 1.11 | 2 | 33 | 540 | 1.9726 | -22.7506 | -4.2459 | 514.284 | 8.5006 | 52.4905 | 5.8968 | 5.8968 | 47.3432 | 132.6568 | 56.6844 | 0 | 0 | 1.8949 | 1.8949 | -96.0064 | 0% | 0.85687 | 0 | 0 | 100.8545 | 100.8545 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 34 | 10 | -7.7 | 0.28 | 16.25 | 16.53 | 16.25 | 8.13 | 2 | 34 | 600 | 1.9726 | -22.7506 | -4.2459 | 574.284 | 9.5006 | 37.4905 | 12.6677 | 12.6677 | 35.1192 | 144.8808 | 43.9975 | 0.9185 | 0.9185 | 13.8702 | 14.7887 | -11.426 | 0% | 6.6875 | 0 | 0 | 102.9009 | 102.9009 | 0% | 12.55% | 0% | 80% | 0% | 0 | 13.091 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 35 | 11 | -6.4 | 0.83 | 47.22 | 48.05 | 47.22 | 23.61 | 2 | 35 | 660 | 1.9726 | -22.7506 | -4.2459 | 634.284 | 10.5006 | 22.4905 | 17.5601 | 17.5601 | 21.7162 | 158.2838 | 32.897 | 2.3099 | 2.3099 | 40.3048 | 42.6147 | -3.362 | 0% | 19.2704 | 0 | 0 | 105.5015 | 105.5015 | 0% | 12.45% | 12.45% | 80% | 9.961% | 1.9196 | 12.5884 | 6 | 11.5176 | 4.245 | 10.92% | 10.92%
1 | 2 | 2 | 36 | 12 | -6.1 | 1.25 | 93.19 | 94.44 | 93.19 | 46.6 | 2 | 36 | 720 | 1.9726 | -22.7506 | -4.2459 | 694.284 | 11.5006 | 7.4905 | 20.1421 | 20.1421 | 7.3569 | 172.6431 | 25.5926 | 3.2739 | 3.2739 | 79.5426 | 82.8165 | -1.3304 | 0% | 37.4496 | 0 | 0 | 106.7957 | 106.7957 | 0% | 12.38% | 12.38% | 80% | 9.905% | 3.7095 | 12.4742 | 6 | 22.2568 | 8.2032 | 20.84% | 20.84%
1 | 2 | 2 | 37 | 13 | -5.8 | 1.11 | 104.25 | 105.36 | 104.25 | 52.13 | 2 | 37 | 780 | 1.9726 | -22.7506 | -4.2459 | 754.284 | 12.5006 | -7.5095 | 20.1405 | 20.1405 | 7.3756 | 187.3756 | 25.5979 | 2.9073 | 2.9073 | 88.9829 | 91.8902 | -1.1114 | 0% | 41.5528 | 0 | 0 | 107.5622 | 107.5622 | 0% | 12.36% | 12.36% | 80% | 9.885% | 4.1077 | 12.3605 | 6 | 24.6461 | 9.0838 | 22.91% | 22.91%
1 | 2 | 2 | 38 | 14 | -4.9 | 1.11 | 110.83 | 111.94 | 110.83 | 55.42 | 2 | 38 | 840 | 1.9726 | -22.7506 | -4.2459 | 814.284 | 13.5006 | -22.5095 | 17.5553 | 17.5553 | 21.7339 | 201.7339 | 32.9094 | 3.0895 | 3.0895 | 94.5993 | 97.6888 | -0.97426 | 0% | 44.1749 | 0 | 0 | 109.0506 | 109.0506 | 0% | 12.31% | 12.31% | 80% | 9.851% | 4.3517 | 12.0233 | 6 | 26.1102 | 9.6234 | 23.94% | 23.94%
1 | 2 | 2 | 39 | 15 | -5 | 0.83 | 89.81 | 90.64 | 89.81 | 44.91 | 2 | 39 | 900 | 1.9726 | -22.7506 | -4.2459 | 874.284 | 14.5006 | -37.5095 | 12.6602 | 12.6602 | 35.1355 | 215.1355 | 44.0129 | 2.7236 | 2.7236 | 76.6576 | 79.3812 | -1.3876 | 0% | 35.8962 | 0 | 0 | 128.399 | 128.399 | 0% | 12.34% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 40 | 16 | -4.8 | 0.83 | 73.61 | 74.44 | 73.61 | 36.81 | 2 | 40 | 960 | 1.9726 | -22.7506 | -4.2459 | 934.284 | 15.5006 | -52.5095 | 5.8873 | 5.8873 | 47.358 | 227.358 | 56.7011 | 0 | 0 | 62.8301 | 62.8301 | -1.9568 | 0% | 28.4118 | 0 | 0 | 127.5715 | 127.5715 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 41 | 17 | -4.3 | 0.56 | 29.03 | 29.59 | 29.03 | 14.52 | 2 | 41 | 1020 | 1.9726 | -22.7506 | -4.2459 | 994.284 | 16.5006 | -67.5095 | -2.3051 | 0 | 55.6186 | 235.6186 | 66.4654 | 0 | 0 | 24.7787 | 24.7787 | -6.1455 | 0% | 11.2049 | 0 | 0 | 125.7846 | 125.7846 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 42 | 18 | -2.8 | 0 | 0 | 0 | 0 | 0 | 2 | 42 | 1080 | 1.9726 | -22.7506 | -4.2459 | 1054.284 | 17.5006 | -82.5095 | -11.5064 | 0 | 55.6186 | 235.6186 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.0563 | 126.0563 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 43 | 19 | -1.7 | 0 | 0 | 0 | 0 | 0 | 2 | 43 | 1140 | 1.9726 | -22.7506 | -4.2459 | 1114.284 | 18.5006 | -97.5095 | -21.3672 | 0 | 55.6186 | 235.6186 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.9335 | 126.9335 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 44 | 20 | -2.6 | 0 | 0 | 0 | 0 | 0 | 2 | 44 | 1200 | 1.9726 | -22.7506 | -4.2459 | 1174.284 | 19.5006 | -112.5095 | -31.573 | 0 | 55.6186 | 235.6186 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.3891 | 124.3891 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 45 | 21 | -3.7 | 0 | 0 | 0 | 0 | 0 | 2 | 45 | 1260 | 1.9726 | -22.7506 | -4.2459 | 1234.284 | 20.5006 | -127.5095 | -41.7859 | 0 | 55.6186 | 235.6186 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5684 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 46 | 22 | -3.7 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 1320 | 1.9726 | -22.7506 | -4.2459 | 1294.284 | 21.5006 | -142.5095 | -51.5276 | 0 | 55.6186 | 235.6186 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8238 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 47 | 23 | -4.2 | 0 | 0 | 0 | 0 | 0 | 2 | 47 | 1380 | 1.9726 | -22.7506 | -4.2459 | 1354.284 | 22.5006 | -157.5095 | -59.919 | 0 | 55.6186 | 235.6186 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.5202 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
1 | 2 | 2 | 48 | 24 | -4.7 | 0 | 0 | 0 | 0 | 0 | 2 | 48 | 1440 | 1.9726 | -22.7506 | -4.2459 | 1414.284 | 23.5006 | -172.5095 | -65.2252 | 0 | 55.6186 | 235.6186 | 66.4654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2165 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 49 | 1 | -5.3 | 0 | 0 | 0 | 0 | 0 | 3 | 49 | 60 | 2.9589 | -22.6595 | -4.4484 | 34.284 | 0.49726 | 172.5411 | -65.1424 | 0 | 55.7672 | 124.2328 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.7986 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.1725 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 50 | 2 | -7.2 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 120 | 2.9589 | -22.6595 | -4.4484 | 94.284 | 1.4973 | 157.5411 | -59.8565 | 0 | 55.7672 | 124.2328 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5165 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 51 | 3 | -8 | 0 | 0 | 0 | 0 | 0 | 3 | 51 | 180 | 2.9589 | -22.6595 | -4.4484 | 154.284 | 2.4973 | 142.5411 | -51.4795 | 0 | 55.7672 | 124.2328 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.5581 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.2086 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 52 | 4 | -9.6 | 0 | 0 | 0 | 0 | 0 | 3 | 52 | 240 | 2.9589 | -22.6595 | -4.4484 | 214.284 | 3.4973 | 127.5411 | -41.7447 | 0 | 55.7672 | 124.2328 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.9964 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 53 | 5 | -10.3 | 0 | 0 | 0 | 0 | 0 | 3 | 53 | 300 | 2.9589 | -22.6595 | -4.4484 | 274.284 | 4.4973 | 112.5411 | -31.5336 | 0 | 55.7672 | 124.2328 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6165 | 0 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.1315 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 54 | 6 | -10.7 | 0 | 0 | 0 | 0 | 0 | 3 | 54 | 360 | 2.9589 | -22.6595 | -4.4484 | 334.284 | 5.4973 | 97.5411 | -21.326 | 0 | 55.7672 | 124.2328 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1114 | 0 | 0% | 12.7% | 0% | 80% | 0% | 0 | 14.2958 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 55 | 7 | -11.2 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | 420 | 2.9589 | -22.6595 | -4.4484 | 394.284 | 6.4973 | 82.5411 | -11.4609 | 0 | 55.7672 | 124.2328 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.9965 | 130.9965 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.5027 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 56 | 8 | -11.3 | 0 | 0 | 0 | 0 | 0 | 3 | 56 | 480 | 2.9589 | -22.6595 | -4.4484 | 454.284 | 7.4973 | 67.5411 | -2.2531 | 0 | 55.7672 | 124.2328 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.752 | 134.752 | 0% | 12.73% | 0% | 80% | 0% | 0 | 14.5443 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 57 | 9 | -11.4 | 0 | 2.08 | 2.08 | 2.08 | 1.04 | 3 | 57 | 540 | 2.9589 | -22.6595 | -4.4484 | 514.284 | 8.4973 | 52.5411 | 5.9476 | 5.9476 | 47.4326 | 132.5674 | 56.7 | 0 | 0 | 1.7754 | 1.7754 | -106.4821 | 0% | 0.80283 | 0 | 0 | 114.664 | 114.664 | 0% | 12.73% | 0% | 80% | 0% | 0 | 14.5859 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 58 | 10 | -11.1 | 0 | 14.72 | 14.72 | 14.72 | 7.36 | 3 | 58 | 600 | 2.9589 | -22.6595 | -4.4484 | 574.284 | 9.4973 | 37.5411 | 12.7301 | 12.7301 | 35.2024 | 144.7976 | 43.9945 | 0 | 0 | 12.5643 | 12.5643 | -14.2934 | 0% | 5.6816 | 0 | 0 | 116.6801 | 116.6801 | 0% | 12.7% | 0% | 80% | 0% | 0 | 14.4612 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 59 | 11 | -10.4 | 0.28 | 50.42 | 50.7 | 50.42 | 25.21 | 3 | 59 | 660 | 2.9589 | -22.6595 | -4.4484 | 634.284 | 10.4973 | 22.5411 | 17.6348 | 17.6348 | 21.7896 | 158.2104 | 32.8653 | 0.77632 | 0.77632 | 43.0362 | 43.8125 | -3.4838 | 0% | 19.812 | 0 | 0 | 117.6144 | 117.6144 | 0% | 12.62% | 12.62% | 80% | 10.09% | 1.9996 | 14.1724 | 6 | 11.9978 | 4.422 | 10.2% | 10.2%
1 | 3 | 3 | 60 | 12 | -10.3 | 90.19 | 90 | 180.19 | 90 | 45 | 3 | 60 | 720 | 2.9589 | -22.6595 | -4.4484 | 694.284 | 11.4973 | 7.5411 | 20.2283 | 20.2283 | 7.4157 | 172.5843 | 25.52 | 235.3947 | 235.3947 | 76.8198 | 312.2145 | 0.20313 | 20.31% | 141.1834 | 28.6792 | 20.0754 | 120.6814 | 120.6814 | 16.64% | 12.16% | 12.16% | 85% | 10.34% | 14.5986 | 14.1315 | 6 | 87.5915 | 32.2835 | 72.58% | 72.58%
1 | 3 | 3 | 61 | 13 | -9.6 | 121.39 | 120.47 | 241.86 | 120.47 | 60.24 | 3 | 61 | 780 | 2.9589 | -22.6595 | -4.4484 | 754.284 | 12.4973 | -7.4589 | 20.2356 | 20.2356 | 7.3352 | 187.3352 | 25.497 | 316.7785 | 316.7785 | 102.8276 | 419.6061 | 0.36126 | 36.13% | 189.7459 | 68.5471 | 47.983 | 102.5761 | 102.5761 | 46.78% | 11.97% | 11.97% | 85% | 10.18% | 19.3078 | 13.8467 | 6 | 115.8466 | 42.6974 | 112.9% | 112.9%
1 | 3 | 3 | 62 | 14 | -9.5 | 127.22 | 111.19 | 238.41 | 111.19 | 55.6 | 3 | 62 | 840 | 2.9589 | -22.6595 | -4.4484 | 814.284 | 13.4973 | -22.4589 | 17.6557 | 17.6557 | 21.7131 | 201.7131 | 32.8118 | 352.5355 | 352.5355 | 94.9066 | 447.4422 | 0.38938 | 38.94% | 202.3333 | 78.7849 | 55.1494 | 101.7819 | 101.7819 | 54.18% | 11.92% | 11.92% | 85% | 10.14% | 20.5073 | 13.8063 | 6 | 123.044 | 45.3501 | 120.9% | 120.9%
1 | 3 | 3 | 63 | 15 | -9.9 | 128.33 | 100.47 | 228.8 | 100.47 | 50.24 | 3 | 63 | 900 | 2.9589 | -22.6595 | -4.4484 | 874.284 | 14.4973 | -37.4589 | 12.7625 | 12.7625 | 35.1321 | 215.1321 | 43.928 | 418.3807 | 418.3807 | 85.7565 | 504.1373 | 0.43395 | 43.39% | 227.9709 | 98.9274 | 69.2492 | 99.0783 | 99.0783 | 69.89% | 11.84% | 0% | 90% | 0% | 0 | 13.9683 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 64 | 16 | -9.7 | 58.33 | 75.19 | 133.52 | 75.19 | 37.6 | 3 | 64 | 960 | 2.9589 | -22.6595 | -4.4484 | 934.284 | 15.4973 | -52.4589 | 5.9891 | 5.9891 | 47.3687 | 227.3687 | 56.628 | 0 | 0 | 64.1787 | 64.1787 | -2.0947 | 0% | 29.0216 | 0 | 0 | 135.8644 | 135.8644 | 0% | 12.55% | 0% | 80% | 0% | 0 | 13.8872 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 65 | 17 | -10.3 | 11.86 | 31.75 | 43.61 | 31.75 | 15.88 | 3 | 65 | 1020 | 2.9589 | -22.6595 | -4.4484 | 994.284 | 16.4973 | -67.4589 | -2.205 | 0 | 55.7672 | 235.7672 | 66.56 | 0 | 0 | 27.1003 | 27.1003 | -6.1184 | 0% | 12.2548 | 0 | 0 | 128.1189 | 128.1189 | 0% | 12.64% | 0% | 80% | 0% | 0 | 14.1315 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 66 | 18 | -10.3 | 0 | 2.14 | 2.14 | 2.14 | 1.07 | 3 | 66 | 1080 | 2.9589 | -22.6595 | -4.4484 | 1054.284 | 17.4973 | -82.4589 | -11.4083 | 0 | 55.7672 | 235.7672 | 66.56 | 0 | 0 | 1.8266 | 1.8266 | -101.8997 | 0% | 0.82599 | 0 | 0 | 122.8058 | 122.8058 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.1315 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 67 | 19 | -11.5 | 0 | 0 | 0 | 0 | 0 | 3 | 67 | 1140 | 2.9589 | -22.6595 | -4.4484 | 1114.284 | 18.4973 | -97.4589 | -21.2708 | 0 | 55.7672 | 235.7672 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 118.2928 | 118.2928 | 0% | 12.74% | 0% | 80% | 0% | 0 | 14.6277 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 68 | 20 | -12.1 | 0 | 0 | 0 | 0 | 0 | 3 | 68 | 1200 | 2.9589 | -22.6595 | -4.4484 | 1174.284 | 19.4973 | -112.4589 | -31.4773 | 0 | 55.7672 | 235.7672 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 113.969 | 113.969 | 0% | 12.76% | 0% | 80% | 0% | 0 | 14.8796 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 69 | 21 | -12.9 | 0 | 0 | 0 | 0 | 0 | 3 | 69 | 1260 | 2.9589 | -22.6595 | -4.4484 | 1234.284 | 20.4973 | -127.4589 | -41.6895 | 0 | 55.7672 | 235.7672 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -34.1162 | 0 | 0% | 12.8% | 0% | 80% | 0% | 0 | 15.2193 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 70 | 22 | -13.2 | 0 | 0 | 0 | 0 | 0 | 3 | 70 | 1320 | 2.9589 | -22.6595 | -4.4484 | 1294.284 | 21.4973 | -142.4589 | -51.4287 | 0 | 55.7672 | 235.7672 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.3711 | 0 | 0% | 12.81% | 0% | 80% | 0% | 0 | 15.3479 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 71 | 23 | -14.5 | 0 | 0 | 0 | 0 | 0 | 3 | 71 | 1380 | 2.9589 | -22.6595 | -4.4484 | 1354.284 | 22.4973 | -157.4589 | -59.8169 | 0 | 55.7672 | 235.7672 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -37.1746 | 0 | 0% | 12.87% | 0% | 80% | 0% | 0 | 15.9123 | 6 | 0 | 0 | 0% | 0%
1 | 3 | 3 | 72 | 24 | -14.5 | 0 | 0 | 0 | 0 | 0 | 3 | 72 | 1440 | 2.9589 | -22.6595 | -4.4484 | 1414.284 | 23.4973 | -172.4589 | -65.1262 | 0 | 55.7672 | 235.7672 | 66.56 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -36.997 | 0 | 0% | 12.87% | 0% | 80% | 0% | 0 | 15.9123 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 73 | 1 | -15.1 | 0 | 0 | 0 | 0 | 0 | 4 | 73 | 60 | 3.9452 | -22.5614 | -4.6456 | 34.284 | 0.49397 | 172.5904 | -65.056 | 0 | 55.9269 | 124.0731 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -33.4678 | 0 | 0% | 12.9% | 0% | 80% | 0% | 0 | 16.1768 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 74 | 2 | -15 | 0 | 0 | 0 | 0 | 0 | 4 | 74 | 120 | 3.9452 | -22.5614 | -4.6456 | 94.284 | 1.494 | 157.5904 | -59.7964 | 0 | 55.9269 | 124.0731 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.8358 | 0 | 0% | 12.89% | 0% | 80% | 0% | 0 | 16.1325 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 75 | 3 | -16 | 0 | 0 | 0 | 0 | 0 | 4 | 75 | 180 | 3.9452 | -22.5614 | -4.6456 | 154.284 | 2.494 | 142.5904 | -51.4369 | 0 | 55.9269 | 124.0731 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -33.8802 | 0 | 0% | 12.94% | 0% | 80% | 0% | 0 | 16.5782 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 76 | 4 | -16.3 | 0 | 0 | 0 | 0 | 0 | 4 | 76 | 240 | 3.9452 | -22.5614 | -4.6456 | 214.284 | 3.494 | 127.5904 | -41.7105 | 0 | 55.9269 | 124.0731 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -34.3374 | 0 | 0% | 12.95% | 0% | 80% | 0% | 0 | 16.7133 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 77 | 5 | -17.9 | 0 | 0 | 0 | 0 | 0 | 4 | 77 | 300 | 3.9452 | -22.5614 | -4.6456 | 274.284 | 4.494 | 112.5904 | -31.5016 | 0 | 55.9269 | 124.0731 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.4907 | 0 | 0% | 13.02% | 0% | 80% | 0% | 0 | 17.4443 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 78 | 6 | -17.8 | 0 | 0 | 0 | 0 | 0 | 4 | 78 | 360 | 3.9452 | -22.5614 | -4.6456 | 334.284 | 5.494 | 97.5904 | -21.292 | 0 | 55.9269 | 124.0731 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6634 | 0 | 0% | 13.02% | 0% | 80% | 0% | 0 | 17.3981 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 79 | 7 | -18.4 | 0 | 0 | 0 | 0 | 0 | 4 | 79 | 420 | 3.9452 | -22.5614 | -4.6456 | 394.284 | 6.494 | 82.5904 | -11.4217 | 0 | 55.9269 | 124.0731 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.9838 | 145.9838 | 0% | 13.04% | 0% | 80% | 0% | 0 | 17.6764 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 80 | 8 | -18.5 | 0 | 0 | 0 | 0 | 0 | 4 | 80 | 480 | 3.9452 | -22.5614 | -4.6456 | 454.284 | 7.494 | 67.5904 | -2.206 | 0 | 55.9269 | 124.0731 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 153.5904 | 153.5904 | 0% | 13.05% | 0% | 80% | 0% | 0 | 17.7231 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 81 | 9 | -17.5 | 0.14 | 2.36 | 2.5 | 2.36 | 1.18 | 4 | 81 | 540 | 3.9452 | -22.5614 | -4.6456 | 514.284 | 8.494 | 52.5904 | 6.0049 | 6.0049 | 47.5248 | 132.4752 | 56.7125 | 0 | 0 | 2.0144 | 2.0144 | -101.8163 | 0% | 0.91091 | 0 | 0 | 135.7983 | 135.7983 | 0% | 13% | 0% | 80% | 0% | 0 | 17.2599 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 82 | 10 | -16.7 | 48.61 | 26.67 | 75.28 | 26.67 | 13.34 | 4 | 82 | 600 | 3.9452 | -22.5614 | -4.6456 | 574.284 | 9.494 | 37.5904 | 12.7993 | 12.7993 | 35.2876 | 144.7124 | 43.9874 | 157.8729 | 157.8729 | 22.7643 | 180.6372 | -0.32843 | 0% | 81.6841 | 0 | 0 | 143.2398 | 143.2398 | 0% | 12.6% | 0% | 80% | 0% | 0 | 16.8944 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 83 | 11 | -13.9 | 107.03 | 47.97 | 155 | 47.97 | 23.99 | 4 | 83 | 660 | 3.9452 | -22.5614 | -4.6456 | 634.284 | 10.494 | 22.5904 | 17.7166 | 17.7166 | 21.8639 | 158.1361 | 32.8282 | 295.5468 | 295.5468 | 40.945 | 336.4918 | 0.21834 | 21.83% | 152.1616 | 33.2224 | 23.2556 | 144.7744 | 144.7744 | 16.06% | 12.22% | 12.22% | 85% | 10.38% | 15.8001 | 15.6503 | 6 | 94.8007 | 34.9406 | 65.48% | 65.48%
1 | 4 | 4 | 84 | 12 | -13.2 | 240.14 | 52.92 | 293.06 | 52.92 | 26.46 | 4 | 84 | 720 | 3.9452 | -22.5614 | -4.6456 | 694.284 | 11.494 | 7.5904 | 20.3216 | 20.3216 | 7.4741 | 172.5259 | 25.4405 | 624.4192 | 624.4192 | 45.17 | 669.5892 | 0.51245 | 51.25% | 302.7883 | 155.1652 | 108.6156 | 121.5008 | 121.5008 | 89.4% | 11.59% | 11.59% | 90% | 10.43% | 31.5842 | 15.3479 | 6 | 189.5052 | 69.8456 | 156% | 156%
1 | 4 | 4 | 85 | 13 | -9.7 | 185.56 | 83.81 | 269.37 | 83.81 | 41.91 | 4 | 85 | 780 | 3.9452 | -22.5614 | -4.6456 | 754.284 | 12.494 | -7.4096 | 20.3375 | 20.3375 | 7.2968 | 187.2968 | 25.3897 | 482.34 | 482.34 | 71.5363 | 553.8763 | 0.46812 | 46.81% | 250.4629 | 117.2461 | 82.0723 | 122.3401 | 122.3401 | 67.09% | 11.75% | 11.75% | 90% | 10.58% | 26.4956 | 13.8872 | 6 | 158.9734 | 58.5926 | 129.9% | 129.9%
1 | 4 | 4 | 86 | 14 | -9.3 | 188.89 | 83.25 | 272.14 | 83.25 | 41.63 | 4 | 86 | 840 | 3.9452 | -22.5614 | -4.6456 | 814.284 | 13.494 | -22.4096 | 17.7625 | 17.7625 | 21.6954 | 201.6954 | 32.7102 | 520.975 | 520.975 | 71.0583 | 592.0333 | 0.49152 | 49.15% | 267.7174 | 131.5884 | 92.1119 | 120.8377 | 120.8377 | 76.23% | 11.69% | 11.69% | 90% | 10.52% | 28.1597 | 13.7257 | 6 | 168.9579 | 62.2726 | 139.8% | 139.8%
1 | 4 | 4 | 87 | 15 | -8.4 | 156.39 | 69.81 | 226.2 | 69.81 | 34.91 | 4 | 87 | 900 | 3.9452 | -22.5614 | -4.6456 | 874.284 | 14.494 | -37.4096 | 12.8707 | 12.8707 | 35.1328 | 215.1328 | 43.8409 | 506.3897 | 506.3897 | 59.5866 | 565.9763 | 0.48125 | 48.12% | 255.9345 | 123.168 | 86.2176 | 116.0307 | 116.0307 | 74.31% | 11.72% | 0% | 90% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 88 | 16 | -9.2 | 101.11 | 55.47 | 156.58 | 55.47 | 27.74 | 4 | 88 | 960 | 3.9452 | -22.5614 | -4.6456 | 934.284 | 15.494 | -52.4096 | 6.0961 | 6.0961 | 47.3842 | 227.3842 | 56.5539 | 0 | 0 | 47.3466 | 47.3466 | -3.0979 | 0% | 21.4101 | 0 | 0 | 109.4758 | 109.4758 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 89 | 17 | -11.2 | 27.03 | 23.53 | 50.56 | 23.53 | 11.77 | 4 | 89 | 1020 | 3.9452 | -22.5614 | -4.6456 | 994.284 | 16.494 | -67.4096 | -2.1003 | 0 | 55.9269 | 235.9269 | 66.6619 | 0 | 0 | 20.0841 | 20.0841 | -8.6538 | 0% | 9.082 | 0 | 0 | 138.9431 | 138.9431 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.5027 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 90 | 18 | -12.8 | 0 | 1.81 | 1.81 | 1.81 | 0.91 | 4 | 90 | 1080 | 3.9452 | -22.5614 | -4.6456 | 1054.284 | 17.494 | -82.4096 | -11.306 | 0 | 55.9269 | 235.9269 | 66.6619 | 0 | 0 | 1.5449 | 1.5449 | -124.8704 | 0% | 0.69862 | 0 | 0 | 127.579 | 127.579 | 0% | 12.79% | 0% | 80% | 0% | 0 | 15.1766 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 91 | 19 | -14.2 | 0 | 0 | 0 | 0 | 0 | 4 | 91 | 1140 | 3.9452 | -22.5614 | -4.6456 | 1114.284 | 18.494 | -97.4096 | -21.1704 | 0 | 55.9269 | 235.9269 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.1899 | 121.1899 | 0% | 12.86% | 0% | 80% | 0% | 0 | 15.781 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 92 | 20 | -14.8 | 0 | 0 | 0 | 0 | 0 | 4 | 92 | 1200 | 3.9452 | -22.5614 | -4.6456 | 1174.284 | 19.494 | -112.4096 | -31.3778 | 0 | 55.9269 | 235.9269 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 114.3755 | 114.3755 | 0% | 12.88% | 0% | 80% | 0% | 0 | 16.0442 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 93 | 21 | -15.9 | 0 | 0 | 0 | 0 | 0 | 4 | 93 | 1260 | 3.9452 | -22.5614 | -4.6456 | 1234.284 | 20.494 | -127.4096 | -41.5891 | 0 | 55.9269 | 235.9269 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -34.7581 | 0 | 0% | 12.93% | 0% | 80% | 0% | 0 | 16.5333 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 94 | 22 | -16.2 | 0 | 0 | 0 | 0 | 0 | 4 | 94 | 1320 | 3.9452 | -22.5614 | -4.6456 | 1294.284 | 21.494 | -142.4096 | -51.3253 | 0 | 55.9269 | 235.9269 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -36.5831 | 0 | 0% | 12.94% | 0% | 80% | 0% | 0 | 16.6682 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 95 | 23 | -15.8 | 0 | 0 | 0 | 0 | 0 | 4 | 95 | 1380 | 3.9452 | -22.5614 | -4.6456 | 1354.284 | 22.494 | -157.4096 | -59.7095 | 0 | 55.9269 | 235.9269 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.4939 | 0 | 0% | 12.93% | 0% | 80% | 0% | 0 | 16.4885 | 6 | 0 | 0 | 0% | 0%
1 | 4 | 4 | 96 | 24 | -14.9 | 0 | 0 | 0 | 0 | 0 | 4 | 96 | 1440 | 3.9452 | -22.5614 | -4.6456 | 1414.284 | 23.494 | -172.4096 | -65.0207 | 0 | 55.9269 | 235.9269 | 66.6619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -33.6427 | 0 | 0% | 12.89% | 0% | 80% | 0% | 0 | 16.0883 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 97 | 1 | -14.4 | 0 | 0 | 0 | 0 | 0 | 5 | 97 | 60 | 4.9315 | -22.4564 | -4.8371 | 34.284 | 0.49078 | 172.6383 | -64.9625 | 0 | 56.0978 | 123.9022 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -37.5029 | 0 | 0% | 12.87% | 0% | 80% | 0% | 0 | 15.8684 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 98 | 2 | -13.3 | 0 | 0 | 0 | 0 | 0 | 5 | 98 | 120 | 4.9315 | -22.4564 | -4.8371 | 94.284 | 1.4908 | 157.6383 | -59.7294 | 0 | 56.0978 | 123.9022 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.6889 | 0 | 0% | 12.82% | 0% | 80% | 0% | 0 | 15.3909 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 99 | 3 | -13.1 | 0 | 0 | 0 | 0 | 0 | 5 | 99 | 180 | 4.9315 | -22.4564 | -4.8371 | 154.284 | 2.4908 | 142.6383 | -51.3881 | 0 | 56.0978 | 123.9022 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -35.2465 | 0 | 0% | 12.81% | 0% | 80% | 0% | 0 | 15.305 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 100 | 4 | -12.8 | 0 | 0 | 0 | 0 | 0 | 5 | 100 | 240 | 4.9315 | -22.4564 | -4.8371 | 214.284 | 3.4908 | 127.6383 | -41.6704 | 0 | 56.0978 | 123.9022 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -34.7894 | 0 | 0% | 12.8% | 0% | 80% | 0% | 0 | 15.1766 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 101 | 5 | -12.5 | 0 | 0 | 0 | 0 | 0 | 5 | 101 | 300 | 4.9315 | -22.4564 | -4.8371 | 274.284 | 4.4908 | 112.6383 | -31.4639 | 0 | 56.0978 | 123.9022 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.1739 | 0 | 0% | 12.78% | 0% | 80% | 0% | 0 | 15.0489 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 102 | 6 | -12.1 | 0 | 0 | 0 | 0 | 0 | 5 | 102 | 360 | 4.9315 | -22.4564 | -4.8371 | 334.284 | 5.4908 | 97.6383 | -21.2523 | 0 | 56.0978 | 123.9022 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.4037 | 0 | 0% | 12.76% | 0% | 80% | 0% | 0 | 14.8796 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 103 | 7 | -12 | 0 | 0 | 0 | 0 | 0 | 5 | 103 | 420 | 4.9315 | -22.4564 | -4.8371 | 394.284 | 6.4908 | 82.6383 | -11.3766 | 0 | 56.0978 | 123.9022 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.9248 | 124.9248 | 0% | 12.76% | 0% | 80% | 0% | 0 | 14.8374 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 104 | 8 | -11.2 | 0 | 0 | 0 | 0 | 0 | 5 | 104 | 480 | 4.9315 | -22.4564 | -4.8371 | 454.284 | 7.4908 | 67.6383 | -2.1528 | 0 | 56.0978 | 123.9022 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.1014 | 129.1014 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.5027 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 105 | 9 | -10.7 | 0 | 1.75 | 1.75 | 1.75 | 0.88 | 5 | 105 | 540 | 4.9315 | -22.4564 | -4.8371 | 514.284 | 8.4908 | 52.6383 | 6.0686 | 6.0686 | 47.6198 | 132.3802 | 56.7217 | 0 | 0 | 1.4937 | 1.4937 | -125.4868 | 0% | 0.67546 | 0 | 0 | 109.6501 | 109.6501 | 0% | 12.7% | 0% | 80% | 0% | 0 | 14.2958 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 106 | 10 | -10.4 | 5.83 | 22.5 | 28.33 | 22.5 | 11.25 | 5 | 106 | 600 | 4.9315 | -22.4564 | -4.8371 | 574.284 | 9.4908 | 37.6383 | 12.8752 | 12.8752 | 35.3748 | 144.6252 | 43.9761 | 18.8281 | 18.8281 | 19.205 | 38.0331 | -4.1354 | 0% | 17.1986 | 0 | 0 | 112.291 | 112.291 | 0% | 12.63% | 0% | 80% | 0% | 0 | 14.1724 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 107 | 11 | -9.6 | 17.58 | 74.53 | 92.11 | 74.53 | 37.27 | 5 | 107 | 660 | 4.9315 | -22.4564 | -4.8371 | 634.284 | 10.4908 | 22.6383 | 17.8053 | 17.8053 | 21.939 | 158.061 | 32.7855 | 48.3335 | 48.3335 | 63.6153 | 111.9489 | -0.85548 | 0% | 50.6233 | 0 | 0 | 115.015 | 115.015 | 0% | 12.47% | 12.47% | 80% | 9.978% | 5.051 | 13.8467 | 6 | 30.3063 | 11.1699 | 26.35% | 26.35%
1 | 5 | 5 | 108 | 12 | -8.6 | 62.69 | 87.58 | 150.27 | 87.58 | 43.79 | 5 | 108 | 720 | 4.9315 | -22.4564 | -4.8371 | 694.284 | 11.4908 | 7.6383 | 20.4219 | 20.4219 | 7.5319 | 172.4681 | 25.3542 | 162.358 | 162.358 | 74.7542 | 237.1122 | 0.031427 | 3.143% | 107.2221 | 3.3697 | 2.3588 | 116.5364 | 116.5364 | 2.024% | 12.24% | 12.24% | 80% | 9.79% | 10.497 | 13.4458 | 6 | 62.9819 | 23.2131 | 54.04% | 54.04%
1 | 5 | 5 | 109 | 13 | -7.3 | 95.36 | 104.08 | 199.44 | 104.08 | 52.04 | 5 | 109 | 780 | 4.9315 | -22.4564 | -4.8371 | 754.284 | 12.4908 | -7.3617 | 20.4462 | 20.4462 | 7.2604 | 187.2604 | 25.2763 | 246.8455 | 246.8455 | 88.8378 | 335.6834 | 0.26826 | 26.83% | 151.796 | 40.7211 | 28.5048 | 120.0039 | 120.0039 | 23.75% | 12.05% | 12.05% | 85% | 10.24% | 15.5466 | 12.9351 | 6 | 93.2798 | 34.38 | 77.73% | 77.73%
1 | 5 | 5 | 110 | 14 | -6.2 | 97.69 | 106.11 | 203.8 | 106.11 | 53.06 | 5 | 110 | 840 | 4.9315 | -22.4564 | -4.8371 | 814.284 | 13.4908 | -22.3617 | 17.8756 | 17.8756 | 21.681 | 201.681 | 32.6045 | 268.104 | 268.104 | 90.5706 | 358.6746 | 0.31045 | 31.05% | 162.1926 | 50.3531 | 35.2472 | 100.2802 | 100.2802 | 35.15% | 11.99% | 11.99% | 85% | 10.19% | 16.527 | 12.5122 | 6 | 99.1622 | 36.5481 | 98.89% | 98.89%
1 | 5 | 5 | 111 | 15 | -6.5 | 82.97 | 85.92 | 168.89 | 85.92 | 42.96 | 5 | 111 | 900 | 4.9315 | -22.4564 | -4.8371 | 874.284 | 14.4908 | -37.3617 | 12.9845 | 12.9845 | 35.1378 | 215.1378 | 43.7517 | 266.7384 | 266.7384 | 73.3373 | 340.0758 | 0.28121 | 28.12% | 153.7823 | 43.2447 | 30.2713 | 96.9025 | 96.9025 | 31.24% | 12.02% | 0% | 85% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 112 | 16 | -7.1 | 40.47 | 40.64 | 81.11 | 40.64 | 20.32 | 5 | 112 | 960 | 4.9315 | -22.4564 | -4.8371 | 934.284 | 15.4908 | -52.3617 | 6.2082 | 6.2082 | 47.4046 | 227.4046 | 56.4789 | 0 | 0 | 34.6884 | 34.6884 | -4.3656 | 0% | 15.6861 | 0 | 0 | 133.0879 | 133.0879 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 113 | 17 | -7.5 | 3.25 | 19.72 | 22.97 | 19.72 | 9.86 | 5 | 113 | 1020 | 4.9315 | -22.4564 | -4.8371 | 994.284 | 16.4908 | -67.3617 | -1.991 | 0 | 56.0978 | 236.0978 | 66.771 | 0 | 0 | 16.8321 | 16.8321 | -9.9108 | 0% | 7.6115 | 0 | 0 | 127.5403 | 127.5403 | 0% | 12.54% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 114 | 18 | -8 | 0 | 0.97 | 0.97 | 0.97 | 0.49 | 5 | 114 | 1080 | 4.9315 | -22.4564 | -4.8371 | 1054.284 | 17.4908 | -82.3617 | -11.1996 | 0 | 56.0978 | 236.0978 | 66.771 | 0 | 0 | 0.82795 | 0.82795 | -218.58 | 0% | 0.3744 | 0 | 0 | 123.6523 | 123.6523 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.2086 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 115 | 19 | -8.2 | 0 | 0 | 0 | 0 | 0 | 5 | 115 | 1140 | 4.9315 | -22.4564 | -4.8371 | 1114.284 | 18.4908 | -97.3617 | -21.0662 | 0 | 56.0978 | 236.0978 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.3659 | 121.3659 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.2874 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 116 | 20 | -8.4 | 0 | 0 | 0 | 0 | 0 | 5 | 116 | 1200 | 4.9315 | -22.4564 | -4.8371 | 1174.284 | 19.4908 | -112.3617 | -31.2745 | 0 | 56.0978 | 236.0978 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 118.4801 | 118.4801 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 117 | 21 | -8.6 | 0 | 0 | 0 | 0 | 0 | 5 | 117 | 1260 | 4.9315 | -22.4564 | -4.8371 | 1234.284 | 20.4908 | -127.3617 | -41.4848 | 0 | 56.0978 | 236.0978 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.4764 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4458 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 118 | 22 | -8.9 | 0 | 0 | 0 | 0 | 0 | 5 | 118 | 1320 | 4.9315 | -22.4564 | -4.8371 | 1294.284 | 21.4908 | -142.3617 | -51.2176 | 0 | 56.0978 | 236.0978 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.5336 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5653 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 119 | 23 | -8.5 | 0 | 0 | 0 | 0 | 0 | 5 | 119 | 1380 | 4.9315 | -22.4564 | -4.8371 | 1354.284 | 22.4908 | -157.3617 | -59.5968 | 0 | 56.0978 | 236.0978 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.7864 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4061 | 6 | 0 | 0 | 0% | 0%
1 | 5 | 5 | 120 | 24 | -8.5 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 1440 | 4.9315 | -22.4564 | -4.8371 | 1414.284 | 23.4908 | -172.3617 | -64.9086 | 0 | 56.0978 | 236.0978 | 66.771 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.6489 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4061 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 121 | 1 | -8.7 | 0 | 0 | 0 | 0 | 0 | 6 | 121 | 60 | 5.9178 | -22.3445 | -5.0224 | 34.284 | 0.48769 | 172.6846 | -64.8618 | 0 | 56.2797 | 123.7203 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.7938 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 122 | 2 | -8.9 | 0 | 0 | 0 | 0 | 0 | 6 | 122 | 120 | 5.9178 | -22.3445 | -5.0224 | 94.284 | 1.4877 | 157.6846 | -59.6556 | 0 | 56.2797 | 123.7203 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.9105 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5653 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 123 | 3 | -8.8 | 0 | 0 | 0 | 0 | 0 | 6 | 123 | 180 | 5.9178 | -22.3445 | -5.0224 | 154.284 | 2.4877 | 142.6846 | -51.333 | 0 | 56.2797 | 123.7203 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.5701 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5254 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 124 | 4 | -9 | 0 | 0 | 0 | 0 | 0 | 6 | 124 | 240 | 5.9178 | -22.3445 | -5.0224 | 214.284 | 3.4877 | 127.6846 | -41.6245 | 0 | 56.2797 | 123.7203 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.8749 | 0 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6053 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 125 | 5 | -9.3 | 0 | 0 | 0 | 0 | 0 | 6 | 125 | 300 | 5.9178 | -22.3445 | -5.0224 | 274.284 | 4.4877 | 112.6846 | -31.4204 | 0 | 56.2797 | 123.7203 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.3781 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.7257 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 126 | 6 | -9.6 | 0 | 0 | 0 | 0 | 0 | 6 | 126 | 360 | 5.9178 | -22.3445 | -5.0224 | 334.284 | 5.4877 | 97.6846 | -21.2067 | 0 | 56.2797 | 123.7203 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0697 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 127 | 7 | -9.6 | 0 | 0 | 0 | 0 | 0 | 6 | 127 | 420 | 5.9178 | -22.3445 | -5.0224 | 394.284 | 6.4877 | 82.6846 | -11.3255 | 0 | 56.2797 | 123.7203 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.8969 | 129.8969 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 128 | 8 | -9.4 | 0 | 0 | 0 | 0 | 0 | 6 | 128 | 480 | 5.9178 | -22.3445 | -5.0224 | 454.284 | 7.4877 | 67.6846 | -2.0933 | 0 | 56.2797 | 123.7203 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.3814 | 133.3814 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.7659 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 129 | 9 | -9.3 | 0 | 2.42 | 2.42 | 2.42 | 1.21 | 6 | 129 | 540 | 5.9178 | -22.3445 | -5.0224 | 514.284 | 8.4877 | 52.6846 | 6.1388 | 6.1388 | 47.7175 | 132.2825 | 56.7276 | 0 | 0 | 2.0656 | 2.0656 | -88.7578 | 0% | 0.93406 | 0 | 0 | 113.1845 | 113.1845 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.7257 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 130 | 10 | -8.7 | 1.94 | 26.86 | 28.8 | 26.86 | 13.43 | 6 | 130 | 600 | 5.9178 | -22.3445 | -5.0224 | 574.284 | 9.4877 | 37.6846 | 12.9579 | 12.9579 | 35.4638 | 144.5362 | 43.9605 | 6.2276 | 6.2276 | 22.9264 | 29.154 | -5.4883 | 0% | 13.1835 | 0 | 0 | 115.1926 | 115.1926 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 131 | 11 | -7.9 | 26.94 | 62.14 | 89.08 | 62.14 | 31.07 | 6 | 131 | 660 | 5.9178 | -22.3445 | -5.0224 | 634.284 | 10.4877 | 22.6846 | 17.9009 | 17.9009 | 22.0149 | 157.9851 | 32.7373 | 73.7243 | 73.7243 | 53.0398 | 126.7641 | -0.62685 | 0% | 57.3227 | 0 | 0 | 117.264 | 117.264 | 0% | 12.39% | 12.39% | 80% | 9.908% | 5.6796 | 13.1693 | 6 | 34.0774 | 12.5599 | 29.06% | 29.06%
1 | 6 | 6 | 132 | 12 | -6.2 | 45.75 | 118.81 | 164.56 | 118.81 | 59.41 | 6 | 132 | 720 | 5.9178 | -22.3445 | -5.0224 | 694.284 | 11.4877 | 7.6846 | 20.5291 | 20.5291 | 7.589 | 172.411 | 25.2612 | 117.984 | 117.984 | 101.4107 | 219.3947 | -0.0028694 | 0% | 99.2103 | 0 | 0 | 119.548 | 119.548 | 0% | 12.19% | 12.19% | 80% | 9.751% | 9.6739 | 12.5122 | 6 | 58.0435 | 21.393 | 48.55% | 48.55%
1 | 6 | 6 | 133 | 13 | -5.6 | 6.94 | 160.64 | 167.58 | 160.64 | 80.32 | 6 | 133 | 780 | 5.9178 | -22.3445 | -5.0224 | 754.284 | 12.4877 | -7.3154 | 20.5617 | 20.5617 | 7.226 | 187.226 | 25.1566 | 17.8857 | 17.8857 | 137.1148 | 155.0005 | -0.32822 | 0% | 70.0912 | 0 | 0 | 119.6628 | 119.6628 | 0% | 12.26% | 12.26% | 80% | 9.808% | 6.8746 | 12.2851 | 6 | 41.2478 | 15.2026 | 34.47% | 34.47%
1 | 6 | 6 | 134 | 14 | -5.5 | 19.17 | 173.14 | 192.31 | 173.14 | 86.57 | 6 | 134 | 840 | 5.9178 | -22.3445 | -5.0224 | 814.284 | 13.4877 | -22.3154 | 17.995 | 17.995 | 21.6698 | 201.6698 | 32.495 | 52.3371 | 52.3371 | 147.7842 | 200.1213 | -0.071667 | 0% | 90.4948 | 0 | 0 | 120.1706 | 120.1706 | 0% | 12.19% | 12.19% | 80% | 9.755% | 8.8275 | 12.2475 | 6 | 52.9648 | 19.5212 | 44.07% | 44.07%
1 | 6 | 6 | 135 | 15 | -6 | 3.33 | 137.03 | 140.36 | 137.03 | 68.52 | 6 | 135 | 900 | 5.9178 | -22.3445 | -5.0224 | 874.284 | 14.4877 | -37.3154 | 13.104 | 13.104 | 35.147 | 215.147 | 43.6604 | 10.6258 | 10.6258 | 116.9624 | 127.5882 | -0.57946 | 0% | 57.6954 | 0 | 0 | 136.2769 | 136.2769 | 0% | 12.31% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 136 | 16 | -6.7 | 4.72 | 94.08 | 98.8 | 94.08 | 47.04 | 6 | 136 | 960 | 5.9178 | -22.3445 | -5.0224 | 934.284 | 15.4877 | -52.3154 | 6.3254 | 6.3254 | 47.4299 | 227.4299 | 56.4031 | 0 | 0 | 80.3023 | 80.3023 | -1.4164 | 0% | 36.3127 | 0 | 0 | 132.1724 | 132.1724 | 0% | 12.41% | 0% | 80% | 0% | 0 | 12.7034 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 137 | 17 | -7 | 5.19 | 42.03 | 47.22 | 42.03 | 21.02 | 6 | 137 | 1020 | 5.9178 | -22.3445 | -5.0224 | 994.284 | 16.4877 | -67.3154 | -1.8772 | 0 | 56.2797 | 236.2797 | 66.8872 | 0 | 0 | 35.8748 | 35.8748 | -4.1875 | 0% | 16.2226 | 0 | 0 | 128.0908 | 128.0908 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.8189 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 138 | 18 | -7.7 | 0 | 2.36 | 2.36 | 2.36 | 1.18 | 6 | 138 | 1080 | 5.9178 | -22.3445 | -5.0224 | 1054.284 | 17.4877 | -82.3154 | -11.0891 | 0 | 56.2797 | 236.2797 | 66.8872 | 0 | 0 | 2.0144 | 2.0144 | -88.9832 | 0% | 0.91091 | 0 | 0 | 122.9175 | 122.9175 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.091 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 139 | 19 | -7.8 | 0 | 0 | 0 | 0 | 0 | 6 | 139 | 1140 | 5.9178 | -22.3445 | -5.0224 | 1114.284 | 18.4877 | -97.3154 | -20.9582 | 0 | 56.2797 | 236.2797 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.8869 | 120.8869 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 140 | 20 | -7.7 | 0 | 0 | 0 | 0 | 0 | 6 | 140 | 1200 | 5.9178 | -22.3445 | -5.0224 | 1174.284 | 19.4877 | -112.3154 | -31.1676 | 0 | 56.2797 | 236.2797 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 118.3937 | 118.3937 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.091 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 141 | 21 | -7.5 | 0 | 0 | 0 | 0 | 0 | 6 | 141 | 1260 | 5.9178 | -22.3445 | -5.0224 | 1234.284 | 20.4877 | -127.3154 | -41.3768 | 0 | 56.2797 | 236.2797 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.9394 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 142 | 22 | -7.3 | 0 | 0 | 0 | 0 | 0 | 6 | 142 | 1320 | 5.9178 | -22.3445 | -5.0224 | 1294.284 | 21.4877 | -142.3154 | -51.1057 | 0 | 56.2797 | 236.2797 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.2244 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 143 | 23 | -7.3 | 0 | 0 | 0 | 0 | 0 | 6 | 143 | 1380 | 5.9178 | -22.3445 | -5.0224 | 1354.284 | 22.4877 | -157.3154 | -59.4789 | 0 | 56.2797 | 236.2797 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.0363 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
1 | 6 | 6 | 144 | 24 | -7.3 | 0 | 0 | 0 | 0 | 0 | 6 | 144 | 1440 | 5.9178 | -22.3445 | -5.0224 | 1414.284 | 23.4877 | -172.3154 | -64.7901 | 0 | 56.2797 | 236.2797 | 66.8872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.8483 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 145 | 1 | -7.3 | 0 | 0 | 0 | 0 | 0 | 7 | 145 | 60 | 6.9041 | -22.2257 | -5.2013 | 34.284 | 0.48471 | 172.7293 | -64.754 | 0 | 56.4725 | 123.5275 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.9633 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 146 | 2 | -7.3 | 0 | 0 | 0 | 0 | 0 | 7 | 146 | 120 | 6.9041 | -22.2257 | -5.2013 | 94.284 | 1.4847 | 157.7293 | -59.575 | 0 | 56.4725 | 123.5275 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.7263 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 147 | 3 | -7.1 | 0 | 0 | 0 | 0 | 0 | 7 | 147 | 180 | 6.9041 | -22.2257 | -5.2013 | 154.284 | 2.4847 | 142.7293 | -51.2716 | 0 | 56.4725 | 123.5275 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.1844 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 148 | 4 | -7.1 | 0 | 0 | 0 | 0 | 0 | 7 | 148 | 240 | 6.9041 | -22.2257 | -5.2013 | 214.284 | 3.4847 | 127.7293 | -41.5726 | 0 | 56.4725 | 123.5275 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.1844 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 149 | 5 | -6.9 | 0 | 0 | 0 | 0 | 0 | 7 | 149 | 300 | 6.9041 | -22.2257 | -5.2013 | 274.284 | 4.4847 | 112.7293 | -31.3712 | 0 | 56.4725 | 123.5275 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.782 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.7803 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 150 | 6 | -6.7 | 0 | 0 | 0 | 0 | 0 | 7 | 150 | 360 | 6.9041 | -22.2257 | -5.2013 | 334.284 | 5.4847 | 97.7293 | -21.1554 | 0 | 56.4725 | 123.5275 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0007 | 0 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7034 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 151 | 7 | -6.1 | 0 | 0 | 0 | 0 | 0 | 7 | 151 | 420 | 6.9041 | -22.2257 | -5.2013 | 394.284 | 6.4847 | 82.7293 | -11.2685 | 0 | 56.4725 | 123.5275 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.6662 | 137.6662 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 152 | 8 | -5.7 | 0 | 0 | 0 | 0 | 0 | 7 | 152 | 480 | 6.9041 | -22.2257 | -5.2013 | 454.284 | 7.4847 | 67.7293 | -2.0277 | 0 | 56.4725 | 123.5275 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.138 | 142.138 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 153 | 9 | -5.8 | 0.19 | 2.03 | 2.22 | 2.03 | 1.02 | 7 | 153 | 540 | 6.9041 | -22.2257 | -5.2013 | 514.284 | 8.4847 | 52.7293 | 6.2155 | 6.2155 | 47.8178 | 132.1822 | 56.7303 | 0 | 0 | 1.7327 | 1.7327 | -100.7726 | 0% | 0.78353 | 0 | 0 | 121.7866 | 121.7866 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 154 | 10 | -5.4 | 17.69 | 27.69 | 45.38 | 27.69 | 13.85 | 7 | 154 | 600 | 6.9041 | -22.2257 | -5.2013 | 574.284 | 9.4847 | 37.7293 | 13.0474 | 13.0474 | 35.5545 | 144.4455 | 43.9407 | 56.4228 | 56.4228 | 23.6349 | 80.0577 | -1.3817 | 0% | 36.2021 | 0 | 0 | 125.1788 | 125.1788 | 0% | 12.36% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 155 | 11 | -5.2 | 40.75 | 56.03 | 96.78 | 56.03 | 28.02 | 7 | 155 | 660 | 6.9041 | -22.2257 | -5.2013 | 634.284 | 10.4847 | 22.7293 | 18.0036 | 18.0036 | 22.0914 | 157.9086 | 32.6837 | 110.9689 | 110.9689 | 47.8246 | 158.7935 | -0.29477 | 0% | 71.8064 | 0 | 0 | 124.7738 | 124.7738 | 0% | 12.24% | 12.24% | 80% | 9.793% | 7.0317 | 12.1351 | 6 | 42.1902 | 15.55 | 33.81% | 33.81%
1 | 7 | 7 | 156 | 12 | -4.5 | 72.31 | 91.47 | 163.78 | 91.47 | 45.74 | 7 | 156 | 720 | 6.9041 | -22.2257 | -5.2013 | 694.284 | 11.4847 | 7.7293 | 20.6433 | 20.6433 | 7.6455 | 172.3545 | 25.1615 | 185.6447 | 185.6447 | 78.0745 | 263.7193 | 0.14912 | 14.91% | 119.2539 | 17.7835 | 12.4484 | 124.1291 | 124.1291 | 10.03% | 12.07% | 12.07% | 80% | 9.66% | 11.5196 | 11.8753 | 6 | 69.1175 | 25.4745 | 55.68% | 55.68%
1 | 7 | 7 | 157 | 13 | -4.2 | 91.31 | 133.81 | 225.12 | 133.81 | 66.91 | 7 | 157 | 780 | 6.9041 | -22.2257 | -5.2013 | 754.284 | 12.4847 | -7.2707 | 20.6838 | 20.6838 | 7.1938 | 187.1938 | 25.0309 | 234.2346 | 234.2346 | 114.214 | 348.4486 | 0.31054 | 31.05% | 157.5684 | 48.9313 | 34.2519 | 104.989 | 104.989 | 32.62% | 11.95% | 11.95% | 85% | 10.16% | 16.0091 | 11.765 | 6 | 96.0543 | 35.4026 | 91.49% | 91.49%
1 | 7 | 7 | 158 | 14 | -4.1 | 83.42 | 100.28 | 183.7 | 100.28 | 50.14 | 7 | 158 | 840 | 6.9041 | -22.2257 | -5.2013 | 814.284 | 13.4847 | -22.2707 | 18.1206 | 18.1206 | 21.6621 | 201.6621 | 32.3817 | 226.5081 | 226.5081 | 85.5943 | 312.1024 | 0.25388 | 25.39% | 141.1327 | 35.8311 | 25.0818 | 123.1522 | 123.1522 | 20.37% | 12% | 12% | 85% | 10.2% | 14.394 | 11.7284 | 6 | 86.3639 | 31.831 | 70.13% | 70.13%
1 | 7 | 7 | 159 | 15 | -3.5 | 63.81 | 98.06 | 161.87 | 98.06 | 49.03 | 7 | 159 | 900 | 6.9041 | -22.2257 | -5.2013 | 874.284 | 14.4847 | -37.2707 | 13.2291 | 13.2291 | 35.1605 | 215.1605 | 43.5672 | 202.0338 | 202.0338 | 83.6994 | 285.7333 | 0.20841 | 20.84% | 129.2086 | 26.9278 | 18.8495 | 100.2108 | 100.2108 | 18.81% | 12.02% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 160 | 16 | -3.9 | 30.64 | 73.97 | 104.61 | 73.97 | 36.99 | 7 | 160 | 960 | 6.9041 | -22.2257 | -5.2013 | 934.284 | 15.4847 | -52.2707 | 6.4476 | 6.4476 | 47.4601 | 227.4601 | 56.3267 | 0 | 0 | 63.1373 | 63.1373 | -1.9074 | 0% | 28.5507 | 0 | 0 | 137.6477 | 137.6477 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 161 | 17 | -4.4 | 5.08 | 34.92 | 40 | 34.92 | 17.46 | 7 | 161 | 1020 | 6.9041 | -22.2257 | -5.2013 | 994.284 | 16.4847 | -67.2707 | -1.7589 | 0 | 56.4725 | 236.4725 | 67.0105 | 0 | 0 | 29.8061 | 29.8061 | -4.9818 | 0% | 13.4783 | 0 | 0 | 131.6878 | 131.6878 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 162 | 18 | -4.6 | 0 | 2.22 | 2.22 | 2.22 | 1.11 | 7 | 162 | 1080 | 6.9041 | -22.2257 | -5.2013 | 1054.284 | 17.4847 | -82.2707 | -10.9747 | 0 | 56.4725 | 236.4725 | 67.0105 | 0 | 0 | 1.8949 | 1.8949 | -90.4714 | 0% | 0.85687 | 0 | 0 | 127.1061 | 127.1061 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 163 | 19 | -4.7 | 0 | 0 | 0 | 0 | 0 | 7 | 163 | 1140 | 6.9041 | -22.2257 | -5.2013 | 1114.284 | 18.4847 | -97.2707 | -20.8466 | 0 | 56.4725 | 236.4725 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.7779 | 124.7779 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 164 | 20 | -4.9 | 0 | 0 | 0 | 0 | 0 | 7 | 164 | 1200 | 6.9041 | -22.2257 | -5.2013 | 1174.284 | 19.4847 | -112.2707 | -31.057 | 0 | 56.4725 | 236.4725 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.4173 | 121.4173 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 165 | 21 | -5 | 0 | 0 | 0 | 0 | 0 | 7 | 165 | 1260 | 6.9041 | -22.2257 | -5.2013 | 1234.284 | 20.4847 | -127.2707 | -41.265 | 0 | 56.4725 | 236.4725 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4774 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 166 | 22 | -5 | 0 | 0 | 0 | 0 | 0 | 7 | 166 | 1320 | 6.9041 | -22.2257 | -5.2013 | 1294.284 | 21.4847 | -142.2707 | -50.9895 | 0 | 56.4725 | 236.4725 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.1693 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 167 | 23 | -4.9 | 0 | 0 | 0 | 0 | 0 | 7 | 167 | 1380 | 6.9041 | -22.2257 | -5.2013 | 1354.284 | 22.4847 | -157.2707 | -59.3559 | 0 | 56.4725 | 236.4725 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.7798 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 7 | 7 | 168 | 24 | -4.9 | 0 | 0 | 0 | 0 | 0 | 7 | 168 | 1440 | 6.9041 | -22.2257 | -5.2013 | 1414.284 | 23.4847 | -172.2707 | -64.6652 | 0 | 56.4725 | 236.4725 | 67.0105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5428 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 169 | 1 | -4.9 | 0 | 0 | 0 | 0 | 0 | 8 | 169 | 60 | 7.8904 | -22.1001 | -5.3735 | 34.284 | 0.48184 | 172.7724 | -64.6391 | 0 | 56.6759 | 123.3241 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.3663 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 170 | 2 | -4.8 | 0 | 0 | 0 | 0 | 0 | 8 | 170 | 120 | 7.8904 | -22.1001 | -5.3735 | 94.284 | 1.4818 | 157.7724 | -59.4874 | 0 | 56.6759 | 123.3241 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.1159 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 171 | 3 | -4.9 | 0 | 0 | 0 | 0 | 0 | 8 | 171 | 180 | 7.8904 | -22.1001 | -5.3735 | 154.284 | 2.4818 | 142.7724 | -51.2039 | 0 | 56.6759 | 123.3241 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.1704 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 172 | 4 | -4.9 | 0 | 0 | 0 | 0 | 0 | 8 | 172 | 240 | 7.8904 | -22.1001 | -5.3735 | 214.284 | 3.4818 | 127.7724 | -41.5147 | 0 | 56.6759 | 123.3241 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.1704 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 173 | 5 | -4.9 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 300 | 7.8904 | -22.1001 | -5.3735 | 274.284 | 4.4818 | 112.7724 | -31.3161 | 0 | 56.6759 | 123.3241 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8334 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 174 | 6 | -5.1 | 0 | 0 | 0 | 0 | 0 | 8 | 174 | 360 | 7.8904 | -22.1001 | -5.3735 | 334.284 | 5.4818 | 97.7724 | -21.0982 | 0 | 56.6759 | 123.3241 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4852 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 175 | 7 | -5 | 0 | 0 | 0 | 0 | 0 | 8 | 175 | 420 | 7.8904 | -22.1001 | -5.3735 | 394.284 | 6.4818 | 82.7724 | -11.2055 | 0 | 56.6759 | 123.3241 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.5047 | 128.5047 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 176 | 8 | -5 | 0 | 0 | 0 | 0 | 0 | 8 | 176 | 480 | 7.8904 | -22.1001 | -5.3735 | 454.284 | 7.4818 | 67.7724 | -1.9559 | 0 | 56.6759 | 123.3241 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.8753 | 130.8753 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 177 | 9 | -4.9 | 0 | 1.39 | 1.39 | 1.39 | 0.7 | 8 | 177 | 540 | 7.8904 | -22.1001 | -5.3735 | 514.284 | 8.4818 | 52.7724 | 6.2986 | 6.2986 | 47.9206 | 132.0794 | 56.7296 | 0 | 0 | 1.1864 | 1.1864 | -145.6143 | 0% | 0.53651 | 0 | 0 | 110.6137 | 110.6137 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 178 | 10 | -4 | 3.75 | 32.5 | 36.25 | 32.5 | 16.25 | 8 | 178 | 600 | 7.8904 | -22.1001 | -5.3735 | 574.284 | 9.4818 | 37.7724 | 13.1436 | 13.1436 | 35.647 | 144.353 | 43.9167 | 11.8795 | 11.8795 | 27.7405 | 39.62 | -3.5231 | 0% | 17.9162 | 0 | 0 | 114.1226 | 114.1226 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 179 | 11 | -3.7 | 7.64 | 69.72 | 77.36 | 69.72 | 34.86 | 8 | 179 | 660 | 7.8904 | -22.1001 | -5.3735 | 634.284 | 10.4818 | 22.7724 | 18.113 | 18.113 | 22.1684 | 157.8316 | 32.6247 | 20.697 | 20.697 | 59.5097 | 80.2068 | -1.3241 | 0% | 36.2695 | 0 | 0 | 115.2364 | 115.2364 | 0% | 12.29% | 12.29% | 80% | 9.832% | 3.5661 | 11.5826 | 6 | 21.3965 | 7.8861 | 18.57% | 18.57%
1 | 8 | 8 | 180 | 12 | -3 | 16.58 | 75.19 | 91.77 | 75.19 | 37.6 | 8 | 180 | 720 | 7.8904 | -22.1001 | -5.3735 | 694.284 | 11.4818 | 7.7724 | 20.7643 | 20.7643 | 7.7011 | 172.2989 | 25.0551 | 42.3662 | 42.3662 | 64.1787 | 106.5449 | -0.78148 | 0% | 48.1796 | 0 | 0 | 114.7918 | 114.7918 | 0% | 12.23% | 12.23% | 80% | 9.783% | 4.7136 | 11.3301 | 6 | 28.2815 | 10.4237 | 24.64% | 24.64%
1 | 8 | 8 | 181 | 13 | -2.8 | 48.97 | 139.25 | 188.22 | 139.25 | 69.63 | 8 | 181 | 780 | 7.8904 | -22.1001 | -5.3735 | 754.284 | 12.4818 | -7.2276 | 20.8125 | 20.8125 | 7.1637 | 187.1637 | 24.8992 | 125.0122 | 125.0122 | 118.8573 | 243.8695 | 0.11337 | 11.34% | 110.2778 | 12.5023 | 8.7516 | 119.374 | 119.374 | 7.331% | 12.05% | 12.05% | 80% | 9.64% | 10.6302 | 11.2586 | 6 | 63.7814 | 23.5078 | 53.43% | 53.43%
1 | 8 | 8 | 182 | 14 | -2.6 | 36.19 | 145.28 | 181.47 | 145.28 | 72.64 | 8 | 182 | 840 | 7.8904 | -22.1001 | -5.3735 | 814.284 | 13.4818 | -22.2276 | 18.2523 | 18.2523 | 21.6578 | 201.6578 | 32.2648 | 97.7068 | 97.7068 | 124.0042 | 221.711 | 0.046608 | 4.661% | 100.2577 | 4.6728 | 3.2709 | 119.1313 | 119.1313 | 2.746% | 12.07% | 12.07% | 80% | 9.657% | 9.6815 | 11.1874 | 6 | 58.0892 | 21.4099 | 48.76% | 48.76%
1 | 8 | 8 | 183 | 15 | -2.4 | 16.03 | 101.11 | 117.14 | 101.11 | 50.56 | 8 | 183 | 900 | 7.8904 | -22.1001 | -5.3735 | 874.284 | 14.4818 | -37.2276 | 13.3597 | 13.3597 | 35.1784 | 215.1784 | 43.4722 | 50.3458 | 50.3458 | 86.3028 | 136.6486 | -0.4212 | 0% | 61.7925 | 0 | 0 | 136.379 | 136.379 | 0% | 12.17% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 184 | 16 | -2.8 | 35.64 | 82.42 | 118.06 | 82.42 | 41.21 | 8 | 184 | 960 | 7.8904 | -22.1001 | -5.3735 | 934.284 | 15.4818 | -52.2276 | 6.5746 | 6.5746 | 47.4954 | 227.4954 | 56.2496 | 0 | 0 | 70.3499 | 70.3499 | -1.5901 | 0% | 31.8122 | 0 | 0 | 135.6593 | 135.6593 | 0% | 12.27% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 185 | 17 | -2.9 | 8.06 | 32.97 | 41.03 | 32.97 | 16.49 | 8 | 185 | 1020 | 7.8904 | -22.1001 | -5.3735 | 994.284 | 16.4818 | -67.2276 | -1.6364 | 0 | 56.6759 | 236.6759 | 67.1409 | 0 | 0 | 28.1417 | 28.1417 | -5.1897 | 0% | 12.7257 | 0 | 0 | 130.5505 | 130.5505 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 186 | 18 | -1.9 | 0 | 1.86 | 1.86 | 1.86 | 0.93 | 8 | 186 | 1080 | 7.8904 | -22.1001 | -5.3735 | 1054.284 | 17.4818 | -82.2276 | -10.8564 | 0 | 56.6759 | 236.6759 | 67.1409 | 0 | 0 | 1.5876 | 1.5876 | -103.8646 | 0% | 0.71792 | 0 | 0 | 128.2809 | 128.2809 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 187 | 19 | -1.1 | 0 | 0 | 0 | 0 | 0 | 8 | 187 | 1140 | 7.8904 | -22.1001 | -5.3735 | 1114.284 | 18.4818 | -97.2276 | -20.7314 | 0 | 56.6759 | 236.6759 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.6312 | 127.6312 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 188 | 20 | -1 | 0 | 0 | 0 | 0 | 0 | 8 | 188 | 1200 | 7.8904 | -22.1001 | -5.3735 | 1174.284 | 19.4818 | -112.2276 | -30.943 | 0 | 56.6759 | 236.6759 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.4145 | 125.4145 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 189 | 21 | -0.9 | 0 | 0 | 0 | 0 | 0 | 8 | 189 | 1260 | 7.8904 | -22.1001 | -5.3735 | 1234.284 | 20.4818 | -127.2276 | -41.1496 | 0 | 56.6759 | 236.6759 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0266 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 190 | 22 | -0.7 | 0 | 0 | 0 | 0 | 0 | 8 | 190 | 1320 | 7.8904 | -22.1001 | -5.3735 | 1294.284 | 21.4818 | -142.2276 | -50.8693 | 0 | 56.6759 | 236.6759 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2593 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 191 | 23 | -0.8 | 0 | 0 | 0 | 0 | 0 | 8 | 191 | 1380 | 7.8904 | -22.1001 | -5.3735 | 1354.284 | 22.4818 | -157.2276 | -59.2279 | 0 | 56.6759 | 236.6759 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3137 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
1 | 8 | 8 | 192 | 24 | -0.7 | 0 | 0 | 0 | 0 | 0 | 8 | 192 | 1440 | 7.8904 | -22.1001 | -5.3735 | 1414.284 | 23.4818 | -172.2276 | -64.534 | 0 | 56.6759 | 236.6759 | 67.1409 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0634 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 193 | 1 | -0.7 | 0 | 0 | 0 | 0 | 0 | 9 | 193 | 60 | 8.8767 | -21.9678 | -5.5385 | 34.284 | 0.47909 | 172.8136 | -64.5171 | 0 | 56.89 | 123.11 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9699 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 194 | 2 | -1 | 0 | 0 | 0 | 0 | 0 | 9 | 194 | 120 | 8.8767 | -21.9678 | -5.5385 | 94.284 | 1.4791 | 157.8136 | -59.393 | 0 | 56.89 | 123.11 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0225 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 195 | 3 | -1.1 | 0 | 0 | 0 | 0 | 0 | 9 | 195 | 180 | 8.8767 | -21.9678 | -5.5385 | 154.284 | 2.4791 | 142.8136 | -51.1298 | 0 | 56.89 | 123.11 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7704 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 196 | 4 | -0.9 | 0 | 0 | 0 | 0 | 0 | 9 | 196 | 240 | 8.8767 | -21.9678 | -5.5385 | 214.284 | 3.4791 | 127.8136 | -41.4509 | 0 | 56.89 | 123.11 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4656 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 197 | 5 | -1 | 0 | 0 | 0 | 0 | 0 | 9 | 197 | 300 | 8.8767 | -21.9678 | -5.5385 | 274.284 | 4.4791 | 112.8136 | -31.2552 | 0 | 56.89 | 123.11 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9206 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 198 | 6 | -1 | 0 | 0 | 0 | 0 | 0 | 9 | 198 | 360 | 8.8767 | -21.9678 | -5.5385 | 334.284 | 5.4791 | 97.8136 | -21.0352 | 0 | 56.89 | 123.11 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.1809 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 199 | 7 | -1.2 | 0 | 0 | 0 | 0 | 0 | 9 | 199 | 420 | 8.8767 | -21.9678 | -5.5385 | 394.284 | 6.4791 | 82.8136 | -11.1366 | 0 | 56.89 | 123.11 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 157.5804 | 157.5804 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 200 | 8 | -1.4 | 0 | 0 | 0 | 0 | 0 | 9 | 200 | 480 | 8.8767 | -21.9678 | -5.5385 | 454.284 | 7.4791 | 67.8136 | -1.8779 | 0 | 56.89 | 123.11 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 164.3189 | 164.3189 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 201 | 9 | -1.4 | 0 | 2.22 | 2.22 | 2.22 | 1.11 | 9 | 201 | 540 | 8.8767 | -21.9678 | -5.5385 | 514.284 | 8.4791 | 52.8136 | 6.3882 | 6.3882 | 48.0259 | 131.9741 | 56.7256 | 0 | 0 | 1.8949 | 1.8949 | -86.234 | 0% | 0.85687 | 0 | 0 | 144.9407 | 144.9407 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 202 | 10 | -1.2 | 15.64 | 35.75 | 51.39 | 35.75 | 17.88 | 9 | 202 | 600 | 8.8767 | -21.9678 | -5.5385 | 574.284 | 9.4791 | 37.8136 | 13.2464 | 13.2464 | 35.741 | 144.259 | 43.8885 | 49.1909 | 49.1909 | 30.5145 | 79.7054 | -1.259 | 0% | 36.0428 | 0 | 0 | 149.0219 | 149.0219 | 0% | 12.19% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 203 | 11 | -0.5 | 105.83 | 82.08 | 187.91 | 82.08 | 41.04 | 9 | 203 | 660 | 8.8767 | -21.9678 | -5.5385 | 634.284 | 10.4791 | 22.8136 | 18.2294 | 18.2294 | 22.246 | 157.754 | 32.5602 | 285.1341 | 285.1341 | 70.0597 | 355.1938 | 0.34596 | 34.6% | 160.6186 | 55.5673 | 38.8971 | 152.7887 | 152.7887 | 25.46% | 11.85% | 11.85% | 85% | 10.08% | 16.1831 | 10.4565 | 6 | 97.0987 | 35.7875 | 63.55% | 63.55%
1 | 9 | 9 | 204 | 12 | -0.2 | 173.06 | 120.69 | 293.75 | 120.69 | 60.35 | 9 | 204 | 720 | 8.8767 | -21.9678 | -5.5385 | 694.284 | 11.4791 | 7.8136 | 20.8921 | 20.8921 | 7.7559 | 172.2441 | 24.9421 | 440.0318 | 440.0318 | 103.0154 | 543.0472 | 0.50577 | 50.58% | 245.5659 | 124.2005 | 86.9404 | 128.6602 | 128.6602 | 67.57% | 11.64% | 11.64% | 90% | 10.47% | 25.7199 | 10.3546 | 6 | 154.3194 | 56.8773 | 119.9% | 119.9%
1 | 9 | 9 | 205 | 13 | 0.4 | 229.31 | 138.61 | 367.92 | 138.61 | 69.31 | 9 | 205 | 780 | 8.8767 | -21.9678 | -5.5385 | 754.284 | 12.4791 | -7.1864 | 20.9478 | 20.9478 | 7.136 | 187.136 | 24.7615 | 582.4257 | 582.4257 | 118.311 | 700.7367 | 0.575 | 57.5% | 316.8732 | 182.201 | 127.5407 | 130.253 | 130.253 | 97.92% | 11.46% | 11.46% | 90% | 10.31% | 32.6795 | 10.1527 | 6 | 196.0768 | 72.2677 | 150.5% | 150.5%
1 | 9 | 9 | 206 | 14 | 0.2 | 245.75 | 107.14 | 352.89 | 107.14 | 53.57 | 9 | 206 | 840 | 8.8767 | -21.9678 | -5.5385 | 814.284 | 13.4791 | -22.1864 | 18.39 | 18.39 | 21.657 | 201.657 | 32.1444 | 659.5566 | 659.5566 | 91.4497 | 751.0063 | 0.58967 | 58.97% | 339.6051 | 200.2546 | 140.1782 | 127.1837 | 127.1837 | 110.2% | 11.41% | 11.41% | 90% | 10.26% | 34.8598 | 10.2197 | 6 | 209.1591 | 77.0894 | 164.5% | 164.5%
1 | 9 | 9 | 207 | 15 | 0.3 | 159.36 | 106.47 | 265.83 | 106.47 | 53.24 | 9 | 207 | 900 | 8.8767 | -21.9678 | -5.5385 | 874.284 | 14.4791 | -37.1864 | 13.4957 | 13.4957 | 35.2008 | 215.2008 | 43.3755 | 496.3467 | 496.3467 | 90.8778 | 587.2245 | 0.53031 | 53.03% | 265.5429 | 140.8201 | 98.5741 | 119.7585 | 119.7585 | 82.31% | 11.58% | 0% | 90% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 208 | 16 | 0.2 | 88.25 | 87.31 | 175.56 | 87.31 | 43.66 | 9 | 208 | 960 | 8.8767 | -21.9678 | -5.5385 | 934.284 | 15.4791 | -52.1864 | 6.7064 | 6.7064 | 47.5356 | 227.5356 | 56.1721 | 0 | 0 | 74.5237 | 74.5237 | -1.3559 | 0% | 33.6996 | 0 | 0 | 113.324 | 113.324 | 0% | 12.14% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 209 | 17 | -0.3 | 22.03 | 45.47 | 67.5 | 45.47 | 22.74 | 9 | 209 | 1020 | 8.8767 | -21.9678 | -5.5385 | 994.284 | 16.4791 | -67.1864 | -1.5097 | 0 | 56.89 | 236.89 | 67.2783 | 0 | 0 | 38.8111 | 38.8111 | -3.3752 | 0% | 17.5504 | 0 | 0 | 145.2578 | 145.2578 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 210 | 18 | -0.4 | 0 | 2.97 | 2.97 | 2.97 | 1.49 | 9 | 210 | 1080 | 8.8767 | -21.9678 | -5.5385 | 1054.284 | 17.4791 | -82.1864 | -10.7343 | 0 | 56.89 | 236.89 | 67.2783 | 0 | 0 | 2.5351 | 2.5351 | -63.276 | 0% | 1.1464 | 0 | 0 | 136.4529 | 136.4529 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 211 | 19 | -0.6 | 0 | 0 | 0 | 0 | 0 | 9 | 211 | 1140 | 8.8767 | -21.9678 | -5.5385 | 1114.284 | 18.4791 | -97.1864 | -20.6127 | 0 | 56.89 | 236.89 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.0965 | 132.0965 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 212 | 20 | -0.9 | 0 | 0 | 0 | 0 | 0 | 9 | 212 | 1200 | 8.8767 | -21.9678 | -5.5385 | 1174.284 | 19.4791 | -112.1864 | -30.8256 | 0 | 56.89 | 236.89 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.1512 | 126.1512 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 213 | 21 | -1.1 | 0 | 0 | 0 | 0 | 0 | 9 | 213 | 1260 | 8.8767 | -21.9678 | -5.5385 | 1234.284 | 20.4791 | -127.1864 | -41.0306 | 0 | 56.89 | 236.89 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5178 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 214 | 22 | -1.1 | 0 | 0 | 0 | 0 | 0 | 9 | 214 | 1320 | 8.8767 | -21.9678 | -5.5385 | 1294.284 | 21.4791 | -142.1864 | -50.745 | 0 | 56.89 | 236.89 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.7931 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 215 | 23 | -1.4 | 0 | 0 | 0 | 0 | 0 | 9 | 215 | 1380 | 8.8767 | -21.9678 | -5.5385 | 1354.284 | 22.4791 | -157.1864 | -59.0949 | 0 | 56.89 | 236.89 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8458 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
1 | 9 | 9 | 216 | 24 | -1.2 | 0 | 0 | 0 | 0 | 0 | 9 | 216 | 1440 | 8.8767 | -21.9678 | -5.5385 | 1414.284 | 23.4791 | -172.1864 | -64.3965 | 0 | 56.89 | 236.89 | 67.2783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1364 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 217 | 1 | -1.5 | 0 | 0 | 0 | 0 | 0 | 10 | 217 | 60 | 9.863 | -21.8289 | -5.6961 | 34.284 | 0.47647 | 172.853 | -64.3881 | 0 | 57.1145 | 122.8855 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8561 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 218 | 2 | -1.4 | 0 | 0 | 0 | 0 | 0 | 10 | 218 | 120 | 9.863 | -21.8289 | -5.6961 | 94.284 | 1.4765 | 157.853 | -59.2917 | 0 | 57.1145 | 122.8855 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5139 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 219 | 3 | -1.2 | 0 | 0 | 0 | 0 | 0 | 10 | 219 | 180 | 9.863 | -21.8289 | -5.6961 | 154.284 | 2.4765 | 142.853 | -51.0493 | 0 | 57.1145 | 122.8855 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0193 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 220 | 4 | -1.5 | 0 | 0 | 0 | 0 | 0 | 10 | 220 | 240 | 9.863 | -21.8289 | -5.6961 | 214.284 | 3.4765 | 127.853 | -41.381 | 0 | 57.1145 | 122.8855 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4765 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 221 | 5 | -1.6 | 0 | 0 | 0 | 0 | 0 | 10 | 221 | 300 | 9.863 | -21.8289 | -5.6961 | 274.284 | 4.4765 | 112.853 | -31.1884 | 0 | 57.1145 | 122.8855 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.135 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 222 | 6 | -1.8 | 0 | 0 | 0 | 0 | 0 | 10 | 222 | 360 | 9.863 | -21.8289 | -5.6961 | 334.284 | 5.4765 | 97.853 | -20.9663 | 0 | 57.1145 | 122.8855 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1546 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 223 | 7 | -1.9 | 0 | 0 | 0 | 0 | 0 | 10 | 223 | 420 | 9.863 | -21.8289 | -5.6961 | 394.284 | 6.4765 | 82.853 | -11.0616 | 0 | 57.1145 | 122.8855 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.3691 | 136.3691 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 224 | 8 | -1.8 | 0 | 0 | 0 | 0 | 0 | 10 | 224 | 480 | 9.863 | -21.8289 | -5.6961 | 454.284 | 7.4765 | 67.853 | -1.7937 | 0 | 57.1145 | 122.8855 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.2451 | 139.2451 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 225 | 9 | -1.6 | 0.42 | 2.5 | 2.92 | 2.5 | 1.25 | 10 | 225 | 540 | 9.863 | -21.8289 | -5.6961 | 514.284 | 8.4765 | 52.853 | 6.4843 | 6.4843 | 48.1334 | 131.8666 | 56.7182 | 0 | 0 | 2.1339 | 2.1339 | -76.719 | 0% | 0.96494 | 0 | 0 | 119.0814 | 119.0814 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 226 | 10 | -1.3 | 2.58 | 27.22 | 29.8 | 27.22 | 13.61 | 10 | 226 | 600 | 9.863 | -21.8289 | -5.6961 | 574.284 | 9.4765 | 37.853 | 13.356 | 13.356 | 35.8365 | 144.1635 | 43.856 | 8.0536 | 8.0536 | 23.2337 | 31.2873 | -4.4594 | 0% | 14.1481 | 0 | 0 | 120.4778 | 120.4778 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 227 | 11 | -1.1 | 35.64 | 54.72 | 90.36 | 54.72 | 27.36 | 10 | 227 | 660 | 9.863 | -21.8289 | -5.6961 | 634.284 | 10.4765 | 22.853 | 18.3526 | 18.3526 | 22.3239 | 157.6761 | 32.4903 | 95.4753 | 95.4753 | 46.7064 | 142.1818 | -0.35073 | 0% | 64.2946 | 0 | 0 | 121.7384 | 121.7384 | 0% | 12.12% | 12.12% | 80% | 9.692% | 6.2316 | 10.6622 | 6 | 37.3898 | 13.7807 | 30.71% | 30.71%
1 | 10 | 10 | 228 | 12 | -1 | 17.69 | 91.86 | 109.55 | 91.86 | 45.93 | 10 | 228 | 720 | 9.863 | -21.8289 | -5.6961 | 694.284 | 11.4765 | 7.853 | 21.0267 | 21.0267 | 7.8097 | 172.1903 | 24.8224 | 44.7478 | 44.7478 | 78.4074 | 123.1553 | -0.52711 | 0% | 55.6908 | 0 | 0 | 118.8366 | 118.8366 | 0% | 12.13% | 12.13% | 80% | 9.707% | 5.4059 | 10.6277 | 6 | 32.4355 | 11.9547 | 27.29% | 27.29%
1 | 10 | 10 | 229 | 13 | -0.8 | 2.31 | 93.14 | 95.45 | 93.14 | 46.57 | 10 | 229 | 780 | 9.863 | -21.8289 | -5.6961 | 754.284 | 12.4765 | -7.147 | 21.0895 | 21.0895 | 7.1106 | 187.1106 | 24.618 | 5.8362 | 5.8362 | 79.5 | 85.3362 | -1.1112 | 0% | 38.589 | 0 | 0 | 117.4447 | 117.4447 | 0% | 12.17% | 12.17% | 80% | 9.736% | 3.7569 | 10.559 | 6 | 22.5414 | 8.308 | 19.19% | 19.19%
1 | 10 | 10 | 230 | 14 | -0.5 | 2.31 | 109.81 | 112.12 | 109.81 | 54.91 | 10 | 230 | 840 | 9.863 | -21.8289 | -5.6961 | 814.284 | 13.4765 | -22.147 | 18.5336 | 18.5336 | 21.6599 | 201.6599 | 32.0206 | 6.1616 | 6.1616 | 93.7287 | 99.8903 | -0.82472 | 0% | 45.1704 | 0 | 0 | 117.7807 | 117.7807 | 0% | 12.14% | 12.14% | 80% | 9.713% | 4.3874 | 10.4565 | 6 | 26.3247 | 9.7024 | 22.35% | 22.35%
1 | 10 | 10 | 231 | 15 | -0.7 | 1.11 | 101.86 | 102.97 | 101.86 | 50.93 | 10 | 231 | 900 | 9.863 | -21.8289 | -5.6961 | 874.284 | 14.4765 | -37.147 | 13.637 | 13.637 | 35.2276 | 215.2276 | 43.2774 | 3.4276 | 3.4276 | 86.9429 | 90.3706 | -1.0018 | 0% | 40.8656 | 0 | 0 | 136.4194 | 136.4194 | 0% | 12.16% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 232 | 16 | -0.9 | 0.56 | 63.97 | 64.53 | 63.97 | 31.99 | 10 | 232 | 960 | 9.863 | -21.8289 | -5.6961 | 934.284 | 15.4765 | -52.147 | 6.8428 | 6.8428 | 47.581 | 227.581 | 56.0943 | 0 | 0 | 54.6018 | 54.6018 | -2.1938 | 0% | 24.6909 | 0 | 0 | 133.2085 | 133.2085 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 233 | 17 | -1.1 | 1.11 | 29.72 | 30.83 | 29.72 | 14.86 | 10 | 233 | 1020 | 9.863 | -21.8289 | -5.6961 | 994.284 | 16.4765 | -67.147 | -1.3789 | 0 | 57.1145 | 237.1145 | 67.4225 | 0 | 0 | 25.3676 | 25.3676 | -5.6681 | 0% | 11.4712 | 0 | 0 | 130.1428 | 130.1428 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 234 | 18 | -1.4 | 0 | 2.42 | 2.42 | 2.42 | 1.21 | 10 | 234 | 1080 | 9.863 | -21.8289 | -5.6961 | 1054.284 | 17.4765 | -82.147 | -10.6086 | 0 | 57.1145 | 237.1145 | 67.4225 | 0 | 0 | 2.0656 | 2.0656 | -79.0407 | 0% | 0.93406 | 0 | 0 | 126.9221 | 126.9221 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 235 | 19 | -1.5 | 0 | 0 | 0 | 0 | 0 | 10 | 235 | 1140 | 9.863 | -21.8289 | -5.6961 | 1114.284 | 18.4765 | -97.147 | -20.4905 | 0 | 57.1145 | 237.1145 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.4512 | 125.4512 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 236 | 20 | -1.6 | 0 | 0 | 0 | 0 | 0 | 10 | 236 | 1200 | 9.863 | -21.8289 | -5.6961 | 1174.284 | 19.4765 | -112.147 | -30.7049 | 0 | 57.1145 | 237.1145 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.3249 | 123.3249 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 237 | 21 | -1.7 | 0 | 0 | 0 | 0 | 0 | 10 | 237 | 1260 | 9.863 | -21.8289 | -5.6961 | 1234.284 | 20.4765 | -127.147 | -40.9081 | 0 | 57.1145 | 237.1145 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.292 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 238 | 22 | -1.6 | 0 | 0 | 0 | 0 | 0 | 10 | 238 | 1320 | 9.863 | -21.8289 | -5.6961 | 1294.284 | 21.4765 | -142.147 | -50.6167 | 0 | 57.1145 | 237.1145 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5779 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 239 | 23 | -1.8 | 0 | 0 | 0 | 0 | 0 | 10 | 239 | 1380 | 9.863 | -21.8289 | -5.6961 | 1354.284 | 22.4765 | -157.147 | -58.957 | 0 | 57.1145 | 237.1145 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6929 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 10 | 10 | 240 | 24 | -1.9 | 0 | 0 | 0 | 0 | 0 | 10 | 240 | 1440 | 9.863 | -21.8289 | -5.6961 | 1414.284 | 23.4765 | -172.147 | -64.253 | 0 | 57.1145 | 237.1145 | 67.4225 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6555 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 241 | 1 | -1.9 | 0 | 0 | 0 | 0 | 0 | 11 | 241 | 60 | 10.8493 | -21.6833 | -5.8458 | 34.284 | 0.47397 | 172.8905 | -64.2522 | 0 | 57.3492 | 122.6508 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.7454 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 242 | 2 | -2.1 | 0 | 0 | 0 | 0 | 0 | 11 | 242 | 120 | 10.8493 | -21.6833 | -5.8458 | 94.284 | 1.474 | 157.8905 | -59.1836 | 0 | 57.3492 | 122.6508 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9228 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 243 | 3 | -2.2 | 0 | 0 | 0 | 0 | 0 | 11 | 243 | 180 | 10.8493 | -21.6833 | -5.8458 | 154.284 | 2.474 | 142.8905 | -50.9624 | 0 | 57.3492 | 122.6508 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9479 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 244 | 4 | -2.2 | 0 | 0 | 0 | 0 | 0 | 11 | 244 | 240 | 10.8493 | -21.6833 | -5.8458 | 214.284 | 3.474 | 127.8905 | -41.305 | 0 | 57.3492 | 122.6508 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9479 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 245 | 5 | -2.3 | 0 | 0 | 0 | 0 | 0 | 11 | 245 | 300 | 10.8493 | -21.6833 | -5.8458 | 274.284 | 4.474 | 112.8905 | -31.1157 | 0 | 57.3492 | 122.6508 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8778 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 246 | 6 | -2.5 | 0 | 0 | 0 | 0 | 0 | 11 | 246 | 360 | 10.8493 | -21.6833 | -5.8458 | 334.284 | 5.474 | 97.8905 | -20.8915 | 0 | 57.3492 | 122.6508 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1814 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 247 | 7 | -2.6 | 0 | 0 | 0 | 0 | 0 | 11 | 247 | 420 | 10.8493 | -21.6833 | -5.8458 | 394.284 | 6.474 | 82.8905 | -10.9807 | 0 | 57.3492 | 122.6508 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.1319 | 138.1319 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 248 | 8 | -2.6 | 0 | 0 | 0 | 0 | 0 | 11 | 248 | 480 | 10.8493 | -21.6833 | -5.8458 | 454.284 | 7.474 | 67.8905 | -1.7033 | 0 | 57.3492 | 122.6508 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.8841 | 141.8841 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 249 | 9 | -2.8 | 0 | 3.89 | 3.89 | 3.89 | 1.95 | 11 | 249 | 540 | 10.8493 | -21.6833 | -5.8458 | 514.284 | 8.474 | 52.8905 | 6.5868 | 6.5868 | 48.2432 | 131.7568 | 56.7074 | 0 | 0 | 3.3203 | 3.3203 | -49.921 | 0% | 1.5014 | 0 | 0 | 121.6925 | 121.6925 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 250 | 10 | -2.5 | 11.39 | 35.19 | 46.58 | 35.19 | 17.6 | 11 | 250 | 600 | 10.8493 | -21.6833 | -5.8458 | 574.284 | 9.474 | 37.8905 | 13.4723 | 13.4723 | 35.9334 | 144.0666 | 43.8193 | 35.2751 | 35.2751 | 30.0365 | 65.3116 | -1.7633 | 0% | 29.5339 | 0 | 0 | 125.6788 | 125.6788 | 0% | 12.26% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 251 | 11 | -2 | 35.47 | 68.53 | 104 | 68.53 | 34.27 | 11 | 251 | 660 | 10.8493 | -21.6833 | -5.8458 | 634.284 | 10.474 | 22.8905 | 18.4826 | 18.4826 | 22.4021 | 157.5979 | 32.4151 | 94.4537 | 94.4537 | 58.494 | 152.9477 | -0.2841 | 0% | 69.1629 | 0 | 0 | 127.4238 | 127.4238 | 0% | 12.13% | 12.13% | 80% | 9.708% | 6.7143 | 10.9754 | 6 | 40.2858 | 14.8481 | 31.62% | 31.62%
1 | 11 | 11 | 252 | 12 | -1.7 | 63.69 | 94.64 | 158.33 | 94.64 | 47.32 | 11 | 252 | 720 | 10.8493 | -21.6833 | -5.8458 | 694.284 | 11.474 | 7.8905 | 21.1681 | 21.1681 | 7.8625 | 172.1375 | 24.6962 | 160.2433 | 160.2433 | 80.7803 | 241.0236 | 0.11662 | 11.66% | 108.9909 | 12.7108 | 8.8976 | 126.9584 | 126.9584 | 7.008% | 12.02% | 12.02% | 80% | 9.615% | 10.4798 | 10.8704 | 6 | 62.8789 | 23.1752 | 49.53% | 49.53%
1 | 11 | 11 | 253 | 13 | -2 | 124.17 | 117.58 | 241.75 | 117.58 | 58.79 | 11 | 253 | 780 | 10.8493 | -21.6833 | -5.8458 | 754.284 | 12.474 | -7.1095 | 21.2376 | 21.2376 | 7.0877 | 187.0877 | 24.4686 | 312.0003 | 312.0003 | 100.3608 | 412.3611 | 0.40042 | 40.04% | 186.4697 | 74.6655 | 52.2658 | 109.1935 | 109.1935 | 47.87% | 11.82% | 11.82% | 85% | 10.05% | 18.7363 | 10.9754 | 6 | 112.4176 | 41.4336 | 103% | 103%
1 | 11 | 11 | 254 | 14 | -1.8 | 118.25 | 131.03 | 249.28 | 131.03 | 65.52 | 11 | 254 | 840 | 10.8493 | -21.6833 | -5.8458 | 814.284 | 13.474 | -22.1095 | 18.6832 | 18.6832 | 21.6664 | 201.6664 | 31.8935 | 313.4155 | 313.4155 | 111.8411 | 425.2566 | 0.41383 | 41.38% | 192.301 | 79.5795 | 55.7056 | 109.7325 | 109.7325 | 50.76% | 11.8% | 11.8% | 85% | 10.03% | 19.2899 | 10.9053 | 6 | 115.7397 | 42.658 | 105.5% | 105.5%
1 | 11 | 11 | 255 | 15 | -2 | 83.69 | 112.31 | 196 | 112.31 | 56.16 | 11 | 255 | 900 | 10.8493 | -21.6833 | -5.8458 | 874.284 | 14.474 | -37.1095 | 13.7835 | 13.7835 | 35.2589 | 215.2589 | 43.1778 | 256.1526 | 256.1526 | 95.8626 | 352.0152 | 0.33123 | 33.12% | 159.1813 | 52.7256 | 36.9079 | 105.7268 | 105.7268 | 34.91% | 11.89% | 0% | 85% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 256 | 16 | -2.1 | 58.42 | 61.58 | 120 | 61.58 | 30.79 | 11 | 256 | 960 | 10.8493 | -21.6833 | -5.8458 | 934.284 | 15.474 | -52.1095 | 6.9838 | 6.9838 | 47.6315 | 227.6315 | 56.0162 | 0 | 0 | 52.5618 | 52.5618 | -2.367 | 0% | 23.7685 | 0 | 0 | 143.5691 | 143.5691 | 0% | 12.26% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 257 | 17 | -2.5 | 46.53 | 31.11 | 77.64 | 31.11 | 15.56 | 11 | 257 | 1020 | 10.8493 | -21.6833 | -5.8458 | 994.284 | 16.474 | -67.1095 | -1.244 | 0 | 57.3492 | 237.3492 | 67.5736 | 0 | 0 | 26.554 | 26.554 | -5.5104 | 0% | 12.0077 | 0 | 0 | 140.3287 | 140.3287 | 0% | 12.31% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 258 | 18 | -2.7 | 0 | 3.61 | 3.61 | 3.61 | 1.81 | 11 | 258 | 1080 | 10.8493 | -21.6833 | -5.8458 | 1054.284 | 17.474 | -82.1095 | -10.4792 | 0 | 57.3492 | 237.3492 | 67.5736 | 0 | 0 | 3.0813 | 3.0813 | -53.774 | 0% | 1.3934 | 0 | 0 | 131.1873 | 131.1873 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 259 | 19 | -3 | 0 | 0 | 0 | 0 | 0 | 11 | 259 | 1140 | 10.8493 | -21.6833 | -5.8458 | 1114.284 | 18.474 | -97.1095 | -20.3651 | 0 | 57.3492 | 237.3492 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.2599 | 127.2599 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 260 | 20 | -3.3 | 0 | 0 | 0 | 0 | 0 | 11 | 260 | 1200 | 10.8493 | -21.6833 | -5.8458 | 1174.284 | 19.474 | -112.1095 | -30.5809 | 0 | 57.3492 | 237.3492 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 122.7283 | 122.7283 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 261 | 21 | -3.5 | 0 | 0 | 0 | 0 | 0 | 11 | 261 | 1260 | 10.8493 | -21.6833 | -5.8458 | 1234.284 | 20.474 | -127.1095 | -40.7823 | 0 | 57.3492 | 237.3492 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6235 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 262 | 22 | -3.5 | 0 | 0 | 0 | 0 | 0 | 11 | 262 | 1320 | 10.8493 | -21.6833 | -5.8458 | 1294.284 | 21.474 | -142.1095 | -50.4845 | 0 | 57.3492 | 237.3492 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5659 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 263 | 23 | -3.7 | 0 | 0 | 0 | 0 | 0 | 11 | 263 | 1380 | 10.8493 | -21.6833 | -5.8458 | 1354.284 | 22.474 | -157.1095 | -58.8144 | 0 | 57.3492 | 237.3492 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.7434 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
1 | 11 | 11 | 264 | 24 | -3.8 | 0 | 0 | 0 | 0 | 0 | 11 | 264 | 1440 | 10.8493 | -21.6833 | -5.8458 | 1414.284 | 23.474 | -172.1095 | -64.1033 | 0 | 57.3492 | 237.3492 | 67.5736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.7684 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 265 | 1 | -4 | 0 | 0 | 0 | 0 | 0 | 12 | 265 | 60 | 11.8356 | -21.5312 | -5.9876 | 34.284 | 0.47161 | 172.9259 | -64.1094 | 0 | 57.5942 | 122.4058 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2327 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 266 | 2 | -4.1 | 0 | 0 | 0 | 0 | 0 | 12 | 266 | 120 | 11.8356 | -21.5312 | -5.9876 | 94.284 | 1.4716 | 157.9259 | -59.0686 | 0 | 57.5942 | 122.4058 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.1959 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 267 | 3 | -4.5 | 0 | 0 | 0 | 0 | 0 | 12 | 267 | 180 | 11.8356 | -21.5312 | -5.9876 | 154.284 | 2.4716 | 142.9259 | -50.869 | 0 | 57.5942 | 122.4058 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6163 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 268 | 4 | -4.5 | 0 | 0 | 0 | 0 | 0 | 12 | 268 | 240 | 11.8356 | -21.5312 | -5.9876 | 214.284 | 3.4716 | 127.9259 | -41.2229 | 0 | 57.5942 | 122.4058 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6163 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 269 | 5 | -4.6 | 0 | 0 | 0 | 0 | 0 | 12 | 269 | 300 | 11.8356 | -21.5312 | -5.9876 | 274.284 | 4.4716 | 112.9259 | -31.0371 | 0 | 57.5942 | 122.4058 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2673 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 270 | 6 | -4.6 | 0 | 0 | 0 | 0 | 0 | 12 | 270 | 360 | 11.8356 | -21.5312 | -5.9876 | 334.284 | 5.4716 | 97.9259 | -20.8108 | 0 | 57.5942 | 122.4058 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3474 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 271 | 7 | -4.6 | 0 | 0 | 0 | 0 | 0 | 12 | 271 | 420 | 11.8356 | -21.5312 | -5.9876 | 394.284 | 6.4716 | 82.9259 | -10.8937 | 0 | 57.5942 | 122.4058 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.8003 | 140.8003 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 272 | 8 | -4.8 | 0 | 0 | 0 | 0 | 0 | 12 | 272 | 480 | 11.8356 | -21.5312 | -5.9876 | 454.284 | 7.4716 | 67.9259 | -1.6067 | 0 | 57.5942 | 122.4058 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.0741 | 145.0741 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 273 | 9 | -5 | 0 | 2.31 | 2.31 | 2.31 | 1.16 | 12 | 273 | 540 | 11.8356 | -21.5312 | -5.9876 | 514.284 | 8.4716 | 52.9259 | 6.6957 | 6.6957 | 48.3551 | 131.6449 | 56.6932 | 0 | 0 | 1.9717 | 1.9717 | -87.4291 | 0% | 0.89161 | 0 | 0 | 124.9842 | 124.9842 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 274 | 10 | -4.9 | 2.08 | 42.36 | 44.44 | 42.36 | 21.18 | 12 | 274 | 600 | 11.8356 | -21.5312 | -5.9876 | 574.284 | 9.4716 | 37.9259 | 13.5951 | 13.5951 | 36.0317 | 143.9683 | 43.7784 | 6.389 | 6.389 | 36.1565 | 42.5456 | -3.2791 | 0% | 19.2391 | 0 | 0 | 128.1742 | 128.1742 | 0% | 12.39% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 275 | 11 | -4.7 | 48.33 | 86.39 | 134.72 | 86.39 | 43.2 | 12 | 275 | 660 | 11.8356 | -21.5312 | -5.9876 | 634.284 | 10.4716 | 22.9259 | 18.6193 | 18.6193 | 22.4806 | 157.5194 | 32.3345 | 127.9009 | 127.9009 | 73.7385 | 201.6394 | -0.055008 | 0% | 91.1813 | 0 | 0 | 131.0607 | 131.0607 | 0% | 12.16% | 12.16% | 80% | 9.732% | 8.8737 | 11.9492 | 6 | 53.2421 | 19.6233 | 40.62% | 40.62%
1 | 12 | 12 | 276 | 12 | -4.6 | 68.53 | 109.25 | 177.78 | 109.25 | 54.63 | 12 | 276 | 720 | 11.8356 | -21.5312 | -5.9876 | 694.284 | 11.4716 | 7.9259 | 21.3161 | 21.3161 | 7.9141 | 172.0859 | 24.5635 | 171.4607 | 171.4607 | 93.2507 | 264.7114 | 0.15062 | 15.06% | 119.7025 | 18.0298 | 12.6209 | 128.6148 | 128.6148 | 9.813% | 12.08% | 12.08% | 80% | 9.661% | 11.5645 | 11.9122 | 6 | 69.3867 | 25.5738 | 53.95% | 53.95%
1 | 12 | 12 | 277 | 13 | -4.7 | 97.58 | 150.28 | 247.86 | 150.28 | 75.14 | 12 | 277 | 780 | 11.8356 | -21.5312 | -5.9876 | 754.284 | 12.4716 | -7.0741 | 21.3921 | 21.3921 | 7.0673 | 187.0673 | 24.3136 | 243.7985 | 243.7985 | 128.272 | 372.0705 | 0.33847 | 33.85% | 168.2503 | 56.9478 | 39.8634 | 110.1556 | 110.1556 | 36.19% | 11.93% | 11.93% | 85% | 10.14% | 17.0662 | 11.9492 | 6 | 102.3972 | 37.7404 | 92.96% | 92.96%
1 | 12 | 12 | 278 | 14 | -4.7 | 101.19 | 132.42 | 233.61 | 132.42 | 66.21 | 12 | 278 | 840 | 11.8356 | -21.5312 | -5.9876 | 814.284 | 13.4716 | -22.0741 | 18.8385 | 18.8385 | 21.6766 | 201.6766 | 31.7634 | 266.4421 | 266.4421 | 113.0275 | 379.4696 | 0.34755 | 34.75% | 171.5962 | 59.6378 | 41.7465 | 108.895 | 108.895 | 38.34% | 11.92% | 11.92% | 85% | 10.13% | 17.3909 | 11.9492 | 6 | 104.3455 | 38.4585 | 95.82% | 95.82%
1 | 12 | 12 | 279 | 15 | -4.7 | 144.81 | 96.58 | 241.39 | 96.58 | 48.29 | 12 | 279 | 900 | 11.8356 | -21.5312 | -5.9876 | 874.284 | 14.4716 | -37.0741 | 13.9352 | 13.9352 | 35.2949 | 215.2949 | 43.077 | 439.2174 | 439.2174 | 82.4362 | 521.6536 | 0.47196 | 47.2% | 235.8918 | 111.3315 | 77.932 | 107.5759 | 107.5759 | 72.44% | 11.73% | 0% | 90% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 280 | 16 | -4.8 | 111.31 | 66.67 | 177.98 | 66.67 | 33.34 | 12 | 280 | 960 | 11.8356 | -21.5312 | -5.9876 | 934.284 | 15.4716 | -52.0741 | 7.1294 | 7.1294 | 47.6871 | 227.6871 | 55.9381 | 0 | 0 | 56.9064 | 56.9064 | -2.2442 | 0% | 25.7331 | 0 | 0 | 104.177 | 104.177 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 281 | 17 | -4.8 | 44.36 | 30.47 | 74.83 | 30.47 | 15.24 | 12 | 281 | 1020 | 11.8356 | -21.5312 | -5.9876 | 994.284 | 16.4716 | -67.0741 | -1.1052 | 0 | 57.5942 | 237.5942 | 67.7315 | 0 | 0 | 26.0078 | 26.0078 | -5.8657 | 0% | 11.7607 | 0 | 0 | 139.2043 | 139.2043 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 282 | 18 | -4.9 | 0 | 3.25 | 3.25 | 3.25 | 1.63 | 12 | 282 | 1080 | 11.8356 | -21.5312 | -5.9876 | 1054.284 | 17.4716 | -82.0741 | -10.3463 | 0 | 57.5942 | 237.5942 | 67.7315 | 0 | 0 | 2.774 | 2.774 | -61.818 | 0% | 1.2544 | 0 | 0 | 130.1884 | 130.1884 | 0% | 12.44% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 283 | 19 | -5.2 | 0 | 0 | 0 | 0 | 0 | 12 | 283 | 1140 | 11.8356 | -21.5312 | -5.9876 | 1114.284 | 18.4716 | -97.0741 | -20.2364 | 0 | 57.5942 | 237.5942 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.0371 | 126.0371 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 284 | 20 | -5.4 | 0 | 0 | 0 | 0 | 0 | 12 | 284 | 1200 | 11.8356 | -21.5312 | -5.9876 | 1174.284 | 19.4716 | -112.0741 | -30.4538 | 0 | 57.5942 | 237.5942 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.2471 | 121.2471 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 285 | 21 | -5.6 | 0 | 0 | 0 | 0 | 0 | 12 | 285 | 1260 | 11.8356 | -21.5312 | -5.9876 | 1234.284 | 20.4716 | -127.0741 | -40.6531 | 0 | 57.5942 | 237.5942 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.2 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 286 | 22 | -5.7 | 0 | 0 | 0 | 0 | 0 | 12 | 286 | 1320 | 11.8356 | -21.5312 | -5.9876 | 1294.284 | 21.4716 | -142.0741 | -50.3485 | 0 | 57.5942 | 237.5942 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.3911 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 287 | 23 | -5.5 | 0 | 0 | 0 | 0 | 0 | 12 | 287 | 1380 | 11.8356 | -21.5312 | -5.9876 | 1354.284 | 22.4716 | -157.0741 | -58.6669 | 0 | 57.5942 | 237.5942 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.8971 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
1 | 12 | 12 | 288 | 24 | -5.6 | 0 | 0 | 0 | 0 | 0 | 12 | 288 | 1440 | 11.8356 | -21.5312 | -5.9876 | 1414.284 | 23.4716 | -172.0741 | -63.9477 | 0 | 57.5942 | 237.5942 | 67.7315 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.8603 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 289 | 1 | -5.6 | 0 | 0 | 0 | 0 | 0 | 13 | 289 | 60 | 12.8219 | -21.3726 | -6.1209 | 34.284 | 0.46938 | 172.9592 | -63.9597 | 0 | 57.8491 | 122.1509 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5505 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 290 | 2 | -5.4 | 0 | 0 | 0 | 0 | 0 | 13 | 290 | 120 | 12.8219 | -21.3726 | -6.1209 | 94.284 | 1.4694 | 157.9592 | -58.9467 | 0 | 57.8491 | 122.1509 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9169 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 291 | 3 | -5.5 | 0 | 0 | 0 | 0 | 0 | 13 | 291 | 180 | 12.8219 | -21.3726 | -6.1209 | 154.284 | 2.4694 | 142.9592 | -50.7692 | 0 | 57.8491 | 122.1509 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.7404 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 292 | 4 | -5.4 | 0 | 0 | 0 | 0 | 0 | 13 | 292 | 240 | 12.8219 | -21.3726 | -6.1209 | 214.284 | 3.4694 | 127.9592 | -41.1348 | 0 | 57.8491 | 122.1509 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.588 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 293 | 5 | -5.5 | 0 | 0 | 0 | 0 | 0 | 13 | 293 | 300 | 12.8219 | -21.3726 | -6.1209 | 274.284 | 4.4694 | 112.9592 | -30.9525 | 0 | 57.8491 | 122.1509 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0814 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 294 | 6 | -5.5 | 0 | 0 | 0 | 0 | 0 | 13 | 294 | 360 | 12.8219 | -21.3726 | -6.1209 | 334.284 | 5.4694 | 97.9592 | -20.7241 | 0 | 57.8491 | 122.1509 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8355 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 295 | 7 | -5.7 | 0 | 0 | 0 | 0 | 0 | 13 | 295 | 420 | 12.8219 | -21.3726 | -6.1209 | 394.284 | 6.4694 | 82.9592 | -10.8007 | 0 | 57.8491 | 122.1509 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.2203 | 147.2203 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 296 | 8 | -5.7 | 0 | 0 | 0 | 0 | 0 | 13 | 296 | 480 | 12.8219 | -21.3726 | -6.1209 | 454.284 | 7.4694 | 67.9592 | -1.5038 | 0 | 57.8491 | 122.1509 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 152.7756 | 152.7756 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 297 | 9 | -5.9 | 0.08 | 4.08 | 4.16 | 4.08 | 2.04 | 13 | 297 | 540 | 12.8219 | -21.3726 | -6.1209 | 514.284 | 8.4694 | 52.9592 | 6.8111 | 6.8111 | 48.4691 | 131.5309 | 56.6755 | 0 | 0 | 3.4825 | 3.4825 | -49.8085 | 0% | 1.5748 | 0 | 0 | 132.7633 | 132.7633 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 298 | 10 | -6.2 | 22.5 | 34.44 | 56.94 | 34.44 | 17.22 | 13 | 298 | 600 | 12.8219 | -21.3726 | -6.1209 | 574.284 | 9.4694 | 37.9592 | 13.7246 | 13.7246 | 36.1312 | 143.8688 | 43.7332 | 68.5242 | 68.5242 | 29.3964 | 97.9206 | -1.0038 | 0% | 44.2797 | 0 | 0 | 136.0744 | 136.0744 | 0% | 12.36% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 299 | 11 | -6.1 | 86.39 | 75.28 | 161.67 | 75.28 | 37.64 | 13 | 299 | 660 | 12.8219 | -21.3726 | -6.1209 | 634.284 | 10.4694 | 22.9592 | 18.7627 | 18.7627 | 22.5592 | 157.4408 | 32.2486 | 227.1529 | 227.1529 | 64.2555 | 291.4084 | 0.1974 | 19.74% | 131.7749 | 26.0127 | 18.2089 | 137.467 | 137.467 | 13.25% | 12.08% | 12.08% | 80% | 9.666% | 12.7369 | 12.4742 | 6 | 76.4215 | 28.1666 | 55.59% | 55.59%
1 | 13 | 13 | 300 | 12 | -6 | 114.08 | 98.33 | 212.41 | 98.33 | 49.17 | 13 | 300 | 720 | 12.8219 | -21.3726 | -6.1209 | 694.284 | 11.4694 | 7.9592 | 21.4707 | 21.4707 | 7.9646 | 172.0354 | 24.4243 | 283.7805 | 283.7805 | 83.9299 | 367.7104 | 0.32397 | 32.4% | 166.2786 | 53.869 | 37.7083 | 111.852 | 111.852 | 33.71% | 11.97% | 11.97% | 85% | 10.17% | 16.9183 | 12.4362 | 6 | 101.5096 | 37.4132 | 90.75% | 90.75%
1 | 13 | 13 | 301 | 13 | -5.7 | 178.75 | 118.47 | 297.22 | 118.47 | 59.24 | 13 | 301 | 780 | 12.8219 | -21.3726 | -6.1209 | 754.284 | 12.4694 | -7.0408 | 21.5529 | 21.5529 | 7.0495 | 187.0495 | 24.153 | 443.9833 | 443.9833 | 101.1205 | 545.1038 | 0.48159 | 48.16% | 246.4959 | 118.7093 | 83.0965 | 114.1623 | 114.1623 | 72.79% | 11.71% | 11.71% | 90% | 10.54% | 25.9833 | 12.3228 | 6 | 155.8998 | 57.4598 | 136.6% | 136.6%
1 | 13 | 13 | 302 | 14 | -5.4 | 127.58 | 97.58 | 225.16 | 97.58 | 48.79 | 13 | 302 | 840 | 12.8219 | -21.3726 | -6.1209 | 814.284 | 13.4694 | -22.0408 | 18.9996 | 18.9996 | 21.6906 | 201.6906 | 31.6302 | 333.664 | 333.664 | 83.2897 | 416.9537 | 0.38432 | 38.43% | 188.5465 | 72.4629 | 50.7241 | 109.7931 | 109.7931 | 46.2% | 11.89% | 11.89% | 85% | 10.1% | 19.0508 | 12.2099 | 6 | 114.305 | 42.1292 | 104.1% | 104.1%
1 | 13 | 13 | 303 | 15 | -5.6 | 133.53 | 60.56 | 194.09 | 60.56 | 30.28 | 13 | 303 | 900 | 12.8219 | -21.3726 | -6.1209 | 874.284 | 14.4694 | -37.0408 | 14.092 | 14.092 | 35.3355 | 215.3355 | 42.9751 | 401.2554 | 401.2554 | 51.6912 | 452.9466 | 0.41655 | 41.66% | 204.8224 | 85.3189 | 59.7232 | 105.3544 | 105.3544 | 56.69% | 11.84% | 0% | 85% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 304 | 16 | -5.5 | 75.56 | 44.64 | 120.2 | 44.64 | 22.32 | 13 | 304 | 960 | 12.8219 | -21.3726 | -6.1209 | 934.284 | 15.4694 | -52.0408 | 7.2793 | 7.2793 | 47.7479 | 227.7479 | 55.86 | 0 | 0 | 38.1026 | 38.1026 | -3.7951 | 0% | 17.23 | 0 | 0 | 142.5183 | 142.5183 | 0% | 12.42% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 305 | 17 | -5.6 | 16.19 | 30.75 | 46.94 | 30.75 | 15.38 | 13 | 305 | 1020 | 12.8219 | -21.3726 | -6.1209 | 994.284 | 16.4694 | -67.0408 | -0.96258 | 0 | 57.8491 | 237.8491 | 67.8961 | 0 | 0 | 26.2468 | 26.2468 | -5.8823 | 0% | 11.8688 | 0 | 0 | 135.5407 | 135.5407 | 0% | 12.44% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 306 | 18 | -5.8 | 0 | 3.89 | 3.89 | 3.89 | 1.95 | 13 | 306 | 1080 | 12.8219 | -21.3726 | -6.1209 | 1054.284 | 17.4694 | -82.0408 | -10.2101 | 0 | 57.8491 | 237.8491 | 67.8961 | 0 | 0 | 3.3203 | 3.3203 | -52.2038 | 0% | 1.5014 | 0 | 0 | 128.9912 | 128.9912 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 307 | 19 | -5.9 | 0 | 0 | 0 | 0 | 0 | 13 | 307 | 1140 | 12.8219 | -21.3726 | -6.1209 | 1114.284 | 18.4694 | -97.0408 | -20.1045 | 0 | 57.8491 | 237.8491 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.5151 | 125.5151 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 308 | 20 | -5.9 | 0 | 0 | 0 | 0 | 0 | 13 | 308 | 1200 | 12.8219 | -21.3726 | -6.1209 | 1174.284 | 19.4694 | -112.0408 | -30.3235 | 0 | 57.8491 | 237.8491 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.108 | 121.108 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 309 | 21 | -5.9 | 0 | 0 | 0 | 0 | 0 | 13 | 309 | 1260 | 12.8219 | -21.3726 | -6.1209 | 1234.284 | 20.4694 | -127.0408 | -40.5206 | 0 | 57.8491 | 237.8491 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.9798 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 310 | 22 | -5.9 | 0 | 0 | 0 | 0 | 0 | 13 | 310 | 1320 | 12.8219 | -21.3726 | -6.1209 | 1294.284 | 21.4694 | -142.0408 | -50.2088 | 0 | 57.8491 | 237.8491 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.9942 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 311 | 23 | -5.9 | 0 | 0 | 0 | 0 | 0 | 13 | 311 | 1380 | 12.8219 | -21.3726 | -6.1209 | 1354.284 | 22.4694 | -157.0408 | -58.5148 | 0 | 57.8491 | 237.8491 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.6654 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 13 | 13 | 312 | 24 | -5.9 | 0 | 0 | 0 | 0 | 0 | 13 | 312 | 1440 | 12.8219 | -21.3726 | -6.1209 | 1414.284 | 23.4694 | -172.0408 | -63.7861 | 0 | 57.8491 | 237.8491 | 67.8961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.3365 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 313 | 1 | -6.1 | 0 | 0 | 0 | 0 | 0 | 14 | 313 | 60 | 13.8082 | -21.2076 | -6.2456 | 34.284 | 0.46731 | 172.9904 | -63.8033 | 0 | 58.1139 | 121.8861 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.0977 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 314 | 2 | -6 | 0 | 0 | 0 | 0 | 0 | 14 | 314 | 120 | 13.8082 | -21.2076 | -6.2456 | 94.284 | 1.4673 | 157.9904 | -58.8179 | 0 | 58.1139 | 121.8861 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.7313 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 315 | 3 | -6.1 | 0 | 0 | 0 | 0 | 0 | 14 | 315 | 180 | 13.8082 | -21.2076 | -6.2456 | 154.284 | 2.4673 | 142.9904 | -50.6629 | 0 | 58.1139 | 121.8861 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.6697 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 316 | 4 | -6.1 | 0 | 0 | 0 | 0 | 0 | 14 | 316 | 240 | 13.8082 | -21.2076 | -6.2456 | 214.284 | 3.4673 | 127.9904 | -41.0404 | 0 | 58.1139 | 121.8861 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.6697 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 317 | 5 | -6.1 | 0 | 0 | 0 | 0 | 0 | 14 | 317 | 300 | 13.8082 | -21.2076 | -6.2456 | 274.284 | 4.4673 | 112.9904 | -30.8619 | 0 | 58.1139 | 121.8861 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1066 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 318 | 6 | -6.1 | 0 | 0 | 0 | 0 | 0 | 14 | 318 | 360 | 13.8082 | -21.2076 | -6.2456 | 334.284 | 5.4673 | 97.9904 | -20.6315 | 0 | 58.1139 | 121.8861 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0154 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 319 | 7 | -6.1 | 0 | 0 | 0 | 0 | 0 | 14 | 319 | 420 | 13.8082 | -21.2076 | -6.2456 | 394.284 | 6.4673 | 82.9904 | -10.7016 | 0 | 58.1139 | 121.8861 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.0532 | 136.0532 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 320 | 8 | -6.1 | 0 | 0 | 0 | 0 | 0 | 14 | 320 | 480 | 13.8082 | -21.2076 | -6.2456 | 454.284 | 7.4673 | 67.9904 | -1.3948 | 0 | 58.1139 | 121.8861 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.6028 | 139.6028 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 321 | 9 | -6.2 | 0.36 | 3.81 | 4.17 | 3.81 | 1.91 | 14 | 321 | 540 | 13.8082 | -21.2076 | -6.2456 | 514.284 | 8.4673 | 52.9904 | 6.9328 | 6.9328 | 48.585 | 131.415 | 56.6544 | 0 | 0 | 3.252 | 3.252 | -53.6304 | 0% | 1.4706 | 0 | 0 | 119.2811 | 119.2811 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 322 | 10 | -6.2 | 16.47 | 37.42 | 53.89 | 37.42 | 18.71 | 14 | 322 | 600 | 13.8082 | -21.2076 | -6.2456 | 574.284 | 9.4673 | 37.9904 | 13.8607 | 13.8607 | 36.2318 | 143.7682 | 43.6838 | 49.7178 | 49.7178 | 31.94 | 81.6577 | -1.3639 | 0% | 36.9256 | 0 | 0 | 122.338 | 122.338 | 0% | 12.39% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 323 | 11 | -6.1 | 46.31 | 75.19 | 121.5 | 75.19 | 37.6 | 14 | 323 | 660 | 13.8082 | -21.2076 | -6.2456 | 634.284 | 10.4673 | 22.9904 | 18.9128 | 18.9128 | 22.6379 | 157.3621 | 32.1575 | 120.9568 | 120.9568 | 64.1787 | 185.1355 | -0.1508 | 0% | 83.7183 | 0 | 0 | 123.0043 | 123.0043 | 0% | 12.23% | 12.23% | 80% | 9.788% | 8.1941 | 12.4742 | 6 | 49.1646 | 18.1205 | 39.97% | 39.97%
1 | 14 | 14 | 324 | 12 | -5.7 | 68.06 | 105.08 | 173.14 | 105.08 | 52.54 | 14 | 324 | 720 | 13.8082 | -21.2076 | -6.2456 | 694.284 | 11.4673 | 7.9904 | 21.6319 | 21.6319 | 8.0138 | 171.9862 | 24.2787 | 168.295 | 168.295 | 89.6914 | 257.9864 | 0.12277 | 12.28% | 116.6615 | 14.3224 | 10.0256 | 121.5292 | 121.5292 | 8.25% | 12.12% | 12.12% | 80% | 9.695% | 11.3098 | 12.3228 | 6 | 67.8585 | 25.0105 | 55.84% | 55.84%
1 | 14 | 14 | 325 | 13 | -5.4 | 82.31 | 122.22 | 204.53 | 122.22 | 61.11 | 14 | 325 | 780 | 13.8082 | -21.2076 | -6.2456 | 754.284 | 12.4673 | -7.0096 | 21.7198 | 21.7198 | 7.0344 | 187.0344 | 23.9869 | 203.2102 | 203.2102 | 104.3213 | 307.5315 | 0.235 | 23.5% | 139.0657 | 32.6804 | 22.8763 | 101.1459 | 101.1459 | 22.62% | 12.04% | 12.04% | 85% | 10.23% | 14.232 | 12.2099 | 6 | 85.3918 | 31.4727 | 84.42% | 84.42%
1 | 14 | 14 | 326 | 14 | -5.3 | 91.75 | 122.31 | 214.06 | 122.31 | 61.16 | 14 | 326 | 840 | 13.8082 | -21.2076 | -6.2456 | 814.284 | 13.4673 | -22.0096 | 19.1663 | 19.1663 | 21.7085 | 201.7085 | 31.4943 | 238.2944 | 238.2944 | 104.3981 | 342.6925 | 0.29412 | 29.41% | 154.9655 | 45.5787 | 31.9051 | 100.7288 | 100.7288 | 31.67% | 11.99% | 11.99% | 85% | 10.19% | 15.7911 | 12.1725 | 6 | 94.7468 | 34.9207 | 94.06% | 94.06%
1 | 14 | 14 | 327 | 15 | -5.2 | 72.03 | 95.47 | 167.5 | 95.47 | 47.74 | 14 | 327 | 900 | 13.8082 | -21.2076 | -6.2456 | 874.284 | 14.4673 | -37.0096 | 14.2536 | 14.2536 | 35.3807 | 215.3807 | 42.8723 | 214.4013 | 214.4013 | 81.4887 | 295.8901 | 0.21433 | 21.43% | 133.8015 | 28.6777 | 20.0744 | 97.0806 | 97.0806 | 20.68% | 12.05% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 328 | 16 | -5.2 | 11.47 | 74.72 | 86.19 | 74.72 | 37.36 | 14 | 328 | 960 | 13.8082 | -21.2076 | -6.2456 | 934.284 | 15.4673 | -52.0096 | 7.4335 | 7.4335 | 47.8139 | 227.8139 | 55.782 | 0 | 0 | 63.7775 | 63.7775 | -1.9317 | 0% | 28.8402 | 0 | 0 | 133.7776 | 133.7776 | 0% | 12.37% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 329 | 17 | -5.4 | 3.53 | 31.11 | 34.64 | 31.11 | 15.56 | 14 | 329 | 1020 | 13.8082 | -21.2076 | -6.2456 | 994.284 | 16.4673 | -67.0096 | -0.8162 | 0 | 58.1139 | 238.1139 | 68.0673 | 0 | 0 | 26.554 | 26.554 | -5.7858 | 0% | 12.0077 | 0 | 0 | 129.2762 | 129.2762 | 0% | 12.43% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 330 | 18 | -5.4 | 0 | 3.14 | 3.14 | 3.14 | 1.57 | 14 | 330 | 1080 | 13.8082 | -21.2076 | -6.2456 | 1054.284 | 17.4673 | -82.0096 | -10.0705 | 0 | 58.1139 | 238.1139 | 68.0673 | 0 | 0 | 2.6802 | 2.6802 | -64.4852 | 0% | 1.212 | 0 | 0 | 125.5992 | 125.5992 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 331 | 19 | -5.4 | 0 | 0 | 0 | 0 | 0 | 14 | 331 | 1140 | 13.8082 | -21.2076 | -6.2456 | 1114.284 | 18.4673 | -97.0096 | -19.9696 | 0 | 58.1139 | 238.1139 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.4935 | 123.4935 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 332 | 20 | -5.8 | 0 | 0 | 0 | 0 | 0 | 14 | 332 | 1200 | 13.8082 | -21.2076 | -6.2456 | 1174.284 | 19.4673 | -112.0096 | -30.1903 | 0 | 58.1139 | 238.1139 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.0509 | 120.0509 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 333 | 21 | -5.6 | 0 | 0 | 0 | 0 | 0 | 14 | 333 | 1260 | 13.8082 | -21.2076 | -6.2456 | 1234.284 | 20.4673 | -127.0096 | -40.385 | 0 | 58.1139 | 238.1139 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.3349 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 334 | 22 | -5.6 | 0 | 0 | 0 | 0 | 0 | 14 | 334 | 1320 | 13.8082 | -21.2076 | -6.2456 | 1294.284 | 21.4673 | -142.0096 | -50.0654 | 0 | 58.1139 | 238.1139 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.9777 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 335 | 23 | -5.6 | 0 | 0 | 0 | 0 | 0 | 14 | 335 | 1380 | 13.8082 | -21.2076 | -6.2456 | 1354.284 | 22.4673 | -157.0096 | -58.3581 | 0 | 58.1139 | 238.1139 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.7637 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
1 | 14 | 14 | 336 | 24 | -5.8 | 0 | 0 | 0 | 0 | 0 | 14 | 336 | 1440 | 13.8082 | -21.2076 | -6.2456 | 1414.284 | 23.4673 | -172.0096 | -63.6187 | 0 | 58.1139 | 238.1139 | 68.0673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.8545 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 337 | 1 | -5.9 | 0 | 0 | 0 | 0 | 0 | 15 | 337 | 60 | 14.7945 | -21.0362 | -6.3614 | 34.284 | 0.46538 | 173.0193 | -63.6401 | 0 | 58.3883 | 121.6117 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.3043 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 338 | 2 | -5.9 | 0 | 0 | 0 | 0 | 0 | 15 | 338 | 120 | 14.7945 | -21.0362 | -6.3614 | 94.284 | 1.4654 | 158.0193 | -58.6823 | 0 | 58.3883 | 121.6117 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.0516 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 339 | 3 | -5.9 | 0 | 0 | 0 | 0 | 0 | 15 | 339 | 180 | 14.7945 | -21.0362 | -6.3614 | 154.284 | 2.4654 | 143.0193 | -50.5502 | 0 | 58.3883 | 121.6117 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.7989 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 340 | 4 | -5.9 | 0 | 0 | 0 | 0 | 0 | 15 | 340 | 240 | 14.7945 | -21.0362 | -6.3614 | 214.284 | 3.4654 | 128.0193 | -40.9399 | 0 | 58.3883 | 121.6117 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.7989 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 341 | 5 | -5.9 | 0 | 0 | 0 | 0 | 0 | 15 | 341 | 300 | 14.7945 | -21.0362 | -6.3614 | 274.284 | 4.4654 | 113.0193 | -30.7653 | 0 | 58.3883 | 121.6117 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9023 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 342 | 6 | -6 | 0 | 0 | 0 | 0 | 0 | 15 | 342 | 360 | 14.7945 | -21.0362 | -6.3614 | 334.284 | 5.4654 | 98.0193 | -20.533 | 0 | 58.3883 | 121.6117 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9987 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 343 | 7 | -6.3 | 0 | 0 | 0 | 0 | 0 | 15 | 343 | 420 | 14.7945 | -21.0362 | -6.3614 | 394.284 | 6.4654 | 83.0193 | -10.5965 | 0 | 58.3883 | 121.6117 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.4489 | 140.4489 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5503 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 344 | 8 | -6.4 | 0 | 0 | 0 | 0 | 0 | 15 | 344 | 480 | 14.7945 | -21.0362 | -6.3614 | 454.284 | 7.4654 | 68.0193 | -1.2796 | 0 | 58.3883 | 121.6117 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.8643 | 144.8643 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 345 | 9 | -6.4 | 0.28 | 3.53 | 3.81 | 3.53 | 1.77 | 15 | 345 | 540 | 14.7945 | -21.0362 | -6.3614 | 514.284 | 8.4654 | 53.0193 | 7.0609 | 7.0609 | 48.7028 | 131.2972 | 56.6298 | 0 | 0 | 3.013 | 3.013 | -58.1177 | 0% | 1.3625 | 0 | 0 | 124.9974 | 124.9974 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 346 | 10 | -6.4 | 18.14 | 33.89 | 52.03 | 33.89 | 16.95 | 15 | 346 | 600 | 14.7945 | -21.0362 | -6.3614 | 574.284 | 9.4654 | 38.0193 | 14.0033 | 14.0033 | 36.3336 | 143.6664 | 43.6303 | 54.2607 | 54.2607 | 28.9269 | 83.1876 | -1.3301 | 0% | 37.6174 | 0 | 0 | 128.5367 | 128.5367 | 0% | 12.39% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 347 | 11 | -6.2 | 63.25 | 85.75 | 149 | 85.75 | 42.88 | 15 | 347 | 660 | 14.7945 | -21.0362 | -6.3614 | 634.284 | 10.4654 | 23.0193 | 19.0695 | 19.0695 | 22.7165 | 157.2835 | 32.0611 | 164.0677 | 164.0677 | 73.1922 | 237.2599 | 0.057886 | 5.789% | 107.2889 | 6.2106 | 4.3474 | 130.5699 | 130.5699 | 3.33% | 12.16% | 12.16% | 80% | 9.73% | 10.4396 | 12.5122 | 6 | 62.6374 | 23.0862 | 47.97% | 47.97%
1 | 15 | 15 | 348 | 12 | -5.3 | 96.19 | 80.64 | 176.83 | 80.64 | 40.32 | 15 | 348 | 720 | 14.7945 | -21.0362 | -6.3614 | 694.284 | 11.4654 | 8.0193 | 21.7995 | 21.7995 | 8.0616 | 171.9384 | 24.1267 | 236.3938 | 236.3938 | 68.8305 | 305.2243 | 0.23153 | 23.15% | 138.0224 | 31.9565 | 22.3695 | 127.8144 | 127.8144 | 17.5% | 12.04% | 12.04% | 85% | 10.23% | 14.1258 | 12.1725 | 6 | 84.7547 | 31.2379 | 66.31% | 66.31%
1 | 15 | 15 | 349 | 13 | -5.4 | 122.42 | 119.92 | 242.34 | 119.92 | 59.96 | 15 | 349 | 780 | 14.7945 | -21.0362 | -6.3614 | 754.284 | 12.4654 | -6.9807 | 21.8929 | 21.8929 | 7.022 | 187.022 | 23.8154 | 300.3603 | 300.3603 | 102.3581 | 402.7184 | 0.36949 | 36.95% | 182.1093 | 67.2874 | 47.1012 | 108.1926 | 108.1926 | 43.53% | 11.91% | 11.91% | 85% | 10.12% | 18.4312 | 12.2099 | 6 | 110.5871 | 40.7589 | 102.2% | 102.2%
1 | 15 | 15 | 350 | 14 | -5.2 | 154.08 | 113.14 | 267.22 | 113.14 | 56.57 | 15 | 350 | 840 | 14.7945 | -21.0362 | -6.3614 | 814.284 | 13.4654 | -21.9807 | 19.3385 | 19.3385 | 21.7303 | 201.7303 | 31.3556 | 397.3362 | 397.3362 | 96.571 | 493.9072 | 0.45074 | 45.07% | 223.3448 | 100.6705 | 70.4694 | 108.3516 | 108.3516 | 65.04% | 11.78% | 11.78% | 85% | 10.01% | 22.3564 | 12.1351 | 6 | 134.1383 | 49.4392 | 123.8% | 123.8%
1 | 15 | 15 | 351 | 15 | -5.4 | 131.47 | 72.78 | 204.25 | 72.78 | 36.39 | 15 | 351 | 900 | 14.7945 | -21.0362 | -6.3614 | 874.284 | 14.4654 | -36.9807 | 14.4202 | 14.4202 | 35.4307 | 215.4307 | 42.7686 | 387.5516 | 387.5516 | 62.1216 | 449.6732 | 0.41486 | 41.49% | 203.3422 | 84.3587 | 59.0511 | 103.0787 | 103.0787 | 57.29% | 11.84% | 0% | 85% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 352 | 16 | -5.7 | 64.72 | 62.78 | 127.5 | 62.78 | 31.39 | 15 | 352 | 960 | 14.7945 | -21.0362 | -6.3614 | 934.284 | 15.4654 | -51.9807 | 7.5919 | 7.5919 | 47.8851 | 227.8851 | 55.7043 | 0 | 0 | 53.5861 | 53.5861 | -2.4757 | 0% | 24.2316 | 0 | 0 | 139.7417 | 139.7417 | 0% | 12.41% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 353 | 17 | -5.9 | 21.75 | 32.5 | 54.25 | 32.5 | 16.25 | 15 | 353 | 1020 | 14.7945 | -21.0362 | -6.3614 | 994.284 | 16.4654 | -66.9807 | -0.66617 | 0 | 58.3883 | 238.3883 | 68.2451 | 0 | 0 | 27.7405 | 27.7405 | -5.5498 | 0% | 12.5442 | 0 | 0 | 133.542 | 133.542 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 354 | 18 | -6.2 | 0 | 3.25 | 3.25 | 3.25 | 1.63 | 15 | 354 | 1080 | 14.7945 | -21.0362 | -6.3614 | 1054.284 | 17.4654 | -81.9807 | -9.9276 | 0 | 58.3883 | 238.3883 | 68.2451 | 0 | 0 | 2.774 | 2.774 | -63.0099 | 0% | 1.2544 | 0 | 0 | 126.8455 | 126.8455 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 355 | 19 | -6.4 | 0 | 0 | 0 | 0 | 0 | 15 | 355 | 1140 | 14.7945 | -21.0362 | -6.3614 | 1114.284 | 18.4654 | -96.9807 | -19.8317 | 0 | 58.3883 | 238.3883 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.6872 | 123.6872 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 356 | 20 | -6.5 | 0 | 0 | 0 | 0 | 0 | 15 | 356 | 1200 | 14.7945 | -21.0362 | -6.3614 | 1174.284 | 19.4654 | -111.9807 | -30.0541 | 0 | 58.3883 | 238.3883 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 119.8096 | 119.8096 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 357 | 21 | -6.7 | 0 | 0 | 0 | 0 | 0 | 15 | 357 | 1260 | 14.7945 | -21.0362 | -6.3614 | 1234.284 | 20.4654 | -126.9807 | -40.2463 | 0 | 58.3883 | 238.3883 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.4213 | 0 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7034 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 358 | 22 | -6.7 | 0 | 0 | 0 | 0 | 0 | 15 | 358 | 1320 | 14.7945 | -21.0362 | -6.3614 | 1294.284 | 21.4654 | -141.9807 | -49.9183 | 0 | 58.3883 | 238.3883 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.2816 | 0 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7034 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 359 | 23 | -6.9 | 0 | 0 | 0 | 0 | 0 | 15 | 359 | 1380 | 14.7945 | -21.0362 | -6.3614 | 1354.284 | 22.4654 | -156.9807 | -58.1969 | 0 | 58.3883 | 238.3883 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.3337 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.7803 | 6 | 0 | 0 | 0% | 0%
1 | 15 | 15 | 360 | 24 | -7.1 | 0 | 0 | 0 | 0 | 0 | 15 | 360 | 1440 | 14.7945 | -21.0362 | -6.3614 | 1414.284 | 23.4654 | -171.9807 | -63.4456 | 0 | 58.3883 | 238.3883 | 68.2451 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.3858 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 361 | 1 | -7.1 | 0 | 0 | 0 | 0 | 0 | 16 | 361 | 60 | 15.7808 | -20.8586 | -6.4679 | 34.284 | 0.4636 | 173.046 | -63.4702 | 0 | 58.6723 | 121.3277 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.9527 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 362 | 2 | -7.4 | 0 | 0 | 0 | 0 | 0 | 16 | 362 | 120 | 15.7808 | -20.8586 | -6.4679 | 94.284 | 1.4636 | 158.046 | -58.5399 | 0 | 58.6723 | 121.3277 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.1517 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 12.9739 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 363 | 3 | -7.5 | 0 | 0 | 0 | 0 | 0 | 16 | 363 | 180 | 15.7808 | -20.8586 | -6.4679 | 154.284 | 2.4636 | 143.046 | -50.4309 | 0 | 58.6723 | 121.3277 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.0459 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 364 | 4 | -7.6 | 0 | 0 | 0 | 0 | 0 | 16 | 364 | 240 | 15.7808 | -20.8586 | -6.4679 | 214.284 | 3.4636 | 128.046 | -40.8332 | 0 | 58.6723 | 121.3277 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.1983 | 0 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.0519 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 365 | 5 | -7.8 | 0 | 0 | 0 | 0 | 0 | 16 | 365 | 300 | 15.7808 | -20.8586 | -6.4679 | 274.284 | 4.4636 | 113.046 | -30.6628 | 0 | 58.6723 | 121.3277 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2442 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 366 | 6 | -8.2 | 0 | 0 | 0 | 0 | 0 | 16 | 366 | 360 | 15.7808 | -20.8586 | -6.4679 | 334.284 | 5.4636 | 98.046 | -20.4284 | 0 | 58.6723 | 121.3277 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5616 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.2874 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 367 | 7 | -8.1 | 0 | 0 | 0 | 0 | 0 | 16 | 367 | 420 | 15.7808 | -20.8586 | -6.4679 | 394.284 | 6.4636 | 83.046 | -10.4854 | 0 | 58.6723 | 121.3277 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.992 | 139.992 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.248 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 368 | 8 | -8.4 | 0 | 0 | 0 | 0 | 0 | 16 | 368 | 480 | 15.7808 | -20.8586 | -6.4679 | 454.284 | 7.4636 | 68.046 | -1.1583 | 0 | 58.6723 | 121.3277 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.2312 | 144.2312 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 369 | 9 | -8.7 | 0.47 | 2.78 | 3.25 | 2.78 | 1.39 | 16 | 369 | 540 | 15.7808 | -20.8586 | -6.4679 | 514.284 | 8.4636 | 53.046 | 7.1954 | 7.1954 | 48.8224 | 131.1776 | 56.6017 | 0 | 0 | 2.3729 | 2.3729 | -76.505 | 0% | 1.073 | 0 | 0 | 123.8711 | 123.8711 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 370 | 10 | -8.5 | 25.75 | 36.47 | 62.22 | 36.47 | 18.24 | 16 | 370 | 600 | 15.7808 | -20.8586 | -6.4679 | 574.284 | 9.4636 | 38.046 | 14.1524 | 14.1524 | 36.4363 | 143.5637 | 43.5725 | 76.3018 | 76.3018 | 31.1291 | 107.4309 | -0.89875 | 0% | 48.5803 | 0 | 0 | 128.3401 | 128.3401 | 0% | 12.44% | 0% | 80% | 0% | 0 | 13.4061 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 371 | 11 | -8.5 | 62.58 | 75.47 | 138.05 | 75.47 | 37.74 | 16 | 371 | 660 | 15.7808 | -20.8586 | -6.4679 | 634.284 | 10.4636 | 23.046 | 19.2327 | 19.2327 | 22.7951 | 157.2049 | 31.9596 | 161.1817 | 161.1817 | 64.4177 | 225.5994 | -0.0068536 | 0% | 102.016 | 0 | 0 | 128.4523 | 128.4523 | 0% | 12.25% | 12.25% | 80% | 9.802% | 9.9995 | 13.4061 | 6 | 59.9971 | 22.113 | 46.71% | 46.71%
1 | 16 | 16 | 372 | 12 | -7.5 | 63.25 | 98.97 | 162.22 | 98.97 | 49.49 | 16 | 372 | 720 | 15.7808 | -20.8586 | -6.4679 | 694.284 | 11.4636 | 8.046 | 21.9736 | 21.9736 | 8.108 | 171.892 | 23.9683 | 154.4603 | 154.4603 | 84.4762 | 238.9365 | 0.049189 | 4.919% | 108.0471 | 5.3147 | 3.7203 | 125.2591 | 125.2591 | 2.97% | 12.2% | 12.2% | 80% | 9.76% | 10.5459 | 13.0129 | 6 | 63.2755 | 23.3214 | 50.52% | 50.52%
1 | 16 | 16 | 373 | 13 | -7 | 74.81 | 109.64 | 184.45 | 109.64 | 54.82 | 16 | 373 | 780 | 15.7808 | -20.8586 | -6.4679 | 754.284 | 12.4636 | -6.954 | 22.072 | 22.072 | 7.0125 | 187.0125 | 23.6385 | 182.3792 | 182.3792 | 93.5836 | 275.9628 | 0.15511 | 15.51% | 124.7904 | 19.3565 | 13.5496 | 125.8542 | 125.8542 | 10.77% | 12.13% | 12.13% | 80% | 9.704% | 12.1099 | 12.8189 | 6 | 72.6591 | 26.7799 | 57.73% | 57.73%
1 | 16 | 16 | 374 | 14 | -6.9 | 114.36 | 119.81 | 234.17 | 119.81 | 59.91 | 16 | 374 | 840 | 15.7808 | -20.8586 | -6.4679 | 814.284 | 13.4636 | -21.954 | 19.5162 | 19.5162 | 21.756 | 201.756 | 31.2144 | 292.7637 | 292.7637 | 102.2642 | 395.0279 | 0.35134 | 35.13% | 178.6316 | 62.7608 | 43.9325 | 106.1769 | 106.1769 | 41.38% | 11.95% | 11.95% | 85% | 10.16% | 18.1463 | 12.7803 | 6 | 108.8776 | 40.1288 | 102.5% | 102.5%
1 | 16 | 16 | 375 | 15 | -6.7 | 137.97 | 109.44 | 247.41 | 109.44 | 54.72 | 16 | 375 | 900 | 15.7808 | -20.8586 | -6.4679 | 874.284 | 14.4636 | -36.954 | 14.5915 | 14.5915 | 35.4855 | 215.4855 | 42.6642 | 402.7157 | 402.7157 | 93.4129 | 496.1286 | 0.44462 | 44.46% | 224.3493 | 99.7494 | 69.8245 | 105.1897 | 105.1897 | 66.38% | 11.8% | 0% | 85% | 0% | 0 | 12.7034 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 376 | 16 | -7 | 85.56 | 83.14 | 168.7 | 83.14 | 41.57 | 16 | 376 | 960 | 15.7808 | -20.8586 | -6.4679 | 934.284 | 15.4636 | -51.954 | 7.7545 | 7.7545 | 47.9616 | 227.9616 | 55.627 | 0 | 0 | 70.9644 | 70.9644 | -1.7194 | 0% | 32.0901 | 0 | 0 | 100.0995 | 100.0995 | 0% | 12.43% | 0% | 80% | 0% | 0 | 12.8189 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 377 | 17 | -7.1 | 19.44 | 40.92 | 60.36 | 40.92 | 20.46 | 16 | 377 | 1020 | 15.7808 | -20.8586 | -6.4679 | 994.284 | 16.4636 | -66.954 | -0.51259 | 0 | 58.6723 | 238.6723 | 68.4294 | 0 | 0 | 34.9274 | 34.9274 | -4.3302 | 0% | 15.7942 | 0 | 0 | 133.9647 | 133.9647 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 378 | 18 | -7.3 | 0 | 5 | 5 | 5 | 2.5 | 16 | 378 | 1080 | 15.7808 | -20.8586 | -6.4679 | 1054.284 | 17.4636 | -81.954 | -9.7816 | 0 | 58.6723 | 238.6723 | 68.4294 | 0 | 0 | 4.2678 | 4.2678 | -41.3347 | 0% | 1.9299 | 0 | 0 | 127.157 | 127.157 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 379 | 19 | -7.5 | 0 | 0 | 0 | 0 | 0 | 16 | 379 | 1140 | 15.7808 | -20.8586 | -6.4679 | 1114.284 | 18.4636 | -96.954 | -19.6909 | 0 | 58.6723 | 238.6723 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.6383 | 123.6383 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 380 | 20 | -7.6 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 1200 | 15.7808 | -20.8586 | -6.4679 | 1174.284 | 19.4636 | -111.954 | -29.9151 | 0 | 58.6723 | 238.6723 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 119.4428 | 119.4428 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.0519 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 381 | 21 | -7.8 | 0 | 0 | 0 | 0 | 0 | 16 | 381 | 1260 | 15.7808 | -20.8586 | -6.4679 | 1234.284 | 20.4636 | -126.954 | -40.1045 | 0 | 58.6723 | 238.6723 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.8668 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 382 | 22 | -8.3 | 0 | 0 | 0 | 0 | 0 | 16 | 382 | 1320 | 15.7808 | -20.8586 | -6.4679 | 1294.284 | 21.4636 | -141.954 | -49.7677 | 0 | 58.6723 | 238.6723 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.556 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 383 | 23 | -8.6 | 0 | 0 | 0 | 0 | 0 | 16 | 383 | 1380 | 15.7808 | -20.8586 | -6.4679 | 1354.284 | 22.4636 | -156.954 | -58.0312 | 0 | 58.6723 | 238.6723 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.755 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4458 | 6 | 0 | 0 | 0% | 0%
1 | 16 | 16 | 384 | 24 | -8.4 | 0 | 0 | 0 | 0 | 0 | 16 | 384 | 1440 | 15.7808 | -20.8586 | -6.4679 | 1414.284 | 23.4636 | -171.954 | -63.2667 | 0 | 58.6723 | 238.6723 | 68.4294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.192 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 385 | 1 | -8.6 | 0 | 0 | 0 | 0 | 0 | 17 | 385 | 60 | 16.7671 | -20.6748 | -6.565 | 34.284 | 0.46198 | 173.0703 | -63.2937 | 0 | 58.9657 | 121.0343 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.104 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4458 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 386 | 2 | -8.8 | 0 | 0 | 0 | 0 | 0 | 17 | 386 | 120 | 16.7671 | -20.6748 | -6.565 | 94.284 | 1.462 | 158.0703 | -58.3907 | 0 | 58.9657 | 121.0343 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.0046 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5254 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 387 | 3 | -8.3 | 0 | 0 | 0 | 0 | 0 | 17 | 387 | 180 | 16.7671 | -20.6748 | -6.565 | 154.284 | 2.462 | 143.0703 | -50.3051 | 0 | 58.9657 | 121.0343 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.8384 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 388 | 4 | -8.2 | 0 | 0 | 0 | 0 | 0 | 17 | 388 | 240 | 16.7671 | -20.6748 | -6.565 | 214.284 | 3.462 | 128.0703 | -40.7203 | 0 | 58.9657 | 121.0343 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.686 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.2874 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 389 | 5 | -7.9 | 0 | 0 | 0 | 0 | 0 | 17 | 389 | 300 | 16.7671 | -20.6748 | -6.565 | 274.284 | 4.462 | 113.0703 | -30.5542 | 0 | 58.9657 | 121.0343 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8818 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1693 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 390 | 6 | -7.9 | 0 | 0 | 0 | 0 | 0 | 17 | 390 | 360 | 16.7671 | -20.6748 | -6.565 | 334.284 | 5.462 | 98.0703 | -20.3179 | 0 | 58.9657 | 121.0343 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4765 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1693 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 391 | 7 | -7.7 | 0 | 0 | 0 | 0 | 0 | 17 | 391 | 420 | 16.7671 | -20.6748 | -6.565 | 394.284 | 6.462 | 83.0703 | -10.3683 | 0 | 58.9657 | 121.0343 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 150.5154 | 150.5154 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.091 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 392 | 8 | -7.4 | 0 | 0 | 0 | 0 | 0 | 17 | 392 | 480 | 16.7671 | -20.6748 | -6.565 | 454.284 | 7.462 | 68.0703 | -1.0307 | 0 | 58.9657 | 121.0343 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 157.533 | 157.533 | 0% | 12.56% | 0% | 80% | 0% | 0 | 12.9739 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 393 | 9 | -7.1 | 0.47 | 4.72 | 5.19 | 4.72 | 2.36 | 17 | 393 | 540 | 16.7671 | -20.6748 | -6.565 | 514.284 | 8.462 | 53.0703 | 7.3361 | 7.3361 | 48.9438 | 131.0562 | 56.5701 | 0 | 0 | 4.0288 | 4.0288 | -43.7071 | 0% | 1.8218 | 0 | 0 | 138.4967 | 138.4967 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 394 | 10 | -6.5 | 36.31 | 41.47 | 77.78 | 41.47 | 20.74 | 17 | 394 | 600 | 16.7671 | -20.6748 | -6.565 | 574.284 | 9.462 | 38.0703 | 14.308 | 14.308 | 36.54 | 143.46 | 43.5106 | 106.5564 | 106.5564 | 35.3969 | 141.9532 | -0.44845 | 0% | 64.1913 | 0 | 0 | 144.5736 | 144.5736 | 0% | 12.31% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 395 | 11 | -6.4 | 110.47 | 77.69 | 188.16 | 77.69 | 38.85 | 17 | 395 | 660 | 16.7671 | -20.6748 | -6.565 | 634.284 | 10.462 | 23.0703 | 19.4025 | 19.4025 | 22.8735 | 157.1265 | 31.8529 | 282.4597 | 282.4597 | 66.3126 | 348.7723 | 0.29498 | 29.5% | 157.7148 | 46.5221 | 32.5654 | 145.0911 | 145.0911 | 22.44% | 12.01% | 12.01% | 85% | 10.21% | 16.0965 | 12.5884 | 6 | 96.5792 | 35.5961 | 66.56% | 66.56%
1 | 17 | 17 | 396 | 12 | -6 | 195.36 | 94.36 | 289.72 | 94.36 | 47.18 | 17 | 396 | 720 | 16.7671 | -20.6748 | -6.565 | 694.284 | 11.462 | 8.0703 | 22.1541 | 22.1541 | 8.153 | 171.847 | 23.8037 | 473.9903 | 473.9903 | 80.5413 | 554.5316 | 0.48569 | 48.57% | 250.7592 | 121.7913 | 85.2539 | 120.9413 | 120.9413 | 70.49% | 11.7% | 11.7% | 90% | 10.53% | 26.4118 | 12.4362 | 6 | 158.4705 | 58.4072 | 131% | 131%
1 | 17 | 17 | 397 | 13 | -5.3 | 187.97 | 109.17 | 297.14 | 109.17 | 54.59 | 17 | 397 | 780 | 16.7671 | -20.6748 | -6.565 | 754.284 | 12.462 | -6.9297 | 22.2571 | 22.2571 | 7.0058 | 187.0058 | 23.4564 | 455.2617 | 455.2617 | 93.1824 | 548.4442 | 0.48541 | 48.54% | 248.0064 | 120.3836 | 84.2685 | 119.5251 | 119.5251 | 70.5% | 11.7% | 11.7% | 90% | 10.53% | 26.1196 | 12.1725 | 6 | 156.7178 | 57.7612 | 131.1% | 131.1%
1 | 17 | 17 | 398 | 14 | -5.1 | 222.5 | 122.22 | 344.72 | 122.22 | 61.11 | 17 | 398 | 840 | 16.7671 | -20.6748 | -6.565 | 814.284 | 13.462 | -21.9297 | 19.6993 | 19.6993 | 21.7859 | 201.7859 | 31.0709 | 565.3729 | 565.3729 | 104.3213 | 669.6942 | 0.54385 | 54.38% | 302.8357 | 164.696 | 115.2872 | 119.9304 | 119.9304 | 96.13% | 11.53% | 11.53% | 90% | 10.38% | 31.4304 | 12.0978 | 6 | 188.5824 | 69.5055 | 157.2% | 157.2%
1 | 17 | 17 | 399 | 15 | -5.1 | 151.53 | 105 | 256.53 | 105 | 52.5 | 17 | 399 | 900 | 16.7671 | -20.6748 | -6.565 | 874.284 | 14.462 | -36.9297 | 14.7675 | 14.7675 | 35.5451 | 215.5451 | 42.5593 | 437.8759 | 437.8759 | 89.6231 | 527.499 | 0.47372 | 47.37% | 238.5351 | 112.9983 | 79.0988 | 112.6765 | 112.6765 | 70.2% | 11.73% | 0% | 90% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 400 | 16 | -4.9 | 85.97 | 95.42 | 181.39 | 95.42 | 47.71 | 17 | 400 | 960 | 16.7671 | -20.6748 | -6.565 | 934.284 | 15.462 | -51.9297 | 7.9211 | 7.9211 | 48.0433 | 228.0433 | 55.5502 | 0 | 0 | 81.4461 | 81.4461 | -1.3289 | 0% | 36.8299 | 0 | 0 | 107.5428 | 107.5428 | 0% | 12.34% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 401 | 17 | -5.3 | 16.11 | 64.17 | 80.28 | 64.17 | 32.09 | 17 | 401 | 1020 | 16.7671 | -20.6748 | -6.565 | 994.284 | 16.462 | -66.9297 | -0.35555 | 0 | 58.9657 | 238.9657 | 68.6201 | 0 | 0 | 54.7725 | 54.7725 | -2.3861 | 0% | 24.7681 | 0 | 0 | 140.1196 | 140.1196 | 0% | 12.39% | 0% | 80% | 0% | 0 | 12.1725 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 402 | 18 | -5.8 | 0 | 5.28 | 5.28 | 5.28 | 2.64 | 17 | 402 | 1080 | 16.7671 | -20.6748 | -6.565 | 1054.284 | 17.462 | -81.9297 | -9.6326 | 0 | 58.9657 | 238.9657 | 68.6201 | 0 | 0 | 4.5068 | 4.5068 | -38.2491 | 0% | 2.038 | 0 | 0 | 131.1428 | 131.1428 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 403 | 19 | -6.5 | 0 | 0 | 0 | 0 | 0 | 17 | 403 | 1140 | 16.7671 | -20.6748 | -6.565 | 1114.284 | 18.462 | -96.9297 | -19.5472 | 0 | 58.9657 | 238.9657 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.3049 | 126.3049 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 404 | 20 | -7.2 | 0 | 0 | 0 | 0 | 0 | 17 | 404 | 1200 | 16.7671 | -20.6748 | -6.565 | 1174.284 | 19.462 | -111.9297 | -29.7733 | 0 | 58.9657 | 238.9657 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.21 | 120.21 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 405 | 21 | -8.3 | 0 | 0 | 0 | 0 | 0 | 17 | 405 | 1260 | 16.7671 | -20.6748 | -6.565 | 1234.284 | 20.462 | -126.9297 | -39.9597 | 0 | 58.9657 | 238.9657 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.7018 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 406 | 22 | -9.2 | 0 | 0 | 0 | 0 | 0 | 17 | 406 | 1320 | 16.7671 | -20.6748 | -6.565 | 1294.284 | 21.462 | -141.9297 | -49.6136 | 0 | 58.9657 | 238.9657 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.231 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 407 | 23 | -9.1 | 0 | 0 | 0 | 0 | 0 | 17 | 407 | 1380 | 16.7671 | -20.6748 | -6.565 | 1354.284 | 22.462 | -156.9297 | -57.8611 | 0 | 58.9657 | 238.9657 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.6744 | 0 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6454 | 6 | 0 | 0 | 0% | 0%
1 | 17 | 17 | 408 | 24 | -8.8 | 0 | 0 | 0 | 0 | 0 | 17 | 408 | 1440 | 16.7671 | -20.6748 | -6.565 | 1414.284 | 23.462 | -171.9297 | -63.0823 | 0 | 58.9657 | 238.9657 | 68.6201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.813 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5254 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 409 | 1 | -8.6 | 0 | 0 | 0 | 0 | 0 | 18 | 409 | 60 | 17.7534 | -20.4848 | -6.6525 | 34.284 | 0.46053 | 173.0921 | -63.1107 | 0 | 59.2683 | 120.7317 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.0422 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4458 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 410 | 2 | -8.1 | 0 | 0 | 0 | 0 | 0 | 18 | 410 | 120 | 17.7534 | -20.4848 | -6.6525 | 94.284 | 1.4605 | 158.0921 | -58.2347 | 0 | 59.2683 | 120.7317 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.0873 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.248 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 411 | 3 | -8.4 | 0 | 0 | 0 | 0 | 0 | 18 | 411 | 180 | 17.7534 | -20.4848 | -6.6525 | 154.284 | 2.4605 | 143.0921 | -50.1728 | 0 | 59.2683 | 120.7317 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.3515 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 412 | 4 | -8.8 | 0 | 0 | 0 | 0 | 0 | 18 | 412 | 240 | 17.7534 | -20.4848 | -6.6525 | 214.284 | 3.4605 | 128.0921 | -40.6012 | 0 | 59.2683 | 120.7317 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.9611 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5254 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 413 | 5 | -9.2 | 0 | 0 | 0 | 0 | 0 | 18 | 413 | 300 | 17.7534 | -20.4848 | -6.6525 | 274.284 | 4.4605 | 113.0921 | -30.4396 | 0 | 59.2683 | 120.7317 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8353 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 414 | 6 | -9.7 | 0 | 0 | 0 | 0 | 0 | 18 | 414 | 360 | 17.7534 | -20.4848 | -6.6525 | 334.284 | 5.4605 | 98.0921 | -20.2014 | 0 | 59.2683 | 120.7317 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.256 | 0 | 0% | 12.66% | 0% | 80% | 0% | 0 | 13.8872 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 415 | 7 | -10.5 | 0 | 0 | 0 | 0 | 0 | 18 | 415 | 420 | 17.7534 | -20.4848 | -6.6525 | 394.284 | 6.4605 | 83.0921 | -10.2451 | 0 | 59.2683 | 120.7317 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.6811 | 131.6811 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.2135 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 416 | 8 | -11 | 0 | 0 | 0 | 0 | 0 | 18 | 416 | 480 | 17.7534 | -20.4848 | -6.6525 | 454.284 | 7.4605 | 68.0921 | -0.89704 | 0 | 59.2683 | 120.7317 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.9407 | 134.9407 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4197 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 417 | 9 | -10.4 | 0 | 3.89 | 3.89 | 3.89 | 1.95 | 18 | 417 | 540 | 17.7534 | -20.4848 | -6.6525 | 514.284 | 8.4605 | 53.0921 | 7.4832 | 7.4832 | 49.0668 | 130.9332 | 56.5351 | 0 | 0 | 3.3203 | 3.3203 | -55.7748 | 0% | 1.5014 | 0 | 0 | 115.9548 | 115.9548 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.1724 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 418 | 10 | -9.9 | 7.22 | 39.44 | 46.66 | 39.44 | 19.72 | 18 | 418 | 600 | 17.7534 | -20.4848 | -6.6525 | 574.284 | 9.4605 | 38.0921 | 14.47 | 14.47 | 36.6446 | 143.3554 | 43.4446 | 20.9787 | 20.9787 | 33.6641 | 54.6428 | -2.6101 | 0% | 24.7095 | 0 | 0 | 119.7968 | 119.7968 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.9683 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 419 | 11 | -9.2 | 42.58 | 67.31 | 109.89 | 67.31 | 33.66 | 18 | 419 | 660 | 17.7534 | -20.4848 | -6.6525 | 634.284 | 10.4605 | 23.0921 | 19.5788 | 19.5788 | 22.9517 | 157.0483 | 31.7411 | 108.0608 | 108.0608 | 57.4527 | 165.5135 | -0.31216 | 0% | 74.8452 | 0 | 0 | 121.9921 | 121.9921 | 0% | 12.37% | 12.37% | 80% | 9.897% | 7.4073 | 13.6855 | 6 | 44.4436 | 16.3805 | 36.43% | 36.43%
1 | 18 | 18 | 420 | 12 | -9 | 77.97 | 110.56 | 188.53 | 110.56 | 55.28 | 18 | 420 | 720 | 17.7534 | -20.4848 | -6.6525 | 694.284 | 11.4605 | 8.0921 | 22.3409 | 22.3409 | 8.1963 | 171.8037 | 23.6329 | 187.9182 | 187.9182 | 94.3689 | 282.2871 | 0.1514 | 15.14% | 127.6502 | 19.3259 | 13.5282 | 121.8771 | 121.8771 | 11.1% | 12.18% | 12.18% | 80% | 9.742% | 12.4359 | 13.6053 | 6 | 74.6156 | 27.501 | 61.22% | 61.22%
1 | 18 | 18 | 421 | 13 | -8.3 | 141.11 | 144.03 | 285.14 | 144.03 | 72.02 | 18 | 421 | 780 | 17.7534 | -20.4848 | -6.6525 | 754.284 | 12.4605 | -6.9079 | 22.4482 | 22.4482 | 7.0021 | 187.0021 | 23.2692 | 339.4861 | 339.4861 | 122.9373 | 462.4234 | 0.40953 | 40.95% | 209.1079 | 85.6361 | 59.9453 | 105.3377 | 105.3377 | 56.91% | 11.88% | 11.88% | 85% | 10.1% | 21.1112 | 13.3269 | 6 | 126.667 | 46.6854 | 120.2% | 120.2%
1 | 18 | 18 | 422 | 14 | -6.7 | 104.17 | 108.89 | 213.06 | 108.89 | 54.45 | 18 | 422 | 840 | 17.7534 | -20.4848 | -6.6525 | 814.284 | 13.4605 | -21.9079 | 19.8877 | 19.8877 | 21.8198 | 201.8198 | 30.9251 | 262.6903 | 262.6903 | 92.9434 | 355.6337 | 0.30264 | 30.26% | 160.8176 | 48.6698 | 34.0689 | 103.5371 | 103.5371 | 32.9% | 12% | 12% | 85% | 10.2% | 16.4096 | 12.7034 | 6 | 98.4577 | 36.2884 | 95.09% | 95.09%
1 | 18 | 18 | 423 | 15 | -6.2 | 25.56 | 139.44 | 165 | 139.44 | 69.72 | 18 | 423 | 900 | 17.7534 | -20.4848 | -6.6525 | 874.284 | 14.4605 | -36.9079 | 14.9481 | 14.9481 | 35.6096 | 215.6096 | 42.4539 | 73.1113 | 73.1113 | 119.0195 | 192.1308 | -0.11737 | 0% | 86.8816 | 0 | 0 | 99.8582 | 99.8582 | 0% | 12.23% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 424 | 16 | -6.6 | 31.81 | 104.17 | 135.98 | 104.17 | 52.09 | 18 | 424 | 960 | 17.7534 | -20.4848 | -6.6525 | 934.284 | 15.4605 | -51.9079 | 8.0915 | 8.0915 | 48.1304 | 228.1304 | 55.474 | 0 | 0 | 88.9147 | 88.9147 | -1.1984 | 0% | 40.2072 | 0 | 0 | 138.8024 | 138.8024 | 0% | 12.39% | 0% | 80% | 0% | 0 | 12.665 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 425 | 17 | -7.2 | 27.14 | 50.19 | 77.33 | 50.19 | 25.1 | 18 | 425 | 1020 | 17.7534 | -20.4848 | -6.6525 | 994.284 | 16.4605 | -66.9079 | -0.19513 | 0 | 59.2683 | 239.2683 | 68.8172 | 0 | 0 | 42.8398 | 42.8398 | -3.3879 | 0% | 19.3722 | 0 | 0 | 133.6294 | 133.6294 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 426 | 18 | -7.8 | 0 | 6.75 | 6.75 | 6.75 | 3.38 | 18 | 426 | 1080 | 17.7534 | -20.4848 | -6.6525 | 1054.284 | 17.4605 | -81.9079 | -9.4806 | 0 | 59.2683 | 239.2683 | 68.8172 | 0 | 0 | 5.7615 | 5.7615 | -30.6329 | 0% | 2.6053 | 0 | 0 | 125.7066 | 125.7066 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 427 | 19 | -8.4 | 0 | 0 | 0 | 0 | 0 | 18 | 427 | 1140 | 17.7534 | -20.4848 | -6.6525 | 1114.284 | 18.4605 | -96.9079 | -19.4009 | 0 | 59.2683 | 239.2683 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.8623 | 121.8623 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 428 | 20 | -8.7 | 0 | 0 | 0 | 0 | 0 | 18 | 428 | 1200 | 17.7534 | -20.4848 | -6.6525 | 1174.284 | 19.4605 | -111.9079 | -29.6288 | 0 | 59.2683 | 239.2683 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 117.9139 | 117.9139 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 429 | 21 | -9.3 | 0 | 0 | 0 | 0 | 0 | 18 | 429 | 1260 | 17.7534 | -20.4848 | -6.6525 | 1234.284 | 20.4605 | -126.9079 | -39.812 | 0 | 59.2683 | 239.2683 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.8788 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.7257 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 430 | 22 | -9.3 | 0 | 0 | 0 | 0 | 0 | 18 | 430 | 1320 | 17.7534 | -20.4848 | -6.6525 | 1294.284 | 21.4605 | -141.9079 | -49.4561 | 0 | 59.2683 | 239.2683 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.6879 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.7257 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 431 | 23 | -9.5 | 0 | 0 | 0 | 0 | 0 | 18 | 431 | 1380 | 17.7534 | -20.4848 | -6.6525 | 1354.284 | 22.4605 | -156.9079 | -57.6867 | 0 | 59.2683 | 239.2683 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.7997 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8063 | 6 | 0 | 0 | 0% | 0%
1 | 18 | 18 | 432 | 24 | -8.3 | 0 | 0 | 0 | 0 | 0 | 18 | 432 | 1440 | 17.7534 | -20.4848 | -6.6525 | 1414.284 | 23.4605 | -171.9079 | -62.8923 | 0 | 59.2683 | 239.2683 | 68.8172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.778 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 433 | 1 | -8.3 | 0 | 0 | 0 | 0 | 0 | 19 | 433 | 60 | 18.7397 | -20.2888 | -6.73 | 34.284 | 0.45923 | 173.1115 | -62.9213 | 0 | 59.5799 | 120.4201 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.5433 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 434 | 2 | -8.2 | 0 | 0 | 0 | 0 | 0 | 19 | 434 | 120 | 18.7397 | -20.2888 | -6.73 | 94.284 | 1.4592 | 158.1115 | -58.072 | 0 | 59.5799 | 120.4201 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.2133 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.2874 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 435 | 3 | -8 | 0 | 0 | 0 | 0 | 0 | 19 | 435 | 180 | 18.7397 | -20.2888 | -6.73 | 154.284 | 2.4592 | 143.1115 | -50.034 | 0 | 59.5799 | 120.4201 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.731 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.2086 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 436 | 4 | -7.9 | 0 | 0 | 0 | 0 | 0 | 19 | 436 | 240 | 18.7397 | -20.2888 | -6.73 | 214.284 | 3.4592 | 128.1115 | -40.4759 | 0 | 59.5799 | 120.4201 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.5786 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1693 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 437 | 5 | -7.8 | 0 | 0 | 0 | 0 | 0 | 19 | 437 | 300 | 18.7397 | -20.2888 | -6.73 | 274.284 | 4.4592 | 113.1115 | -30.3189 | 0 | 59.5799 | 120.4201 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.013 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 438 | 6 | -7.6 | 0 | 0 | 0 | 0 | 0 | 19 | 438 | 360 | 18.7397 | -20.2888 | -6.73 | 334.284 | 5.4592 | 98.1115 | -20.0789 | 0 | 59.5799 | 120.4201 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4209 | 0 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.0519 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 439 | 7 | -7.5 | 0 | 0 | 0 | 0 | 0 | 19 | 439 | 420 | 18.7397 | -20.2888 | -6.73 | 394.284 | 6.4592 | 83.1115 | -10.1159 | 0 | 59.5799 | 120.4201 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.245 | 130.245 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 440 | 8 | -7.5 | 0 | 0 | 0 | 0 | 0 | 19 | 440 | 480 | 18.7397 | -20.2888 | -6.73 | 454.284 | 7.4592 | 68.1115 | -0.75724 | 0 | 59.5799 | 120.4201 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.113 | 133.113 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 441 | 9 | -7.3 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 19 | 441 | 540 | 18.7397 | -20.2888 | -6.73 | 514.284 | 8.4592 | 53.1115 | 7.6366 | 7.6366 | 49.1913 | 130.8087 | 56.4965 | 0 | 0 | 1.6559 | 1.6559 | -107.801 | 0% | 0.7488 | 0 | 0 | 113.0394 | 113.0394 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 442 | 10 | -6.6 | 12.97 | 34.36 | 47.33 | 34.36 | 17.18 | 19 | 442 | 600 | 18.7397 | -20.2888 | -6.73 | 574.284 | 9.4592 | 38.1115 | 14.6384 | 14.6384 | 36.7499 | 143.2501 | 43.3745 | 37.305 | 37.305 | 29.3281 | 66.6331 | -1.868 | 0% | 30.1315 | 0 | 0 | 116.7835 | 116.7835 | 0% | 12.42% | 0% | 80% | 0% | 0 | 12.665 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 443 | 11 | -5.7 | 7.14 | 82.42 | 89.56 | 82.42 | 41.21 | 19 | 443 | 660 | 18.7397 | -20.2888 | -6.73 | 634.284 | 10.4592 | 23.1115 | 19.7615 | 19.7615 | 23.0296 | 156.9704 | 31.6243 | 17.9818 | 17.9818 | 70.3499 | 88.3317 | -1.1856 | 0% | 39.9436 | 0 | 0 | 117.7023 | 117.7023 | 0% | 12.36% | 12.36% | 80% | 9.886% | 3.949 | 12.3228 | 6 | 23.6938 | 8.7328 | 20.13% | 20.13%
1 | 19 | 19 | 444 | 12 | -5.6 | 70.47 | 111.47 | 181.94 | 111.47 | 55.74 | 19 | 444 | 720 | 18.7397 | -20.2888 | -6.73 | 694.284 | 11.4592 | 8.1115 | 22.534 | 22.534 | 8.238 | 171.762 | 23.4559 | 168.6889 | 168.6889 | 95.1456 | 263.8345 | 0.13883 | 13.88% | 119.306 | 16.5636 | 11.5945 | 119.0778 | 119.0778 | 9.737% | 12.11% | 12.11% | 80% | 9.686% | 11.5554 | 12.2851 | 6 | 69.3325 | 25.5538 | 58.22% | 58.22%
1 | 19 | 19 | 445 | 13 | -4.9 | 8.89 | 116.75 | 125.64 | 116.75 | 58.38 | 19 | 445 | 780 | 18.7397 | -20.2888 | -6.73 | 754.284 | 12.4592 | -6.8885 | 22.645 | 22.645 | 7.0014 | 187.0014 | 23.077 | 21.242 | 21.242 | 99.6524 | 120.8944 | -0.63293 | 0% | 54.6684 | 0 | 0 | 116.4085 | 116.4085 | 0% | 12.28% | 12.28% | 80% | 9.826% | 5.3715 | 12.0233 | 6 | 32.2291 | 11.8786 | 27.69% | 27.69%
1 | 19 | 19 | 446 | 14 | -4.6 | 0.64 | 101.58 | 102.22 | 101.58 | 50.79 | 19 | 446 | 840 | 18.7397 | -20.2888 | -6.73 | 814.284 | 13.4592 | -21.8885 | 20.0812 | 20.0812 | 21.8579 | 201.8579 | 30.7773 | 1.6015 | 1.6015 | 86.704 | 88.3054 | -1.1546 | 0% | 39.9317 | 0 | 0 | 114.8606 | 114.8606 | 0% | 12.31% | 12.31% | 80% | 9.852% | 3.934 | 11.9122 | 6 | 23.6043 | 8.6998 | 20.55% | 20.55%
1 | 19 | 19 | 447 | 15 | -4 | 2.58 | 86.31 | 88.89 | 86.31 | 43.16 | 19 | 447 | 900 | 18.7397 | -20.2888 | -6.73 | 874.284 | 14.4592 | -36.8885 | 15.1333 | 15.1333 | 35.679 | 215.679 | 42.3484 | 7.3039 | 7.3039 | 73.6702 | 80.9741 | -1.3132 | 0% | 36.6165 | 0 | 0 | 134.2716 | 134.2716 | 0% | 12.3% | 12.3% | 80% | 9.841% | 3.6034 | 11.6918 | 6 | 21.6203 | 7.9686 | 16.1% | 16.1%
1 | 19 | 19 | 448 | 16 | -3.9 | 9.08 | 56.94 | 66.02 | 56.94 | 28.47 | 19 | 448 | 960 | 18.7397 | -20.2888 | -6.73 | 934.284 | 15.4592 | -51.8885 | 8.2659 | 8.2659 | 48.2229 | 228.2229 | 55.3986 | 0 | 0 | 48.6013 | 48.6013 | -2.7183 | 0% | 21.9775 | 0 | 0 | 132.3099 | 132.3099 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 449 | 17 | -3.9 | 1.58 | 32.03 | 33.61 | 32.03 | 16.02 | 19 | 449 | 1020 | 18.7397 | -20.2888 | -6.73 | 994.284 | 16.4592 | -66.8885 | -0.031444 | 0 | 59.5799 | 239.5799 | 69.0205 | 0 | 0 | 27.3393 | 27.3393 | -5.4576 | 0% | 12.3628 | 0 | 0 | 129.3133 | 129.3133 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 450 | 18 | -3.8 | 0 | 7.5 | 7.5 | 7.5 | 3.75 | 19 | 450 | 1080 | 18.7397 | -20.2888 | -6.73 | 1054.284 | 17.4592 | -81.8885 | -9.3257 | 0 | 59.5799 | 239.5799 | 69.0205 | 0 | 0 | 6.4017 | 6.4017 | -25.8979 | 0% | 2.8948 | 0 | 0 | 126.6778 | 126.6778 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 451 | 19 | -3.9 | 0 | 0 | 0 | 0 | 0 | 19 | 451 | 1140 | 18.7397 | -20.2888 | -6.73 | 1114.284 | 18.4592 | -96.8885 | -19.2518 | 0 | 59.5799 | 239.5799 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.7641 | 124.7641 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 452 | 20 | -3.9 | 0 | 0 | 0 | 0 | 0 | 19 | 452 | 1200 | 18.7397 | -20.2888 | -6.73 | 1174.284 | 19.4592 | -111.8885 | -29.4817 | 0 | 59.5799 | 239.5799 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 122.6297 | 122.6297 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 453 | 21 | -4.4 | 0 | 0 | 0 | 0 | 0 | 19 | 453 | 1260 | 18.7397 | -20.2888 | -6.73 | 1234.284 | 20.4592 | -126.8885 | -39.6615 | 0 | 59.5799 | 239.5799 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6479 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 454 | 22 | -4.4 | 0 | 0 | 0 | 0 | 0 | 19 | 454 | 1320 | 18.7397 | -20.2888 | -6.73 | 1294.284 | 21.4592 | -141.8885 | -49.2952 | 0 | 59.5799 | 239.5799 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.1323 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 455 | 23 | -4.3 | 0 | 0 | 0 | 0 | 0 | 19 | 455 | 1380 | 18.7397 | -20.2888 | -6.73 | 1354.284 | 22.4592 | -156.8885 | -57.508 | 0 | 59.5799 | 239.5799 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8024 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
1 | 19 | 19 | 456 | 24 | -4.3 | 0 | 0 | 0 | 0 | 0 | 19 | 456 | 1440 | 18.7397 | -20.2888 | -6.73 | 1414.284 | 23.4592 | -171.8885 | -62.6969 | 0 | 59.5799 | 239.5799 | 69.0205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6248 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 457 | 1 | -4.2 | 0 | 0 | 0 | 0 | 0 | 20 | 457 | 60 | 19.726 | -20.0868 | -6.7975 | 34.284 | 0.45811 | 173.1284 | -62.7254 | 0 | 59.9005 | 120.0995 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.8378 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 458 | 2 | -4.2 | 0 | 0 | 0 | 0 | 0 | 20 | 458 | 120 | 19.726 | -20.0868 | -6.7975 | 94.284 | 1.4581 | 158.1284 | -57.9025 | 0 | 59.9005 | 120.0995 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5994 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 459 | 3 | -4.2 | 0 | 0 | 0 | 0 | 0 | 20 | 459 | 180 | 19.726 | -20.0868 | -6.7975 | 154.284 | 2.4581 | 143.1284 | -49.8887 | 0 | 59.9005 | 120.0995 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.361 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 460 | 4 | -4.1 | 0 | 0 | 0 | 0 | 0 | 20 | 460 | 240 | 19.726 | -20.0868 | -6.7975 | 214.284 | 3.4581 | 128.1284 | -40.3443 | 0 | 59.9005 | 120.0995 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2086 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 461 | 5 | -4.1 | 0 | 0 | 0 | 0 | 0 | 20 | 461 | 300 | 19.726 | -20.0868 | -6.7975 | 274.284 | 4.4581 | 113.1284 | -30.1922 | 0 | 59.9005 | 120.0995 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7407 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 462 | 6 | -4.1 | 0 | 0 | 0 | 0 | 0 | 20 | 462 | 360 | 19.726 | -20.0868 | -6.7975 | 334.284 | 5.4581 | 98.1284 | -19.9505 | 0 | 59.9005 | 120.0995 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9986 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 463 | 7 | -4.1 | 0 | 0 | 0 | 0 | 0 | 20 | 463 | 420 | 19.726 | -20.0868 | -6.7975 | 394.284 | 6.4581 | 83.1284 | -9.9807 | 0 | 59.9005 | 120.0995 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.2532 | 140.2532 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 464 | 8 | -3.8 | 0 | 0 | 0 | 0 | 0 | 20 | 464 | 480 | 19.726 | -20.0868 | -6.7975 | 454.284 | 7.4581 | 68.1284 | -0.61133 | 0 | 59.9005 | 120.0995 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.8102 | 144.8102 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 465 | 9 | -3.7 | 0.28 | 2.5 | 2.78 | 2.5 | 1.25 | 20 | 465 | 540 | 19.726 | -20.0868 | -6.7975 | 514.284 | 8.4581 | 53.1284 | 7.7962 | 7.7962 | 49.3173 | 130.6827 | 56.4545 | 0 | 0 | 2.1339 | 2.1339 | -79.1837 | 0% | 0.96494 | 0 | 0 | 124.847 | 124.847 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 466 | 10 | -3.2 | 18.89 | 20 | 38.89 | 20 | 10 | 20 | 466 | 600 | 19.726 | -20.0868 | -6.7975 | 574.284 | 9.4581 | 38.1284 | 14.8132 | 14.8132 | 36.8559 | 143.1441 | 43.3002 | 53.7711 | 53.7711 | 17.0711 | 70.8422 | -1.5876 | 0% | 32.0348 | 0 | 0 | 127.9862 | 127.9862 | 0% | 12.28% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 467 | 11 | -3 | 57.69 | 41.47 | 99.16 | 41.47 | 20.74 | 20 | 467 | 660 | 19.726 | -20.0868 | -6.7975 | 634.284 | 10.4581 | 23.1284 | 19.9505 | 19.9505 | 23.1072 | 156.8928 | 31.5025 | 144.1567 | 144.1567 | 35.3969 | 179.5535 | -0.1368 | 0% | 81.1941 | 0 | 0 | 128.1249 | 128.1249 | 0% | 12.14% | 12.14% | 80% | 9.709% | 7.8835 | 11.3301 | 6 | 47.3012 | 17.4337 | 36.92% | 36.92%
1 | 20 | 20 | 468 | 12 | -2.8 | 87.86 | 102.97 | 190.83 | 102.97 | 51.49 | 20 | 468 | 720 | 19.726 | -20.0868 | -6.7975 | 694.284 | 11.4581 | 8.1284 | 22.7332 | 22.7332 | 8.278 | 171.722 | 23.2727 | 208.858 | 208.858 | 87.8904 | 296.7484 | 0.23644 | 23.64% | 134.1896 | 31.7275 | 22.2092 | 127.5136 | 127.5136 | 17.42% | 11.98% | 11.98% | 80% | 9.586% | 12.864 | 11.2586 | 6 | 77.1842 | 28.4477 | 60.53% | 60.53%
1 | 20 | 20 | 469 | 13 | -2 | 109.53 | 133.69 | 243.22 | 133.69 | 66.85 | 20 | 469 | 780 | 19.726 | -20.0868 | -6.7975 | 754.284 | 12.4581 | -6.8716 | 22.8476 | 22.8476 | 7.0038 | 187.0038 | 22.8799 | 259.8946 | 259.8946 | 114.1116 | 374.0062 | 0.35903 | 35.9% | 169.1256 | 60.7208 | 42.5046 | 108.805 | 108.805 | 39.06% | 11.87% | 11.87% | 85% | 10.09% | 17.0603 | 10.9754 | 6 | 102.3616 | 37.7273 | 94.08% | 94.08%
1 | 20 | 20 | 470 | 14 | -1.8 | 104.17 | 118.89 | 223.06 | 118.89 | 59.45 | 20 | 470 | 840 | 19.726 | -20.0868 | -6.7975 | 814.284 | 13.4581 | -21.8716 | 20.2799 | 20.2799 | 21.9002 | 201.9002 | 30.6276 | 258.6154 | 258.6154 | 101.479 | 360.0944 | 0.34322 | 34.32% | 162.8347 | 55.8885 | 39.122 | 107.1636 | 107.1636 | 36.51% | 11.88% | 11.88% | 85% | 10.1% | 16.4423 | 10.9053 | 6 | 98.6537 | 36.3606 | 92.06% | 92.06%
1 | 20 | 20 | 471 | 15 | -1.6 | 86.39 | 83.81 | 170.2 | 83.81 | 41.91 | 20 | 471 | 900 | 19.726 | -20.0868 | -6.7975 | 874.284 | 14.4581 | -36.8716 | 15.3228 | 15.3228 | 35.7534 | 215.7534 | 42.2427 | 242.0184 | 242.0184 | 71.5363 | 313.5547 | 0.27642 | 27.64% | 141.7894 | 39.1935 | 27.4354 | 103.2682 | 103.2682 | 26.57% | 11.93% | 11.93% | 85% | 10.14% | 14.378 | 10.8355 | 6 | 86.2682 | 31.7957 | 83.54% | 83.54%
1 | 20 | 20 | 472 | 16 | -1.7 | 61.94 | 67.97 | 129.91 | 67.97 | 33.99 | 20 | 472 | 960 | 19.726 | -20.0868 | -6.7975 | 934.284 | 15.4581 | -51.8716 | 8.4439 | 8.4439 | 48.3206 | 228.3206 | 55.3241 | 0 | 0 | 58.016 | 58.016 | -2.0517 | 0% | 26.2348 | 0 | 0 | 142.3127 | 142.3127 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 473 | 17 | -1.9 | 25.19 | 35 | 60.19 | 35 | 17.5 | 20 | 473 | 1020 | 19.726 | -20.0868 | -6.7975 | 994.284 | 16.4581 | -66.8716 | 0.13543 | 0.13543 | 59.7337 | 239.7337 | 69.0185 | 0 | 0 | 29.8744 | 29.8744 | -4.7584 | 0% | 13.5092 | 0 | 0 | 136.8548 | 136.8548 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 474 | 18 | -1.9 | 0 | 4.53 | 4.53 | 4.53 | 2.27 | 20 | 474 | 1080 | 19.726 | -20.0868 | -6.7975 | 1054.284 | 17.4581 | -81.8716 | -9.168 | 0 | 59.9005 | 239.9005 | 69.23 | 0 | 0 | 3.8666 | 3.8666 | -42.1725 | 0% | 1.7485 | 0 | 0 | 130.7499 | 130.7499 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 475 | 19 | -1.9 | 0 | 0 | 0 | 0 | 0 | 20 | 475 | 1140 | 19.726 | -20.0868 | -6.7975 | 1114.284 | 18.4581 | -96.8716 | -19.1002 | 0 | 59.9005 | 239.9005 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.0609 | 128.0609 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 476 | 20 | -2 | 0 | 0 | 0 | 0 | 0 | 20 | 476 | 1200 | 19.726 | -20.0868 | -6.7975 | 1174.284 | 19.4581 | -111.8716 | -29.332 | 0 | 59.9005 | 239.9005 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.4379 | 124.4379 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 477 | 21 | -2 | 0 | 0 | 0 | 0 | 0 | 20 | 477 | 1260 | 19.726 | -20.0868 | -6.7975 | 1234.284 | 20.4581 | -126.8716 | -39.5081 | 0 | 59.9005 | 239.9005 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4135 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 478 | 22 | -2 | 0 | 0 | 0 | 0 | 0 | 20 | 478 | 1320 | 19.726 | -20.0868 | -6.7975 | 1294.284 | 21.4581 | -141.8716 | -49.1309 | 0 | 59.9005 | 239.9005 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2002 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 479 | 23 | -1.8 | 0 | 0 | 0 | 0 | 0 | 20 | 479 | 1380 | 19.726 | -20.0868 | -6.7975 | 1354.284 | 22.4581 | -156.8716 | -57.325 | 0 | 59.9005 | 239.9005 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.657 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 20 | 20 | 480 | 24 | -1.6 | 0 | 0 | 0 | 0 | 0 | 20 | 480 | 1440 | 19.726 | -20.0868 | -6.7975 | 1414.284 | 23.4581 | -171.8716 | -62.496 | 0 | 59.9005 | 239.9005 | 69.23 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1138 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 481 | 1 | -2 | 0 | 0 | 0 | 0 | 0 | 21 | 481 | 60 | 20.7123 | -19.8789 | -6.8546 | 34.284 | 0.45716 | 173.1426 | -62.5232 | 0 | 60.2297 | 119.7703 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.1472 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 482 | 2 | -1.7 | 0 | 0 | 0 | 0 | 0 | 21 | 482 | 120 | 20.7123 | -19.8789 | -6.8546 | 94.284 | 1.4572 | 158.1426 | -57.7264 | 0 | 60.2297 | 119.7703 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3085 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 483 | 3 | -1.8 | 0 | 0 | 0 | 0 | 0 | 21 | 483 | 180 | 20.7123 | -19.8789 | -6.8546 | 154.284 | 2.4572 | 143.1426 | -49.7369 | 0 | 60.2297 | 119.7703 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0795 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 484 | 4 | -1.9 | 0 | 0 | 0 | 0 | 0 | 21 | 484 | 240 | 20.7123 | -19.8789 | -6.8546 | 214.284 | 3.4572 | 128.1426 | -40.2065 | 0 | 60.2297 | 119.7703 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2319 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 485 | 5 | -1.8 | 0 | 0 | 0 | 0 | 0 | 21 | 485 | 300 | 20.7123 | -19.8789 | -6.8546 | 274.284 | 4.4572 | 113.1426 | -30.0594 | 0 | 60.2297 | 119.7703 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2356 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 486 | 6 | -1.8 | 0 | 0 | 0 | 0 | 0 | 21 | 486 | 360 | 20.7123 | -19.8789 | -6.8546 | 334.284 | 5.4572 | 98.1426 | -19.8161 | 0 | 60.2297 | 119.7703 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.8826 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 487 | 7 | -1.8 | 0 | 0 | 0 | 0 | 0 | 21 | 487 | 420 | 20.7123 | -19.8789 | -6.8546 | 394.284 | 6.4572 | 83.1426 | -9.8395 | 0 | 60.2297 | 119.7703 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.5378 | 149.5378 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 488 | 8 | -1.2 | 0 | 0 | 0 | 0 | 0 | 21 | 488 | 480 | 20.7123 | -19.8789 | -6.8546 | 454.284 | 7.4572 | 68.1426 | -0.45934 | 0 | 60.2297 | 119.7703 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 155.7052 | 155.7052 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 489 | 9 | -1 | 0.14 | 4.03 | 4.17 | 4.03 | 2.02 | 21 | 489 | 540 | 20.7123 | -19.8789 | -6.8546 | 514.284 | 8.4572 | 53.1426 | 7.962 | 7.962 | 49.4447 | 130.5553 | 56.4089 | 0 | 0 | 3.4398 | 3.4398 | -46.8535 | 0% | 1.5555 | 0 | 0 | 135.957 | 135.957 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 490 | 10 | -0.3 | 31.67 | 37.92 | 69.59 | 37.92 | 18.96 | 21 | 490 | 600 | 20.7123 | -19.8789 | -6.8546 | 574.284 | 9.4572 | 38.1426 | 14.9943 | 14.9943 | 36.9625 | 143.0375 | 43.222 | 89.2003 | 89.2003 | 32.3667 | 121.567 | -0.53023 | 0% | 54.9726 | 0 | 0 | 140.4051 | 140.4051 | 0% | 12.11% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 491 | 11 | 0.6 | 85.97 | 84.31 | 170.28 | 84.31 | 42.16 | 21 | 491 | 660 | 20.7123 | -19.8789 | -6.8546 | 634.284 | 10.4572 | 23.1426 | 20.1459 | 20.1459 | 23.1843 | 156.8157 | 31.3758 | 213.1132 | 213.1132 | 71.9631 | 285.0763 | 0.24282 | 24.28% | 128.9115 | 31.3026 | 21.9118 | 141.6843 | 141.6843 | 15.47% | 11.9% | 11.9% | 80% | 9.521% | 12.2738 | 10.0859 | 6 | 73.6431 | 27.1425 | 51.98% | 51.98%
1 | 21 | 21 | 492 | 12 | 1.1 | 33.25 | 164.25 | 197.5 | 164.25 | 82.13 | 21 | 492 | 720 | 20.7123 | -19.8789 | -6.8546 | 694.284 | 11.4572 | 8.1426 | 22.9386 | 22.9386 | 8.3162 | 171.6838 | 23.0835 | 78.4818 | 78.4818 | 140.1961 | 218.678 | 0.078048 | 7.805% | 98.8862 | 7.7179 | 5.4025 | 135.7226 | 135.7226 | 3.981% | 11.96% | 11.96% | 80% | 9.565% | 9.4585 | 9.9203 | 6 | 56.7509 | 20.9166 | 41.81% | 41.81%
1 | 21 | 21 | 493 | 13 | 1.3 | 66.75 | 169.08 | 235.83 | 169.08 | 84.54 | 21 | 493 | 780 | 20.7123 | -19.8789 | -6.8546 | 754.284 | 12.4572 | -6.8574 | 23.0559 | 23.0559 | 7.0093 | 187.0093 | 22.6779 | 157.2642 | 157.2642 | 144.3188 | 301.583 | 0.27924 | 27.92% | 136.3758 | 38.0814 | 26.657 | 114.5611 | 114.5611 | 23.27% | 11.86% | 11.86% | 85% | 10.08% | 13.7534 | 9.8546 | 6 | 82.5204 | 30.4144 | 72.03% | 72.03%
1 | 21 | 21 | 494 | 14 | 1.2 | 46.03 | 139.44 | 185.47 | 139.44 | 69.72 | 21 | 494 | 840 | 20.7123 | -19.8789 | -6.8546 | 814.284 | 13.4572 | -21.8574 | 20.4837 | 20.4837 | 21.9467 | 201.9467 | 30.4762 | 113.3636 | 113.3636 | 119.0195 | 232.3831 | 0.12192 | 12.19% | 105.0836 | 12.8116 | 8.9681 | 131.2106 | 131.2106 | 6.835% | 11.94% | 11.94% | 80% | 9.551% | 10.0367 | 9.8874 | 6 | 60.2201 | 22.1952 | 45.9% | 45.9%
1 | 21 | 21 | 495 | 15 | 3.4 | 23.33 | 115.47 | 138.8 | 115.47 | 57.74 | 21 | 495 | 900 | 20.7123 | -19.8789 | -6.8546 | 874.284 | 14.4572 | -36.8574 | 15.5166 | 15.5166 | 35.8327 | 215.8327 | 42.1371 | 64.6694 | 64.6694 | 98.5598 | 163.2292 | -0.13419 | 0% | 73.8123 | 0 | 0 | 150.3574 | 150.3574 | 0% | 11.93% | 11.93% | 80% | 9.547% | 7.0466 | 9.181 | 6 | 42.2798 | 15.583 | 28.12% | 28.12%
1 | 21 | 21 | 496 | 16 | 3.2 | 3.69 | 57.97 | 61.66 | 57.97 | 28.99 | 21 | 496 | 960 | 20.7123 | -19.8789 | -6.8546 | 934.284 | 15.4572 | -51.8574 | 8.6256 | 8.6256 | 48.4238 | 228.4238 | 55.2505 | 0 | 0 | 49.4805 | 49.4805 | -2.3008 | 0% | 22.3751 | 0 | 0 | 144.2204 | 144.2204 | 0% | 12.05% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 497 | 17 | 3.7 | 0.56 | 22.58 | 23.14 | 22.58 | 11.29 | 21 | 497 | 1020 | 20.7123 | -19.8789 | -6.8546 | 994.284 | 16.4572 | -66.8574 | 0.30539 | 0.30539 | 59.8542 | 239.8542 | 68.9689 | 0 | 0 | 19.2732 | 19.2732 | -7.1041 | 0% | 8.7154 | 0 | 0 | 140.7384 | 140.7384 | 0% | 12.05% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 498 | 18 | 3.1 | 0 | 6.67 | 6.67 | 6.67 | 3.34 | 21 | 498 | 1080 | 20.7123 | -19.8789 | -6.8546 | 1054.284 | 17.4572 | -81.8574 | -9.0076 | 0 | 60.2297 | 240.2297 | 69.4457 | 0 | 0 | 5.6932 | 5.6932 | -26.2226 | 0% | 2.5745 | 0 | 0 | 136.3957 | 136.3957 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 499 | 19 | 3.3 | 0 | 0 | 0 | 0 | 0 | 21 | 499 | 1140 | 20.7123 | -19.8789 | -6.8546 | 1114.284 | 18.4572 | -96.8574 | -18.9461 | 0 | 60.2297 | 240.2297 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.1358 | 134.1358 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 500 | 20 | 3.5 | 0 | 0 | 0 | 0 | 0 | 21 | 500 | 1200 | 20.7123 | -19.8789 | -6.8546 | 1174.284 | 19.4572 | -111.8574 | -29.1797 | 0 | 60.2297 | 240.2297 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.768 | 130.768 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 501 | 21 | 3.5 | 0 | 0 | 0 | 0 | 0 | 21 | 501 | 1260 | 20.7123 | -19.8789 | -6.8546 | 1234.284 | 20.4572 | -126.8574 | -39.352 | 0 | 60.2297 | 240.2297 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0926 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 502 | 22 | 3.7 | 0 | 0 | 0 | 0 | 0 | 21 | 502 | 1320 | 20.7123 | -19.8789 | -6.8546 | 1294.284 | 21.4572 | -141.8574 | -48.9634 | 0 | 60.2297 | 240.2297 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6047 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 503 | 23 | 3.7 | 0 | 0 | 0 | 0 | 0 | 21 | 503 | 1380 | 20.7123 | -19.8789 | -6.8546 | 1354.284 | 22.4572 | -156.8574 | -57.138 | 0 | 60.2297 | 240.2297 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2233 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
1 | 21 | 21 | 504 | 24 | 3.2 | 0 | 0 | 0 | 0 | 0 | 21 | 504 | 1440 | 20.7123 | -19.8789 | -6.8546 | 1414.284 | 23.4572 | -171.8574 | -62.2899 | 0 | 60.2297 | 240.2297 | 69.4457 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6039 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 505 | 1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 22 | 505 | 60 | 21.6986 | -19.6651 | -6.9012 | 34.284 | 0.45638 | 173.1543 | -62.3147 | 0 | 60.5675 | 119.4325 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9661 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 506 | 2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 22 | 506 | 120 | 21.6986 | -19.6651 | -6.9012 | 94.284 | 1.4564 | 158.1543 | -57.5437 | 0 | 60.5675 | 119.4325 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.524 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 507 | 3 | 3.2 | 0 | 0 | 0 | 0 | 0 | 22 | 507 | 180 | 21.6986 | -19.6651 | -6.9012 | 154.284 | 2.4564 | 143.1543 | -49.5787 | 0 | 60.5675 | 119.4325 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.2343 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 508 | 4 | 3.1 | 0 | 0 | 0 | 0 | 0 | 22 | 508 | 240 | 21.6986 | -19.6651 | -6.9012 | 214.284 | 3.4564 | 128.1543 | -40.0625 | 0 | 60.5675 | 119.4325 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3867 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 509 | 5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 22 | 509 | 300 | 21.6986 | -19.6651 | -6.9012 | 274.284 | 4.4564 | 113.1543 | -29.9206 | 0 | 60.5675 | 119.4325 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6927 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 510 | 6 | 2.7 | 0 | 0 | 0 | 0 | 0 | 22 | 510 | 360 | 21.6986 | -19.6651 | -6.9012 | 334.284 | 5.4564 | 98.1543 | -19.6757 | 0 | 60.5675 | 119.4325 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.9813 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 511 | 7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 22 | 511 | 420 | 21.6986 | -19.6651 | -6.9012 | 394.284 | 6.4564 | 83.1543 | -9.6924 | 0 | 60.5675 | 119.4325 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.9432 | 148.9432 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 512 | 8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 22 | 512 | 480 | 21.6986 | -19.6651 | -6.9012 | 454.284 | 7.4564 | 68.1543 | -0.30129 | 0 | 60.5675 | 119.4325 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 152.336 | 152.336 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 513 | 9 | 2.4 | 0.28 | 5.83 | 6.11 | 5.83 | 2.92 | 22 | 513 | 540 | 21.6986 | -19.6651 | -6.9012 | 514.284 | 8.4564 | 53.1543 | 8.1339 | 8.1339 | 49.5734 | 130.4266 | 56.3599 | 0 | 0 | 4.9762 | 4.9762 | -30.4588 | 0% | 2.2502 | 0 | 0 | 132.6638 | 132.6638 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 514 | 10 | 3.2 | 24.08 | 32.86 | 56.94 | 32.86 | 16.43 | 22 | 514 | 600 | 21.6986 | -19.6651 | -6.9012 | 574.284 | 9.4564 | 38.1543 | 15.1816 | 15.1816 | 37.0697 | 142.9303 | 43.1397 | 67.0954 | 67.0954 | 28.0478 | 95.1431 | -0.81068 | 0% | 43.0237 | 0 | 0 | 136.5212 | 136.5212 | 0% | 12% | 12% | 80% | 9.603% | 4.1314 | 9.2438 | 6 | 24.7885 | 9.1362 | 18.16% | 18.16%
1 | 22 | 22 | 515 | 11 | 6.1 | 70.47 | 70.56 | 141.03 | 70.56 | 35.28 | 22 | 515 | 660 | 21.6986 | -19.6651 | -6.9012 | 634.284 | 10.4564 | 23.1543 | 20.3475 | 20.3475 | 23.2608 | 156.7392 | 31.2442 | 173.2731 | 173.2731 | 60.2267 | 233.4998 | 0.17597 | 17.6% | 105.5886 | 18.58 | 13.006 | 141.1929 | 141.1929 | 9.212% | 11.79% | 11.79% | 80% | 9.428% | 9.955 | 8.3603 | 6 | 59.7298 | 22.0145 | 42.3% | 42.3%
1 | 22 | 22 | 516 | 12 | 5.5 | 37.58 | 99.72 | 137.3 | 99.72 | 49.86 | 22 | 516 | 720 | 21.6986 | -19.6651 | -6.9012 | 694.284 | 11.4564 | 8.1543 | 23.15 | 23.15 | 8.3525 | 171.6475 | 22.8883 | 88.0633 | 88.0633 | 85.1163 | 173.1796 | -0.05107 | 0% | 78.3118 | 0 | 0 | 133.8236 | 133.8236 | 0% | 11.85% | 11.85% | 80% | 9.482% | 7.4251 | 8.5383 | 6 | 44.5509 | 16.42 | 33.29% | 33.29%
1 | 22 | 22 | 517 | 13 | 4.6 | 8.06 | 123.06 | 131.12 | 123.06 | 61.53 | 22 | 517 | 780 | 21.6986 | -19.6651 | -6.9012 | 754.284 | 12.4564 | -6.8457 | 23.2698 | 23.2698 | 7.0181 | 187.0181 | 22.4714 | 18.8528 | 18.8528 | 105.0383 | 123.8911 | -0.40869 | 0% | 56.0235 | 0 | 0 | 130.6629 | 130.6629 | 0% | 11.92% | 11.92% | 80% | 9.54% | 5.3445 | 8.8099 | 6 | 32.067 | 11.8189 | 24.54% | 24.54%
1 | 22 | 22 | 518 | 14 | 4.2 | 13.42 | 123.69 | 137.11 | 123.69 | 61.85 | 22 | 518 | 840 | 21.6986 | -19.6651 | -6.9012 | 814.284 | 13.4564 | -21.8457 | 20.6923 | 20.6923 | 21.9976 | 201.9976 | 30.3232 | 32.7835 | 32.7835 | 105.576 | 138.3595 | -0.28885 | 0% | 62.5662 | 0 | 0 | 129.0325 | 129.0325 | 0% | 11.93% | 11.93% | 80% | 9.542% | 5.9698 | 8.9325 | 6 | 35.8188 | 13.2017 | 27.76% | 27.76%
1 | 22 | 22 | 519 | 15 | 4.2 | 19.08 | 118.97 | 138.05 | 118.97 | 59.49 | 22 | 519 | 900 | 21.6986 | -19.6651 | -6.9012 | 874.284 | 14.4564 | -36.8457 | 15.7146 | 15.7146 | 35.917 | 215.917 | 42.0317 | 52.3255 | 52.3255 | 101.5472 | 153.8728 | -0.17867 | 0% | 69.5813 | 0 | 0 | 147.7652 | 147.7652 | 0% | 11.91% | 11.91% | 80% | 9.531% | 6.6316 | 8.9325 | 6 | 39.7899 | 14.6653 | 26.93% | 26.93%
1 | 22 | 22 | 520 | 16 | 3.7 | 2.5 | 84.92 | 87.42 | 84.92 | 42.46 | 22 | 520 | 960 | 21.6986 | -19.6651 | -6.9012 | 934.284 | 15.4564 | -51.8457 | 8.8108 | 8.8108 | 48.5323 | 228.5323 | 55.178 | 0 | 0 | 72.4838 | 72.4838 | -1.2987 | 0% | 32.7772 | 0 | 0 | 142.9619 | 142.9619 | 0% | 12% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 521 | 17 | 3.1 | 13.97 | 48.97 | 62.94 | 48.97 | 24.49 | 22 | 521 | 1020 | 21.6986 | -19.6651 | -6.9012 | 994.284 | 16.4564 | -66.8457 | 0.47836 | 0.47836 | 59.9803 | 239.9803 | 68.921 | 0 | 0 | 41.7985 | 41.7985 | -2.8772 | 0% | 18.9013 | 0 | 0 | 139.4683 | 139.4683 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 522 | 18 | 2.3 | 0 | 5.69 | 5.69 | 5.69 | 2.85 | 22 | 522 | 1080 | 21.6986 | -19.6651 | -6.9012 | 1054.284 | 17.4564 | -81.8457 | -8.8446 | 0 | 60.5675 | 240.5675 | 69.6673 | 0 | 0 | 4.8567 | 4.8567 | -31.2782 | 0% | 2.1962 | 0 | 0 | 132.7831 | 132.7831 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 523 | 19 | 1.9 | 0 | 0 | 0 | 0 | 0 | 22 | 523 | 1140 | 21.6986 | -19.6651 | -6.9012 | 1114.284 | 18.4564 | -96.8457 | -18.7896 | 0 | 60.5675 | 240.5675 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.8872 | 129.8872 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 524 | 20 | 1.5 | 0 | 0 | 0 | 0 | 0 | 22 | 524 | 1200 | 21.6986 | -19.6651 | -6.9012 | 1174.284 | 19.4564 | -111.8457 | -29.0251 | 0 | 60.5675 | 240.5675 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.1612 | 126.1612 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 525 | 21 | 1.4 | 0 | 0 | 0 | 0 | 0 | 22 | 525 | 1260 | 21.6986 | -19.6651 | -6.9012 | 1234.284 | 20.4564 | -126.8457 | -39.1933 | 0 | 60.5675 | 240.5675 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7311 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 526 | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 22 | 526 | 1320 | 21.6986 | -19.6651 | -6.9012 | 1294.284 | 21.4564 | -141.8457 | -48.7927 | 0 | 60.5675 | 240.5675 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0357 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 527 | 23 | 0.7 | 0 | 0 | 0 | 0 | 0 | 22 | 527 | 1380 | 21.6986 | -19.6651 | -6.9012 | 1354.284 | 22.4564 | -156.8457 | -56.9468 | 0 | 60.5675 | 240.5675 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2032 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
1 | 22 | 22 | 528 | 24 | 0.2 | 0 | 0 | 0 | 0 | 0 | 22 | 528 | 1440 | 21.6986 | -19.6651 | -6.9012 | 1414.284 | 23.4564 | -171.8457 | -62.0785 | 0 | 60.5675 | 240.5675 | 69.6673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6754 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 529 | 1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 23 | 529 | 60 | 22.6849 | -19.4456 | -6.9372 | 34.284 | 0.45578 | 173.1633 | -62.1 | 0 | 60.9138 | 119.0862 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2921 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 530 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 23 | 530 | 120 | 22.6849 | -19.4456 | -6.9372 | 94.284 | 1.4558 | 158.1633 | -57.3543 | 0 | 60.9138 | 119.0862 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.046 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 531 | 3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 23 | 531 | 180 | 22.6849 | -19.4456 | -6.9372 | 154.284 | 2.4558 | 143.1633 | -49.4139 | 0 | 60.9138 | 119.0862 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2571 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 532 | 4 | -0.1 | 0 | 0 | 0 | 0 | 0 | 23 | 532 | 240 | 22.6849 | -19.4456 | -6.9372 | 214.284 | 3.4558 | 128.1633 | -39.9123 | 0 | 60.9138 | 119.0862 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7143 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 533 | 5 | -0.2 | 0 | 0 | 0 | 0 | 0 | 23 | 533 | 300 | 22.6849 | -19.4456 | -6.9372 | 274.284 | 4.4558 | 113.1633 | -29.7758 | 0 | 60.9138 | 119.0862 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4706 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 534 | 6 | -0.2 | 0 | 0 | 0 | 0 | 0 | 23 | 534 | 360 | 22.6849 | -19.4456 | -6.9372 | 334.284 | 5.4558 | 98.1633 | -19.5293 | 0 | 60.9138 | 119.0862 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7097 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 535 | 7 | -0.4 | 0 | 0 | 0 | 0 | 0 | 23 | 535 | 420 | 22.6849 | -19.4456 | -6.9372 | 394.284 | 6.4558 | 83.1633 | -9.5392 | 0 | 60.9138 | 119.0862 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.7631 | 133.7631 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 536 | 8 | -0.5 | 0 | 0 | 0 | 0 | 0 | 23 | 536 | 480 | 22.6849 | -19.4456 | -6.9372 | 454.284 | 7.4558 | 68.1633 | -0.13722 | 0 | 60.9138 | 119.0862 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.0927 | 136.0927 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 537 | 9 | -0.9 | 0.08 | 2.97 | 3.05 | 2.97 | 1.49 | 23 | 537 | 540 | 22.6849 | -19.4456 | -6.9372 | 514.284 | 8.4558 | 53.1633 | 8.312 | 8.312 | 49.7033 | 130.2967 | 56.3074 | 0 | 0 | 2.5351 | 2.5351 | -63.7647 | 0% | 1.1464 | 0 | 0 | 115.1731 | 115.1731 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 538 | 10 | -0.5 | 0.83 | 31.19 | 32.02 | 31.19 | 15.6 | 23 | 538 | 600 | 22.6849 | -19.4456 | -6.9372 | 574.284 | 9.4558 | 38.1633 | 15.3752 | 15.3752 | 37.1774 | 142.8226 | 43.0534 | 2.2875 | 2.2875 | 26.6223 | 28.9098 | -4.8236 | 0% | 13.073 | 0 | 0 | 117.5914 | 117.5914 | 0% | 12.22% | 12.22% | 80% | 9.777% | 1.2782 | 10.4565 | 6 | 7.669 | 2.8265 | 6.522% | 6.522%
1 | 23 | 23 | 539 | 11 | 0.6 | 3.53 | 79.36 | 82.89 | 79.36 | 39.68 | 23 | 539 | 660 | 22.6849 | -19.4456 | -6.9372 | 634.284 | 10.4558 | 23.1633 | 20.5553 | 20.5553 | 23.3368 | 156.6632 | 31.1078 | 8.608 | 8.608 | 67.738 | 76.346 | -1.2914 | 0% | 34.5237 | 0 | 0 | 120.535 | 120.535 | 0% | 12.12% | 12.12% | 80% | 9.699% | 3.3486 | 10.0859 | 6 | 20.0913 | 7.405 | 16.67% | 16.67%
1 | 23 | 23 | 540 | 12 | 0.8 | 8.81 | 137.31 | 146.12 | 137.31 | 68.66 | 23 | 540 | 720 | 22.6849 | -19.4456 | -6.9372 | 694.284 | 11.4558 | 8.1633 | 23.3674 | 23.3674 | 8.387 | 171.613 | 22.6871 | 20.4937 | 20.4937 | 117.2014 | 137.6951 | -0.35426 | 0% | 62.2657 | 0 | 0 | 121.7064 | 121.7064 | 0% | 12.05% | 12.05% | 80% | 9.641% | 6.0031 | 10.0195 | 6 | 36.0187 | 13.2753 | 29.59% | 29.59%
1 | 23 | 23 | 541 | 13 | 0.8 | 34.92 | 171.47 | 206.39 | 171.47 | 85.74 | 23 | 541 | 780 | 22.6849 | -19.4456 | -6.9372 | 754.284 | 12.4558 | -6.8367 | 23.4892 | 23.4892 | 7.0302 | 187.0302 | 22.2602 | 81.0823 | 81.0823 | 146.3588 | 227.4411 | 0.10278 | 10.28% | 102.8489 | 10.5707 | 7.3995 | 103.4108 | 103.4108 | 7.155% | 11.96% | 11.96% | 80% | 9.565% | 9.8378 | 10.0195 | 6 | 59.0268 | 21.7554 | 57.08% | 57.08%
1 | 23 | 23 | 542 | 14 | 1 | 16.39 | 135 | 151.39 | 135 | 67.5 | 23 | 542 | 840 | 22.6849 | -19.4456 | -6.9372 | 814.284 | 13.4558 | -21.8367 | 20.9059 | 20.9059 | 22.0529 | 202.0529 | 30.1689 | 39.7102 | 39.7102 | 115.2297 | 154.9399 | -0.22217 | 0% | 70.0638 | 0 | 0 | 121.9419 | 121.9419 | 0% | 12.03% | 12.03% | 80% | 9.621% | 6.7408 | 9.9533 | 6 | 40.4445 | 14.9066 | 33.17% | 33.17%
1 | 23 | 23 | 543 | 15 | 0.8 | 23.25 | 77.5 | 100.75 | 77.5 | 38.75 | 23 | 543 | 900 | 22.6849 | -19.4456 | -6.9372 | 874.284 | 14.4558 | -36.8367 | 15.9167 | 15.9167 | 36.0064 | 216.0064 | 41.9266 | 63.0762 | 63.0762 | 66.1504 | 129.2266 | -0.43016 | 0% | 58.4363 | 0 | 0 | 139.1655 | 139.1655 | 0% | 12.06% | 12.06% | 80% | 9.648% | 5.6381 | 10.0195 | 6 | 33.8285 | 12.4681 | 24.31% | 24.31%
1 | 23 | 23 | 544 | 16 | 0.8 | 45.36 | 53.42 | 98.78 | 53.42 | 26.71 | 23 | 544 | 960 | 22.6849 | -19.4456 | -6.9372 | 934.284 | 15.4558 | -51.8367 | 8.9995 | 8.9995 | 48.6462 | 228.6462 | 55.1068 | 0 | 0 | 45.5968 | 45.5968 | -2.6938 | 0% | 20.6189 | 0 | 0 | 138.8706 | 138.8706 | 0% | 12.15% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 545 | 17 | 0.2 | 6.19 | 35.83 | 42.02 | 35.83 | 17.92 | 23 | 545 | 1020 | 22.6849 | -19.4456 | -6.9372 | 994.284 | 16.4558 | -66.8367 | 0.65423 | 0.65423 | 60.1119 | 240.1119 | 68.8748 | 0 | 0 | 30.5828 | 30.5828 | -4.4592 | 0% | 13.8296 | 0 | 0 | 133.7444 | 133.7444 | 0% | 12.19% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 546 | 18 | -0.1 | 0 | 7.31 | 7.31 | 7.31 | 3.66 | 23 | 546 | 1080 | 22.6849 | -19.4456 | -6.9372 | 1054.284 | 17.4558 | -81.8367 | -8.6791 | 0 | 60.9138 | 240.9138 | 69.8949 | 0 | 0 | 6.2395 | 6.2395 | -25.1124 | 0% | 2.8215 | 0 | 0 | 129.8959 | 129.8959 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 547 | 19 | -0.4 | 0 | 0 | 0 | 0 | 0 | 23 | 547 | 1140 | 22.6849 | -19.4456 | -6.9372 | 1114.284 | 18.4558 | -96.8367 | -18.6307 | 0 | 60.9138 | 240.9138 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.1377 | 127.1377 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 548 | 20 | -0.8 | 0 | 0 | 0 | 0 | 0 | 23 | 548 | 1200 | 22.6849 | -19.4456 | -6.9372 | 1174.284 | 19.4558 | -111.8367 | -28.8681 | 0 | 60.9138 | 240.9138 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.9719 | 123.9719 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 549 | 21 | -1 | 0 | 0 | 0 | 0 | 0 | 23 | 549 | 1260 | 22.6849 | -19.4456 | -6.9372 | 1234.284 | 20.4558 | -126.8367 | -39.0319 | 0 | 60.9138 | 240.9138 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.975 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 550 | 22 | -1.1 | 0 | 0 | 0 | 0 | 0 | 23 | 550 | 1320 | 22.6849 | -19.4456 | -6.9372 | 1294.284 | 21.4558 | -141.8367 | -48.6188 | 0 | 60.9138 | 240.9138 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.7068 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 551 | 23 | -1.5 | 0 | 0 | 0 | 0 | 0 | 23 | 551 | 1380 | 22.6849 | -19.4456 | -6.9372 | 1354.284 | 22.4558 | -156.8367 | -56.7516 | 0 | 60.9138 | 240.9138 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2227 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
1 | 23 | 23 | 552 | 24 | -2 | 0 | 0 | 0 | 0 | 0 | 23 | 552 | 1440 | 22.6849 | -19.4456 | -6.9372 | 1414.284 | 23.4558 | -171.8367 | -61.862 | 0 | 60.9138 | 240.9138 | 69.8949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.891 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 553 | 1 | -2.1 | 0 | 0 | 0 | 0 | 0 | 24 | 553 | 60 | 23.6712 | -19.2204 | -6.9623 | 34.284 | 0.45536 | 173.1696 | -61.8793 | 0 | 61.2683 | 118.7317 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6868 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 554 | 2 | -2.1 | 0 | 0 | 0 | 0 | 0 | 24 | 554 | 120 | 23.6712 | -19.2204 | -6.9623 | 94.284 | 1.4554 | 158.1696 | -57.1585 | 0 | 61.2683 | 118.7317 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6419 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 555 | 3 | -2.8 | 0 | 0 | 0 | 0 | 0 | 24 | 555 | 180 | 23.6712 | -19.2204 | -6.9623 | 154.284 | 2.4554 | 143.1696 | -49.2428 | 0 | 61.2683 | 118.7317 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6638 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 556 | 4 | -2.3 | 0 | 0 | 0 | 0 | 0 | 24 | 556 | 240 | 23.6712 | -19.2204 | -6.9623 | 214.284 | 3.4554 | 128.1696 | -39.7559 | 0 | 61.2683 | 118.7317 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.9018 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 557 | 5 | -2.7 | 0 | 0 | 0 | 0 | 0 | 24 | 557 | 300 | 23.6712 | -19.2204 | -6.9623 | 274.284 | 4.4554 | 113.1696 | -29.625 | 0 | 61.2683 | 118.7317 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2169 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 558 | 6 | -2.8 | 0 | 0 | 0 | 0 | 0 | 24 | 558 | 360 | 23.6712 | -19.2204 | -6.9623 | 334.284 | 5.4554 | 98.1696 | -19.3771 | 0 | 61.2683 | 118.7317 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7406 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 559 | 7 | -2.9 | 0 | 0 | 0 | 0 | 0 | 24 | 559 | 420 | 23.6712 | -19.2204 | -6.9623 | 394.284 | 6.4554 | 83.1696 | -9.3802 | 0 | 61.2683 | 118.7317 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.0311 | 131.0311 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 560 | 8 | -2.8 | 0 | 0 | 0 | 0 | 0 | 24 | 560 | 480 | 23.6712 | -19.2204 | -6.9623 | 454.284 | 7.4554 | 68.1696 | 0.032848 | 0.032848 | 61.2284 | 118.7716 | 70.0774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.7586 | 133.7586 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 561 | 9 | -3.3 | 0.14 | 5 | 5.14 | 5 | 2.5 | 24 | 561 | 540 | 23.6712 | -19.2204 | -6.9623 | 514.284 | 8.4554 | 53.1696 | 8.4962 | 8.4962 | 49.8345 | 130.1655 | 56.2515 | 0 | 0 | 4.2678 | 4.2678 | -38.9541 | 0% | 1.9299 | 0 | 0 | 112.9522 | 112.9522 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 562 | 10 | -3.1 | 0.64 | 32.03 | 32.67 | 32.03 | 16.02 | 24 | 562 | 600 | 23.6712 | -19.2204 | -6.9623 | 574.284 | 9.4554 | 38.1696 | 15.5749 | 15.5749 | 37.2856 | 142.7144 | 42.9633 | 1.7443 | 1.7443 | 27.3393 | 29.0836 | -5.0129 | 0% | 13.1516 | 0 | 0 | 115.6587 | 115.6587 | 0% | 12.33% | 12.33% | 80% | 9.865% | 1.2974 | 11.366 | 6 | 7.7846 | 2.8691 | 6.731% | 6.731%
1 | 24 | 24 | 563 | 11 | -2.8 | 3.42 | 77.42 | 80.84 | 77.42 | 38.71 | 24 | 563 | 660 | 23.6712 | -19.2204 | -6.9623 | 634.284 | 10.4554 | 23.1696 | 20.7693 | 20.7693 | 23.4122 | 156.5878 | 30.9666 | 8.2699 | 8.2699 | 66.0821 | 74.352 | -1.4612 | 0% | 33.622 | 0 | 0 | 117.693 | 117.693 | 0% | 12.26% | 12.26% | 80% | 9.81% | 3.2982 | 11.2586 | 6 | 19.789 | 7.2936 | 16.81% | 16.81%
1 | 24 | 24 | 564 | 12 | -2.3 | 14.36 | 104.81 | 119.17 | 104.81 | 52.41 | 24 | 564 | 720 | 23.6712 | -19.2204 | -6.9623 | 694.284 | 11.4554 | 8.1696 | 23.5907 | 23.5907 | 8.4195 | 171.5805 | 22.4801 | 33.1555 | 33.1555 | 89.4609 | 122.6164 | -0.55937 | 0% | 55.4471 | 0 | 0 | 118.5547 | 118.5547 | 0% | 12.18% | 12.18% | 80% | 9.746% | 5.404 | 11.0811 | 6 | 32.4241 | 11.9505 | 27.35% | 27.35%
1 | 24 | 24 | 565 | 13 | -2.1 | 101.75 | 65.83 | 167.58 | 65.83 | 32.92 | 24 | 565 | 780 | 23.6712 | -19.2204 | -6.9623 | 754.284 | 12.4554 | -6.8304 | 23.7141 | 23.7141 | 7.0456 | 187.0456 | 22.0446 | 234.5044 | 234.5044 | 56.1894 | 290.6938 | 0.23064 | 23.06% | 131.4517 | 30.3181 | 21.2227 | 121.527 | 121.527 | 17.46% | 11.97% | 11.97% | 80% | 9.577% | 12.5889 | 11.0106 | 6 | 75.5336 | 27.8393 | 62.15% | 62.15%
1 | 24 | 24 | 566 | 14 | -1.8 | 88.53 | 82.31 | 170.84 | 82.31 | 41.16 | 24 | 566 | 840 | 23.6712 | -19.2204 | -6.9623 | 814.284 | 13.4554 | -21.8304 | 21.1241 | 21.1241 | 22.1126 | 202.1126 | 30.0133 | 212.7111 | 212.7111 | 70.256 | 282.9671 | 0.21763 | 21.76% | 127.9577 | 27.8474 | 19.4932 | 122.411 | 122.411 | 15.92% | 11.97% | 11.97% | 80% | 9.578% | 12.2552 | 10.9053 | 6 | 73.5312 | 27.1013 | 60.07% | 60.07%
1 | 24 | 24 | 567 | 15 | -1.4 | 80.36 | 72.78 | 153.14 | 72.78 | 36.39 | 24 | 567 | 900 | 23.6712 | -19.2204 | -6.9623 | 874.284 | 14.4554 | -36.8304 | 16.1229 | 16.1229 | 36.1009 | 216.1009 | 41.822 | 215.6505 | 215.6505 | 62.1216 | 277.7721 | 0.21025 | 21.02% | 125.6085 | 26.4092 | 18.4864 | 100.6422 | 100.6422 | 18.37% | 11.97% | 11.97% | 80% | 9.573% | 12.0249 | 10.7659 | 6 | 72.1495 | 26.592 | 71.69% | 71.69%
1 | 24 | 24 | 568 | 16 | -1.3 | 68.69 | 82.58 | 151.27 | 82.58 | 41.29 | 24 | 568 | 960 | 23.6712 | -19.2204 | -6.9623 | 934.284 | 15.4554 | -51.8304 | 9.1915 | 9.1915 | 48.7655 | 228.7655 | 55.0369 | 0 | 0 | 70.4864 | 70.4864 | -1.5323 | 0% | 31.874 | 0 | 0 | 100.8333 | 100.8333 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 569 | 17 | -1.4 | 61.03 | 42.69 | 103.72 | 42.69 | 21.35 | 24 | 569 | 1020 | 23.6712 | -19.2204 | -6.9623 | 994.284 | 16.4554 | -66.8304 | 0.83292 | 0.83292 | 60.2491 | 240.2491 | 68.8304 | 0 | 0 | 36.4382 | 36.4382 | -3.7222 | 0% | 16.4774 | 0 | 0 | 140.26 | 140.26 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 570 | 18 | -1.5 | 0 | 6.03 | 6.03 | 6.03 | 3.02 | 24 | 570 | 1080 | 23.6712 | -19.2204 | -6.9623 | 1054.284 | 17.4554 | -81.8304 | -8.511 | 0 | 61.2683 | 241.2683 | 70.1284 | 0 | 0 | 5.1469 | 5.1469 | -31.2882 | 0% | 2.3274 | 0 | 0 | 131.0883 | 131.0883 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 571 | 19 | -1.5 | 0 | 0 | 0 | 0 | 0 | 24 | 571 | 1140 | 23.6712 | -19.2204 | -6.9623 | 1114.284 | 18.4554 | -96.8304 | -18.4695 | 0 | 61.2683 | 241.2683 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.978 | 127.978 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 572 | 20 | -1.7 | 0 | 0 | 0 | 0 | 0 | 24 | 572 | 1200 | 23.6712 | -19.2204 | -6.9623 | 1174.284 | 19.4554 | -111.8304 | -28.7087 | 0 | 61.2683 | 241.2683 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.4032 | 124.4032 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 573 | 21 | -1.8 | 0 | 0 | 0 | 0 | 0 | 24 | 573 | 1260 | 23.6712 | -19.2204 | -6.9623 | 1234.284 | 20.4554 | -126.8304 | -38.868 | 0 | 61.2683 | 241.2683 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6045 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 574 | 22 | -1.8 | 0 | 0 | 0 | 0 | 0 | 24 | 574 | 1320 | 23.6712 | -19.2204 | -6.9623 | 1294.284 | 21.4554 | -141.8304 | -48.4418 | 0 | 61.2683 | 241.2683 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3643 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 575 | 23 | -2.3 | 0 | 0 | 0 | 0 | 0 | 24 | 575 | 1380 | 23.6712 | -19.2204 | -6.9623 | 1354.284 | 22.4554 | -156.8304 | -56.5524 | 0 | 61.2683 | 241.2683 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0814 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
1 | 24 | 24 | 576 | 24 | -2.2 | 0 | 0 | 0 | 0 | 0 | 24 | 576 | 1440 | 23.6712 | -19.2204 | -6.9623 | 1414.284 | 23.4554 | -171.8304 | -61.6404 | 0 | 61.2683 | 241.2683 | 70.1284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8841 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 577 | 1 | -2.3 | 0 | 0 | 0 | 0 | 0 | 25 | 577 | 60 | 24.6575 | -18.9896 | -6.9766 | 34.284 | 0.45512 | 173.1731 | -61.6525 | 0 | 61.6308 | 118.3692 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5295 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 578 | 2 | -2.6 | 0 | 0 | 0 | 0 | 0 | 25 | 578 | 120 | 24.6575 | -18.9896 | -6.9766 | 94.284 | 1.4551 | 158.1731 | -56.9561 | 0 | 61.6308 | 118.3692 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.841 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 579 | 3 | -2.9 | 0 | 0 | 0 | 0 | 0 | 25 | 579 | 180 | 24.6575 | -18.9896 | -6.9766 | 154.284 | 2.4551 | 143.1731 | -49.0652 | 0 | 61.6308 | 118.3692 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.1525 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 580 | 4 | -3.2 | 0 | 0 | 0 | 0 | 0 | 25 | 580 | 240 | 24.6575 | -18.9896 | -6.9766 | 214.284 | 3.4551 | 128.1731 | -39.5933 | 0 | 61.6308 | 118.3692 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.6097 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 581 | 5 | -3 | 0 | 0 | 0 | 0 | 0 | 25 | 581 | 300 | 24.6575 | -18.9896 | -6.9766 | 274.284 | 4.4551 | 113.1731 | -29.4681 | 0 | 61.6308 | 118.3692 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6591 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 582 | 6 | -2.9 | 0 | 0 | 0 | 0 | 0 | 25 | 582 | 360 | 24.6575 | -18.9896 | -6.9766 | 334.284 | 5.4551 | 98.1731 | -19.2189 | 0 | 61.6308 | 118.3692 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.7535 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 583 | 7 | -2.8 | 0 | 0 | 0 | 0 | 0 | 25 | 583 | 420 | 24.6575 | -18.9896 | -6.9766 | 394.284 | 6.4551 | 83.1731 | -9.2152 | 0 | 61.6308 | 118.3692 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.7641 | 130.7641 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 584 | 8 | -2.6 | 0 | 0 | 0 | 0 | 0 | 25 | 584 | 480 | 24.6575 | -18.9896 | -6.9766 | 454.284 | 7.4551 | 68.1731 | 0.20888 | 0.20888 | 61.3777 | 118.6223 | 70.0437 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.2755 | 133.2755 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 585 | 9 | -2.4 | 0.19 | 4.44 | 4.63 | 4.44 | 2.22 | 25 | 585 | 540 | 24.6575 | -18.9896 | -6.9766 | 514.284 | 8.4551 | 53.1731 | 8.6864 | 8.6864 | 49.9667 | 130.0333 | 56.1922 | 0 | 0 | 3.7898 | 3.7898 | -43.3732 | 0% | 1.7137 | 0 | 0 | 113.1035 | 113.1035 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 586 | 10 | -2.1 | 8.69 | 34.25 | 42.94 | 34.25 | 17.13 | 25 | 586 | 600 | 24.6575 | -18.9896 | -6.9766 | 574.284 | 9.4551 | 38.1731 | 15.7807 | 15.7807 | 37.3941 | 142.6059 | 42.8692 | 23.4191 | 23.4191 | 29.2342 | 52.6533 | -2.3615 | 0% | 23.8098 | 0 | 0 | 115.1442 | 115.1442 | 0% | 12.26% | 12.26% | 80% | 9.808% | 2.3353 | 11.0106 | 6 | 14.0121 | 5.1644 | 12.17% | 12.17%
1 | 25 | 25 | 587 | 11 | -1.4 | 4.36 | 53.69 | 58.05 | 53.69 | 26.85 | 25 | 587 | 660 | 24.6575 | -18.9896 | -6.9766 | 634.284 | 10.4551 | 23.1731 | 20.9893 | 20.9893 | 23.4869 | 156.5131 | 30.8208 | 10.4531 | 10.4531 | 45.8273 | 56.2804 | -2.1265 | 0% | 25.45 | 0 | 0 | 114.7719 | 114.7719 | 0% | 12.23% | 12.23% | 80% | 9.782% | 2.4895 | 10.7659 | 6 | 14.9369 | 5.5053 | 13.01% | 13.01%
1 | 25 | 25 | 588 | 12 | -1.1 | 5.47 | 89.53 | 95 | 89.53 | 44.77 | 25 | 588 | 720 | 24.6575 | -18.9896 | -6.9766 | 694.284 | 11.4551 | 8.1731 | 23.8198 | 23.8198 | 8.4499 | 171.5501 | 22.2672 | 12.5342 | 12.5342 | 76.4186 | 88.9528 | -1.0417 | 0% | 40.2245 | 0 | 0 | 114.107 | 114.107 | 0% | 12.18% | 12.18% | 80% | 9.742% | 3.9186 | 10.6622 | 6 | 23.5114 | 8.6656 | 20.6% | 20.6%
1 | 25 | 25 | 589 | 13 | -0.6 | 2.97 | 93.42 | 96.39 | 93.42 | 46.71 | 25 | 589 | 780 | 24.6575 | -18.9896 | -6.9766 | 754.284 | 12.4551 | -6.8269 | 23.9443 | 23.9443 | 7.0644 | 187.0644 | 21.8247 | 6.7935 | 6.7935 | 79.739 | 86.5325 | -1.079 | 0% | 39.13 | 0 | 0 | 114.2686 | 114.2686 | 0% | 12.16% | 12.16% | 80% | 9.728% | 3.8067 | 10.4906 | 6 | 22.8401 | 8.4181 | 19.99% | 19.99%
1 | 25 | 25 | 590 | 14 | 0 | 2.22 | 91.86 | 94.08 | 91.86 | 45.93 | 25 | 590 | 840 | 24.6575 | -18.9896 | -6.9766 | 814.284 | 13.4551 | -21.8269 | 21.3471 | 21.3471 | 22.1768 | 202.1768 | 29.8568 | 5.2892 | 5.2892 | 78.4074 | 83.6966 | -1.1251 | 0% | 37.8476 | 0 | 0 | 114.5094 | 114.5094 | 0% | 12.14% | 12.14% | 80% | 9.712% | 3.6757 | 10.287 | 6 | 22.0544 | 8.1286 | 19.26% | 19.26%
1 | 25 | 25 | 591 | 15 | 1.9 | 2.86 | 134.92 | 137.78 | 134.92 | 67.46 | 25 | 591 | 900 | 24.6575 | -18.9896 | -6.9766 | 874.284 | 14.4551 | -36.8269 | 16.333 | 16.333 | 36.2005 | 216.2005 | 41.7181 | 7.5912 | 7.5912 | 115.1614 | 122.7526 | -0.47329 | 0% | 55.5087 | 0 | 0 | 139.4182 | 139.4182 | 0% | 12.03% | 12.03% | 80% | 9.621% | 5.3405 | 9.659 | 6 | 32.0428 | 11.81 | 22.98% | 22.98%
1 | 25 | 25 | 592 | 16 | 4.5 | 2.64 | 75.42 | 78.06 | 75.42 | 37.71 | 25 | 592 | 960 | 24.6575 | -18.9896 | -6.9766 | 934.284 | 15.4551 | -51.8269 | 9.3868 | 9.3868 | 48.8903 | 228.8903 | 54.9685 | 0 | 0 | 64.375 | 64.375 | -1.5336 | 0% | 29.1104 | 0 | 0 | 139.798 | 139.798 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 593 | 17 | 6.6 | 0.14 | 32.64 | 32.78 | 32.64 | 16.32 | 25 | 593 | 1020 | 24.6575 | -18.9896 | -6.9766 | 994.284 | 16.4551 | -66.8269 | 1.0143 | 1.0143 | 60.3919 | 240.3919 | 68.788 | 0 | 0 | 27.86 | 27.86 | -4.4169 | 0% | 12.5983 | 0 | 0 | 139.9698 | 139.9698 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 594 | 18 | 5.8 | 0 | 8.33 | 8.33 | 8.33 | 4.17 | 25 | 594 | 1080 | 24.6575 | -18.9896 | -6.9766 | 1054.284 | 17.4551 | -81.8269 | -8.3406 | 0 | 61.6308 | 241.6308 | 70.3677 | 0 | 0 | 7.1101 | 7.1101 | -19.9218 | 0% | 3.2152 | 0 | 0 | 136.5482 | 136.5482 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 595 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 25 | 595 | 1140 | 24.6575 | -18.9896 | -6.9766 | 1114.284 | 18.4551 | -96.8269 | -18.3061 | 0 | 61.6308 | 241.6308 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.7823 | 133.7823 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 596 | 20 | 5.3 | 0 | 0 | 0 | 0 | 0 | 25 | 596 | 1200 | 24.6575 | -18.9896 | -6.9766 | 1174.284 | 19.4551 | -111.8269 | -28.5472 | 0 | 61.6308 | 241.6308 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.4334 | 132.4334 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 597 | 21 | 4.8 | 0 | 0 | 0 | 0 | 0 | 25 | 597 | 1260 | 24.6575 | -18.9896 | -6.9766 | 1234.284 | 20.4551 | -126.8269 | -38.7015 | 0 | 61.6308 | 241.6308 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7532 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 598 | 22 | 3.9 | 0 | 0 | 0 | 0 | 0 | 25 | 598 | 1320 | 24.6575 | -18.9896 | -6.9766 | 1294.284 | 21.4551 | -141.8269 | -48.2617 | 0 | 61.6308 | 241.6308 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5179 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 599 | 23 | 2.7 | 0 | 0 | 0 | 0 | 0 | 25 | 599 | 1380 | 24.6575 | -18.9896 | -6.9766 | 1354.284 | 22.4551 | -156.8269 | -56.3492 | 0 | 61.6308 | 241.6308 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.201 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
1 | 25 | 25 | 600 | 24 | 1.4 | 0 | 0 | 0 | 0 | 0 | 25 | 600 | 1440 | 24.6575 | -18.9896 | -6.9766 | 1414.284 | 23.4551 | -171.8269 | -61.4138 | 0 | 61.6308 | 241.6308 | 70.3677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0365 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 601 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 26 | 601 | 60 | 25.6438 | -18.7532 | -6.9797 | 34.284 | 0.45507 | 173.1739 | -61.4198 | 0 | 62.0013 | 117.9987 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4678 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 602 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 26 | 602 | 120 | 25.6438 | -18.7532 | -6.9797 | 94.284 | 1.4551 | 158.1739 | -56.7473 | 0 | 62.0013 | 117.9987 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.9768 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 603 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 603 | 180 | 25.6438 | -18.7532 | -6.9797 | 154.284 | 2.4551 | 143.1739 | -48.8812 | 0 | 62.0013 | 117.9987 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4002 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 604 | 4 | -0.7 | 0 | 0 | 0 | 0 | 0 | 26 | 604 | 240 | 25.6438 | -18.7532 | -6.9797 | 214.284 | 3.4551 | 128.1739 | -39.4246 | 0 | 62.0013 | 117.9987 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.467 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 605 | 5 | -1.5 | 0 | 0 | 0 | 0 | 0 | 26 | 605 | 300 | 25.6438 | -18.7532 | -6.9797 | 274.284 | 4.4551 | 113.1739 | -29.3053 | 0 | 62.0013 | 117.9987 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9555 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 606 | 6 | -1.5 | 0 | 0 | 0 | 0 | 0 | 26 | 606 | 360 | 25.6438 | -18.7532 | -6.9797 | 334.284 | 5.4551 | 98.1739 | -19.0548 | 0 | 62.0013 | 117.9987 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9559 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 607 | 7 | -2.7 | 0 | 0 | 0 | 0 | 0 | 26 | 607 | 420 | 25.6438 | -18.7532 | -6.9797 | 394.284 | 6.4551 | 83.1739 | -9.0444 | 0 | 62.0013 | 117.9987 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.653 | 140.653 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 608 | 8 | -0.9 | 0 | 0 | 0 | 0 | 0 | 26 | 608 | 480 | 25.6438 | -18.7532 | -6.9797 | 454.284 | 7.4551 | 68.1739 | 0.39084 | 0.39084 | 61.5285 | 118.4715 | 70.0068 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.7272 | 147.7272 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 609 | 9 | -2.1 | 0.08 | 3.97 | 4.05 | 3.97 | 1.99 | 26 | 609 | 540 | 25.6438 | -18.7532 | -6.9797 | 514.284 | 8.4551 | 53.1739 | 8.8827 | 8.8827 | 50.1 | 129.9 | 56.1294 | 0 | 0 | 3.3886 | 3.3886 | -48.382 | 0% | 1.5323 | 0 | 0 | 125.9165 | 125.9165 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 610 | 10 | -1.1 | 16.67 | 38.81 | 55.48 | 38.81 | 19.41 | 26 | 610 | 600 | 25.6438 | -18.7532 | -6.9797 | 574.284 | 9.4551 | 38.1739 | 15.9926 | 15.9926 | 37.5029 | 142.4971 | 42.7713 | 44.415 | 44.415 | 33.1264 | 77.5414 | -1.3133 | 0% | 35.0642 | 0 | 0 | 130.3597 | 130.3597 | 0% | 12.19% | 12.19% | 80% | 9.752% | 3.4196 | 10.6622 | 6 | 20.5175 | 7.5621 | 15.74% | 15.74%
1 | 26 | 26 | 611 | 11 | 0.5 | 56.31 | 85.56 | 141.87 | 85.56 | 42.78 | 26 | 611 | 660 | 25.6438 | -18.7532 | -6.9797 | 634.284 | 10.4551 | 23.1739 | 21.2154 | 21.2154 | 23.5608 | 156.4392 | 30.6704 | 133.8395 | 133.8395 | 73.03 | 206.8695 | 0.029479 | 2.948% | 93.5464 | 2.7577 | 1.9304 | 133.8803 | 133.8803 | 1.442% | 11.99% | 11.99% | 80% | 9.591% | 8.9716 | 10.1193 | 6 | 53.8294 | 19.8398 | 40.21% | 40.21%
1 | 26 | 26 | 612 | 12 | 2.3 | 98.14 | 140.19 | 238.33 | 140.19 | 70.1 | 26 | 612 | 720 | 25.6438 | -18.7532 | -6.9797 | 694.284 | 11.4551 | 8.1739 | 24.0547 | 24.0547 | 8.4783 | 171.5217 | 22.0486 | 223.1614 | 223.1614 | 119.6596 | 342.8211 | 0.34949 | 34.95% | 155.0237 | 54.1798 | 37.9259 | 114.8419 | 114.8419 | 33.02% | 11.8% | 11.8% | 85% | 10.03% | 15.545 | 9.53 | 6 | 93.27 | 34.3764 | 81.22% | 81.22%
1 | 26 | 26 | 613 | 13 | 2.9 | 108.53 | 169.17 | 277.7 | 169.17 | 84.59 | 26 | 613 | 780 | 25.6438 | -18.7532 | -6.9797 | 754.284 | 12.4551 | -6.8261 | 24.1797 | 24.1797 | 7.0866 | 187.0866 | 21.6007 | 246.3577 | 246.3577 | 144.3956 | 390.7533 | 0.40898 | 40.9% | 176.6986 | 72.2669 | 50.5869 | 116.0782 | 116.0782 | 43.58% | 11.74% | 11.74% | 85% | 9.976% | 17.6281 | 9.3386 | 6 | 105.7686 | 38.983 | 91.12% | 91.12%
1 | 26 | 26 | 614 | 14 | 3.5 | 119.17 | 146.39 | 265.56 | 146.39 | 73.2 | 26 | 614 | 840 | 25.6438 | -18.7532 | -6.9797 | 814.284 | 13.4551 | -21.8261 | 21.5746 | 21.5746 | 22.2455 | 202.2455 | 29.6995 | 281.5117 | 281.5117 | 124.9517 | 406.4634 | 0.42783 | 42.78% | 183.8027 | 78.6369 | 55.0458 | 115.1908 | 115.1908 | 47.79% | 11.71% | 11.71% | 85% | 9.953% | 18.2935 | 9.1497 | 6 | 109.7607 | 40.4543 | 95.29% | 95.29%
1 | 26 | 26 | 615 | 15 | 2.8 | 78.81 | 138.69 | 217.5 | 138.69 | 69.35 | 26 | 615 | 900 | 25.6438 | -18.7532 | -6.9797 | 874.284 | 14.4551 | -36.8261 | 16.5469 | 16.5469 | 36.3053 | 216.3053 | 41.615 | 206.8827 | 206.8827 | 118.3793 | 325.262 | 0.3287 | 32.87% | 147.0835 | 48.3464 | 33.8425 | 109.9474 | 109.9474 | 30.78% | 11.8% | 11.8% | 85% | 10.03% | 14.7539 | 9.3703 | 6 | 88.5231 | 32.6268 | 80.51% | 80.51%
1 | 26 | 26 | 616 | 16 | 2.6 | 50.19 | 92.5 | 142.69 | 92.5 | 46.25 | 26 | 616 | 960 | 25.6438 | -18.7532 | -6.9797 | 934.284 | 15.4551 | -51.8261 | 9.5852 | 9.5852 | 49.0204 | 229.0204 | 54.9016 | 0 | 0 | 78.9537 | 78.9537 | -1.1602 | 0% | 35.7029 | 0 | 0 | 146.9249 | 146.9249 | 0% | 12.04% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 617 | 17 | 2.4 | 21.67 | 57.03 | 78.7 | 57.03 | 28.52 | 26 | 617 | 1020 | 25.6438 | -18.7532 | -6.9797 | 994.284 | 16.4551 | -66.8261 | 1.1984 | 1.1984 | 60.5401 | 240.5401 | 68.7476 | 0 | 0 | 48.6781 | 48.6781 | -2.3919 | 0% | 22.0123 | 0 | 0 | 141.6296 | 141.6296 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 618 | 18 | 2.1 | 0 | 11.53 | 11.53 | 11.53 | 5.77 | 26 | 618 | 1080 | 25.6438 | -18.7532 | -6.9797 | 1054.284 | 17.4551 | -81.8261 | -8.168 | 0 | 62.0013 | 242.0013 | 70.6127 | 0 | 0 | 9.8415 | 9.8415 | -15.078 | 0% | 4.4503 | 0 | 0 | 134.8103 | 134.8103 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 619 | 19 | 1.8 | 0 | 0 | 0 | 0 | 0 | 26 | 619 | 1140 | 25.6438 | -18.7532 | -6.9797 | 1114.284 | 18.4551 | -96.8261 | -18.1405 | 0 | 62.0013 | 242.0013 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.3211 | 131.3211 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 620 | 20 | 1.6 | 0 | 0 | 0 | 0 | 0 | 26 | 620 | 1200 | 25.6438 | -18.7532 | -6.9797 | 1174.284 | 19.4551 | -111.8261 | -28.3834 | 0 | 62.0013 | 242.0013 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.451 | 127.451 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 621 | 21 | 1.2 | 0 | 0 | 0 | 0 | 0 | 26 | 621 | 1260 | 25.6438 | -18.7532 | -6.9797 | 1234.284 | 20.4551 | -126.8261 | -38.5326 | 0 | 62.0013 | 242.0013 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0293 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 622 | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 26 | 622 | 1320 | 25.6438 | -18.7532 | -6.9797 | 1294.284 | 21.4551 | -141.8261 | -48.0786 | 0 | 62.0013 | 242.0013 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1411 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 623 | 23 | 1 | 0 | 0 | 0 | 0 | 0 | 26 | 623 | 1380 | 25.6438 | -18.7532 | -6.9797 | 1354.284 | 22.4551 | -156.8261 | -56.1422 | 0 | 62.0013 | 242.0013 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8881 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
1 | 26 | 26 | 624 | 24 | 1.1 | 0 | 0 | 0 | 0 | 0 | 26 | 624 | 1440 | 25.6438 | -18.7532 | -6.9797 | 1414.284 | 23.4551 | -171.8261 | -61.1822 | 0 | 62.0013 | 242.0013 | 70.6127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4828 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 625 | 1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 27 | 625 | 60 | 26.6301 | -18.5115 | -6.9717 | 34.284 | 0.45521 | 173.1719 | -61.1812 | 0 | 62.3795 | 117.6205 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3326 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 626 | 2 | 1.3 | 0 | 0 | 0 | 0 | 0 | 27 | 626 | 120 | 26.6301 | -18.5115 | -6.9717 | 94.284 | 1.4552 | 158.1719 | -56.5321 | 0 | 62.3795 | 117.6205 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9413 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 627 | 3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 27 | 627 | 180 | 26.6301 | -18.5115 | -6.9717 | 154.284 | 2.4552 | 143.1719 | -48.6909 | 0 | 62.3795 | 117.6205 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7023 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 628 | 4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 27 | 628 | 240 | 26.6301 | -18.5115 | -6.9717 | 214.284 | 3.4552 | 128.1719 | -39.2496 | 0 | 62.3795 | 117.6205 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3119 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 629 | 5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 27 | 629 | 300 | 26.6301 | -18.5115 | -6.9717 | 274.284 | 4.4552 | 113.1719 | -29.1364 | 0 | 62.3795 | 117.6205 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7804 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 630 | 6 | 0.2 | 0 | 0 | 0 | 0 | 0 | 27 | 630 | 360 | 26.6301 | -18.5115 | -6.9717 | 334.284 | 5.4552 | 98.1719 | -18.8849 | 0 | 62.3795 | 117.6205 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6397 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 631 | 7 | -0.5 | 0 | 0 | 0 | 0 | 0 | 27 | 631 | 420 | 26.6301 | -18.5115 | -6.9717 | 394.284 | 6.4552 | 83.1719 | -8.8677 | 0 | 62.3795 | 117.6205 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.0267 | 141.0267 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 632 | 8 | -0.2 | 0 | 0 | 0 | 0 | 0 | 27 | 632 | 480 | 26.6301 | -18.5115 | -6.9717 | 454.284 | 7.4552 | 68.1719 | 0.57868 | 0.57868 | 61.6808 | 118.3192 | 69.9668 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.7027 | 145.7027 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 633 | 9 | -0.3 | 0.28 | 4.64 | 4.92 | 4.64 | 2.32 | 27 | 633 | 540 | 26.6301 | -18.5115 | -6.9717 | 514.284 | 8.4552 | 53.1719 | 9.0849 | 9.0849 | 50.2342 | 129.7658 | 56.0632 | 0 | 0 | 3.9605 | 3.9605 | -40.1502 | 0% | 1.7909 | 0 | 0 | 125.7223 | 125.7223 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 634 | 10 | 1.6 | 11.19 | 33.81 | 45 | 33.81 | 16.91 | 27 | 634 | 600 | 26.6301 | -18.5115 | -6.9717 | 574.284 | 9.4552 | 38.1719 | 16.2105 | 16.2105 | 37.612 | 142.388 | 42.6696 | 29.4723 | 29.4723 | 28.8586 | 58.331 | -1.8965 | 0% | 26.3773 | 0 | 0 | 131.4472 | 131.4472 | 0% | 12.1% | 12.1% | 80% | 9.682% | 2.5539 | 9.7564 | 6 | 15.3232 | 5.6476 | 11.66% | 11.66%
1 | 27 | 27 | 635 | 11 | 3.4 | 52.5 | 77.69 | 130.19 | 77.69 | 38.85 | 27 | 635 | 660 | 26.6301 | -18.5115 | -6.9717 | 634.284 | 10.4552 | 23.1719 | 21.4474 | 21.4474 | 23.634 | 156.366 | 30.5155 | 123.6941 | 123.6941 | 66.3126 | 190.0067 | -0.0019735 | 0% | 85.921 | 0 | 0 | 135.9627 | 135.9627 | 0% | 11.91% | 11.91% | 80% | 9.527% | 8.1858 | 9.181 | 6 | 49.1149 | 18.1022 | 36.12% | 36.12%
1 | 27 | 27 | 636 | 12 | 5 | 103.19 | 122.78 | 225.97 | 122.78 | 61.39 | 27 | 636 | 720 | 26.6301 | -18.5115 | -6.9717 | 694.284 | 11.4552 | 8.1719 | 24.2953 | 24.2953 | 8.5045 | 171.4955 | 21.8242 | 232.8266 | 232.8266 | 104.7993 | 337.6259 | 0.36185 | 36.19% | 152.6744 | 55.2458 | 38.6721 | 117.2831 | 117.2831 | 32.97% | 11.73% | 11.73% | 85% | 9.973% | 15.2269 | 8.6885 | 6 | 91.3614 | 33.6729 | 77.9% | 77.9%
1 | 27 | 27 | 637 | 13 | 4.4 | 163.06 | 112.36 | 275.42 | 112.36 | 56.18 | 27 | 637 | 780 | 26.6301 | -18.5115 | -6.9717 | 754.284 | 12.4552 | -6.8281 | 24.4204 | 24.4204 | 7.1124 | 187.1124 | 21.3726 | 367.286 | 367.286 | 95.9053 | 463.1913 | 0.4786 | 47.86% | 209.4551 | 100.2447 | 70.1713 | 116.8677 | 116.8677 | 60.04% | 11.64% | 11.64% | 85% | 9.895% | 20.7252 | 8.8711 | 6 | 124.3514 | 45.832 | 106.4% | 106.4%
1 | 27 | 27 | 638 | 14 | 5.3 | 85.28 | 147.22 | 232.5 | 147.22 | 73.61 | 27 | 638 | 840 | 26.6301 | -18.5115 | -6.9717 | 814.284 | 13.4552 | -21.8281 | 21.8066 | 21.8066 | 22.3188 | 202.3188 | 29.5415 | 199.7267 | 199.7267 | 125.6601 | 325.3869 | 0.34744 | 34.74% | 147.1399 | 51.1217 | 35.7852 | 114.9985 | 114.9985 | 31.12% | 11.74% | 11.74% | 85% | 9.975% | 14.6777 | 8.5982 | 6 | 88.0665 | 32.4585 | 76.58% | 76.58%
1 | 27 | 27 | 639 | 15 | 5.9 | 40.19 | 141.03 | 181.22 | 141.03 | 70.52 | 27 | 639 | 900 | 26.6301 | -18.5115 | -6.9717 | 874.284 | 14.4552 | -36.8281 | 16.7646 | 16.7646 | 36.4152 | 216.4152 | 41.5129 | 104.3357 | 104.3357 | 120.3766 | 224.7123 | 0.14928 | 14.93% | 101.6149 | 15.1691 | 10.6184 | 110.8545 | 110.8545 | 9.579% | 11.8% | 11.8% | 80% | 9.439% | 9.5909 | 8.4194 | 6 | 57.5456 | 21.2095 | 51.91% | 51.91%
1 | 27 | 27 | 640 | 16 | 4.7 | 26.19 | 82.69 | 108.88 | 82.69 | 41.35 | 27 | 640 | 960 | 26.6301 | -18.5115 | -6.9717 | 934.284 | 15.4552 | -51.8281 | 9.7867 | 9.7867 | 49.156 | 229.156 | 54.8364 | 0 | 0 | 70.5803 | 70.5803 | -1.3213 | 0% | 31.9164 | 0 | 0 | 146.0942 | 146.0942 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 641 | 17 | 4 | 5.08 | 46.86 | 51.94 | 46.86 | 23.43 | 27 | 641 | 1020 | 26.6301 | -18.5115 | -6.9717 | 994.284 | 16.4552 | -66.8281 | 1.385 | 1.385 | 60.6939 | 240.6939 | 68.7092 | 0 | 0 | 39.9975 | 39.9975 | -2.9885 | 0% | 18.0869 | 0 | 0 | 139.9413 | 139.9413 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 642 | 18 | 3.5 | 0 | 12.22 | 12.22 | 12.22 | 6.11 | 27 | 642 | 1080 | 26.6301 | -18.5115 | -6.9717 | 1054.284 | 17.4552 | -81.8281 | -7.993 | 0 | 62.3795 | 242.3795 | 70.8633 | 0 | 0 | 10.4304 | 10.4304 | -13.8549 | 0% | 4.7166 | 0 | 0 | 134.8112 | 134.8112 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 643 | 19 | 3 | 0 | 0 | 0 | 0 | 0 | 27 | 643 | 1140 | 26.6301 | -18.5115 | -6.9717 | 1114.284 | 18.4552 | -96.8281 | -17.9729 | 0 | 62.3795 | 242.3795 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.3201 | 131.3201 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 644 | 20 | 2.8 | 0 | 0 | 0 | 0 | 0 | 27 | 644 | 1200 | 26.6301 | -18.5115 | -6.9717 | 1174.284 | 19.4552 | -111.8281 | -28.2175 | 0 | 62.3795 | 242.3795 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.8871 | 127.8871 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 645 | 21 | 4.3 | 0 | 0 | 0 | 0 | 0 | 27 | 645 | 1260 | 26.6301 | -18.5115 | -6.9717 | 1234.284 | 20.4552 | -126.8281 | -38.3612 | 0 | 62.3795 | 242.3795 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.599 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 646 | 22 | 4.1 | 0 | 0 | 0 | 0 | 0 | 27 | 646 | 1320 | 26.6301 | -18.5115 | -6.9717 | 1294.284 | 21.4552 | -141.8281 | -47.8925 | 0 | 62.3795 | 242.3795 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6298 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 647 | 23 | 4.5 | 0 | 0 | 0 | 0 | 0 | 27 | 647 | 1380 | 26.6301 | -18.5115 | -6.9717 | 1354.284 | 22.4552 | -156.8281 | -55.9313 | 0 | 62.3795 | 242.3795 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7812 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
1 | 27 | 27 | 648 | 24 | 4.9 | 0 | 0 | 0 | 0 | 0 | 27 | 648 | 1440 | 26.6301 | -18.5115 | -6.9717 | 1414.284 | 23.4552 | -171.8281 | -60.9457 | 0 | 62.3795 | 242.3795 | 70.8633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9327 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 649 | 1 | 5.2 | 0 | 0 | 0 | 0 | 0 | 28 | 649 | 60 | 27.6164 | -18.2643 | -6.9524 | 34.284 | 0.45553 | 173.1671 | -60.9368 | 0 | 62.7654 | 117.2346 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5359 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 650 | 2 | 6.4 | 0 | 0 | 0 | 0 | 0 | 28 | 650 | 120 | 27.6164 | -18.2643 | -6.9524 | 94.284 | 1.4555 | 158.1671 | -56.3106 | 0 | 62.7654 | 117.2346 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.323 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 651 | 3 | 6.3 | 0 | 0 | 0 | 0 | 0 | 28 | 651 | 180 | 27.6164 | -18.2643 | -6.9524 | 154.284 | 2.4555 | 143.1671 | -48.4943 | 0 | 62.7654 | 117.2346 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0913 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 652 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 28 | 652 | 240 | 27.6164 | -18.2643 | -6.9524 | 214.284 | 3.4555 | 128.1671 | -39.0686 | 0 | 62.7654 | 117.2346 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5485 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 653 | 5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 28 | 653 | 300 | 27.6164 | -18.2643 | -6.9524 | 274.284 | 4.4555 | 113.1671 | -28.9617 | 0 | 62.7654 | 117.2346 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.776 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 654 | 6 | 5.3 | 0 | 0 | 0 | 0 | 0 | 28 | 654 | 360 | 27.6164 | -18.2643 | -6.9524 | 334.284 | 5.4555 | 98.1671 | -18.7091 | 0 | 62.7654 | 117.2346 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.0455 | 1.0455 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 655 | 7 | 5.4 | 0 | 0 | 0 | 0 | 0 | 28 | 655 | 420 | 27.6164 | -18.2643 | -6.9524 | 394.284 | 6.4555 | 83.1671 | -8.6852 | 0 | 62.7654 | 117.2346 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 159.916 | 159.916 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 656 | 8 | 5.5 | 0 | 0 | 0 | 0 | 0 | 28 | 656 | 480 | 27.6164 | -18.2643 | -6.9524 | 454.284 | 7.4555 | 68.1671 | 0.77236 | 0.77236 | 61.8344 | 118.1656 | 69.9237 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 166.2528 | 166.2528 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 657 | 9 | 5.1 | 0.64 | 5.19 | 5.83 | 5.19 | 2.6 | 28 | 657 | 540 | 27.6164 | -18.2643 | -6.9524 | 514.284 | 8.4555 | 53.1671 | 9.293 | 9.293 | 50.3694 | 129.6306 | 55.9937 | 0 | 0 | 4.4299 | 4.4299 | -32.8398 | 0% | 2.0032 | 0 | 0 | 146.1491 | 146.1491 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 658 | 10 | 4.9 | 44.53 | 30.36 | 74.89 | 30.36 | 15.18 | 28 | 658 | 600 | 27.6164 | -18.2643 | -6.9524 | 574.284 | 9.4555 | 38.1671 | 16.4344 | 16.4344 | 37.7213 | 142.2787 | 42.5642 | 115.9253 | 115.9253 | 25.9139 | 141.8392 | -0.25015 | 0% | 64.1397 | 0 | 0 | 150.7234 | 150.7234 | 0% | 11.9% | 11.9% | 80% | 9.519% | 6.1054 | 8.7188 | 6 | 36.6323 | 13.5015 | 24.3% | 24.3%
1 | 28 | 28 | 659 | 11 | 6.1 | 109.25 | 50.36 | 159.61 | 50.36 | 25.18 | 28 | 659 | 660 | 27.6164 | -18.2643 | -6.9524 | 634.284 | 10.4555 | 23.1671 | 21.6853 | 21.6853 | 23.7063 | 156.2937 | 30.3562 | 255.1284 | 255.1284 | 42.9849 | 298.1134 | 0.31209 | 31.21% | 134.8069 | 42.0715 | 29.45 | 151.8363 | 151.8363 | 19.4% | 11.74% | 11.74% | 80% | 9.389% | 12.6564 | 8.3603 | 6 | 75.9385 | 27.9885 | 50.01% | 50.01%
1 | 28 | 28 | 660 | 12 | 7 | 191.47 | 53.53 | 245 | 53.53 | 26.77 | 28 | 660 | 720 | 27.6164 | -18.2643 | -6.9524 | 694.284 | 11.4555 | 8.1671 | 24.5416 | 24.5416 | 8.5285 | 171.4715 | 21.5943 | 428.6264 | 428.6264 | 45.6907 | 474.3171 | 0.49935 | 49.93% | 214.4862 | 107.1027 | 74.9719 | 128.2619 | 128.2619 | 58.45% | 11.58% | 11.58% | 85% | 9.847% | 21.1207 | 8.0981 | 6 | 126.7244 | 46.7066 | 98.8% | 98.8%
1 | 28 | 28 | 661 | 13 | 8.7 | 231.19 | 57.42 | 288.61 | 57.42 | 28.71 | 28 | 661 | 780 | 27.6164 | -18.2643 | -6.9524 | 754.284 | 12.4555 | -6.8329 | 24.6661 | 24.6661 | 7.1417 | 187.1417 | 21.1406 | 516.6908 | 516.6908 | 49.011 | 565.7018 | 0.55566 | 55.57% | 255.8104 | 142.1445 | 99.5012 | 130.0598 | 130.0598 | 76.5% | 11.5% | 11.5% | 90% | 10.35% | 26.4709 | 7.6183 | 6 | 158.8253 | 58.538 | 122.1% | 122.1%
1 | 28 | 28 | 662 | 14 | 9.4 | 171.31 | 90 | 261.31 | 90 | 45 | 28 | 662 | 840 | 27.6164 | -18.2643 | -6.9524 | 814.284 | 13.4555 | -21.8329 | 22.043 | 22.043 | 22.3967 | 202.3967 | 29.3831 | 397.7389 | 397.7389 | 76.8198 | 474.5587 | 0.51143 | 51.14% | 214.5955 | 109.7509 | 76.8256 | 127.9328 | 127.9328 | 60.05% | 11.54% | 11.54% | 85% | 9.81% | 21.0528 | 7.4266 | 6 | 126.317 | 46.5565 | 98.74% | 98.74%
1 | 28 | 28 | 663 | 15 | 10.9 | 104.81 | 134.17 | 238.98 | 134.17 | 67.09 | 28 | 663 | 900 | 27.6164 | -18.2643 | -6.9524 | 874.284 | 14.4555 | -36.8329 | 16.9858 | 16.9858 | 36.5304 | 216.5304 | 41.4118 | 269.0698 | 269.0698 | 114.5213 | 383.591 | 0.45117 | 45.12% | 173.4599 | 78.2603 | 54.7822 | 125.8823 | 125.8823 | 43.52% | 11.56% | 11.56% | 85% | 9.826% | 17.0448 | 7.0274 | 6 | 102.2687 | 37.693 | 81.24% | 81.24%
1 | 28 | 28 | 664 | 16 | 9.2 | 56.47 | 93.42 | 149.89 | 93.42 | 46.71 | 28 | 664 | 960 | 27.6164 | -18.2643 | -6.9524 | 934.284 | 15.4555 | -51.8329 | 9.9912 | 9.9912 | 49.297 | 229.297 | 54.7729 | 0 | 0 | 79.739 | 79.739 | -0.94307 | 0% | 36.058 | 0 | 0 | 159.0139 | 159.0139 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 665 | 17 | 7.9 | 35.28 | 46.39 | 81.67 | 46.39 | 23.2 | 28 | 665 | 1020 | 27.6164 | -18.2643 | -6.9524 | 994.284 | 16.4555 | -66.8329 | 1.5741 | 1.5741 | 60.8532 | 240.8532 | 68.673 | 0 | 0 | 39.5963 | 39.5963 | -2.7915 | 0% | 17.9055 | 0 | 0 | 151.0347 | 151.0347 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 666 | 18 | 6.9 | 0 | 10.83 | 10.83 | 10.83 | 5.42 | 28 | 666 | 1080 | 27.6164 | -18.2643 | -6.9524 | 1054.284 | 17.4555 | -81.8329 | -7.816 | 0 | 62.7654 | 242.7654 | 71.1194 | 0 | 0 | 9.244 | 9.244 | -14.8538 | 0% | 4.1801 | 0 | 0 | 141.4338 | 141.4338 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 667 | 19 | 5.8 | 0 | 0 | 0 | 0 | 0 | 28 | 667 | 1140 | 27.6164 | -18.2643 | -6.9524 | 1114.284 | 18.4555 | -96.8329 | -17.8032 | 0 | 62.7654 | 242.7654 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.0562 | 136.0562 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 668 | 20 | 5.3 | 0 | 0 | 0 | 0 | 0 | 28 | 668 | 1200 | 27.6164 | -18.2643 | -6.9524 | 1174.284 | 19.4555 | -111.8329 | -28.0495 | 0 | 62.7654 | 242.7654 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.6637 | 130.6637 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 669 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 28 | 669 | 1260 | 27.6164 | -18.2643 | -6.9524 | 1234.284 | 20.4555 | -126.8329 | -38.1875 | 0 | 62.7654 | 242.7654 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9274 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 670 | 22 | 4.6 | 0 | 0 | 0 | 0 | 0 | 28 | 670 | 1320 | 27.6164 | -18.2643 | -6.9524 | 1294.284 | 21.4555 | -141.8329 | -47.7034 | 0 | 62.7654 | 242.7654 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6028 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 671 | 23 | 3.9 | 0 | 0 | 0 | 0 | 0 | 28 | 671 | 1380 | 27.6164 | -18.2643 | -6.9524 | 1354.284 | 22.4555 | -156.8329 | -55.7166 | 0 | 62.7654 | 242.7654 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2854 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
1 | 28 | 28 | 672 | 24 | 3.5 | 0 | 0 | 0 | 0 | 0 | 28 | 672 | 1440 | 27.6164 | -18.2643 | -6.9524 | 1414.284 | 23.4555 | -171.8329 | -60.7045 | 0 | 62.7654 | 242.7654 | 71.1194 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5109 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 673 | 1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 29 | 673 | 60 | 28.6027 | -18.0119 | -6.9217 | 34.284 | 0.45604 | 173.1594 | -60.6867 | 0 | 63.1587 | 116.8413 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0076 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 674 | 2 | 9.1 | 0 | 0 | 0 | 0 | 0 | 29 | 674 | 120 | 28.6027 | -18.0119 | -6.9217 | 94.284 | 1.456 | 158.1594 | -56.0828 | 0 | 63.1587 | 116.8413 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.447 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 675 | 3 | 11.1 | 0 | 0 | 0 | 0 | 0 | 29 | 675 | 180 | 28.6027 | -18.0119 | -6.9217 | 154.284 | 2.456 | 143.1594 | -48.2914 | 0 | 63.1587 | 116.8413 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1535 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 676 | 4 | 11.1 | 0 | 0 | 0 | 0 | 0 | 29 | 676 | 240 | 28.6027 | -18.0119 | -6.9217 | 214.284 | 3.456 | 128.1594 | -38.8815 | 0 | 63.1587 | 116.8413 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1535 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 677 | 5 | 11 | 0 | 0 | 0 | 0 | 0 | 29 | 677 | 300 | 28.6027 | -18.0119 | -6.9217 | 274.284 | 4.456 | 113.1594 | -28.781 | 0 | 63.1587 | 116.8413 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.3821 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 678 | 6 | 9.6 | 0 | 0 | 0 | 0 | 0 | 29 | 678 | 360 | 28.6027 | -18.0119 | -6.9217 | 334.284 | 5.456 | 98.1594 | -18.5274 | 0 | 63.1587 | 116.8413 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.2415 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 679 | 7 | 8.6 | 0 | 0 | 0 | 0 | 0 | 29 | 679 | 420 | 28.6027 | -18.0119 | -6.9217 | 394.284 | 6.456 | 83.1594 | -8.4969 | 0 | 63.1587 | 116.8413 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.7773 | 149.7773 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 680 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 29 | 680 | 480 | 28.6027 | -18.0119 | -6.9217 | 454.284 | 7.456 | 68.1594 | 0.97185 | 0.97185 | 61.9893 | 118.0107 | 69.8775 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 152.2642 | 152.2642 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 681 | 9 | 7.4 | 1.11 | 4.72 | 5.83 | 4.72 | 2.36 | 29 | 681 | 540 | 28.6027 | -18.0119 | -6.9217 | 514.284 | 8.456 | 53.1594 | 9.5069 | 9.5069 | 50.5054 | 129.4946 | 55.9209 | 0 | 0 | 4.0288 | 4.0288 | -34.8281 | 0% | 1.8218 | 0 | 0 | 131.0514 | 131.0514 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 682 | 10 | 9.9 | 24.44 | 55.56 | 80 | 55.56 | 27.78 | 29 | 682 | 600 | 28.6027 | -18.0119 | -6.9217 | 574.284 | 9.456 | 38.1594 | 16.6641 | 16.6641 | 37.8307 | 142.1693 | 42.4551 | 62.8817 | 62.8817 | 47.4234 | 110.3051 | -0.44409 | 0% | 49.88 | 0 | 0 | 138.1522 | 138.1522 | 0% | 11.74% | 11.74% | 80% | 9.388% | 4.6828 | 7.2918 | 6 | 28.0967 | 10.3556 | 20.34% | 20.34%
1 | 29 | 29 | 683 | 11 | 11.7 | 2.22 | 75.47 | 77.69 | 75.47 | 37.74 | 29 | 683 | 660 | 28.6027 | -18.0119 | -6.9217 | 634.284 | 10.456 | 23.1594 | 21.9289 | 21.9289 | 23.7776 | 156.2224 | 30.1925 | 5.138 | 5.138 | 64.4177 | 69.5557 | -1.1151 | 0% | 31.4531 | 0 | 0 | 136.7713 | 136.7713 | 0% | 11.69% | 11.69% | 80% | 9.348% | 2.9403 | 6.8209 | 6 | 17.6421 | 6.5023 | 12.9% | 12.9%
1 | 29 | 29 | 684 | 12 | 12.7 | 2.31 | 89.44 | 91.75 | 89.44 | 44.72 | 29 | 684 | 720 | 28.6027 | -18.0119 | -6.9217 | 694.284 | 11.456 | 8.1594 | 24.7933 | 24.7933 | 8.5502 | 171.4498 | 21.3587 | 5.1302 | 5.1302 | 76.3418 | 81.472 | -0.80615 | 0% | 36.8417 | 0 | 0 | 134.1536 | 134.1536 | 0% | 11.64% | 11.64% | 80% | 9.312% | 3.4308 | 6.5691 | 6 | 20.585 | 7.587 | 15.34% | 15.34%
1 | 29 | 29 | 685 | 13 | 13.1 | 2.22 | 110.36 | 112.58 | 110.36 | 55.18 | 29 | 685 | 780 | 28.6027 | -18.0119 | -6.9217 | 754.284 | 12.456 | -6.8406 | 24.9169 | 24.9169 | 7.1747 | 187.1747 | 20.9049 | 4.9225 | 4.9225 | 94.1982 | 99.1207 | -0.51019 | 0% | 44.8224 | 0 | 0 | 134.5965 | 134.5965 | 0% | 11.62% | 11.62% | 80% | 9.294% | 4.166 | 6.4703 | 6 | 24.9958 | 9.2127 | 18.57% | 18.57%
1 | 29 | 29 | 686 | 14 | 12.9 | 1.86 | 122.5 | 124.36 | 122.5 | 61.25 | 29 | 686 | 840 | 28.6027 | -18.0119 | -6.9217 | 814.284 | 13.456 | -21.8406 | 22.2837 | 22.2837 | 22.4792 | 202.4792 | 29.2245 | 4.2808 | 4.2808 | 104.5603 | 108.8411 | -0.39704 | 0% | 49.2179 | 0 | 0 | 133.8905 | 133.8905 | 0% | 11.62% | 11.62% | 80% | 9.298% | 4.576 | 6.5196 | 6 | 27.4563 | 10.1195 | 20.51% | 20.51%
1 | 29 | 29 | 687 | 15 | 11.7 | 15.83 | 133.25 | 149.08 | 133.25 | 66.63 | 29 | 687 | 900 | 28.6027 | -18.0119 | -6.9217 | 874.284 | 14.456 | -36.8406 | 17.2107 | 17.2107 | 36.6507 | 216.6507 | 41.312 | 40.1855 | 40.1855 | 113.736 | 153.9214 | -0.063243 | 0% | 69.6033 | 0 | 0 | 152.5624 | 152.5624 | 0% | 11.65% | 11.65% | 80% | 9.318% | 6.4853 | 6.8209 | 6 | 38.9119 | 14.3417 | 25.51% | 25.51%
1 | 29 | 29 | 688 | 16 | 11.6 | 18.53 | 84.53 | 103.06 | 84.53 | 42.27 | 29 | 688 | 960 | 28.6027 | -18.0119 | -6.9217 | 934.284 | 15.456 | -51.8406 | 10.1985 | 10.1985 | 49.4434 | 229.4434 | 54.7114 | 60.4583 | 60.4583 | 72.1509 | 132.6091 | -0.20437 | 0% | 59.9658 | 0 | 0 | 149.1394 | 149.1394 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 689 | 17 | 10.9 | 10.92 | 43.81 | 54.73 | 43.81 | 21.91 | 29 | 689 | 1020 | 28.6027 | -18.0119 | -6.9217 | 994.284 | 16.456 | -66.8406 | 1.7656 | 1.7656 | 61.0179 | 241.0179 | 68.639 | 0 | 0 | 37.3942 | 37.3942 | -2.8153 | 0% | 16.9096 | 0 | 0 | 144.5165 | 144.5165 | 0% | 11.73% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 690 | 18 | 9.6 | 0 | 11.31 | 11.31 | 11.31 | 5.66 | 29 | 690 | 1080 | 28.6027 | -18.0119 | -6.9217 | 1054.284 | 17.456 | -81.8406 | -7.6368 | 0 | 63.1587 | 243.1587 | 71.381 | 0 | 0 | 9.6537 | 9.6537 | -13.5296 | 0% | 4.3654 | 0 | 0 | 138.4033 | 138.4033 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 691 | 19 | 9.6 | 0 | 0 | 0 | 0 | 0 | 29 | 691 | 1140 | 28.6027 | -18.0119 | -6.9217 | 1114.284 | 18.456 | -96.8406 | -17.6317 | 0 | 63.1587 | 243.1587 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.1864 | 136.1864 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 692 | 20 | 10.3 | 0 | 0 | 0 | 0 | 0 | 29 | 692 | 1200 | 28.6027 | -18.0119 | -6.9217 | 1174.284 | 19.456 | -111.8406 | -27.8795 | 0 | 63.1587 | 243.1587 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.6004 | 134.6004 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 693 | 21 | 10.1 | 0 | 0 | 0 | 0 | 0 | 29 | 693 | 1260 | 28.6027 | -18.0119 | -6.9217 | 1234.284 | 20.456 | -126.8406 | -38.0114 | 0 | 63.1587 | 243.1587 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3253 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 694 | 22 | 10.1 | 0 | 0 | 0 | 0 | 0 | 29 | 694 | 1320 | 28.6027 | -18.0119 | -6.9217 | 1294.284 | 21.456 | -141.8406 | -47.5115 | 0 | 63.1587 | 243.1587 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9048 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 695 | 23 | 10.5 | 0 | 0 | 0 | 0 | 0 | 29 | 695 | 1380 | 28.6027 | -18.0119 | -6.9217 | 1354.284 | 22.456 | -156.8406 | -55.4982 | 0 | 63.1587 | 243.1587 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0498 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
1 | 29 | 29 | 696 | 24 | 8.7 | 0 | 0 | 0 | 0 | 0 | 29 | 696 | 1440 | 28.6027 | -18.0119 | -6.9217 | 1414.284 | 23.456 | -171.8406 | -60.4585 | 0 | 63.1587 | 243.1587 | 71.381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5475 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 697 | 1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 30 | 697 | 60 | 29.589 | -17.7542 | -6.8796 | 34.284 | 0.45674 | 173.1489 | -60.4309 | 0 | 63.5592 | 116.4408 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3652 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 698 | 2 | 4.9 | 0 | 0 | 0 | 0 | 0 | 30 | 698 | 120 | 29.589 | -17.7542 | -6.8796 | 94.284 | 1.4567 | 158.1489 | -55.8489 | 0 | 63.5592 | 116.4408 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7745 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 699 | 3 | 2.4 | 0 | 0 | 0 | 0 | 0 | 30 | 699 | 180 | 29.589 | -17.7542 | -6.8796 | 154.284 | 2.4567 | 143.1489 | -48.0823 | 0 | 63.5592 | 116.4408 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3361 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 700 | 4 | 2.1 | 0 | 0 | 0 | 0 | 0 | 30 | 700 | 240 | 29.589 | -17.7542 | -6.8796 | 214.284 | 3.4567 | 128.1489 | -38.6883 | 0 | 63.5592 | 116.4408 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7933 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 701 | 5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 30 | 701 | 300 | 29.589 | -17.7542 | -6.8796 | 274.284 | 4.4567 | 113.1489 | -28.5944 | 0 | 63.5592 | 116.4408 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9395 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 702 | 6 | 0.4 | 0 | 0 | 0 | 0 | 0 | 30 | 702 | 360 | 29.589 | -17.7542 | -6.8796 | 334.284 | 5.4567 | 98.1489 | -18.34 | 0 | 63.5592 | 116.4408 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8083 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 703 | 7 | -0.6 | 0 | 0 | 0 | 0 | 0 | 30 | 703 | 420 | 29.589 | -17.7542 | -6.8796 | 394.284 | 6.4567 | 83.1489 | -8.3029 | 0 | 63.5592 | 116.4408 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.2393 | 141.2393 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 704 | 8 | -1 | 0 | 0 | 0 | 0 | 0 | 30 | 704 | 480 | 29.589 | -17.7542 | -6.8796 | 454.284 | 7.4567 | 68.1489 | 1.1771 | 1.1771 | 62.1454 | 117.8546 | 69.8281 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.9219 | 144.9219 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 705 | 9 | -0.2 | 0.83 | 5.83 | 6.66 | 5.83 | 2.92 | 30 | 705 | 540 | 29.589 | -17.7542 | -6.8796 | 514.284 | 8.4567 | 53.1489 | 9.7266 | 9.7266 | 50.6422 | 129.3578 | 55.8447 | 0 | 0 | 4.9762 | 4.9762 | -31.7411 | 0% | 2.2502 | 0 | 0 | 126.2992 | 126.2992 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 706 | 10 | 2.2 | 28.89 | 38.42 | 67.31 | 38.42 | 19.21 | 30 | 706 | 600 | 29.589 | -17.7542 | -6.8796 | 574.284 | 9.4567 | 38.1489 | 16.8997 | 16.8997 | 37.9403 | 142.0597 | 42.3424 | 73.4565 | 73.4565 | 32.7935 | 106.25 | -0.66478 | 0% | 48.0463 | 0 | 0 | 133.775 | 133.775 | 0% | 12.03% | 12.03% | 80% | 9.625% | 4.6244 | 9.5621 | 6 | 27.7466 | 10.2265 | 20.74% | 20.74%
1 | 30 | 30 | 707 | 11 | 4.9 | 65.08 | 70.28 | 135.36 | 70.28 | 35.14 | 30 | 707 | 660 | 29.589 | -17.7542 | -6.8796 | 634.284 | 10.4567 | 23.1489 | 22.1784 | 22.1784 | 23.8481 | 156.1519 | 30.0245 | 149.267 | 149.267 | 59.9877 | 209.2547 | 0.089463 | 8.946% | 94.625 | 8.4654 | 5.9258 | 137.8635 | 137.8635 | 4.298% | 11.84% | 11.84% | 80% | 9.474% | 8.9649 | 8.7188 | 6 | 53.7891 | 19.825 | 39.02% | 39.02%
1 | 30 | 30 | 708 | 12 | 5.5 | 97.58 | 91.75 | 189.33 | 91.75 | 45.88 | 30 | 708 | 720 | 29.589 | -17.7542 | -6.8796 | 694.284 | 11.4567 | 8.1489 | 25.0506 | 25.0506 | 8.5697 | 171.4303 | 21.1177 | 214.9808 | 214.9808 | 78.3135 | 293.2943 | 0.29911 | 29.91% | 132.6277 | 39.6706 | 27.7694 | 135.9567 | 135.9567 | 20.43% | 11.76% | 11.76% | 80% | 9.405% | 12.4735 | 8.5383 | 6 | 74.8408 | 27.584 | 55.05% | 55.05%
1 | 30 | 30 | 709 | 13 | 7.3 | 142.97 | 112.31 | 255.28 | 112.31 | 56.16 | 30 | 709 | 780 | 29.589 | -17.7542 | -6.8796 | 754.284 | 12.4567 | -6.8511 | 25.1726 | 25.1726 | 7.2113 | 187.2113 | 20.6655 | 314.4986 | 314.4986 | 95.8626 | 410.3612 | 0.4536 | 45.36% | 185.5653 | 84.1723 | 58.9206 | 119.2422 | 119.2422 | 49.41% | 11.62% | 11.62% | 85% | 9.881% | 18.3349 | 8.012 | 6 | 110.0091 | 40.5459 | 92.26% | 92.26%
1 | 30 | 30 | 710 | 14 | 11.8 | 117.42 | 129.08 | 246.5 | 129.08 | 64.54 | 30 | 710 | 840 | 29.589 | -17.7542 | -6.8796 | 814.284 | 13.4567 | -21.8511 | 22.5286 | 22.5286 | 22.5664 | 202.5664 | 29.0658 | 267.8685 | 267.8685 | 110.1767 | 378.0452 | 0.45151 | 45.15% | 170.952 | 77.187 | 54.0309 | 124.5891 | 124.5891 | 43.37% | 11.54% | 11.54% | 85% | 9.811% | 16.772 | 6.7954 | 6 | 100.6322 | 37.0899 | 80.77% | 80.77%
1 | 30 | 30 | 711 | 15 | 11.9 | 105.56 | 120 | 225.56 | 120 | 60 | 30 | 711 | 900 | 29.589 | -17.7542 | -6.8796 | 874.284 | 14.4567 | -36.8511 | 17.439 | 17.439 | 36.7763 | 216.7763 | 41.2136 | 264.9687 | 264.9687 | 102.4264 | 367.3951 | 0.44192 | 44.19% | 166.1361 | 73.4194 | 51.3936 | 121.8313 | 121.8313 | 42.18% | 11.54% | 11.54% | 85% | 9.813% | 16.303 | 6.77 | 6 | 97.8178 | 36.0525 | 80.29% | 80.29%
1 | 30 | 30 | 712 | 16 | 12.1 | 71.19 | 75.36 | 146.55 | 75.36 | 37.68 | 30 | 712 | 960 | 29.589 | -17.7542 | -6.8796 | 934.284 | 15.4567 | -51.8511 | 10.4087 | 10.4087 | 49.5953 | 229.5953 | 54.6518 | 227.9681 | 227.9681 | 64.3238 | 292.2919 | 0.35047 | 35.05% | 132.1744 | 46.323 | 32.4261 | 159.3921 | 159.3921 | 20.34% | 11.57% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 713 | 17 | 11.7 | 30.64 | 36.58 | 67.22 | 36.58 | 18.29 | 30 | 713 | 1020 | 29.589 | -17.7542 | -6.8796 | 994.284 | 16.4567 | -66.8511 | 1.9594 | 1.9594 | 61.1881 | 241.1881 | 68.6073 | 0 | 0 | 31.223 | 31.223 | -3.4713 | 0% | 14.119 | 0 | 0 | 153.0207 | 153.0207 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 714 | 18 | 9.3 | 0 | 7.78 | 7.78 | 7.78 | 3.89 | 30 | 714 | 1080 | 29.589 | -17.7542 | -6.8796 | 1054.284 | 17.4567 | -81.8511 | -7.4557 | 0 | 63.5592 | 243.5592 | 71.6479 | 0 | 0 | 6.6406 | 6.6406 | -20.139 | 0% | 3.0029 | 0 | 0 | 143.058 | 143.058 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 715 | 19 | 8.6 | 0 | 0 | 0 | 0 | 0 | 30 | 715 | 1140 | 29.589 | -17.7542 | -6.8796 | 1114.284 | 18.4567 | -96.8511 | -17.4582 | 0 | 63.5592 | 243.5592 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.0971 | 139.0971 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 716 | 20 | 6.6 | 0 | 0 | 0 | 0 | 0 | 30 | 716 | 1200 | 29.589 | -17.7542 | -6.8796 | 1174.284 | 19.4567 | -111.8511 | -27.7075 | 0 | 63.5592 | 243.5592 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.504 | 132.504 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 717 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 30 | 717 | 1260 | 29.589 | -17.7542 | -6.8796 | 1234.284 | 20.4567 | -126.8511 | -37.8331 | 0 | 63.5592 | 243.5592 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8067 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 718 | 22 | 3.3 | 0 | 0 | 0 | 0 | 0 | 30 | 718 | 1320 | 29.589 | -17.7542 | -6.8796 | 1294.284 | 21.4567 | -141.8511 | -47.3166 | 0 | 63.5592 | 243.5592 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2062 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 719 | 23 | 2.2 | 0 | 0 | 0 | 0 | 0 | 30 | 719 | 1380 | 29.589 | -17.7542 | -6.8796 | 1354.284 | 22.4567 | -156.8511 | -55.2761 | 0 | 63.5592 | 243.5592 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6343 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
1 | 30 | 30 | 720 | 24 | 1.3 | 0 | 0 | 0 | 0 | 0 | 30 | 720 | 1440 | 29.589 | -17.7542 | -6.8796 | 1414.284 | 23.4567 | -171.8511 | -60.2078 | 0 | 63.5592 | 243.5592 | 71.6479 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.7575 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 721 | 1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 31 | 721 | 60 | 30.5753 | -17.4915 | -6.8261 | 34.284 | 0.45763 | 173.1355 | -60.1697 | 0 | 63.9669 | 116.0331 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2302 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 722 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 31 | 722 | 120 | 30.5753 | -17.4915 | -6.8261 | 94.284 | 1.4576 | 158.1355 | -55.6088 | 0 | 63.9669 | 116.0331 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.764 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 723 | 3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 31 | 723 | 180 | 30.5753 | -17.4915 | -6.8261 | 154.284 | 2.4576 | 143.1355 | -47.8669 | 0 | 63.9669 | 116.0331 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1454 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 724 | 4 | -0.4 | 0 | 0 | 0 | 0 | 0 | 31 | 724 | 240 | 30.5753 | -17.4915 | -6.8261 | 214.284 | 3.4576 | 128.1355 | -38.4891 | 0 | 63.9669 | 116.0331 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0598 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 725 | 5 | -0.5 | 0 | 0 | 0 | 0 | 0 | 31 | 725 | 300 | 30.5753 | -17.4915 | -6.8261 | 274.284 | 4.4576 | 113.1355 | -28.402 | 0 | 63.9669 | 116.0331 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0419 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 726 | 6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 31 | 726 | 360 | 30.5753 | -17.4915 | -6.8261 | 334.284 | 5.4576 | 98.1355 | -18.1469 | 0 | 63.9669 | 116.0331 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4512 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 727 | 7 | -0.9 | 0 | 0 | 0 | 0 | 0 | 31 | 727 | 420 | 30.5753 | -17.4915 | -6.8261 | 394.284 | 6.4576 | 83.1355 | -8.1032 | 0 | 63.9669 | 116.0331 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.4771 | 127.4771 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 728 | 8 | -1.4 | 0 | 0 | 0 | 0 | 0 | 31 | 728 | 480 | 30.5753 | -17.4915 | -6.8261 | 454.284 | 7.4576 | 68.1355 | 1.388 | 1.388 | 62.3026 | 117.6974 | 69.7757 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.1579 | 128.1579 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 729 | 9 | -1.7 | 0 | 3.81 | 3.81 | 3.81 | 1.91 | 31 | 729 | 540 | 30.5753 | -17.4915 | -6.8261 | 514.284 | 8.4576 | 53.1355 | 9.9521 | 9.9521 | 50.7797 | 129.2203 | 55.7653 | 0 | 0 | 3.252 | 3.252 | -50.1407 | 0% | 1.4706 | 0 | 0 | 107.1279 | 107.1279 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 730 | 10 | -0.4 | 0.14 | 30.14 | 30.28 | 30.14 | 15.07 | 31 | 730 | 600 | 30.5753 | -17.4915 | -6.8261 | 574.284 | 9.4576 | 38.1355 | 17.141 | 17.141 | 38.0499 | 141.9501 | 42.2262 | 0.35175 | 0.35175 | 25.7261 | 26.0779 | -5.4253 | 0% | 11.7924 | 0 | 0 | 110.2152 | 110.2152 | 0% | 12.22% | 12.22% | 80% | 9.776% | 1.1529 | 10.4224 | 6 | 6.9171 | 2.5494 | 6.276% | 6.276%
1 | 31 | 31 | 731 | 11 | 0.2 | 0.56 | 56.11 | 56.67 | 56.11 | 28.06 | 31 | 731 | 660 | 30.5753 | -17.4915 | -6.8261 | 634.284 | 10.4576 | 23.1355 | 22.4335 | 22.4335 | 23.9175 | 156.0825 | 29.8524 | 1.2727 | 1.2727 | 47.8929 | 49.1656 | -2.4699 | 0% | 22.2327 | 0 | 0 | 111.412 | 111.412 | 0% | 12.17% | 12.17% | 80% | 9.736% | 2.1645 | 10.2197 | 6 | 12.9871 | 4.7866 | 11.66% | 11.66%
1 | 31 | 31 | 732 | 12 | 0.8 | 6.11 | 117.97 | 124.08 | 117.97 | 58.99 | 31 | 732 | 720 | 30.5753 | -17.4915 | -6.8261 | 694.284 | 11.4576 | 8.1355 | 25.3132 | 25.3132 | 8.5868 | 171.4132 | 20.8713 | 13.3525 | 13.3525 | 100.6937 | 114.0462 | -0.59444 | 0% | 51.5717 | 0 | 0 | 113.9808 | 113.9808 | 0% | 12.08% | 12.08% | 80% | 9.661% | 4.9824 | 10.0195 | 6 | 29.8943 | 11.0181 | 26.23% | 26.23%
1 | 31 | 31 | 733 | 13 | 3.4 | 10.28 | 119.36 | 129.64 | 119.36 | 59.68 | 31 | 733 | 780 | 30.5753 | -17.4915 | -6.8261 | 754.284 | 12.4576 | -6.8645 | 25.4331 | 25.4331 | 7.2517 | 187.2517 | 20.4228 | 22.4326 | 22.4326 | 101.8801 | 124.3127 | -0.4279 | 0% | 56.2142 | 0 | 0 | 117.923 | 117.923 | 0% | 11.97% | 11.97% | 80% | 9.575% | 5.3826 | 9.181 | 6 | 32.2955 | 11.9031 | 27.39% | 27.39%
1 | 31 | 31 | 734 | 14 | 6.1 | 1.67 | 98.42 | 100.09 | 98.42 | 49.21 | 31 | 734 | 840 | 30.5753 | -17.4915 | -6.8261 | 814.284 | 13.4576 | -21.8645 | 22.7776 | 22.7776 | 22.6584 | 202.6584 | 28.9073 | 3.7761 | 3.7761 | 84.0067 | 87.7828 | -0.86655 | 0% | 39.6954 | 0 | 0 | 120.4191 | 120.4191 | 0% | 11.9% | 11.9% | 80% | 9.517% | 3.7779 | 8.3603 | 6 | 22.6673 | 8.3545 | 18.82% | 18.82%
1 | 31 | 31 | 735 | 15 | 7.6 | 1.47 | 96.11 | 97.58 | 96.11 | 48.06 | 31 | 735 | 900 | 30.5753 | -17.4915 | -6.8261 | 874.284 | 14.4576 | -36.8645 | 17.6706 | 17.6706 | 36.9071 | 216.9071 | 41.1168 | 3.6484 | 3.6484 | 82.035 | 85.6834 | -0.86587 | 0% | 38.746 | 0 | 0 | 142.9486 | 142.9486 | 0% | 11.84% | 11.84% | 80% | 9.471% | 3.6698 | 7.9264 | 6 | 22.0186 | 8.1154 | 15.4% | 15.4%
1 | 31 | 31 | 736 | 16 | 8.2 | 1.11 | 64.81 | 65.92 | 64.81 | 32.41 | 31 | 736 | 960 | 30.5753 | -17.4915 | -6.8261 | 934.284 | 15.4576 | -51.8645 | 10.6215 | 10.6215 | 49.7525 | 229.7525 | 54.5944 | 3.489 | 3.489 | 55.3188 | 58.8078 | -1.6049 | 0% | 26.5929 | 0 | 0 | 141.9195 | 141.9195 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 737 | 17 | 7.47 | 2.03 | 36.03 | 38.06 | 36.03 | 18.02 | 31 | 737 | 1020 | 30.5753 | -17.4915 | -6.8261 | 994.284 | 16.4576 | -66.8645 | 2.1554 | 2.1554 | 61.3637 | 241.3637 | 68.578 | 0 | 0 | 30.7535 | 30.7535 | -3.8585 | 0% | 13.9067 | 0 | 0 | 138.974 | 138.974 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.9634 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 738 | 18 | 6.21 | 0 | 14.72 | 14.72 | 14.72 | 7.36 | 31 | 738 | 1080 | 30.5753 | -17.4915 | -6.8261 | 1054.284 | 17.4576 | -81.8645 | -7.2726 | 0 | 63.9669 | 243.9669 | 71.9201 | 0 | 0 | 12.5643 | 12.5643 | -10.8467 | 0% | 5.6816 | 0 | 0 | 135.1962 | 135.1962 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.328 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 739 | 19 | 4.68 | 0 | 0 | 0 | 0 | 0 | 31 | 739 | 1140 | 30.5753 | -17.4915 | -6.8261 | 1114.284 | 18.4576 | -96.8645 | -17.2829 | 0 | 63.9669 | 243.9669 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.2541 | 131.2541 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7856 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 740 | 20 | 3.54 | 0 | 0 | 0 | 0 | 0 | 31 | 740 | 1200 | 30.5753 | -17.4915 | -6.8261 | 1174.284 | 19.4576 | -111.8645 | -27.5336 | 0 | 63.9669 | 243.9669 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.1809 | 128.1809 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1372 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 741 | 21 | 3.23 | 0 | 0 | 0 | 0 | 0 | 31 | 741 | 1260 | 30.5753 | -17.4915 | -6.8261 | 1234.284 | 20.4576 | -126.8645 | -37.6525 | 0 | 63.9669 | 243.9669 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6135 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2344 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 742 | 22 | 2.97 | 0 | 0 | 0 | 0 | 0 | 31 | 742 | 1320 | 30.5753 | -17.4915 | -6.8261 | 1294.284 | 21.4576 | -141.8645 | -47.119 | 0 | 63.9669 | 243.9669 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.303 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3164 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 743 | 23 | 2.59 | 0 | 0 | 0 | 0 | 0 | 31 | 743 | 1380 | 30.5753 | -17.4915 | -6.8261 | 1354.284 | 22.4576 | -156.8645 | -55.0503 | 0 | 63.9669 | 243.9669 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.8063 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4371 | 6 | 0 | 0 | 0% | 0%
1 | 31 | 31 | 744 | 24 | 1.11 | 0 | 0 | 0 | 0 | 0 | 31 | 744 | 1440 | 30.5753 | -17.4915 | -6.8261 | 1414.284 | 23.4576 | -171.8645 | -59.9525 | 0 | 63.9669 | 243.9669 | 71.9201 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.986 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.917 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 745 | 1 | -0.25 | 0 | 0 | 0 | 0 | 0 | 32 | 745 | 60 | 31.5616 | -17.2237 | -6.761 | 34.284 | 0.45872 | 173.1193 | -59.9029 | 0 | 64.3816 | 115.6184 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4966 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3715 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 746 | 2 | -1.05 | 0 | 0 | 0 | 0 | 0 | 32 | 746 | 120 | 31.5616 | -17.2237 | -6.761 | 94.284 | 1.4587 | 158.1193 | -55.3627 | 0 | 64.3816 | 115.6184 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4431 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6449 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 747 | 3 | -0.84 | 0 | 0 | 0 | 0 | 0 | 32 | 747 | 180 | 31.5616 | -17.2237 | -6.761 | 154.284 | 2.4587 | 143.1193 | -47.6455 | 0 | 64.3816 | 115.6184 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.8503 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5727 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 748 | 4 | -1.04 | 0 | 0 | 0 | 0 | 0 | 32 | 748 | 240 | 31.5616 | -17.2237 | -6.761 | 214.284 | 3.4587 | 128.1193 | -38.2839 | 0 | 64.3816 | 115.6184 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.1551 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6415 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 749 | 5 | -1.92 | 0 | 0 | 0 | 0 | 0 | 32 | 749 | 300 | 31.5616 | -17.2237 | -6.761 | 274.284 | 4.4587 | 113.1193 | -28.2037 | 0 | 64.3816 | 115.6184 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7863 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9473 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 750 | 6 | -2.93 | 0 | 0 | 0 | 0 | 0 | 32 | 750 | 360 | 31.5616 | -17.2237 | -6.761 | 334.284 | 5.4587 | 98.1193 | -17.9481 | 0 | 64.3816 | 115.6184 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.4888 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.305 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 751 | 7 | -3.55 | 0 | 0 | 0 | 0 | 0 | 32 | 751 | 420 | 31.5616 | -17.2237 | -6.761 | 394.284 | 6.4587 | 83.1193 | -7.8978 | 0 | 64.3816 | 115.6184 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.7782 | 147.7782 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5282 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 752 | 8 | -3.7 | 0 | 0 | 0 | 0 | 0 | 32 | 752 | 480 | 31.5616 | -17.2237 | -6.761 | 454.284 | 7.4587 | 68.1193 | 1.6046 | 1.6046 | 62.4609 | 117.5391 | 69.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 153.669 | 153.669 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 753 | 9 | -4 | 0.28 | 6.19 | 6.47 | 6.19 | 3.1 | 32 | 753 | 540 | 31.5616 | -17.2237 | -6.761 | 514.284 | 8.4587 | 53.1193 | 10.1833 | 10.1833 | 50.918 | 129.082 | 55.6827 | 0.89287 | 0.89287 | 5.2835 | 6.1764 | -26.9535 | 0% | 2.793 | 0 | 0 | 133.9137 | 133.9137 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 754 | 10 | -3.9 | 0.56 | 40 | 40.56 | 40 | 20 | 32 | 754 | 600 | 31.5616 | -17.2237 | -6.761 | 574.284 | 9.4587 | 38.1193 | 17.3879 | 17.3879 | 38.1594 | 141.8406 | 42.1066 | 1.3903 | 1.3903 | 34.1421 | 35.5324 | -4.0138 | 0% | 16.0677 | 0 | 0 | 136.3469 | 136.3469 | 0% | 12.36% | 12.36% | 80% | 9.886% | 1.5884 | 11.6553 | 6 | 9.5303 | 3.5126 | 6.99% | 6.99%
2 | 32 | 1 | 755 | 11 | -3.8 | 6.31 | 344.36 | 350.67 | 344.36 | 172.18 | 32 | 755 | 660 | 31.5616 | -17.2237 | -6.761 | 634.284 | 10.4587 | 23.1193 | 22.6942 | 22.6942 | 23.9859 | 156.0141 | 29.6762 | 14.2099 | 14.2099 | 293.9296 | 308.1396 | 0.24926 | 24.93% | 139.3407 | 34.7325 | 24.3127 | 126.941 | 126.941 | 19.15% | 12% | 12% | 85% | 10.2% | 14.2078 | 11.6189 | 6 | 85.247 | 31.4194 | 67.15% | 67.15%
2 | 32 | 1 | 756 | 12 | -2.9 | 85.28 | 137.58 | 222.86 | 137.58 | 68.79 | 32 | 756 | 720 | 31.5616 | -17.2237 | -6.761 | 694.284 | 11.4587 | 8.1193 | 25.5811 | 25.5811 | 8.6015 | 171.3985 | 20.6195 | 184.852 | 184.852 | 117.4319 | 302.2838 | 0.246 | 24.6% | 136.6927 | 33.6266 | 23.5386 | 116.6487 | 116.6487 | 20.18% | 11.98% | 11.98% | 85% | 10.18% | 13.9181 | 11.2943 | 6 | 83.5087 | 30.7787 | 71.59% | 71.59%
2 | 32 | 1 | 757 | 13 | -2 | 112.97 | 182.97 | 295.94 | 182.97 | 91.49 | 32 | 757 | 780 | 31.5616 | -17.2237 | -6.761 | 754.284 | 12.4587 | -6.8807 | 25.6984 | 25.6984 | 7.2958 | 187.2958 | 20.1767 | 244.532 | 244.532 | 156.1747 | 400.7067 | 0.38868 | 38.87% | 181.1996 | 70.4283 | 49.2998 | 120.4424 | 120.4424 | 40.93% | 11.84% | 11.84% | 85% | 10.06% | 18.2284 | 10.9754 | 6 | 109.3707 | 40.3106 | 90.81% | 90.81%
2 | 32 | 1 | 758 | 14 | -2 | 164.36 | 172.5 | 336.86 | 172.5 | 86.25 | 32 | 758 | 840 | 31.5616 | -17.2237 | -6.761 | 814.284 | 13.4587 | -21.8807 | 23.0307 | 23.0307 | 22.7551 | 202.7551 | 28.7491 | 368.3318 | 368.3318 | 147.238 | 515.5697 | 0.48121 | 48.12% | 233.1406 | 112.1889 | 78.5322 | 121.1083 | 121.1083 | 64.84% | 11.7% | 11.7% | 90% | 10.53% | 24.5417 | 10.9754 | 6 | 147.2499 | 54.2717 | 121.6% | 121.6%
2 | 32 | 1 | 759 | 15 | -1.9 | 168.53 | 109.25 | 277.78 | 109.25 | 54.63 | 32 | 759 | 900 | 31.5616 | -17.2237 | -6.761 | 874.284 | 14.4587 | -36.8807 | 17.9055 | 17.9055 | 37.0431 | 217.0431 | 41.0217 | 413.5647 | 413.5647 | 93.2507 | 506.8154 | 0.47612 | 47.61% | 229.1819 | 109.1189 | 76.3832 | 116.1347 | 116.1347 | 65.77% | 11.71% | 11.71% | 90% | 10.53% | 24.1435 | 10.9403 | 6 | 144.8608 | 53.3911 | 124.7% | 124.7%
2 | 32 | 1 | 760 | 16 | -1.4 | 112.22 | 100.47 | 212.69 | 100.47 | 50.24 | 32 | 760 | 960 | 31.5616 | -17.2237 | -6.761 | 934.284 | 15.4587 | -51.8807 | 10.837 | 10.837 | 49.9152 | 229.9152 | 54.5391 | 346.2712 | 346.2712 | 85.7565 | 432.0277 | 0.42225 | 42.22% | 195.3629 | 82.4917 | 57.7442 | 112.7444 | 112.7444 | 51.22% | 11.79% | 0% | 85% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 761 | 17 | -1.6 | 52.14 | 63.53 | 115.67 | 63.53 | 31.77 | 32 | 761 | 1020 | 31.5616 | -17.2237 | -6.761 | 994.284 | 16.4587 | -66.8807 | 2.3535 | 2.3535 | 61.5447 | 241.5447 | 68.5511 | 0 | 0 | 54.2262 | 54.2262 | -2.2466 | 0% | 24.5211 | 0 | 0 | 147.2075 | 147.2075 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 762 | 18 | -2.6 | 0 | 20.97 | 20.97 | 20.97 | 10.49 | 32 | 762 | 1080 | 31.5616 | -17.2237 | -6.761 | 1054.284 | 17.4587 | -81.8807 | -7.0877 | 0 | 64.3816 | 244.3816 | 72.1976 | 0 | 0 | 17.899 | 17.899 | -8.5776 | 0% | 8.0939 | 0 | 0 | 136.0445 | 136.0445 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 763 | 19 | -3.7 | 0 | 0 | 0 | 0 | 0 | 32 | 763 | 1140 | 31.5616 | -17.2237 | -6.761 | 1114.284 | 18.4587 | -96.8807 | -17.1058 | 0 | 64.3816 | 244.3816 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.0255 | 129.0255 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 764 | 20 | -4.7 | 0 | 0 | 0 | 0 | 0 | 32 | 764 | 1200 | 31.5616 | -17.2237 | -6.761 | 1174.284 | 19.4587 | -111.8807 | -27.3578 | 0 | 64.3816 | 244.3816 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.6806 | 121.6806 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 765 | 21 | -4.5 | 0 | 0 | 0 | 0 | 0 | 32 | 765 | 1260 | 31.5616 | -17.2237 | -6.761 | 1234.284 | 20.4587 | -126.8807 | -37.4696 | 0 | 64.3816 | 244.3816 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4683 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 766 | 22 | -3.8 | 0 | 0 | 0 | 0 | 0 | 32 | 766 | 1320 | 31.5616 | -17.2237 | -6.761 | 1294.284 | 21.4587 | -141.8807 | -46.9185 | 0 | 64.3816 | 244.3816 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.7251 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 767 | 23 | -4.7 | 0 | 0 | 0 | 0 | 0 | 32 | 767 | 1380 | 31.5616 | -17.2237 | -6.761 | 1354.284 | 22.4587 | -156.8807 | -54.821 | 0 | 64.3816 | 244.3816 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.8239 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
2 | 32 | 1 | 768 | 24 | -5.5 | 0 | 0 | 0 | 0 | 0 | 32 | 768 | 1440 | 31.5616 | -17.2237 | -6.761 | 1414.284 | 23.4587 | -171.8807 | -59.6927 | 0 | 64.3816 | 244.3816 | 72.1976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.7703 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 769 | 1 | -5.5 | 0 | 0 | 0 | 0 | 0 | 33 | 769 | 60 | 32.5479 | -16.9509 | -6.6845 | 34.284 | 0.45999 | 173.1001 | -59.6309 | 0 | 64.803 | 115.197 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.2148 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 770 | 2 | -4.9 | 0 | 0 | 0 | 0 | 0 | 33 | 770 | 120 | 32.5479 | -16.9509 | -6.6845 | 94.284 | 1.46 | 158.1001 | -55.1107 | 0 | 64.803 | 115.197 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.0134 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 771 | 3 | -4.6 | 0 | 0 | 0 | 0 | 0 | 33 | 771 | 180 | 32.5479 | -16.9509 | -6.6845 | 154.284 | 2.46 | 143.1001 | -47.418 | 0 | 64.803 | 115.197 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2692 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 772 | 4 | -4.6 | 0 | 0 | 0 | 0 | 0 | 33 | 772 | 240 | 32.5479 | -16.9509 | -6.6845 | 214.284 | 3.46 | 128.1001 | -38.0727 | 0 | 64.803 | 115.197 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2692 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 773 | 5 | -5.3 | 0 | 0 | 0 | 0 | 0 | 33 | 773 | 300 | 32.5479 | -16.9509 | -6.6845 | 274.284 | 4.46 | 113.1001 | -27.9997 | 0 | 64.803 | 115.197 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8975 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.1725 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 774 | 6 | -5.5 | 0 | 0 | 0 | 0 | 0 | 33 | 774 | 360 | 32.5479 | -16.9509 | -6.6845 | 334.284 | 5.46 | 98.1001 | -17.7436 | 0 | 64.803 | 115.197 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0723 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 775 | 7 | -5.5 | 0 | 0 | 0 | 0 | 0 | 33 | 775 | 420 | 32.5479 | -16.9509 | -6.6845 | 394.284 | 6.46 | 83.1001 | -7.6868 | 0 | 64.803 | 115.197 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.9719 | 145.9719 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 776 | 8 | -5.6 | 0 | 0 | 0 | 0 | 0 | 33 | 776 | 480 | 32.5479 | -16.9509 | -6.6845 | 454.284 | 7.46 | 68.1001 | 1.8268 | 1.8268 | 62.6203 | 117.3797 | 69.6616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 151.3629 | 151.3629 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 777 | 9 | -5.9 | 0.92 | 10 | 10.92 | 10 | 5 | 33 | 777 | 540 | 32.5479 | -16.9509 | -6.6845 | 514.284 | 8.46 | 53.1001 | 10.42 | 10.42 | 51.0569 | 128.9431 | 55.597 | 2.8741 | 2.8741 | 8.5355 | 11.4096 | -14.6442 | 0% | 5.1594 | 0 | 0 | 131.7551 | 131.7551 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 778 | 10 | -6.1 | 14.64 | 62.22 | 76.86 | 62.22 | 31.11 | 33 | 778 | 600 | 32.5479 | -16.9509 | -6.6845 | 574.284 | 9.46 | 38.1001 | 17.6406 | 17.6406 | 38.269 | 141.731 | 41.9836 | 35.9104 | 35.9104 | 53.1081 | 89.0185 | -1.1817 | 0% | 40.2542 | 0 | 0 | 135.3875 | 135.3875 | 0% | 12.37% | 12.37% | 80% | 9.898% | 3.9844 | 12.4742 | 6 | 23.9064 | 8.8111 | 17.66% | 17.66%
2 | 33 | 2 | 779 | 11 | -4.7 | 98.97 | 107.69 | 206.66 | 107.69 | 53.85 | 33 | 779 | 660 | 32.5479 | -16.9509 | -6.6845 | 634.284 | 10.46 | 23.1001 | 22.9604 | 22.9604 | 24.0532 | 155.9468 | 29.4961 | 220.824 | 220.824 | 91.9192 | 312.7432 | 0.25016 | 25.02% | 141.4225 | 35.3782 | 24.7647 | 119.687 | 119.687 | 20.69% | 12.01% | 12.01% | 85% | 10.21% | 14.4418 | 11.9492 | 6 | 86.6511 | 31.9369 | 72.4% | 72.4%
2 | 33 | 2 | 780 | 12 | -4.7 | 196.67 | 93.14 | 289.81 | 93.14 | 46.57 | 33 | 780 | 720 | 32.5479 | -16.9509 | -6.6845 | 694.284 | 11.46 | 8.1001 | 25.8543 | 25.8543 | 8.6138 | 171.3862 | 20.3625 | 422.8092 | 422.8092 | 79.5 | 502.3091 | 0.45917 | 45.92% | 227.1442 | 104.2985 | 73.0089 | 117.0157 | 117.0157 | 62.39% | 11.76% | 11.76% | 90% | 10.58% | 24.0336 | 11.9492 | 6 | 144.2016 | 53.1482 | 123.2% | 123.2%
2 | 33 | 2 | 781 | 13 | -4 | 233.33 | 96.86 | 330.19 | 96.86 | 48.43 | 33 | 781 | 780 | 32.5479 | -16.9509 | -6.6845 | 754.284 | 12.46 | -6.8999 | 25.9683 | 25.9683 | 7.3437 | 187.3437 | 19.9276 | 500.9634 | 500.9634 | 82.6752 | 583.6386 | 0.51026 | 51.03% | 263.9214 | 134.6673 | 94.2671 | 118.1455 | 118.1455 | 79.79% | 11.64% | 11.64% | 90% | 10.47% | 27.6427 | 11.6918 | 6 | 165.8562 | 61.1294 | 140.4% | 140.4%
2 | 33 | 2 | 782 | 14 | -3.6 | 212.22 | 113.33 | 325.55 | 113.33 | 56.67 | 33 | 782 | 840 | 32.5479 | -16.9509 | -6.6845 | 814.284 | 13.46 | -21.8999 | 23.2876 | 23.2876 | 22.8566 | 202.8566 | 28.5915 | 471.3346 | 471.3346 | 96.7332 | 568.0678 | 0.50398 | 50.4% | 256.8803 | 129.462 | 90.6234 | 117.3126 | 117.3126 | 77.25% | 11.65% | 11.65% | 90% | 10.49% | 26.9409 | 11.5463 | 6 | 161.6456 | 59.5775 | 137.8% | 137.8%
2 | 33 | 2 | 783 | 15 | -4 | 194.92 | 87.42 | 282.34 | 87.42 | 43.71 | 33 | 783 | 900 | 32.5479 | -16.9509 | -6.6845 | 874.284 | 14.46 | -36.8999 | 18.1435 | 18.1435 | 37.1845 | 217.1845 | 40.9284 | 472.9243 | 472.9243 | 74.6176 | 547.5419 | 0.49089 | 49.09% | 247.5985 | 121.5437 | 85.0806 | 112.5276 | 112.5276 | 75.61% | 11.69% | 11.69% | 90% | 10.52% | 26.0392 | 11.6918 | 6 | 156.2354 | 57.5835 | 138.8% | 138.8%
2 | 33 | 2 | 784 | 16 | -3.7 | 146.86 | 63.06 | 209.92 | 63.06 | 31.53 | 33 | 784 | 960 | 32.5479 | -16.9509 | -6.6845 | 934.284 | 15.46 | -51.8999 | 11.0549 | 11.0549 | 50.0832 | 230.0832 | 54.4861 | 444.9077 | 444.9077 | 53.8251 | 498.7328 | 0.46176 | 46.18% | 225.527 | 104.1401 | 72.8981 | 108.8069 | 108.8069 | 67% | 11.74% | 0% | 85% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 785 | 17 | -4.4 | 75.75 | 38.81 | 114.56 | 38.81 | 19.41 | 33 | 785 | 1020 | 32.5479 | -16.9509 | -6.6845 | 994.284 | 16.46 | -66.8999 | 2.5537 | 2.5537 | 61.731 | 241.731 | 68.5267 | 0 | 0 | 33.1264 | 33.1264 | -4.4018 | 0% | 14.9798 | 0 | 0 | 142.8669 | 142.8669 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 786 | 18 | -4.6 | 0 | 15.56 | 15.56 | 15.56 | 7.78 | 33 | 786 | 1080 | 32.5479 | -16.9509 | -6.6845 | 1054.284 | 17.46 | -81.8999 | -6.901 | 0 | 64.803 | 244.803 | 72.4801 | 0 | 0 | 13.2813 | 13.2813 | -12.2186 | 0% | 6.0058 | 0 | 0 | 132.0552 | 132.0552 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 787 | 19 | -5.4 | 0 | 0 | 0 | 0 | 0 | 33 | 787 | 1140 | 32.5479 | -16.9509 | -6.6845 | 1114.284 | 18.46 | -96.8999 | -16.927 | 0 | 64.803 | 244.803 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.3693 | 126.3693 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 788 | 20 | -6.2 | 0 | 0 | 0 | 0 | 0 | 33 | 788 | 1200 | 32.5479 | -16.9509 | -6.6845 | 1174.284 | 19.46 | -111.8999 | -27.1801 | 0 | 64.803 | 244.803 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.2299 | 120.2299 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 789 | 21 | -6.3 | 0 | 0 | 0 | 0 | 0 | 33 | 789 | 1260 | 32.5479 | -16.9509 | -6.6845 | 1234.284 | 20.46 | -126.8999 | -37.2846 | 0 | 64.803 | 244.803 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.1584 | 0 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5503 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 790 | 22 | -7 | 0 | 0 | 0 | 0 | 0 | 33 | 790 | 1320 | 32.5479 | -16.9509 | -6.6845 | 1294.284 | 21.46 | -141.8999 | -46.7153 | 0 | 64.803 | 244.803 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.3618 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8189 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 791 | 23 | -7 | 0 | 0 | 0 | 0 | 0 | 33 | 791 | 1380 | 32.5479 | -16.9509 | -6.6845 | 1354.284 | 22.46 | -156.8999 | -54.588 | 0 | 64.803 | 244.803 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.0748 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8189 | 6 | 0 | 0 | 0% | 0%
2 | 33 | 2 | 792 | 24 | -7.2 | 0 | 0 | 0 | 0 | 0 | 33 | 792 | 1440 | 32.5479 | -16.9509 | -6.6845 | 1414.284 | 23.46 | -171.8999 | -59.4285 | 0 | 64.803 | 244.803 | 72.4801 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.0926 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 793 | 1 | -7.2 | 0 | 0 | 0 | 0 | 0 | 34 | 793 | 60 | 33.5342 | -16.6733 | -6.5964 | 34.284 | 0.46146 | 173.0781 | -59.3535 | 0 | 65.2312 | 114.7688 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.245 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 794 | 2 | -7.4 | 0 | 0 | 0 | 0 | 0 | 34 | 794 | 120 | 33.5342 | -16.6733 | -6.5964 | 94.284 | 1.4615 | 158.0781 | -54.8527 | 0 | 65.2312 | 114.7688 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.4604 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 12.9739 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 795 | 3 | -8.1 | 0 | 0 | 0 | 0 | 0 | 34 | 795 | 180 | 33.5342 | -16.6733 | -6.5964 | 154.284 | 2.4615 | 143.0781 | -47.1845 | 0 | 65.2312 | 114.7688 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.4379 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.248 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 796 | 4 | -7.8 | 0 | 0 | 0 | 0 | 0 | 34 | 796 | 240 | 33.5342 | -16.6733 | -6.5964 | 214.284 | 3.4615 | 128.0781 | -37.8557 | 0 | 65.2312 | 114.7688 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.9807 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 797 | 5 | -8.6 | 0 | 0 | 0 | 0 | 0 | 34 | 797 | 300 | 33.5342 | -16.6733 | -6.5964 | 274.284 | 4.4615 | 113.0781 | -27.79 | 0 | 65.2312 | 114.7688 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.8689 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4458 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 798 | 6 | -8.7 | 0 | 0 | 0 | 0 | 0 | 34 | 798 | 360 | 33.5342 | -16.6733 | -6.5964 | 334.284 | 5.4615 | 98.0781 | -17.5335 | 0 | 65.2312 | 114.7688 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.3355 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 799 | 7 | -9 | 0 | 0 | 0 | 0 | 0 | 34 | 799 | 420 | 33.5342 | -16.6733 | -6.5964 | 394.284 | 6.4615 | 83.0781 | -7.4703 | 0 | 65.2312 | 114.7688 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.0739 | 124.0739 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6053 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 800 | 8 | -9.1 | 0 | 0 | 0 | 0 | 0 | 34 | 800 | 480 | 33.5342 | -16.6733 | -6.5964 | 454.284 | 7.4615 | 68.0781 | 2.0545 | 2.0545 | 62.7806 | 117.2194 | 69.6 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.5415 | 126.5415 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6454 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 801 | 9 | -8.3 | 0.08 | 5.19 | 5.27 | 5.19 | 2.6 | 34 | 801 | 540 | 33.5342 | -16.6733 | -6.5964 | 514.284 | 8.4615 | 53.0781 | 10.6624 | 10.6624 | 51.1964 | 128.8036 | 55.5081 | 0.24485 | 0.24485 | 4.4299 | 4.6748 | -38.2163 | 0% | 2.1139 | 0 | 0 | 107.7449 | 107.7449 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 802 | 10 | -7.1 | 0.47 | 28.89 | 29.36 | 28.89 | 14.45 | 34 | 802 | 600 | 33.5342 | -16.6733 | -6.5964 | 574.284 | 9.4615 | 38.0781 | 17.8987 | 17.8987 | 38.3785 | 141.6215 | 41.8572 | 1.139 | 1.139 | 24.6592 | 25.7982 | -6.1471 | 0% | 11.6659 | 0 | 0 | 111.6437 | 111.6437 | 0% | 12.51% | 12.51% | 80% | 10% | 1.1671 | 12.8576 | 6 | 7.0029 | 2.581 | 6.273% | 6.273%
2 | 34 | 3 | 803 | 11 | -4.3 | 0.92 | 50.56 | 51.48 | 50.56 | 25.28 | 34 | 803 | 660 | 33.5342 | -16.6733 | -6.5964 | 634.284 | 10.4615 | 23.0781 | 23.2321 | 23.2321 | 24.1194 | 155.8806 | 29.3121 | 2.0337 | 2.0337 | 43.1557 | 45.1894 | -3.0066 | 0% | 20.4346 | 0 | 0 | 116.1082 | 116.1082 | 0% | 12.36% | 12.36% | 80% | 9.889% | 2.0207 | 11.8017 | 6 | 12.1242 | 4.4686 | 10.44% | 10.44%
2 | 34 | 3 | 804 | 12 | -3.4 | 2.86 | 86.31 | 89.17 | 86.31 | 43.16 | 34 | 804 | 720 | 33.5342 | -16.6733 | -6.5964 | 694.284 | 11.4615 | 8.0781 | 26.1325 | 26.1325 | 8.6236 | 171.3764 | 20.1003 | 6.0979 | 6.0979 | 73.6702 | 79.7681 | -1.3263 | 0% | 36.0711 | 0 | 0 | 117.3759 | 117.3759 | 0% | 12.28% | 12.28% | 80% | 9.823% | 3.5433 | 11.4739 | 6 | 21.2599 | 7.8357 | 18.11% | 18.11%
2 | 34 | 3 | 805 | 13 | -3 | 75.92 | 134.44 | 210.36 | 134.44 | 67.22 | 34 | 805 | 780 | 33.5342 | -16.6733 | -6.5964 | 754.284 | 12.4615 | -6.9219 | 26.2429 | 26.2429 | 7.3954 | 187.3954 | 19.6756 | 161.6713 | 161.6713 | 114.7517 | 276.4231 | 0.19289 | 19.29% | 124.9985 | 24.111 | 16.8777 | 102.4097 | 102.4097 | 16.48% | 12.01% | 12.01% | 80% | 9.611% | 12.0142 | 11.3301 | 6 | 72.0851 | 26.5683 | 70.39% | 70.39%
2 | 34 | 3 | 806 | 14 | -2 | 108.25 | 132.14 | 240.39 | 132.14 | 66.07 | 34 | 806 | 840 | 33.5342 | -16.6733 | -6.5964 | 814.284 | 13.4615 | -21.9219 | 23.5484 | 23.5484 | 22.9629 | 202.9629 | 28.4347 | 238.2608 | 238.2608 | 112.7885 | 351.0494 | 0.32993 | 32.99% | 158.7445 | 52.3744 | 36.6621 | 104.7523 | 104.7523 | 35% | 11.9% | 11.9% | 85% | 10.11% | 16.0506 | 10.9754 | 6 | 96.3034 | 35.4944 | 91.93% | 91.93%
2 | 34 | 3 | 807 | 15 | -1.1 | 113.61 | 74.44 | 188.05 | 74.44 | 37.22 | 34 | 807 | 900 | 33.5342 | -16.6733 | -6.5964 | 874.284 | 14.4615 | -36.9219 | 18.3846 | 18.3846 | 37.3311 | 217.3311 | 40.837 | 272.5293 | 272.5293 | 63.5385 | 336.0678 | 0.31546 | 31.55% | 151.9698 | 47.9409 | 33.5586 | 102.61 | 102.61 | 32.71% | 11.89% | 11.89% | 85% | 10.11% | 15.3593 | 10.6622 | 6 | 92.156 | 33.9658 | 89.81% | 89.81%
2 | 34 | 3 | 808 | 16 | -1.2 | 62.31 | 58.53 | 120.84 | 58.53 | 29.27 | 34 | 808 | 960 | 33.5342 | -16.6733 | -6.5964 | 934.284 | 15.4615 | -51.9219 | 11.2753 | 11.2753 | 50.2567 | 230.2567 | 54.4355 | 185.3518 | 185.3518 | 49.9585 | 235.3102 | 0.10522 | 10.52% | 106.4073 | 11.1962 | 7.8374 | 140.8916 | 140.8916 | 5.563% | 12.01% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 809 | 17 | -2 | 30.08 | 38.42 | 68.5 | 38.42 | 19.21 | 34 | 809 | 1020 | 33.5342 | -16.6733 | -6.5964 | 994.284 | 16.4615 | -66.9219 | 2.7559 | 2.7559 | 61.9226 | 241.9226 | 68.5049 | 0 | 0 | 32.7935 | 32.7935 | -4.2709 | 0% | 14.8292 | 0 | 0 | 135.9436 | 135.9436 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 810 | 18 | -2.9 | 0 | 13.06 | 13.06 | 13.06 | 6.53 | 34 | 810 | 1080 | 33.5342 | -16.6733 | -6.5964 | 1054.284 | 17.4615 | -81.9219 | -6.7125 | 0 | 65.2312 | 245.2312 | 72.7676 | 0 | 0 | 11.1474 | 11.1474 | -14.3272 | 0% | 5.0409 | 0 | 0 | 129.4353 | 129.4353 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 811 | 19 | -3.9 | 0 | 0 | 0 | 0 | 0 | 34 | 811 | 1140 | 33.5342 | -16.6733 | -6.5964 | 1114.284 | 18.4615 | -96.9219 | -16.7465 | 0 | 65.2312 | 245.2312 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.2961 | 125.2961 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 812 | 20 | -5.2 | 0 | 0 | 0 | 0 | 0 | 34 | 812 | 1200 | 33.5342 | -16.6733 | -6.5964 | 1174.284 | 19.4615 | -111.9219 | -27.0007 | 0 | 65.2312 | 245.2312 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.7782 | 120.7782 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 813 | 21 | -6.7 | 0 | 0 | 0 | 0 | 0 | 34 | 813 | 1260 | 33.5342 | -16.6733 | -6.5964 | 1234.284 | 20.4615 | -126.9219 | -37.0974 | 0 | 65.2312 | 245.2312 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.1588 | 0 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7034 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 814 | 22 | -7.6 | 0 | 0 | 0 | 0 | 0 | 34 | 814 | 1320 | 33.5342 | -16.6733 | -6.5964 | 1294.284 | 21.4615 | -141.9219 | -46.5094 | 0 | 65.2312 | 245.2312 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.1226 | 0 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.0519 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 815 | 23 | -8.4 | 0 | 0 | 0 | 0 | 0 | 34 | 815 | 1380 | 33.5342 | -16.6733 | -6.5964 | 1354.284 | 22.4615 | -156.9219 | -54.3516 | 0 | 65.2312 | 245.2312 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.2524 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
2 | 34 | 3 | 816 | 24 | -8.9 | 0 | 0 | 0 | 0 | 0 | 34 | 816 | 1440 | 33.5342 | -16.6733 | -6.5964 | 1414.284 | 23.4615 | -171.9219 | -59.1598 | 0 | 65.2312 | 245.2312 | 72.7676 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.9251 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5653 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 817 | 1 | -9.5 | 0 | 0 | 0 | 0 | 0 | 35 | 817 | 60 | 34.5205 | -16.3909 | -6.4969 | 34.284 | 0.46312 | 173.0532 | -59.0709 | 0 | 65.6658 | 114.3342 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.9021 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8063 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 818 | 2 | -9.6 | 0 | 0 | 0 | 0 | 0 | 35 | 818 | 120 | 34.5205 | -16.3909 | -6.4969 | 94.284 | 1.4631 | 158.0532 | -54.5889 | 0 | 65.6658 | 114.3342 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.7307 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 819 | 3 | -10.4 | 0 | 0 | 0 | 0 | 0 | 35 | 819 | 180 | 34.5205 | -16.3909 | -6.4969 | 154.284 | 2.4631 | 143.0532 | -46.945 | 0 | 65.6658 | 114.3342 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.6262 | 0 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.1724 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 820 | 4 | -10.6 | 0 | 0 | 0 | 0 | 0 | 35 | 820 | 240 | 34.5205 | -16.3909 | -6.4969 | 214.284 | 3.4631 | 128.0532 | -37.6329 | 0 | 65.6658 | 114.3342 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.931 | 0 | 0% | 12.7% | 0% | 80% | 0% | 0 | 14.2546 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 821 | 5 | -11 | 0 | 0 | 0 | 0 | 0 | 35 | 821 | 300 | 34.5205 | -16.3909 | -6.4969 | 274.284 | 4.4631 | 113.0532 | -27.5746 | 0 | 65.6658 | 114.3342 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.4648 | 0 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4197 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 822 | 6 | -11.4 | 0 | 0 | 0 | 0 | 0 | 35 | 822 | 360 | 34.5205 | -16.3909 | -6.4969 | 334.284 | 5.4631 | 98.0532 | -17.3179 | 0 | 65.6658 | 114.3342 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2046 | 0 | 0% | 12.73% | 0% | 80% | 0% | 0 | 14.5859 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 823 | 7 | -11.2 | 0 | 0 | 0 | 0 | 0 | 35 | 823 | 420 | 34.5205 | -16.3909 | -6.4969 | 394.284 | 6.4631 | 83.0532 | -7.2484 | 0 | 65.6658 | 114.3342 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.438 | 137.438 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.5027 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 824 | 8 | -11.6 | 0 | 0 | 0 | 0 | 0 | 35 | 824 | 480 | 34.5205 | -16.3909 | -6.4969 | 454.284 | 7.4631 | 68.0532 | 2.2876 | 2.2876 | 62.9419 | 117.0581 | 69.5355 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.7802 | 141.7802 | 0% | 12.74% | 0% | 80% | 0% | 0 | 14.6695 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 825 | 9 | -11.8 | 3.14 | 7.69 | 10.83 | 7.69 | 3.85 | 35 | 825 | 540 | 34.5205 | -16.3909 | -6.4969 | 514.284 | 8.4631 | 53.0532 | 10.9101 | 10.9101 | 51.3364 | 128.6636 | 55.4162 | 9.4167 | 9.4167 | 6.5638 | 15.9806 | -11.1808 | 0% | 7.2264 | 0 | 0 | 122.1982 | 122.1982 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.7533 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 826 | 10 | -10.2 | 38.61 | 31.03 | 69.64 | 31.03 | 15.52 | 35 | 826 | 600 | 34.5205 | -16.3909 | -6.4969 | 574.284 | 9.4631 | 38.0532 | 18.1624 | 18.1624 | 38.4879 | 141.5121 | 41.7277 | 92.4425 | 92.4425 | 26.4858 | 118.9282 | -0.77122 | 0% | 53.7793 | 0 | 0 | 127.5152 | 127.5152 | 0% | 12.48% | 12.48% | 80% | 9.987% | 5.3707 | 14.0906 | 6 | 32.2244 | 11.8769 | 25.27% | 25.27%
2 | 35 | 4 | 827 | 11 | -8.3 | 84.53 | 56.86 | 141.39 | 56.86 | 28.43 | 35 | 827 | 660 | 34.5205 | -16.3909 | -6.4969 | 634.284 | 10.4631 | 23.0532 | 23.5092 | 23.5092 | 24.1845 | 155.8155 | 29.1243 | 185.1172 | 185.1172 | 48.533 | 233.6503 | 0.023296 | 2.33% | 105.6567 | 2.4613 | 1.7229 | 129.519 | 129.519 | 1.33% | 12.23% | 12.23% | 80% | 9.787% | 10.3404 | 13.3269 | 6 | 62.0425 | 22.8669 | 47.9% | 47.9%
2 | 35 | 4 | 828 | 12 | -7.2 | 118.53 | 102.42 | 220.95 | 102.42 | 51.21 | 35 | 828 | 720 | 34.5205 | -16.3909 | -6.4969 | 694.284 | 11.4631 | 8.0532 | 26.4159 | 26.4159 | 8.6309 | 171.3691 | 19.833 | 250.6262 | 250.6262 | 87.4209 | 338.0471 | 0.27277 | 27.28% | 152.8649 | 41.6966 | 29.1876 | 107.1394 | 107.1394 | 27.24% | 12.04% | 12.04% | 85% | 10.24% | 15.6482 | 12.8963 | 6 | 93.8892 | 34.6046 | 87.63% | 87.63%
2 | 35 | 4 | 829 | 13 | -5.5 | 136.94 | 153.61 | 290.55 | 153.61 | 76.81 | 35 | 829 | 780 | 34.5205 | -16.3909 | -6.4969 | 754.284 | 12.4631 | -6.9468 | 26.5219 | 26.5219 | 7.451 | 187.451 | 19.4207 | 289.2206 | 289.2206 | 131.1143 | 420.335 | 0.3871 | 38.71% | 190.0755 | 73.5773 | 51.5041 | 110.9282 | 110.9282 | 46.43% | 11.88% | 11.88% | 85% | 10.1% | 19.2011 | 12.2475 | 6 | 115.2064 | 42.4614 | 103.9% | 103.9%
2 | 35 | 4 | 830 | 14 | -2.9 | 138.97 | 166.39 | 305.36 | 166.39 | 83.2 | 35 | 830 | 840 | 34.5205 | -16.3909 | -6.4969 | 814.284 | 13.4631 | -21.9468 | 23.8129 | 23.8129 | 23.074 | 203.074 | 28.2789 | 303.1179 | 303.1179 | 142.0227 | 445.1407 | 0.42508 | 42.51% | 201.2926 | 85.5649 | 59.8954 | 114.0052 | 114.0052 | 52.54% | 11.8% | 11.8% | 85% | 10.03% | 20.1878 | 11.2943 | 6 | 121.1271 | 44.6436 | 106.2% | 106.2%
2 | 35 | 4 | 831 | 15 | -2.3 | 90.64 | 94.17 | 184.81 | 94.17 | 47.09 | 35 | 831 | 900 | 34.5205 | -16.3909 | -6.4969 | 874.284 | 14.4631 | -36.9468 | 18.6287 | 18.6287 | 37.483 | 217.483 | 40.7478 | 214.9674 | 214.9674 | 80.3791 | 295.3465 | 0.23798 | 23.8% | 133.5557 | 31.7838 | 22.2486 | 107.0477 | 107.0477 | 20.78% | 11.97% | 11.97% | 80% | 9.577% | 12.7903 | 11.0811 | 6 | 76.7419 | 28.2846 | 71.69% | 71.69%
2 | 35 | 4 | 832 | 16 | -1.4 | 50.36 | 80.75 | 131.11 | 80.75 | 40.38 | 35 | 832 | 960 | 34.5205 | -16.3909 | -6.4969 | 934.284 | 15.4631 | -51.9468 | 11.4981 | 11.4981 | 50.4354 | 230.4354 | 54.3874 | 147.113 | 147.113 | 68.9244 | 216.0374 | 0.04058 | 4.058% | 97.6921 | 3.9644 | 2.7751 | 146.3463 | 146.3463 | 1.896% | 12.04% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 833 | 17 | -1.9 | 7.78 | 67.69 | 75.47 | 67.69 | 33.85 | 35 | 833 | 1020 | 34.5205 | -16.3909 | -6.4969 | 994.284 | 16.4631 | -66.9468 | 2.9599 | 2.9599 | 62.1195 | 242.1195 | 68.4856 | 0 | 0 | 57.777 | 57.777 | -2.0721 | 0% | 26.1268 | 0 | 0 | 140.363 | 140.363 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 834 | 18 | -2.8 | 0 | 18.06 | 18.06 | 18.06 | 9.03 | 35 | 834 | 1080 | 34.5205 | -16.3909 | -6.4969 | 1054.284 | 17.4631 | -81.9468 | -6.5224 | 0 | 65.6658 | 245.6658 | 73.0601 | 0 | 0 | 15.4152 | 15.4152 | -10.1218 | 0% | 6.9707 | 0 | 0 | 133.3652 | 133.3652 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 835 | 19 | -3.6 | 0 | 0 | 0 | 0 | 0 | 35 | 835 | 1140 | 34.5205 | -16.3909 | -6.4969 | 1114.284 | 18.4631 | -96.9468 | -16.5645 | 0 | 65.6658 | 245.6658 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.7372 | 128.7372 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 836 | 20 | -4.3 | 0 | 0 | 0 | 0 | 0 | 35 | 836 | 1200 | 34.5205 | -16.3909 | -6.4969 | 1174.284 | 19.4631 | -111.9468 | -26.8195 | 0 | 65.6658 | 245.6658 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.834 | 123.834 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 837 | 21 | -5.1 | 0 | 0 | 0 | 0 | 0 | 35 | 837 | 1260 | 34.5205 | -16.3909 | -6.4969 | 1234.284 | 20.4631 | -126.9468 | -36.9082 | 0 | 65.6658 | 245.6658 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.3065 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 838 | 22 | -6 | 0 | 0 | 0 | 0 | 0 | 35 | 838 | 1320 | 34.5205 | -16.3909 | -6.4969 | 1294.284 | 21.4631 | -141.9468 | -46.3007 | 0 | 65.6658 | 245.6658 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.5392 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 839 | 23 | -7.8 | 0 | 0 | 0 | 0 | 0 | 35 | 839 | 1380 | 34.5205 | -16.3909 | -6.4969 | 1354.284 | 22.4631 | -156.9468 | -54.1116 | 0 | 65.6658 | 245.6658 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.9587 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
2 | 35 | 4 | 840 | 24 | -8.3 | 0 | 0 | 0 | 0 | 0 | 35 | 840 | 1440 | 34.5205 | -16.3909 | -6.4969 | 1414.284 | 23.4631 | -171.9468 | -58.8868 | 0 | 65.6658 | 245.6658 | 73.0601 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.397 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 841 | 1 | -8.5 | 0 | 0 | 0 | 0 | 0 | 36 | 841 | 60 | 35.5068 | -16.1038 | -6.3859 | 34.284 | 0.46497 | 173.0255 | -58.7833 | 0 | 66.1068 | 113.8932 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.5743 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4061 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 842 | 2 | -9.4 | 0 | 0 | 0 | 0 | 0 | 36 | 842 | 120 | 35.5068 | -16.1038 | -6.3859 | 94.284 | 1.465 | 158.0255 | -54.3194 | 0 | 66.1068 | 113.8932 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.8288 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.7659 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 843 | 3 | -9.6 | 0 | 0 | 0 | 0 | 0 | 36 | 843 | 180 | 35.5068 | -16.1038 | -6.3859 | 154.284 | 2.465 | 143.0255 | -46.6997 | 0 | 66.1068 | 113.8932 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.0165 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 844 | 4 | -10.2 | 0 | 0 | 0 | 0 | 0 | 36 | 844 | 240 | 35.5068 | -16.1038 | -6.3859 | 214.284 | 3.465 | 128.0255 | -37.4042 | 0 | 66.1068 | 113.8932 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.9309 | 0 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.0906 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 845 | 5 | -10.6 | 0 | 0 | 0 | 0 | 0 | 36 | 845 | 300 | 35.5068 | -16.1038 | -6.3859 | 274.284 | 4.465 | 113.0255 | -27.3535 | 0 | 66.1068 | 113.8932 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.7787 | 0 | 0% | 12.7% | 0% | 80% | 0% | 0 | 14.2546 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 846 | 6 | -10.9 | 0 | 0 | 0 | 0 | 0 | 36 | 846 | 360 | 35.5068 | -16.1038 | -6.3859 | 334.284 | 5.465 | 98.0255 | -17.0967 | 0 | 66.1068 | 113.8932 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.3613 | 0 | 0% | 12.71% | 0% | 80% | 0% | 0 | 14.3783 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 847 | 7 | -10.9 | 0 | 0 | 0 | 0 | 0 | 36 | 847 | 420 | 35.5068 | -16.1038 | -6.3859 | 394.284 | 6.465 | 83.0255 | -7.021 | 0 | 66.1068 | 113.8932 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.0912 | 126.0912 | 0% | 12.71% | 0% | 80% | 0% | 0 | 14.3783 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 848 | 8 | -11.1 | 0 | 0 | 0 | 0 | 0 | 36 | 848 | 480 | 35.5068 | -16.1038 | -6.3859 | 454.284 | 7.465 | 68.0255 | 2.5262 | 2.5262 | 63.104 | 116.896 | 69.4679 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.5603 | 129.5603 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4612 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 849 | 9 | -11 | 0.08 | 7.69 | 7.77 | 7.69 | 3.85 | 36 | 849 | 540 | 35.5068 | -16.1038 | -6.3859 | 514.284 | 8.465 | 53.0255 | 11.1634 | 11.1634 | 51.477 | 128.523 | 55.3212 | 0.23511 | 0.23511 | 6.5638 | 6.7989 | -27.0573 | 0% | 3.0745 | 0 | 0 | 110.1437 | 110.1437 | 0% | 12.7% | 0% | 80% | 0% | 0 | 14.4197 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 850 | 10 | -10.2 | 1.86 | 42.14 | 44 | 42.14 | 21.07 | 36 | 850 | 600 | 35.5068 | -16.1038 | -6.3859 | 574.284 | 9.465 | 38.0255 | 18.4314 | 18.4314 | 38.5972 | 141.4028 | 41.595 | 4.3996 | 4.3996 | 35.9687 | 40.3683 | -3.8367 | 0% | 18.2546 | 0 | 0 | 114.4779 | 114.4779 | 0% | 12.61% | 12.61% | 80% | 10.09% | 1.8421 | 14.0906 | 6 | 11.0524 | 4.0736 | 9.655% | 9.655%
2 | 36 | 5 | 851 | 11 | -8.5 | 7.97 | 103.97 | 111.94 | 103.97 | 51.99 | 36 | 851 | 660 | 35.5068 | -16.1038 | -6.3859 | 634.284 | 10.465 | 23.0255 | 23.7915 | 23.7915 | 24.2484 | 155.7516 | 28.933 | 17.2907 | 17.2907 | 88.7439 | 106.0346 | -0.92117 | 0% | 47.9489 | 0 | 0 | 119.1402 | 119.1402 | 0% | 12.44% | 12.44% | 80% | 9.952% | 4.7718 | 13.4061 | 6 | 28.6307 | 10.5524 | 24.03% | 24.03%
2 | 36 | 5 | 852 | 12 | -7.4 | 32.78 | 160.64 | 193.42 | 160.64 | 80.32 | 36 | 852 | 720 | 35.5068 | -16.1038 | -6.3859 | 694.284 | 11.465 | 8.0255 | 26.7042 | 26.7042 | 8.6356 | 171.3644 | 19.5607 | 68.7344 | 68.7344 | 137.1148 | 205.8492 | -0.070888 | 0% | 93.085 | 0 | 0 | 122.0082 | 122.0082 | 0% | 12.25% | 12.25% | 80% | 9.798% | 9.1204 | 12.9739 | 6 | 54.7223 | 20.1689 | 44.85% | 44.85%
2 | 36 | 5 | 853 | 13 | -5.5 | 43.97 | 204.72 | 248.69 | 204.72 | 102.36 | 36 | 853 | 780 | 35.5068 | -16.1038 | -6.3859 | 754.284 | 12.465 | -6.9745 | 26.8053 | 26.8053 | 7.5105 | 187.5105 | 19.1634 | 92.1002 | 92.1002 | 174.7395 | 266.8396 | 0.14728 | 14.73% | 120.6649 | 17.7712 | 12.4398 | 106.4535 | 106.4535 | 11.69% | 12.1% | 12.1% | 80% | 9.68% | 11.6801 | 12.2475 | 6 | 70.0808 | 25.8296 | 65.83% | 65.83%
2 | 36 | 5 | 854 | 14 | -4.4 | 107.03 | 165.83 | 272.86 | 165.83 | 82.92 | 36 | 854 | 840 | 35.5068 | -16.1038 | -6.3859 | 814.284 | 13.465 | -21.9745 | 24.081 | 24.081 | 23.1901 | 203.1901 | 28.1243 | 231.3385 | 231.3385 | 141.5448 | 372.8833 | 0.34152 | 34.15% | 168.6178 | 57.5865 | 40.3105 | 108.548 | 108.548 | 37.14% | 11.93% | 11.93% | 85% | 10.14% | 17.0918 | 11.8384 | 6 | 102.5508 | 37.797 | 94.48% | 94.48%
2 | 36 | 5 | 855 | 15 | -4 | 162.14 | 134.36 | 296.5 | 134.36 | 67.18 | 36 | 855 | 900 | 35.5068 | -16.1038 | -6.3859 | 874.284 | 14.465 | -36.9745 | 18.8757 | 18.8757 | 37.6402 | 217.6402 | 40.6609 | 380.1857 | 380.1857 | 114.6834 | 494.8691 | 0.45756 | 45.76% | 223.7798 | 102.3935 | 71.6754 | 108.6606 | 108.6606 | 65.96% | 11.75% | 11.75% | 85% | 9.992% | 22.3591 | 11.6918 | 6 | 134.1545 | 49.4451 | 123.5% | 123.5%
2 | 36 | 5 | 856 | 16 | -3.1 | 106.86 | 120 | 226.86 | 120 | 60 | 36 | 856 | 960 | 35.5068 | -16.1038 | -6.3859 | 934.284 | 15.465 | -51.9745 | 11.7231 | 11.7231 | 50.6195 | 230.6195 | 54.3418 | 306.5926 | 306.5926 | 102.4264 | 409.019 | 0.39039 | 39.04% | 184.9584 | 72.2052 | 50.5437 | 106.4041 | 106.4041 | 47.5% | 11.85% | 0% | 85% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 857 | 17 | -2.8 | 40 | 78.81 | 118.81 | 78.81 | 39.41 | 36 | 857 | 1020 | 35.5068 | -16.1038 | -6.3859 | 994.284 | 16.465 | -66.9745 | 3.1658 | 3.1658 | 62.3217 | 242.3217 | 68.469 | 0 | 0 | 67.2685 | 67.2685 | -1.6997 | 0% | 30.4188 | 0 | 0 | 141.7171 | 141.7171 | 0% | 12.27% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 858 | 18 | -2.9 | 0 | 25.83 | 25.83 | 25.83 | 12.92 | 36 | 858 | 1080 | 35.5068 | -16.1038 | -6.3859 | 1054.284 | 17.465 | -81.9745 | -6.3307 | 0 | 66.1068 | 246.1068 | 73.3574 | 0 | 0 | 22.0473 | 22.0473 | -6.8466 | 0% | 9.9698 | 0 | 0 | 133.6165 | 133.6165 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 859 | 19 | -3.5 | 0 | 0 | 0 | 0 | 0 | 36 | 859 | 1140 | 35.5068 | -16.1038 | -6.3859 | 1114.284 | 18.465 | -96.9745 | -16.3808 | 0 | 66.1068 | 246.1068 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.4149 | 128.4149 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 860 | 20 | -3.6 | 0 | 0 | 0 | 0 | 0 | 36 | 860 | 1200 | 35.5068 | -16.1038 | -6.3859 | 1174.284 | 19.465 | -111.9745 | -26.6366 | 0 | 66.1068 | 246.1068 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.4232 | 124.4232 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 861 | 21 | -3.9 | 0 | 0 | 0 | 0 | 0 | 36 | 861 | 1260 | 35.5068 | -16.1038 | -6.3859 | 1234.284 | 20.465 | -126.9745 | -36.7168 | 0 | 66.1068 | 246.1068 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0215 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 862 | 22 | -4.2 | 0 | 0 | 0 | 0 | 0 | 36 | 862 | 1320 | 35.5068 | -16.1038 | -6.3859 | 1294.284 | 21.465 | -141.9745 | -46.0893 | 0 | 66.1068 | 246.1068 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.3724 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 863 | 23 | -4.1 | 0 | 0 | 0 | 0 | 0 | 36 | 863 | 1380 | 35.5068 | -16.1038 | -6.3859 | 1354.284 | 22.465 | -156.9745 | -53.8682 | 0 | 66.1068 | 246.1068 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.1029 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
2 | 36 | 5 | 864 | 24 | -4.1 | 0 | 0 | 0 | 0 | 0 | 36 | 864 | 1440 | 35.5068 | -16.1038 | -6.3859 | 1414.284 | 23.465 | -171.9745 | -58.6096 | 0 | 66.1068 | 246.1068 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.9858 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 865 | 1 | -3.8 | 0 | 0 | 0 | 0 | 0 | 37 | 865 | 60 | 36.4932 | -15.812 | -6.2635 | 34.284 | 0.46701 | 172.9949 | -58.4906 | 0 | 66.554 | 113.446 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5277 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 866 | 2 | -3.6 | 0 | 0 | 0 | 0 | 0 | 37 | 866 | 120 | 36.4932 | -15.812 | -6.2635 | 94.284 | 1.467 | 157.9949 | -54.0443 | 0 | 66.554 | 113.446 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8711 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 867 | 3 | -3.7 | 0 | 0 | 0 | 0 | 0 | 37 | 867 | 180 | 36.4932 | -15.812 | -6.2635 | 154.284 | 2.467 | 142.9949 | -46.4485 | 0 | 66.554 | 113.446 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6716 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 868 | 4 | -3.2 | 0 | 0 | 0 | 0 | 0 | 37 | 868 | 240 | 36.4932 | -15.812 | -6.2635 | 214.284 | 3.467 | 127.9949 | -37.1699 | 0 | 66.554 | 113.446 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.9096 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 869 | 5 | -3.1 | 0 | 0 | 0 | 0 | 0 | 37 | 869 | 300 | 36.4932 | -15.812 | -6.2635 | 274.284 | 4.467 | 112.9949 | -27.1269 | 0 | 66.554 | 113.446 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7524 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 870 | 6 | -3.1 | 0 | 0 | 0 | 0 | 0 | 37 | 870 | 360 | 36.4932 | -15.812 | -6.2635 | 334.284 | 5.467 | 97.9949 | -16.8702 | 0 | 66.554 | 113.446 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1571 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 871 | 7 | -3 | 0 | 0 | 0 | 0 | 0 | 37 | 871 | 420 | 36.4932 | -15.812 | -6.2635 | 394.284 | 6.467 | 82.9949 | -6.7882 | 0 | 66.554 | 113.446 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.5015 | 149.5015 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 872 | 8 | -3 | 0 | 0 | 0 | 0 | 0 | 37 | 872 | 480 | 36.4932 | -15.812 | -6.2635 | 454.284 | 7.467 | 67.9949 | 2.7701 | 2.7701 | 63.2669 | 116.7331 | 69.3974 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 155.2349 | 155.2349 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 873 | 9 | -2.4 | 1.03 | 12.31 | 13.34 | 12.31 | 6.16 | 37 | 873 | 540 | 36.4932 | -15.812 | -6.2635 | 514.284 | 8.467 | 52.9949 | 11.4219 | 11.4219 | 51.618 | 128.382 | 55.2234 | 2.9666 | 2.9666 | 10.5072 | 13.4739 | -11.6216 | 0% | 6.0929 | 0 | 0 | 136.9904 | 136.9904 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 874 | 10 | -2.4 | 41.11 | 59.81 | 100.92 | 59.81 | 29.91 | 37 | 874 | 600 | 36.4932 | -15.812 | -6.2635 | 574.284 | 9.467 | 37.9949 | 18.7057 | 18.7057 | 38.7063 | 141.2937 | 41.4593 | 96.0654 | 96.0654 | 51.051 | 147.1164 | -0.33402 | 0% | 66.526 | 0 | 0 | 141.914 | 141.914 | 0% | 12.16% | 12.16% | 80% | 9.725% | 6.4697 | 11.1164 | 6 | 38.8183 | 14.3072 | 27.35% | 27.35%
2 | 37 | 6 | 875 | 11 | -1 | 96.58 | 107.03 | 203.61 | 107.03 | 53.52 | 37 | 875 | 660 | 36.4932 | -15.812 | -6.2635 | 634.284 | 10.467 | 22.9949 | 24.0791 | 24.0791 | 24.3111 | 155.6889 | 28.7381 | 207.5602 | 207.5602 | 91.3558 | 298.916 | 0.25557 | 25.56% | 135.1698 | 34.5459 | 24.1822 | 123.5124 | 123.5124 | 19.58% | 11.93% | 11.93% | 80% | 9.545% | 12.9014 | 10.6277 | 6 | 77.4085 | 28.5303 | 62.67% | 62.67%
2 | 37 | 6 | 876 | 12 | -0.3 | 148.89 | 136.47 | 285.36 | 136.47 | 68.24 | 37 | 876 | 720 | 36.4932 | -15.812 | -6.2635 | 694.284 | 11.467 | 7.9949 | 26.9974 | 26.9974 | 8.6378 | 171.3622 | 19.2835 | 309.5862 | 309.5862 | 116.4844 | 426.0706 | 0.42331 | 42.33% | 192.6691 | 81.5597 | 57.0918 | 121.0809 | 121.0809 | 47.15% | 11.77% | 11.77% | 85% | 10% | 19.2748 | 10.3885 | 6 | 115.6485 | 42.6244 | 95.51% | 95.51%
2 | 37 | 6 | 877 | 13 | -0.4 | 197.78 | 173.06 | 370.84 | 173.06 | 86.53 | 37 | 877 | 780 | 36.4932 | -15.812 | -6.2635 | 754.284 | 12.467 | -7.0051 | 27.093 | 27.093 | 7.574 | 187.574 | 18.9037 | 410.8431 | 410.8431 | 147.7159 | 558.559 | 0.51317 | 51.32% | 252.5804 | 129.6165 | 90.7315 | 122.5585 | 122.5585 | 74.03% | 11.62% | 11.62% | 90% | 10.46% | 26.4214 | 10.4224 | 6 | 158.5287 | 58.4287 | 129.3% | 129.3%
2 | 37 | 6 | 878 | 14 | -0.4 | 77.03 | 186.39 | 263.42 | 186.39 | 93.2 | 37 | 878 | 840 | 36.4932 | -15.812 | -6.2635 | 814.284 | 13.467 | -22.0051 | 24.3527 | 24.3527 | 23.311 | 203.311 | 27.9711 | 164.9841 | 164.9841 | 159.0938 | 324.0779 | 0.30274 | 30.27% | 146.548 | 44.3665 | 31.0565 | 116.2042 | 116.2042 | 26.73% | 11.89% | 11.89% | 85% | 10.1% | 14.8059 | 10.4224 | 6 | 88.8353 | 32.7419 | 76.45% | 76.45%
2 | 37 | 6 | 879 | 15 | -0.2 | 96.11 | 135.47 | 231.58 | 135.47 | 67.74 | 37 | 879 | 900 | 36.4932 | -15.812 | -6.2635 | 874.284 | 14.467 | -37.0051 | 19.1254 | 19.1254 | 37.8027 | 217.8027 | 40.5764 | 222.8056 | 222.8056 | 115.6309 | 338.4364 | 0.32547 | 32.55% | 153.041 | 49.8104 | 34.8673 | 111.8514 | 111.8514 | 31.17% | 11.86% | 11.86% | 85% | 10.09% | 15.4343 | 10.3546 | 6 | 92.6058 | 34.1316 | 82.79% | 82.79%
2 | 37 | 6 | 880 | 16 | 0.2 | 61.94 | 103.81 | 165.75 | 103.81 | 51.91 | 37 | 880 | 960 | 36.4932 | -15.812 | -6.2635 | 934.284 | 15.467 | -52.0051 | 11.9502 | 11.9502 | 50.8089 | 230.8089 | 54.2988 | 174.564 | 174.564 | 88.6074 | 263.1714 | 0.19237 | 19.24% | 119.0061 | 22.893 | 16.0251 | 107.5952 | 107.5952 | 14.89% | 11.94% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 881 | 17 | 0.2 | 33.53 | 60.36 | 93.89 | 60.36 | 30.18 | 37 | 881 | 1020 | 36.4932 | -15.812 | -6.2635 | 994.284 | 16.467 | -67.0051 | 3.3735 | 3.3735 | 62.529 | 242.529 | 68.455 | 0 | 0 | 51.5205 | 51.5205 | -2.3203 | 0% | 23.2976 | 0 | 0 | 143.6345 | 143.6345 | 0% | 12.17% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 882 | 18 | -0.1 | 0 | 18.61 | 18.61 | 18.61 | 9.31 | 37 | 882 | 1080 | 36.4932 | -15.812 | -6.2635 | 1054.284 | 17.467 | -82.0051 | -6.1375 | 0 | 66.554 | 246.554 | 73.6594 | 0 | 0 | 15.8846 | 15.8846 | -9.3759 | 0% | 7.183 | 0 | 0 | 135.5674 | 135.5674 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 883 | 19 | -1.2 | 0 | 0 | 0 | 0 | 0 | 37 | 883 | 1140 | 36.4932 | -15.812 | -6.2635 | 1114.284 | 18.467 | -97.0051 | -16.1957 | 0 | 66.554 | 246.554 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.9529 | 129.9529 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 884 | 20 | -1.6 | 0 | 0 | 0 | 0 | 0 | 37 | 884 | 1200 | 36.4932 | -15.812 | -6.2635 | 1174.284 | 19.467 | -112.0051 | -26.452 | 0 | 66.554 | 246.554 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.8732 | 124.8732 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 885 | 21 | -2.4 | 0 | 0 | 0 | 0 | 0 | 37 | 885 | 1260 | 36.4932 | -15.812 | -6.2635 | 1234.284 | 20.467 | -127.0051 | -36.5234 | 0 | 66.554 | 246.554 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4338 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 886 | 22 | -2.7 | 0 | 0 | 0 | 0 | 0 | 37 | 886 | 1320 | 36.4932 | -15.812 | -6.2635 | 1294.284 | 21.467 | -142.0051 | -45.8753 | 0 | 66.554 | 246.554 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.907 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 887 | 23 | -2.8 | 0 | 0 | 0 | 0 | 0 | 37 | 887 | 1380 | 36.4932 | -15.812 | -6.2635 | 1354.284 | 22.467 | -157.0051 | -53.6214 | 0 | 66.554 | 246.554 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.7075 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
2 | 37 | 6 | 888 | 24 | -2.9 | 0 | 0 | 0 | 0 | 0 | 37 | 888 | 1440 | 36.4932 | -15.812 | -6.2635 | 1414.284 | 23.467 | -172.0051 | -58.3281 | 0 | 66.554 | 246.554 | 73.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.508 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 889 | 1 | -3.1 | 0 | 0 | 0 | 0 | 0 | 38 | 889 | 60 | 37.4795 | -15.5158 | -6.1298 | 34.284 | 0.46924 | 172.9614 | -58.193 | 0 | 67.0072 | 112.9928 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.4689 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 890 | 2 | -3.8 | 0 | 0 | 0 | 0 | 0 | 38 | 890 | 120 | 37.4795 | -15.5158 | -6.1298 | 94.284 | 1.4692 | 157.9614 | -53.7636 | 0 | 67.0072 | 112.9928 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2867 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 891 | 3 | -4.8 | 0 | 0 | 0 | 0 | 0 | 38 | 891 | 180 | 37.4795 | -15.5158 | -6.1298 | 154.284 | 2.4692 | 142.9614 | -46.1917 | 0 | 67.0072 | 112.9928 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.5617 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 892 | 4 | -4.8 | 0 | 0 | 0 | 0 | 0 | 38 | 892 | 240 | 37.4795 | -15.5158 | -6.1298 | 214.284 | 3.4692 | 127.9614 | -36.9299 | 0 | 67.0072 | 112.9928 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.5617 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 893 | 5 | -4.9 | 0 | 0 | 0 | 0 | 0 | 38 | 893 | 300 | 37.4795 | -15.5158 | -6.1298 | 274.284 | 4.4692 | 112.9614 | -26.8948 | 0 | 67.0072 | 112.9928 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.7133 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 894 | 6 | -5.5 | 0 | 0 | 0 | 0 | 0 | 38 | 894 | 360 | 37.4795 | -15.5158 | -6.1298 | 334.284 | 5.4692 | 97.9614 | -16.6382 | 0 | 67.0072 | 112.9928 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4976 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 895 | 7 | -5.7 | 0 | 0 | 0 | 0 | 0 | 38 | 895 | 420 | 37.4795 | -15.5158 | -6.1298 | 394.284 | 6.4692 | 82.9614 | -6.5501 | 0 | 67.0072 | 112.9928 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.2823 | 139.2823 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 896 | 8 | -5.4 | 0 | 0 | 0 | 0 | 0 | 38 | 896 | 480 | 37.4795 | -15.5158 | -6.1298 | 454.284 | 7.4692 | 67.9614 | 3.0193 | 3.0193 | 63.4305 | 116.5695 | 69.3241 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.4397 | 144.4397 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 897 | 9 | -5.9 | 2.86 | 10 | 12.86 | 10 | 5 | 38 | 897 | 540 | 37.4795 | -15.5158 | -6.1298 | 514.284 | 8.4692 | 52.9614 | 11.6857 | 11.6857 | 51.7595 | 128.2405 | 55.1227 | 8.0744 | 8.0744 | 8.5355 | 16.6099 | -9.8076 | 0% | 7.511 | 0 | 0 | 124.6891 | 124.6891 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 898 | 10 | -4.4 | 38.14 | 44.36 | 82.5 | 44.36 | 22.18 | 38 | 898 | 600 | 37.4795 | -15.5158 | -6.1298 | 574.284 | 9.4692 | 37.9614 | 18.9854 | 18.9854 | 38.8152 | 141.1848 | 41.3206 | 88.0474 | 88.0474 | 37.8636 | 125.9111 | -0.56562 | 0% | 56.937 | 0 | 0 | 131.482 | 131.482 | 0% | 12.26% | 12.26% | 80% | 9.805% | 5.5828 | 11.8384 | 6 | 33.4971 | 12.346 | 25.48% | 25.48%
2 | 38 | 7 | 899 | 11 | -2.6 | 75.64 | 68.53 | 144.17 | 68.53 | 34.27 | 38 | 899 | 660 | 37.4795 | -15.5158 | -6.1298 | 634.284 | 10.4692 | 22.9614 | 24.3717 | 24.3717 | 24.3726 | 155.6274 | 28.5399 | 161.0269 | 161.0269 | 58.494 | 219.5209 | 0.039051 | 3.905% | 99.2673 | 3.8765 | 2.7136 | 133.9915 | 133.9915 | 2.025% | 12.07% | 12.07% | 80% | 9.659% | 9.5881 | 11.1874 | 6 | 57.5284 | 21.2031 | 42.93% | 42.93%
2 | 38 | 7 | 900 | 12 | -0.5 | 113.89 | 94.08 | 207.97 | 94.08 | 47.04 | 38 | 900 | 720 | 37.4795 | -15.5158 | -6.1298 | 694.284 | 11.4692 | 7.9614 | 27.2954 | 27.2954 | 8.6374 | 171.3626 | 19.0014 | 234.8218 | 234.8218 | 80.3023 | 315.1241 | 0.28772 | 28.77% | 142.4991 | 40.9992 | 28.6995 | 113.7961 | 113.7961 | 25.22% | 11.9% | 11.9% | 85% | 10.11% | 14.4122 | 10.4565 | 6 | 86.4733 | 31.8713 | 75.99% | 75.99%
2 | 38 | 7 | 901 | 13 | 0.1 | 193.61 | 83.81 | 277.42 | 83.81 | 41.91 | 38 | 901 | 780 | 37.4795 | -15.5158 | -6.1298 | 754.284 | 12.4692 | -7.0386 | 27.3849 | 27.3849 | 7.6414 | 187.6414 | 18.6418 | 398.8392 | 398.8392 | 71.5363 | 470.3755 | 0.46127 | 46.13% | 212.7038 | 98.1144 | 68.6801 | 116.3233 | 116.3233 | 59.04% | 11.71% | 11.71% | 85% | 9.956% | 21.1765 | 10.2533 | 6 | 127.0589 | 46.8299 | 109.2% | 109.2%
2 | 38 | 7 | 902 | 14 | 0.4 | 221.94 | 79.25 | 301.19 | 79.25 | 39.63 | 38 | 902 | 840 | 37.4795 | -15.5158 | -6.1298 | 814.284 | 13.4692 | -22.0386 | 24.6279 | 24.6279 | 23.4368 | 203.4368 | 27.8196 | 471.029 | 471.029 | 67.6441 | 538.6731 | 0.5061 | 50.61% | 243.588 | 123.2798 | 86.2958 | 116.419 | 116.419 | 74.13% | 11.63% | 11.63% | 90% | 10.47% | 25.5045 | 10.1527 | 6 | 153.0269 | 56.4009 | 131.4% | 131.4%
2 | 38 | 7 | 903 | 15 | 0.7 | 152.5 | 89.25 | 241.75 | 89.25 | 44.63 | 38 | 903 | 900 | 37.4795 | -15.5158 | -6.1298 | 874.284 | 14.4692 | -37.0386 | 19.3779 | 19.3779 | 37.9704 | 217.9704 | 40.4943 | 349.5264 | 349.5264 | 76.1796 | 425.706 | 0.42878 | 42.88% | 192.5043 | 82.5424 | 57.7797 | 112.1388 | 112.1388 | 51.53% | 11.75% | 11.75% | 85% | 9.987% | 19.2252 | 10.0527 | 6 | 115.3514 | 42.5149 | 102.9% | 102.9%
2 | 38 | 7 | 904 | 16 | 1 | 105.56 | 110.83 | 216.39 | 110.83 | 55.42 | 38 | 904 | 960 | 37.4795 | -15.5158 | -6.1298 | 934.284 | 15.4692 | -52.0386 | 12.1795 | 12.1795 | 51.0036 | 231.0036 | 54.2585 | 292.265 | 292.265 | 94.5993 | 386.8643 | 0.39302 | 39.3% | 174.94 | 68.7541 | 48.1279 | 110.4328 | 110.4328 | 43.58% | 11.78% | 0% | 85% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 905 | 17 | 0.7 | 53.33 | 69.25 | 122.58 | 69.25 | 34.63 | 38 | 905 | 1020 | 37.4795 | -15.5158 | -6.1298 | 994.284 | 16.4692 | -67.0386 | 3.5828 | 3.5828 | 62.7415 | 242.7415 | 68.4438 | 0 | 0 | 59.1086 | 59.1086 | -1.8984 | 0% | 26.7289 | 0 | 0 | 145.3428 | 145.3428 | 0% | 12.14% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 906 | 18 | 0.3 | 0 | 24.36 | 24.36 | 24.36 | 12.18 | 38 | 906 | 1080 | 37.4795 | -15.5158 | -6.1298 | 1054.284 | 17.4692 | -82.0386 | -5.9428 | 0 | 67.0072 | 247.0072 | 73.9661 | 0 | 0 | 20.7926 | 20.7926 | -6.9256 | 0% | 9.4024 | 0 | 0 | 135.8182 | 135.8182 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 907 | 19 | -0.5 | 0 | 0 | 0 | 0 | 0 | 38 | 907 | 1140 | 37.4795 | -15.5158 | -6.1298 | 1114.284 | 18.4692 | -97.0386 | -16.0091 | 0 | 67.0072 | 247.0072 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.5513 | 130.5513 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 908 | 20 | -1.2 | 0 | 0 | 0 | 0 | 0 | 38 | 908 | 1200 | 37.4795 | -15.5158 | -6.1298 | 1174.284 | 19.4692 | -112.0386 | -26.2657 | 0 | 67.0072 | 247.0072 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.5696 | 125.5696 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 909 | 21 | -2.1 | 0 | 0 | 0 | 0 | 0 | 38 | 909 | 1260 | 37.4795 | -15.5158 | -6.1298 | 1234.284 | 20.4692 | -127.0386 | -36.3279 | 0 | 67.0072 | 247.0072 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.7829 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 910 | 22 | -4 | 0 | 0 | 0 | 0 | 0 | 38 | 910 | 1320 | 37.4795 | -15.5158 | -6.1298 | 1294.284 | 21.4692 | -142.0386 | -45.6587 | 0 | 67.0072 | 247.0072 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.5873 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 911 | 23 | -4.6 | 0 | 0 | 0 | 0 | 0 | 38 | 911 | 1380 | 37.4795 | -15.5158 | -6.1298 | 1354.284 | 22.4692 | -157.0386 | -53.3712 | 0 | 67.0072 | 247.0072 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.2528 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 38 | 7 | 912 | 24 | -4.6 | 0 | 0 | 0 | 0 | 0 | 38 | 912 | 1440 | 37.4795 | -15.5158 | -6.1298 | 1414.284 | 23.4692 | -172.0386 | -58.0425 | 0 | 67.0072 | 247.0072 | 73.9661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.0038 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 913 | 1 | -4.6 | 0 | 0 | 0 | 0 | 0 | 39 | 913 | 60 | 38.4658 | -15.2151 | -5.9848 | 34.284 | 0.47165 | 172.9252 | -57.8906 | 0 | 67.4664 | 112.5336 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.4305 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 914 | 2 | -4.5 | 0 | 0 | 0 | 0 | 0 | 39 | 914 | 120 | 38.4658 | -15.2151 | -5.9848 | 94.284 | 1.4717 | 157.9252 | -53.4775 | 0 | 67.4664 | 112.5336 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.0637 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 915 | 3 | -4.6 | 0 | 0 | 0 | 0 | 0 | 39 | 915 | 180 | 38.4658 | -15.2151 | -5.9848 | 154.284 | 2.4717 | 142.9252 | -45.9291 | 0 | 67.4664 | 112.5336 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.0016 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 916 | 4 | -4.3 | 0 | 0 | 0 | 0 | 0 | 39 | 916 | 240 | 38.4658 | -15.2151 | -5.9848 | 214.284 | 3.4717 | 127.9252 | -36.6843 | 0 | 67.4664 | 112.5336 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5445 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 917 | 5 | -4.6 | 0 | 0 | 0 | 0 | 0 | 39 | 917 | 300 | 38.4658 | -15.2151 | -5.9848 | 274.284 | 4.4717 | 112.9252 | -26.6573 | 0 | 67.4664 | 112.5336 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.97 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 918 | 6 | -4.8 | 0 | 0 | 0 | 0 | 0 | 39 | 918 | 360 | 38.4658 | -15.2151 | -5.9848 | 334.284 | 5.4717 | 97.9252 | -16.401 | 0 | 67.4664 | 112.5336 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7029 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 919 | 7 | -4.9 | 0 | 0 | 0 | 0 | 0 | 39 | 919 | 420 | 38.4658 | -15.2151 | -5.9848 | 394.284 | 6.4717 | 82.9252 | -6.3069 | 0 | 67.4664 | 112.5336 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.5502 | 137.5502 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 920 | 8 | -5 | 0 | 0 | 0 | 0 | 0 | 39 | 920 | 480 | 38.4658 | -15.2151 | -5.9848 | 454.284 | 7.4717 | 67.9252 | 3.2736 | 3.2736 | 63.595 | 116.405 | 69.2478 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.4482 | 141.4482 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 921 | 9 | -5.2 | 0.47 | 13.06 | 13.53 | 13.06 | 6.53 | 39 | 921 | 540 | 38.4658 | -15.2151 | -5.9848 | 514.284 | 8.4717 | 52.9252 | 11.9547 | 11.9547 | 51.9014 | 128.0986 | 55.0191 | 1.3008 | 1.3008 | 11.1474 | 12.4482 | -13.2122 | 0% | 5.6291 | 0 | 0 | 121.6815 | 121.6815 | 0% | 12.44% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 922 | 10 | -5.2 | 10.56 | 68.61 | 79.17 | 68.61 | 34.31 | 39 | 922 | 600 | 38.4658 | -15.2151 | -5.9848 | 574.284 | 9.4717 | 37.9252 | 19.2701 | 19.2701 | 38.924 | 141.076 | 41.1791 | 24.0833 | 24.0833 | 58.5623 | 82.6456 | -1.3072 | 0% | 37.3724 | 0 | 0 | 125.1997 | 125.1997 | 0% | 12.35% | 12.35% | 80% | 9.877% | 3.6913 | 12.1351 | 6 | 22.1476 | 8.1629 | 17.69% | 17.69%
2 | 39 | 8 | 923 | 11 | -5.1 | 49.92 | 130.36 | 180.28 | 130.36 | 65.18 | 39 | 923 | 660 | 38.4658 | -15.2151 | -5.9848 | 634.284 | 10.4717 | 22.9252 | 24.6695 | 24.6695 | 24.4328 | 155.5672 | 28.3384 | 105.2692 | 105.2692 | 111.2692 | 216.5384 | -0.00058541 | 0% | 97.9187 | 0 | 0 | 127.7743 | 127.7743 | 0% | 12.16% | 12.16% | 80% | 9.726% | 9.5235 | 12.0978 | 6 | 57.1413 | 21.0605 | 44.72% | 44.72%
2 | 39 | 8 | 924 | 12 | -4.4 | 36.47 | 127.97 | 164.44 | 127.97 | 63.99 | 39 | 924 | 720 | 38.4658 | -15.2151 | -5.9848 | 694.284 | 11.4717 | 7.9252 | 27.5981 | 27.5981 | 8.6344 | 171.3656 | 18.7146 | 74.5613 | 74.5613 | 109.2292 | 183.7905 | -0.1343 | 0% | 83.1101 | 0 | 0 | 123.5117 | 123.5117 | 0% | 12.18% | 12.18% | 80% | 9.743% | 8.0975 | 11.8384 | 6 | 48.5853 | 17.907 | 39.34% | 39.34%
2 | 39 | 8 | 925 | 13 | -4.5 | 74.72 | 166.94 | 241.66 | 166.94 | 83.47 | 39 | 925 | 780 | 38.4658 | -15.2151 | -5.9848 | 754.284 | 12.4717 | -7.0748 | 27.6809 | 27.6809 | 7.7128 | 187.7128 | 18.3781 | 152.6412 | 152.6412 | 142.4922 | 295.1334 | 0.21883 | 21.88% | 133.4593 | 29.2047 | 20.4433 | 104.9617 | 104.9617 | 19.48% | 12.03% | 12.03% | 80% | 9.626% | 12.8466 | 11.8753 | 6 | 77.0795 | 28.4091 | 73.44% | 73.44%
2 | 39 | 8 | 926 | 14 | -3.8 | 140.19 | 178.81 | 319 | 178.81 | 89.41 | 39 | 926 | 840 | 38.4658 | -15.2151 | -5.9848 | 814.284 | 13.4717 | -22.0748 | 24.9063 | 24.9063 | 23.5675 | 203.5675 | 27.6699 | 294.8157 | 294.8157 | 152.6239 | 447.4395 | 0.42197 | 42.2% | 202.3322 | 85.3776 | 59.7643 | 108.3626 | 108.3626 | 55.15% | 11.81% | 11.81% | 85% | 10.04% | 20.3171 | 11.6189 | 6 | 121.9028 | 44.9295 | 112.5% | 112.5%
2 | 39 | 8 | 927 | 15 | -1.9 | 102.14 | 166.86 | 269 | 166.86 | 83.43 | 39 | 927 | 900 | 38.4658 | -15.2151 | -5.9848 | 874.284 | 14.4717 | -37.0748 | 19.6329 | 19.6329 | 38.1434 | 218.1434 | 40.415 | 231.4522 | 231.4522 | 142.4239 | 373.8761 | 0.35954 | 35.95% | 169.0668 | 60.7863 | 42.5504 | 107.2223 | 107.2223 | 39.68% | 11.87% | 11.87% | 85% | 10.09% | 17.0512 | 10.9403 | 6 | 102.3071 | 37.7072 | 95.42% | 95.42%
2 | 39 | 8 | 928 | 16 | 0.1 | 62.14 | 123.89 | 186.03 | 123.89 | 61.95 | 39 | 928 | 960 | 38.4658 | -15.2151 | -5.9848 | 934.284 | 15.4717 | -52.0748 | 12.4108 | 12.4108 | 51.2035 | 231.2035 | 54.2211 | 169.044 | 169.044 | 105.7467 | 274.7907 | 0.21733 | 21.73% | 124.2604 | 27.0059 | 18.9041 | 105.36 | 105.36 | 17.94% | 11.93% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 929 | 17 | 0.4 | 5.92 | 64.72 | 70.64 | 64.72 | 32.36 | 39 | 929 | 1020 | 38.4658 | -15.2151 | -5.9848 | 994.284 | 16.4717 | -67.0748 | 3.7938 | 3.7938 | 62.9591 | 242.9591 | 68.4353 | 0 | 0 | 55.242 | 55.242 | -2.1009 | 0% | 24.9804 | 0 | 0 | 139.9878 | 139.9878 | 0% | 12.15% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 930 | 18 | -0.3 | 0 | 37.08 | 37.08 | 37.08 | 18.54 | 39 | 930 | 1080 | 38.4658 | -15.2151 | -5.9848 | 1054.284 | 17.4717 | -82.0748 | -5.7466 | 0 | 67.4664 | 247.4664 | 74.2773 | 0 | 0 | 31.6498 | 31.6498 | -4.3208 | 0% | 14.312 | 0 | 0 | 134.8408 | 134.8408 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 931 | 19 | -1.5 | 0 | 0 | 0 | 0 | 0 | 39 | 931 | 1140 | 38.4658 | -15.2151 | -5.9848 | 1114.284 | 18.4717 | -97.0748 | -15.8211 | 0 | 67.4664 | 247.4664 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.7706 | 128.7706 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 932 | 20 | -2.2 | 0 | 0 | 0 | 0 | 0 | 39 | 932 | 1200 | 38.4658 | -15.2151 | -5.9848 | 1174.284 | 19.4717 | -112.0748 | -26.0778 | 0 | 67.4664 | 247.4664 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.232 | 124.232 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 933 | 21 | -3 | 0 | 0 | 0 | 0 | 0 | 39 | 933 | 1260 | 38.4658 | -15.2151 | -5.9848 | 1234.284 | 20.4717 | -127.0748 | -36.1304 | 0 | 67.4664 | 247.4664 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8447 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 934 | 22 | -3.8 | 0 | 0 | 0 | 0 | 0 | 39 | 934 | 1320 | 38.4658 | -15.2151 | -5.9848 | 1294.284 | 21.4717 | -142.0748 | -45.4394 | 0 | 67.4664 | 247.4664 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.8545 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 935 | 23 | -4.4 | 0 | 0 | 0 | 0 | 0 | 39 | 935 | 1380 | 38.4658 | -15.2151 | -5.9848 | 1354.284 | 22.4717 | -157.0748 | -53.1177 | 0 | 67.4664 | 247.4664 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.5545 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
2 | 39 | 8 | 936 | 24 | -5 | 0 | 0 | 0 | 0 | 0 | 39 | 936 | 1440 | 38.4658 | -15.2151 | -5.9848 | 1414.284 | 23.4717 | -172.0748 | -57.7528 | 0 | 67.4664 | 247.4664 | 74.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.2545 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 937 | 1 | -5.1 | 0 | 0 | 0 | 0 | 0 | 40 | 937 | 60 | 39.4521 | -14.91 | -5.8286 | 34.284 | 0.47426 | 172.8861 | -57.5834 | 0 | 67.9313 | 112.0687 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.7897 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 938 | 2 | -6.5 | 0 | 0 | 0 | 0 | 0 | 40 | 938 | 120 | 39.4521 | -14.91 | -5.8286 | 94.284 | 1.4743 | 157.8861 | -53.186 | 0 | 67.9313 | 112.0687 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.7604 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 939 | 3 | -5.6 | 0 | 0 | 0 | 0 | 0 | 40 | 939 | 180 | 39.4521 | -14.91 | -5.8286 | 154.284 | 2.4743 | 142.8861 | -45.661 | 0 | 67.9313 | 112.0687 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.2259 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 940 | 4 | -5.8 | 0 | 0 | 0 | 0 | 0 | 40 | 940 | 240 | 39.4521 | -14.91 | -5.8286 | 214.284 | 3.4743 | 127.8861 | -36.4333 | 0 | 67.9313 | 112.0687 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.5307 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 941 | 5 | -5.7 | 0 | 0 | 0 | 0 | 0 | 40 | 941 | 300 | 39.4521 | -14.91 | -5.8286 | 274.284 | 4.4743 | 112.8861 | -26.4144 | 0 | 67.9313 | 112.0687 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4882 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 942 | 6 | -5.5 | 0 | 0 | 0 | 0 | 0 | 40 | 942 | 360 | 39.4521 | -14.91 | -5.8286 | 334.284 | 5.4743 | 97.8861 | -16.1585 | 0 | 67.9313 | 112.0687 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5556 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 943 | 7 | -5 | 0 | 0 | 0 | 0 | 0 | 40 | 943 | 420 | 39.4521 | -14.91 | -5.8286 | 394.284 | 6.4743 | 82.8861 | -6.0584 | 0 | 67.9313 | 112.0687 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.426 | 133.426 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 944 | 8 | -4.5 | 0 | 0 | 0 | 0 | 0 | 40 | 944 | 480 | 39.4521 | -14.91 | -5.8286 | 454.284 | 7.4743 | 67.8861 | 3.5331 | 3.5331 | 63.76 | 116.24 | 69.1688 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.4503 | 137.4503 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 945 | 9 | -4.2 | 1.39 | 21.25 | 22.64 | 21.25 | 10.63 | 40 | 945 | 540 | 39.4521 | -14.91 | -5.8286 | 514.284 | 8.4743 | 52.8861 | 12.2287 | 12.2287 | 52.0437 | 127.9563 | 54.9129 | 3.7722 | 3.7722 | 18.138 | 21.9102 | -7.0437 | 0% | 9.9078 | 0 | 0 | 118.8493 | 118.8493 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 946 | 10 | -3.5 | 3.06 | 66.94 | 70 | 66.94 | 33.47 | 40 | 946 | 600 | 39.4521 | -14.91 | -5.8286 | 574.284 | 9.4743 | 37.8861 | 19.56 | 19.56 | 39.0325 | 140.9675 | 41.0349 | 6.8944 | 6.8944 | 57.1369 | 64.0312 | -1.8538 | 0% | 28.9549 | 0 | 0 | 122.3562 | 122.3562 | 0% | 12.3% | 12.3% | 80% | 9.843% | 2.8499 | 11.5101 | 6 | 17.0995 | 6.3023 | 13.98% | 13.98%
2 | 40 | 9 | 947 | 11 | -2.6 | 3.53 | 92.97 | 96.5 | 92.97 | 46.49 | 40 | 947 | 660 | 39.4521 | -14.91 | -5.8286 | 634.284 | 10.4743 | 22.8861 | 24.9721 | 24.9721 | 24.4918 | 155.5082 | 28.1338 | 7.3735 | 7.3735 | 79.3549 | 86.7284 | -1.1322 | 0% | 39.2186 | 0 | 0 | 122.9699 | 122.9699 | 0% | 12.24% | 12.24% | 80% | 9.791% | 3.8398 | 11.1874 | 6 | 23.039 | 8.4915 | 18.74% | 18.74%
2 | 40 | 9 | 948 | 12 | -1.7 | 103.42 | 70.36 | 173.78 | 70.36 | 35.18 | 40 | 948 | 720 | 39.4521 | -14.91 | -5.8286 | 694.284 | 11.4743 | 7.8861 | 27.9055 | 27.9055 | 8.6287 | 171.3713 | 18.4232 | 209.6509 | 209.6509 | 60.056 | 269.7069 | 0.18973 | 18.97% | 121.9615 | 23.1392 | 16.1974 | 124.6321 | 124.6321 | 13% | 11.98% | 11.98% | 80% | 9.588% | 11.6936 | 10.8704 | 6 | 70.1614 | 25.8593 | 56.29% | 56.29%
2 | 40 | 9 | 949 | 13 | -0.8 | 131.47 | 75.75 | 207.22 | 75.75 | 37.88 | 40 | 949 | 780 | 39.4521 | -14.91 | -5.8286 | 754.284 | 12.4743 | -7.1139 | 27.981 | 27.981 | 7.7883 | 187.7883 | 18.1126 | 266.3281 | 266.3281 | 64.6567 | 330.9847 | 0.31021 | 31.02% | 149.6713 | 46.4295 | 32.5007 | 105.6108 | 105.6108 | 30.77% | 11.89% | 11.89% | 85% | 10.11% | 15.1247 | 10.559 | 6 | 90.7481 | 33.4469 | 85.93% | 85.93%
2 | 40 | 9 | 950 | 14 | -0.7 | 136.39 | 97.78 | 234.17 | 97.78 | 48.89 | 40 | 950 | 840 | 39.4521 | -14.91 | -5.8286 | 814.284 | 13.4743 | -22.1139 | 25.1881 | 25.1881 | 23.7031 | 203.7031 | 27.5223 | 284.2045 | 284.2045 | 83.4605 | 367.6649 | 0.36015 | 36.01% | 166.2581 | 59.8774 | 41.9142 | 106.285 | 106.285 | 39.44% | 11.84% | 11.84% | 85% | 10.07% | 16.7382 | 10.5248 | 6 | 100.429 | 37.015 | 94.49% | 94.49%
2 | 40 | 9 | 951 | 15 | 0 | 116.39 | 100.36 | 216.75 | 100.36 | 50.18 | 40 | 951 | 900 | 39.4521 | -14.91 | -5.8286 | 874.284 | 14.4743 | -37.1139 | 19.8905 | 19.8905 | 38.3217 | 218.3217 | 40.3384 | 260.7598 | 260.7598 | 85.6626 | 346.4224 | 0.33793 | 33.79% | 156.6522 | 52.9373 | 37.0561 | 105.359 | 105.359 | 35.17% | 11.85% | 11.85% | 85% | 10.07% | 15.78 | 10.287 | 6 | 94.6802 | 34.8962 | 89.86% | 89.86%
2 | 40 | 9 | 952 | 16 | 1.5 | 57.31 | 75.08 | 132.39 | 75.08 | 37.54 | 40 | 952 | 960 | 39.4521 | -14.91 | -5.8286 | 934.284 | 15.4743 | -52.1139 | 12.644 | 12.644 | 51.4087 | 231.4087 | 54.1864 | 153.2031 | 153.2031 | 64.0848 | 217.2879 | 0.077917 | 7.792% | 98.2576 | 7.6559 | 5.3592 | 144.9653 | 144.9653 | 3.697% | 11.94% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 953 | 17 | 1.6 | 46.11 | 59.17 | 105.28 | 59.17 | 29.59 | 40 | 953 | 1020 | 39.4521 | -14.91 | -5.8286 | 994.284 | 16.4743 | -67.1139 | 4.0063 | 4.0063 | 63.1817 | 243.1817 | 68.4297 | 0 | 0 | 50.5048 | 50.5048 | -2.315 | 0% | 22.8382 | 0 | 0 | 142.7024 | 142.7024 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 954 | 18 | 0.8 | 0 | 20.75 | 20.75 | 20.75 | 10.38 | 40 | 954 | 1080 | 39.4521 | -14.91 | -5.8286 | 1054.284 | 17.4743 | -82.1139 | -5.5491 | 0 | 67.9313 | 247.9313 | 74.5931 | 0 | 0 | 17.7112 | 17.7112 | -8.2008 | 0% | 8.009 | 0 | 0 | 134.3095 | 134.3095 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 955 | 19 | -0.3 | 0 | 0 | 0 | 0 | 0 | 40 | 955 | 1140 | 39.4521 | -14.91 | -5.8286 | 1114.284 | 18.4743 | -97.1139 | -15.6316 | 0 | 67.9313 | 247.9313 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.4194 | 129.4194 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 956 | 20 | -1.2 | 0 | 0 | 0 | 0 | 0 | 40 | 956 | 1200 | 39.4521 | -14.91 | -5.8286 | 1174.284 | 19.4743 | -112.1139 | -25.8884 | 0 | 67.9313 | 247.9313 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.0872 | 125.0872 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 957 | 21 | -2.4 | 0 | 0 | 0 | 0 | 0 | 40 | 957 | 1260 | 39.4521 | -14.91 | -5.8286 | 1234.284 | 20.4743 | -127.1139 | -35.9309 | 0 | 67.9313 | 247.9313 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4835 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 958 | 22 | -2.9 | 0 | 0 | 0 | 0 | 0 | 40 | 958 | 1320 | 39.4521 | -14.91 | -5.8286 | 1294.284 | 21.4743 | -142.1139 | -45.2176 | 0 | 67.9313 | 247.9313 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9256 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 959 | 23 | -3.6 | 0 | 0 | 0 | 0 | 0 | 40 | 959 | 1380 | 39.4521 | -14.91 | -5.8286 | 1354.284 | 22.4743 | -157.1139 | -52.8609 | 0 | 67.9313 | 247.9313 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.8295 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
2 | 40 | 9 | 960 | 24 | -4.5 | 0 | 0 | 0 | 0 | 0 | 40 | 960 | 1440 | 39.4521 | -14.91 | -5.8286 | 1414.284 | 23.4743 | -172.1139 | -57.4592 | 0 | 67.9313 | 247.9313 | 74.5931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.0382 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 961 | 1 | -5.2 | 0 | 0 | 0 | 0 | 0 | 41 | 961 | 60 | 40.4384 | -14.6007 | -5.6613 | 34.284 | 0.47704 | 172.8443 | -57.2716 | 0 | 68.4019 | 111.5981 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.7688 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 962 | 2 | -5.3 | 0 | 0 | 0 | 0 | 0 | 41 | 962 | 120 | 40.4384 | -14.6007 | -5.6613 | 94.284 | 1.477 | 157.8443 | -52.8893 | 0 | 68.4019 | 111.5981 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.4962 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.1725 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 963 | 3 | -6.2 | 0 | 0 | 0 | 0 | 0 | 41 | 963 | 180 | 40.4384 | -14.6007 | -5.6613 | 154.284 | 2.477 | 142.8443 | -45.3874 | 0 | 68.4019 | 111.5981 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.4427 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 964 | 4 | -6.4 | 0 | 0 | 0 | 0 | 0 | 41 | 964 | 240 | 40.4384 | -14.6007 | -5.6613 | 214.284 | 3.477 | 127.8443 | -36.1768 | 0 | 68.4019 | 111.5981 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.7475 | 0 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 965 | 5 | -6.6 | 0 | 0 | 0 | 0 | 0 | 41 | 965 | 300 | 40.4384 | -14.6007 | -5.6613 | 274.284 | 4.477 | 112.8443 | -26.1662 | 0 | 68.4019 | 111.5981 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4859 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.665 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 966 | 6 | -5.8 | 0 | 0 | 0 | 0 | 0 | 41 | 966 | 360 | 40.4384 | -14.6007 | -5.6613 | 334.284 | 5.477 | 97.8443 | -15.9108 | 0 | 68.4019 | 111.5981 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7302 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 967 | 7 | -5.8 | 0 | 0 | 0 | 0 | 0 | 41 | 967 | 420 | 40.4384 | -14.6007 | -5.6613 | 394.284 | 6.477 | 82.8443 | -5.8049 | 0 | 68.4019 | 111.5981 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 151.1319 | 151.1319 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3605 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 968 | 8 | -5.1 | 0 | 0 | 0 | 0 | 0 | 41 | 968 | 480 | 40.4384 | -14.6007 | -5.6613 | 454.284 | 7.477 | 67.8443 | 3.7976 | 3.7976 | 63.9258 | 116.0742 | 69.0871 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 158.5607 | 158.5607 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 969 | 9 | -5 | 5.28 | 10.97 | 16.25 | 10.97 | 5.49 | 41 | 969 | 540 | 40.4384 | -14.6007 | -5.6613 | 514.284 | 8.477 | 52.8443 | 12.5078 | 12.5078 | 52.1864 | 127.8136 | 54.804 | 14.0519 | 14.0519 | 9.3635 | 23.4154 | -6.6257 | 0% | 10.5884 | 0 | 0 | 140.1333 | 140.1333 | 0% | 12.42% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 970 | 10 | -4.2 | 65.08 | 51.39 | 116.47 | 51.39 | 25.7 | 41 | 970 | 600 | 40.4384 | -14.6007 | -5.6613 | 574.284 | 9.477 | 37.8443 | 19.8548 | 19.8548 | 39.1408 | 140.8592 | 40.8881 | 144.8598 | 144.8598 | 43.8641 | 188.7239 | -0.1071 | 0% | 85.341 | 0 | 0 | 146.1674 | 146.1674 | 0% | 12.17% | 12.17% | 80% | 9.732% | 8.3058 | 11.765 | 6 | 49.8348 | 18.3675 | 34.09% | 34.09%
2 | 41 | 10 | 971 | 11 | -3.3 | 140 | 70.56 | 210.56 | 70.56 | 35.28 | 41 | 971 | 660 | 40.4384 | -14.6007 | -5.6613 | 634.284 | 10.477 | 22.8443 | 25.2797 | 25.2797 | 24.5496 | 155.4504 | 27.9262 | 289.6637 | 289.6637 | 60.2267 | 349.8904 | 0.31905 | 31.91% | 158.2204 | 50.4808 | 35.3365 | 125.253 | 125.253 | 28.21% | 11.93% | 11.93% | 85% | 10.14% | 16.0428 | 11.4379 | 6 | 96.2565 | 35.4771 | 76.85% | 76.85%
2 | 41 | 10 | 972 | 12 | -2.6 | 196.11 | 89.25 | 285.36 | 89.25 | 44.63 | 41 | 972 | 720 | 40.4384 | -14.6007 | -5.6613 | 694.284 | 11.477 | 7.8443 | 28.2173 | 28.2173 | 8.6204 | 171.3796 | 18.1272 | 394.1834 | 394.1834 | 76.1796 | 470.3631 | 0.44699 | 44.7% | 212.6982 | 95.0749 | 66.5524 | 120.6915 | 120.6915 | 55.14% | 11.76% | 11.76% | 85% | 9.997% | 21.2645 | 11.1874 | 6 | 127.5867 | 47.0244 | 105.7% | 105.7%
2 | 41 | 10 | 973 | 13 | -1.5 | 213.61 | 129.17 | 342.78 | 129.17 | 64.59 | 41 | 973 | 780 | 40.4384 | -14.6007 | -5.6613 | 754.284 | 12.477 | -7.1557 | 28.2849 | 28.2849 | 7.8677 | 187.8677 | 17.8457 | 429.1006 | 429.1006 | 110.2535 | 539.3541 | 0.49775 | 49.78% | 243.8959 | 121.3997 | 84.9798 | 122.2445 | 122.2445 | 69.52% | 11.66% | 11.66% | 90% | 10.49% | 25.5949 | 10.8007 | 6 | 153.5694 | 56.6009 | 125.6% | 125.6%
2 | 41 | 10 | 974 | 14 | -0.3 | 149.17 | 152.42 | 301.59 | 152.42 | 76.21 | 41 | 974 | 840 | 40.4384 | -14.6007 | -5.6613 | 814.284 | 13.477 | -22.1557 | 25.473 | 25.473 | 23.8437 | 203.8437 | 27.3769 | 307.9923 | 307.9923 | 130.0986 | 438.0909 | 0.43376 | 43.38% | 198.1047 | 85.9299 | 60.1509 | 120.3859 | 120.3859 | 49.97% | 11.76% | 11.76% | 85% | 9.993% | 19.7959 | 10.3885 | 6 | 118.7756 | 43.7769 | 98.66% | 98.66%
2 | 41 | 10 | 975 | 15 | 0.5 | 120.75 | 149.72 | 270.47 | 149.72 | 74.86 | 41 | 975 | 900 | 40.4384 | -14.6007 | -5.6613 | 874.284 | 14.477 | -37.1557 | 20.1504 | 20.1504 | 38.5052 | 218.5052 | 40.2647 | 267.4716 | 267.4716 | 127.794 | 395.2656 | 0.39864 | 39.86% | 178.7391 | 71.2526 | 49.8768 | 117.1371 | 117.1371 | 42.58% | 11.79% | 11.79% | 85% | 10.02% | 17.9064 | 10.1193 | 6 | 107.4383 | 39.5984 | 91.72% | 91.72%
2 | 41 | 10 | 976 | 16 | 0.6 | 95.56 | 114.64 | 210.2 | 114.64 | 57.32 | 41 | 976 | 960 | 40.4384 | -14.6007 | -5.6613 | 934.284 | 15.477 | -52.1557 | 12.879 | 12.879 | 51.619 | 231.619 | 54.1547 | 251.0616 | 251.0616 | 97.8514 | 348.9129 | 0.34549 | 34.55% | 157.7784 | 54.5116 | 38.1581 | 112.6823 | 112.6823 | 33.86% | 11.83% | 0% | 85% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 977 | 17 | 0.7 | 49.36 | 69.44 | 118.8 | 69.44 | 34.72 | 41 | 977 | 1020 | 40.4384 | -14.6007 | -5.6613 | 994.284 | 16.477 | -67.1557 | 4.2203 | 4.2203 | 63.4093 | 243.4093 | 68.4268 | 0 | 0 | 59.2707 | 59.2707 | -1.891 | 0% | 26.8022 | 0 | 0 | 147.7854 | 147.7854 | 0% | 12.14% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 978 | 18 | -0.1 | 0 | 24.92 | 24.92 | 24.92 | 12.46 | 41 | 978 | 1080 | 40.4384 | -14.6007 | -5.6613 | 1054.284 | 17.477 | -82.1557 | -5.3503 | 0 | 68.4019 | 248.4019 | 74.9132 | 0 | 0 | 21.2706 | 21.2706 | -6.7983 | 0% | 9.6185 | 0 | 0 | 137.3932 | 137.3932 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 979 | 19 | -0.1 | 0 | 0 | 0 | 0 | 0 | 41 | 979 | 1140 | 40.4384 | -14.6007 | -5.6613 | 1114.284 | 18.477 | -97.1557 | -15.4409 | 0 | 68.4019 | 248.4019 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.9146 | 132.9146 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 980 | 20 | -0.4 | 0 | 0 | 0 | 0 | 0 | 41 | 980 | 1200 | 40.4384 | -14.6007 | -5.6613 | 1174.284 | 19.477 | -112.1557 | -25.6973 | 0 | 68.4019 | 248.4019 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.5558 | 127.5558 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 981 | 21 | -0.3 | 0 | 0 | 0 | 0 | 0 | 41 | 981 | 1260 | 40.4384 | -14.6007 | -5.6613 | 1234.284 | 20.477 | -127.1557 | -35.7295 | 0 | 68.4019 | 248.4019 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4718 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 982 | 22 | -1.1 | 0 | 0 | 0 | 0 | 0 | 41 | 982 | 1320 | 40.4384 | -14.6007 | -5.6613 | 1294.284 | 21.477 | -142.1557 | -44.9932 | 0 | 68.4019 | 248.4019 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7957 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 983 | 23 | -2.9 | 0 | 0 | 0 | 0 | 0 | 41 | 983 | 1380 | 40.4384 | -14.6007 | -5.6613 | 1354.284 | 22.477 | -157.1557 | -52.6008 | 0 | 68.4019 | 248.4019 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.1138 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 41 | 10 | 984 | 24 | -2.9 | 0 | 0 | 0 | 0 | 0 | 41 | 984 | 1440 | 40.4384 | -14.6007 | -5.6613 | 1414.284 | 23.477 | -172.1557 | -57.1615 | 0 | 68.4019 | 248.4019 | 74.9132 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6887 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 985 | 1 | -3.9 | 0 | 0 | 0 | 0 | 0 | 42 | 985 | 60 | 41.4247 | -14.2872 | -5.4832 | 34.284 | 0.48001 | 172.7998 | -56.9552 | 0 | 68.8779 | 111.1221 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.7479 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 986 | 2 | -4 | 0 | 0 | 0 | 0 | 0 | 42 | 986 | 120 | 41.4247 | -14.2872 | -5.4832 | 94.284 | 1.48 | 157.7998 | -52.5874 | 0 | 68.8779 | 111.1221 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.6224 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 987 | 3 | -5.6 | 0 | 0 | 0 | 0 | 0 | 42 | 987 | 180 | 41.4247 | -14.2872 | -5.4832 | 154.284 | 2.48 | 142.7998 | -45.1085 | 0 | 68.8779 | 111.1221 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.7829 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 988 | 4 | -4.9 | 0 | 0 | 0 | 0 | 0 | 42 | 988 | 240 | 41.4247 | -14.2872 | -5.4832 | 214.284 | 3.48 | 127.7998 | -35.9149 | 0 | 68.8779 | 111.1221 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.7161 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 989 | 5 | -4.7 | 0 | 0 | 0 | 0 | 0 | 42 | 989 | 300 | 41.4247 | -14.2872 | -5.4832 | 274.284 | 4.48 | 112.7998 | -25.9128 | 0 | 68.8779 | 111.1221 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7389 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 990 | 6 | -4.6 | 0 | 0 | 0 | 0 | 0 | 42 | 990 | 360 | 41.4247 | -14.2872 | -5.4832 | 334.284 | 5.48 | 97.7998 | -15.6581 | 0 | 68.8779 | 111.1221 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9151 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 991 | 7 | -4.6 | 0 | 0 | 0 | 0 | 0 | 42 | 991 | 420 | 41.4247 | -14.2872 | -5.4832 | 394.284 | 6.48 | 82.7998 | -5.5464 | 0 | 68.8779 | 111.1221 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.7481 | 142.7481 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 992 | 8 | -4.6 | 0 | 0 | 0 | 0 | 0 | 42 | 992 | 480 | 41.4247 | -14.2872 | -5.4832 | 454.284 | 7.48 | 67.7998 | 4.067 | 4.067 | 64.0922 | 115.9078 | 69.0027 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.6105 | 147.6105 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 993 | 9 | -4.6 | 4.25 | 12.42 | 16.67 | 12.42 | 6.21 | 42 | 993 | 540 | 41.4247 | -14.2872 | -5.4832 | 514.284 | 8.48 | 52.7998 | 12.7919 | 12.7919 | 52.3294 | 127.6706 | 54.6926 | 11.0941 | 11.0941 | 10.6011 | 21.6952 | -7.1681 | 0% | 9.8106 | 0 | 0 | 128.7661 | 128.7661 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 994 | 10 | -3.8 | 38.42 | 73.42 | 111.84 | 73.42 | 36.71 | 42 | 994 | 600 | 41.4247 | -14.2872 | -5.4832 | 574.284 | 9.48 | 37.7998 | 20.1545 | 20.1545 | 39.2488 | 140.7512 | 40.7388 | 84.4879 | 84.4879 | 62.6679 | 147.1558 | -0.3576 | 0% | 66.5439 | 0 | 0 | 134.6228 | 134.6228 | 0% | 12.21% | 12.21% | 80% | 9.765% | 6.4982 | 11.6189 | 6 | 38.9891 | 14.3701 | 28.96% | 28.96%
2 | 42 | 11 | 995 | 11 | -3.7 | 72.86 | 97.58 | 170.44 | 97.58 | 48.79 | 42 | 995 | 660 | 41.4247 | -14.2872 | -5.4832 | 634.284 | 10.48 | 22.7998 | 25.592 | 25.592 | 24.606 | 155.394 | 27.7158 | 149.3204 | 149.3204 | 83.2897 | 232.6101 | 0.070221 | 7.022% | 105.1863 | 7.3862 | 5.1704 | 133.7031 | 133.7031 | 3.867% | 12.09% | 12.09% | 80% | 9.673% | 10.175 | 11.5826 | 6 | 61.0497 | 22.501 | 45.66% | 45.66%
2 | 42 | 11 | 996 | 12 | -3.3 | 127.22 | 127.78 | 255 | 127.78 | 63.89 | 42 | 996 | 720 | 41.4247 | -14.2872 | -5.4832 | 694.284 | 11.48 | 7.7998 | 28.5336 | 28.5336 | 8.6094 | 171.3906 | 17.8268 | 253.5445 | 253.5445 | 109.0671 | 362.6115 | 0.33607 | 33.61% | 163.9729 | 55.1058 | 38.574 | 111.1895 | 111.1895 | 34.69% | 11.91% | 11.91% | 85% | 10.13% | 16.6033 | 11.4379 | 6 | 99.6198 | 36.7167 | 89.59% | 89.59%
2 | 42 | 11 | 997 | 13 | -3.1 | 149.17 | 182.42 | 331.59 | 182.42 | 91.21 | 42 | 997 | 780 | 41.4247 | -14.2872 | -5.4832 | 754.284 | 12.48 | -7.2002 | 28.5928 | 28.5928 | 7.9513 | 187.9513 | 17.5775 | 297.1392 | 297.1392 | 155.7052 | 452.8444 | 0.43042 | 43.04% | 204.7763 | 88.1388 | 61.6972 | 113.5318 | 113.5318 | 54.34% | 11.79% | 11.79% | 85% | 10.02% | 20.527 | 11.366 | 6 | 123.1619 | 45.3936 | 108.5% | 108.5%
2 | 42 | 11 | 998 | 14 | -2.1 | 125.92 | 155 | 280.92 | 155 | 77.5 | 42 | 998 | 840 | 41.4247 | -14.2872 | -5.4832 | 814.284 | 13.48 | -22.2002 | 25.761 | 25.761 | 23.9892 | 203.9892 | 27.2341 | 257.6081 | 257.6081 | 132.3008 | 389.9089 | 0.37654 | 37.65% | 176.3168 | 66.3896 | 46.4728 | 111.6105 | 111.6105 | 41.64% | 11.85% | 11.85% | 85% | 10.07% | 17.7602 | 11.0106 | 6 | 106.5612 | 39.2751 | 95.48% | 95.48%
2 | 42 | 11 | 999 | 15 | -1.4 | 148.81 | 154.44 | 303.25 | 154.44 | 77.22 | 42 | 999 | 900 | 41.4247 | -14.2872 | -5.4832 | 874.284 | 14.48 | -37.2002 | 20.4128 | 20.4128 | 38.6939 | 218.6939 | 40.194 | 325.9083 | 325.9083 | 131.8228 | 457.731 | 0.44369 | 44.37% | 206.986 | 91.8366 | 64.2856 | 111.7607 | 111.7607 | 57.52% | 11.75% | 11.75% | 85% | 9.992% | 20.6813 | 10.7659 | 6 | 124.0876 | 45.7348 | 111% | 111%
2 | 42 | 11 | 1000 | 16 | 0.1 | 99.64 | 105.36 | 205 | 105.36 | 52.68 | 42 | 1000 | 960 | 41.4247 | -14.2872 | -5.4832 | 934.284 | 15.48 | -52.2002 | 13.1158 | 13.1158 | 51.8344 | 231.8344 | 54.126 | 257.3136 | 257.3136 | 89.9304 | 347.244 | 0.33974 | 33.97% | 157.0237 | 53.3476 | 37.3433 | 108.4387 | 108.4387 | 34.44% | 11.85% | 0% | 85% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 1001 | 17 | -0.1 | 46.94 | 64.72 | 111.66 | 64.72 | 32.36 | 42 | 1001 | 1020 | 41.4247 | -14.2872 | -5.4832 | 994.284 | 16.48 | -67.2002 | 4.4356 | 4.4356 | 63.6418 | 243.6418 | 68.4268 | 0 | 0 | 55.242 | 55.242 | -2.1232 | 0% | 24.9804 | 0 | 0 | 143.6537 | 143.6537 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 1002 | 18 | -0.7 | 0 | 19.72 | 19.72 | 19.72 | 9.86 | 42 | 1002 | 1080 | 41.4247 | -14.2872 | -5.4832 | 1054.284 | 17.48 | -82.2002 | -5.1502 | 0 | 68.8779 | 248.8779 | 75.2376 | 0 | 0 | 16.8321 | 16.8321 | -8.8911 | 0% | 7.6115 | 0 | 0 | 134.482 | 134.482 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 1003 | 19 | -0.8 | 0 | 0 | 0 | 0 | 0 | 42 | 1003 | 1140 | 41.4247 | -14.2872 | -5.4832 | 1114.284 | 18.48 | -97.2002 | -15.2488 | 0 | 68.8779 | 248.8779 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.37 | 130.37 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 1004 | 20 | -0.3 | 0 | 0 | 0 | 0 | 0 | 42 | 1004 | 1200 | 41.4247 | -14.2872 | -5.4832 | 1174.284 | 19.48 | -112.2002 | -25.5048 | 0 | 68.8779 | 248.8779 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.8977 | 126.8977 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 1005 | 21 | -0.5 | 0 | 0 | 0 | 0 | 0 | 42 | 1005 | 1260 | 41.4247 | -14.2872 | -5.4832 | 1234.284 | 20.48 | -127.2002 | -35.5261 | 0 | 68.8779 | 248.8779 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4448 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 1006 | 22 | -0.5 | 0 | 0 | 0 | 0 | 0 | 42 | 1006 | 1320 | 41.4247 | -14.2872 | -5.4832 | 1294.284 | 21.48 | -142.2002 | -44.7663 | 0 | 68.8779 | 248.8779 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4001 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 1007 | 23 | -0.2 | 0 | 0 | 0 | 0 | 0 | 42 | 1007 | 1380 | 41.4247 | -14.2872 | -5.4832 | 1354.284 | 22.48 | -157.2002 | -52.3375 | 0 | 68.8779 | 248.8779 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.665 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
2 | 42 | 11 | 1008 | 24 | -0.1 | 0 | 0 | 0 | 0 | 0 | 42 | 1008 | 1440 | 41.4247 | -14.2872 | -5.4832 | 1414.284 | 23.48 | -172.2002 | -56.8601 | 0 | 68.8779 | 248.8779 | 75.2376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2347 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1009 | 1 | -0.1 | 0 | 0 | 0 | 0 | 0 | 43 | 1009 | 60 | 42.411 | -13.9696 | -5.2942 | 34.284 | 0.48316 | 172.7525 | -56.6343 | 0 | 69.3592 | 110.6408 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0245 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1010 | 2 | -0.3 | 0 | 0 | 0 | 0 | 0 | 43 | 1010 | 120 | 42.411 | -13.9696 | -5.2942 | 94.284 | 1.4832 | 157.7525 | -52.2804 | 0 | 69.3592 | 110.6408 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0353 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1011 | 3 | -0.3 | 0 | 0 | 0 | 0 | 0 | 43 | 1011 | 180 | 42.411 | -13.9696 | -5.2942 | 154.284 | 2.4832 | 142.7525 | -44.8242 | 0 | 69.3592 | 110.6408 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7413 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1012 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 43 | 1012 | 240 | 42.411 | -13.9696 | -5.2942 | 214.284 | 3.4832 | 127.7525 | -35.6478 | 0 | 69.3592 | 110.6408 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8081 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1013 | 5 | -0.6 | 0 | 0 | 0 | 0 | 0 | 43 | 1013 | 300 | 42.411 | -13.9696 | -5.2942 | 274.284 | 4.4832 | 112.7525 | -25.6542 | 0 | 69.3592 | 110.6408 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1077 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1014 | 6 | -0.7 | 0 | 0 | 0 | 0 | 0 | 43 | 1014 | 360 | 42.411 | -13.9696 | -5.2942 | 334.284 | 5.4832 | 97.7525 | -15.4004 | 0 | 69.3592 | 110.6408 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4588 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1015 | 7 | -0.7 | 0 | 0 | 0 | 0 | 0 | 43 | 1015 | 420 | 42.411 | -13.9696 | -5.2942 | 394.284 | 6.4832 | 82.7525 | -5.283 | 0 | 69.3592 | 110.6408 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.218 | 148.218 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1016 | 8 | -0.2 | 0 | 0 | 0 | 0 | 0 | 43 | 1016 | 480 | 42.411 | -13.9696 | -5.2942 | 454.284 | 7.4832 | 67.7525 | 4.3413 | 4.3413 | 64.2591 | 115.7409 | 68.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 154.0871 | 154.0871 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1017 | 9 | -0.2 | 8.89 | 13.75 | 22.64 | 13.75 | 6.88 | 43 | 1017 | 540 | 42.411 | -13.9696 | -5.2942 | 514.284 | 8.4832 | 52.7525 | 13.0807 | 13.0807 | 52.4728 | 127.5272 | 54.5787 | 22.7661 | 22.7661 | 11.7364 | 34.5025 | -3.8899 | 0% | 15.602 | 0 | 0 | 136.1317 | 136.1317 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1018 | 10 | -0.2 | 54.44 | 37.22 | 91.66 | 37.22 | 18.61 | 43 | 1018 | 600 | 42.411 | -13.9696 | -5.2942 | 574.284 | 9.4832 | 37.7525 | 20.459 | 20.459 | 39.3566 | 140.6434 | 40.5871 | 118.2783 | 118.2783 | 31.7693 | 150.0475 | -0.27534 | 0% | 67.8515 | 0 | 0 | 139.6388 | 139.6388 | 0% | 12.07% | 12.07% | 80% | 9.659% | 6.554 | 10.3546 | 6 | 39.3238 | 14.4935 | 28.16% | 28.16%
2 | 43 | 12 | 1019 | 11 | 0.5 | 87.31 | 43.61 | 130.92 | 43.61 | 21.81 | 43 | 1019 | 660 | 42.411 | -13.9696 | -5.2942 | 634.284 | 10.4832 | 22.7525 | 25.909 | 25.909 | 24.6612 | 155.3388 | 27.5028 | 177.238 | 177.238 | 37.2235 | 214.4614 | 0.056897 | 5.69% | 96.9795 | 5.5179 | 3.8625 | 138.3604 | 138.3604 | 2.792% | 11.98% | 11.98% | 80% | 9.584% | 9.2945 | 10.1193 | 6 | 55.767 | 20.554 | 40.31% | 40.31%
2 | 43 | 12 | 1020 | 12 | 2 | 120 | 70.92 | 190.92 | 70.92 | 35.46 | 43 | 1020 | 720 | 42.411 | -13.9696 | -5.2942 | 694.284 | 11.4832 | 7.7525 | 28.8543 | 28.8543 | 8.5957 | 171.4043 | 17.5221 | 237.124 | 237.124 | 60.534 | 297.658 | 0.27807 | 27.81% | 134.6009 | 37.4289 | 26.2002 | 136.9434 | 136.9434 | 19.13% | 11.85% | 11.85% | 80% | 9.479% | 12.7594 | 9.6266 | 6 | 76.5566 | 28.2164 | 55.9% | 55.9%
2 | 43 | 12 | 1021 | 13 | 4.2 | 153.14 | 96.47 | 249.61 | 96.47 | 48.24 | 43 | 1021 | 780 | 42.411 | -13.9696 | -5.2942 | 754.284 | 12.4832 | -7.2475 | 28.9043 | 28.9043 | 8.0388 | 188.0388 | 17.3084 | 302.4846 | 302.4846 | 82.3423 | 384.8269 | 0.41108 | 41.11% | 174.0187 | 71.5357 | 50.075 | 120.4246 | 120.4246 | 41.58% | 11.71% | 11.71% | 85% | 9.956% | 17.3251 | 8.9325 | 6 | 103.9504 | 38.3129 | 86.32% | 86.32%
2 | 43 | 12 | 1022 | 14 | 5.2 | 225.47 | 72.5 | 297.97 | 72.5 | 36.25 | 43 | 1022 | 840 | 42.411 | -13.9696 | -5.2942 | 814.284 | 13.4832 | -22.2475 | 26.0519 | 26.0519 | 24.1396 | 204.1396 | 27.094 | 457.0441 | 457.0441 | 61.8826 | 518.9267 | 0.51725 | 51.73% | 234.6586 | 121.3783 | 84.9648 | 122.5585 | 122.5585 | 69.33% | 11.58% | 11.58% | 90% | 10.42% | 24.4578 | 8.6282 | 6 | 146.7468 | 54.0862 | 119.7% | 119.7%
2 | 43 | 12 | 1023 | 15 | 3.9 | 163.06 | 74.53 | 237.59 | 74.53 | 37.27 | 43 | 1023 | 900 | 42.411 | -13.9696 | -5.2942 | 874.284 | 14.4832 | -37.2475 | 20.6773 | 20.6773 | 38.8878 | 218.8878 | 40.1265 | 353.0955 | 353.0955 | 63.6153 | 416.7108 | 0.43941 | 43.94% | 188.4366 | 82.8002 | 57.9601 | 115.851 | 115.851 | 50.03% | 11.69% | 11.69% | 85% | 9.938% | 18.7263 | 9.0252 | 6 | 112.3575 | 41.4114 | 96.98% | 96.98%
2 | 43 | 12 | 1024 | 16 | 3.4 | 99.17 | 65.83 | 165 | 65.83 | 32.92 | 43 | 1024 | 960 | 42.411 | -13.9696 | -5.2942 | 934.284 | 15.4832 | -52.2475 | 13.3543 | 13.3543 | 52.055 | 232.055 | 54.1003 | 251.7633 | 251.7633 | 56.1894 | 307.9527 | 0.30671 | 30.67% | 139.2562 | 42.7119 | 29.8984 | 110.5284 | 110.5284 | 27.05% | 11.8% | 0% | 85% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1025 | 17 | 2.9 | 73.25 | 52.78 | 126.03 | 52.78 | 26.39 | 43 | 1025 | 1020 | 42.411 | -13.9696 | -5.2942 | 994.284 | 16.4832 | -67.2475 | 4.6524 | 4.6524 | 63.8792 | 243.8792 | 68.4297 | 0 | 0 | 45.0505 | 45.0505 | -2.6222 | 0% | 20.3719 | 0 | 0 | 148.046 | 148.046 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1026 | 18 | 3 | 0 | 28.06 | 28.06 | 28.06 | 14.03 | 43 | 1026 | 1080 | 42.411 | -13.9696 | -5.2942 | 1054.284 | 17.4832 | -82.2475 | -4.9489 | 0 | 69.3592 | 249.3592 | 75.5662 | 0 | 0 | 23.9507 | 23.9507 | -5.6305 | 0% | 10.8305 | 0 | 0 | 138.7232 | 138.7232 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1027 | 19 | 2.9 | 0 | 0 | 0 | 0 | 0 | 43 | 1027 | 1140 | 42.411 | -13.9696 | -5.2942 | 1114.284 | 18.4832 | -97.2475 | -15.0554 | 0 | 69.3592 | 249.3592 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.0668 | 134.0668 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1028 | 20 | 2.9 | 0 | 0 | 0 | 0 | 0 | 43 | 1028 | 1200 | 42.411 | -13.9696 | -5.2942 | 1174.284 | 19.4832 | -112.2475 | -25.3107 | 0 | 69.3592 | 249.3592 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.7332 | 129.7332 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1029 | 21 | 1.8 | 0 | 0 | 0 | 0 | 0 | 43 | 1029 | 1260 | 42.411 | -13.9696 | -5.2942 | 1234.284 | 20.4832 | -127.2475 | -35.3207 | 0 | 69.3592 | 249.3592 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0175 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1030 | 22 | 1.4 | 0 | 0 | 0 | 0 | 0 | 43 | 1030 | 1320 | 42.411 | -13.9696 | -5.2942 | 1294.284 | 21.4832 | -142.2475 | -44.5368 | 0 | 69.3592 | 249.3592 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6206 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1031 | 23 | 1.2 | 0 | 0 | 0 | 0 | 0 | 43 | 1031 | 1380 | 42.411 | -13.9696 | -5.2942 | 1354.284 | 22.4832 | -157.2475 | -52.071 | 0 | 69.3592 | 249.3592 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6314 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
2 | 43 | 12 | 1032 | 24 | 1.2 | 0 | 0 | 0 | 0 | 0 | 43 | 1032 | 1440 | 42.411 | -13.9696 | -5.2942 | 1414.284 | 23.4832 | -172.2475 | -56.5548 | 0 | 69.3592 | 249.3592 | 75.5662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3373 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1033 | 1 | 5.7 | 0 | 0 | 0 | 0 | 0 | 44 | 1033 | 60 | 43.3973 | -13.648 | -5.0946 | 34.284 | 0.48649 | 172.7026 | -56.3091 | 0 | 69.8457 | 110.1543 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3218 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1034 | 2 | 5.8 | 0 | 0 | 0 | 0 | 0 | 44 | 1034 | 120 | 43.3973 | -13.648 | -5.0946 | 94.284 | 1.4865 | 157.7026 | -51.9685 | 0 | 69.8457 | 110.1543 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9585 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1035 | 3 | 5.8 | 0 | 0 | 0 | 0 | 0 | 44 | 1035 | 180 | 43.3973 | -13.648 | -5.0946 | 154.284 | 2.4865 | 142.7026 | -44.5347 | 0 | 69.8457 | 110.1543 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7476 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1036 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 44 | 1036 | 240 | 43.3973 | -13.648 | -5.0946 | 214.284 | 3.4865 | 127.7026 | -35.3755 | 0 | 69.8457 | 110.1543 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4908 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1037 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 44 | 1037 | 300 | 43.3973 | -13.648 | -5.0946 | 274.284 | 4.4865 | 112.7026 | -25.3907 | 0 | 69.8457 | 110.1543 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4122 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1038 | 6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 44 | 1038 | 360 | 43.3973 | -13.648 | -5.0946 | 334.284 | 5.4865 | 97.7026 | -15.1377 | 0 | 69.8457 | 110.1543 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0392 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1039 | 7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 44 | 1039 | 420 | 43.3973 | -13.648 | -5.0946 | 394.284 | 6.4865 | 82.7026 | -5.0148 | 0 | 69.8457 | 110.1543 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.3369 | 143.3369 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1040 | 8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 44 | 1040 | 480 | 43.3973 | -13.648 | -5.0946 | 454.284 | 7.4865 | 67.7026 | 4.6204 | 4.6204 | 64.4267 | 115.5733 | 68.826 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.446 | 147.446 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1041 | 9 | 2.4 | 2.03 | 22.03 | 24.06 | 22.03 | 11.02 | 44 | 1041 | 540 | 43.3973 | -13.648 | -5.0946 | 514.284 | 8.4865 | 52.7026 | 13.3743 | 13.3743 | 52.6164 | 127.3836 | 54.4624 | 5.101 | 5.101 | 18.8038 | 23.9047 | -5.7039 | 0% | 10.8097 | 0 | 0 | 128.2553 | 128.2553 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1042 | 10 | 3.1 | 25.56 | 83.42 | 108.98 | 83.42 | 41.71 | 44 | 1042 | 600 | 43.3973 | -13.648 | -5.0946 | 574.284 | 9.4865 | 37.7026 | 20.7683 | 20.7683 | 39.4641 | 140.5359 | 40.4331 | 54.8672 | 54.8672 | 71.2034 | 126.0706 | -0.41649 | 0% | 57.0091 | 0 | 0 | 133.5681 | 133.5681 | 0% | 11.98% | 11.98% | 80% | 9.583% | 5.463 | 9.2753 | 6 | 32.7782 | 12.081 | 24.54% | 24.54%
2 | 44 | 13 | 1043 | 11 | 3.1 | 53.14 | 157.14 | 210.28 | 157.14 | 78.57 | 44 | 1043 | 660 | 43.3973 | -13.648 | -5.0946 | 634.284 | 10.4865 | 22.7026 | 26.2306 | 26.2306 | 24.7151 | 155.2849 | 27.2873 | 106.8509 | 106.8509 | 134.1274 | 240.9783 | 0.16549 | 16.55% | 108.9704 | 18.0331 | 12.6232 | 114.5111 | 114.5111 | 11.02% | 11.87% | 11.87% | 80% | 9.497% | 10.3492 | 9.2753 | 6 | 62.0954 | 22.8864 | 54.23% | 54.23%
2 | 44 | 13 | 1044 | 12 | 3 | 93.61 | 142.14 | 235.75 | 142.14 | 71.07 | 44 | 1044 | 720 | 43.3973 | -13.648 | -5.0946 | 694.284 | 11.4865 | 7.7026 | 29.1792 | 29.1792 | 8.5793 | 171.4207 | 17.2131 | 183.4041 | 183.4041 | 121.3241 | 304.7282 | 0.29827 | 29.83% | 137.7981 | 41.1008 | 28.7705 | 110.8776 | 110.8776 | 25.95% | 11.82% | 11.82% | 85% | 10.04% | 13.8388 | 9.3069 | 6 | 83.0329 | 30.6033 | 74.89% | 74.89%
2 | 44 | 13 | 1045 | 13 | 3.9 | 113.14 | 163.89 | 277.03 | 163.89 | 81.95 | 44 | 1045 | 780 | 43.3973 | -13.648 | -5.0946 | 754.284 | 12.4865 | -7.2974 | 29.2195 | 29.2195 | 8.1305 | 188.1305 | 17.0386 | 221.5968 | 221.5968 | 139.8889 | 361.4857 | 0.38371 | 38.37% | 163.4638 | 62.722 | 43.9054 | 113.1038 | 113.1038 | 38.82% | 11.74% | 11.74% | 85% | 9.979% | 16.3125 | 9.0252 | 6 | 97.8749 | 36.0736 | 86.54% | 86.54%
2 | 44 | 13 | 1046 | 14 | 5.3 | 118.53 | 184.08 | 302.61 | 184.08 | 92.04 | 44 | 1046 | 840 | 43.3973 | -13.648 | -5.0946 | 814.284 | 13.4865 | -22.2974 | 26.3457 | 26.3457 | 24.295 | 204.295 | 26.9568 | 238.0683 | 238.0683 | 157.1221 | 395.1904 | 0.42808 | 42.81% | 178.7051 | 76.5001 | 53.55 | 115.5771 | 115.5771 | 46.33% | 11.68% | 11.68% | 85% | 9.927% | 17.7408 | 8.5982 | 6 | 106.4446 | 39.2321 | 92.1% | 92.1%
2 | 44 | 13 | 1047 | 15 | 5.5 | 105.47 | 165.75 | 271.22 | 165.75 | 82.88 | 44 | 1047 | 900 | 43.3973 | -13.648 | -5.0946 | 874.284 | 14.4865 | -37.2974 | 20.944 | 20.944 | 39.0869 | 219.0869 | 40.0622 | 225.8214 | 225.8214 | 141.4765 | 367.2978 | 0.40084 | 40.08% | 166.0921 | 66.576 | 46.6032 | 112.942 | 112.942 | 41.26% | 11.7% | 11.7% | 85% | 9.943% | 16.5137 | 8.5383 | 6 | 99.0824 | 36.5187 | 87.73% | 87.73%
2 | 44 | 13 | 1048 | 16 | 5.7 | 80.75 | 110.28 | 191.03 | 110.28 | 55.14 | 44 | 1048 | 960 | 43.3973 | -13.648 | -5.0946 | 934.284 | 15.4865 | -52.2974 | 13.5944 | 13.5944 | 52.2805 | 232.2805 | 54.0777 | 201.5561 | 201.5561 | 94.1299 | 295.6859 | 0.30482 | 30.48% | 133.7092 | 40.7566 | 28.5296 | 108.7159 | 108.7159 | 26.24% | 11.75% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1049 | 17 | 6.7 | 41.67 | 73.14 | 114.81 | 73.14 | 36.57 | 44 | 1049 | 1020 | 43.3973 | -13.648 | -5.0946 | 994.284 | 16.4865 | -67.2974 | 4.8704 | 4.8704 | 64.1213 | 244.1213 | 68.4354 | 0 | 0 | 62.4289 | 62.4289 | -1.5221 | 0% | 28.2303 | 0 | 0 | 147.0503 | 147.0503 | 0% | 11.89% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1050 | 18 | 7.8 | 0 | 28.06 | 28.06 | 28.06 | 14.03 | 44 | 1050 | 1080 | 43.3973 | -13.648 | -5.0946 | 1054.284 | 17.4865 | -82.2974 | -4.7464 | 0 | 69.8457 | 249.8457 | 75.8989 | 0 | 0 | 23.9507 | 23.9507 | -5.1502 | 0% | 10.8305 | 0 | 0 | 141.4351 | 141.4351 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1051 | 19 | 6.4 | 0 | 2.5 | 2.5 | 2.5 | 1.25 | 44 | 1051 | 1140 | 43.3973 | -13.648 | -5.0946 | 1114.284 | 18.4865 | -97.2974 | -14.8609 | 0 | 69.8457 | 249.8457 | 75.8989 | 0 | 0 | 2.1339 | 2.1339 | -67.5832 | 0% | 0.96494 | 0 | 0 | 135.4779 | 135.4779 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1052 | 20 | 6.4 | 0 | 0 | 0 | 0 | 0 | 44 | 1052 | 1200 | 43.3973 | -13.648 | -5.0946 | 1174.284 | 19.4865 | -112.2974 | -25.1151 | 0 | 69.8457 | 249.8457 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.8011 | 131.8011 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1053 | 21 | 6.2 | 0 | 0 | 0 | 0 | 0 | 44 | 1053 | 1260 | 43.3973 | -13.648 | -5.0946 | 1234.284 | 20.4865 | -127.2974 | -35.1135 | 0 | 69.8457 | 249.8457 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3852 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1054 | 22 | 6.4 | 0 | 0 | 0 | 0 | 0 | 44 | 1054 | 1320 | 43.3973 | -13.648 | -5.0946 | 1294.284 | 21.4865 | -142.2974 | -44.3048 | 0 | 69.8457 | 249.8457 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8877 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1055 | 23 | 6 | 0 | 0 | 0 | 0 | 0 | 44 | 1055 | 1380 | 43.3973 | -13.648 | -5.0946 | 1354.284 | 22.4865 | -157.2974 | -51.8013 | 0 | 69.8457 | 249.8457 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2864 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
2 | 44 | 13 | 1056 | 24 | 5.7 | 0 | 0 | 0 | 0 | 0 | 44 | 1056 | 1440 | 43.3973 | -13.648 | -5.0946 | 1414.284 | 23.4865 | -172.2974 | -56.2457 | 0 | 69.8457 | 249.8457 | 75.8989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5327 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1057 | 1 | 5.6 | 0 | 0 | 0 | 0 | 0 | 45 | 1057 | 60 | 44.3836 | -13.3225 | -4.8845 | 34.284 | 0.48999 | 172.6501 | -55.9796 | 0 | 70.3373 | 109.6627 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4535 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1058 | 2 | 4.6 | 0 | 0 | 0 | 0 | 0 | 45 | 1058 | 120 | 44.3836 | -13.3225 | -4.8845 | 94.284 | 1.49 | 157.6501 | -51.6517 | 0 | 70.3373 | 109.6627 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9096 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1059 | 3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 45 | 1059 | 180 | 44.3836 | -13.3225 | -4.8845 | 154.284 | 2.49 | 142.6501 | -44.2401 | 0 | 70.3373 | 109.6627 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4512 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1060 | 4 | 3.7 | 0 | 0 | 0 | 0 | 0 | 45 | 1060 | 240 | 44.3836 | -13.3225 | -4.8845 | 214.284 | 3.49 | 127.6501 | -35.0981 | 0 | 70.3373 | 109.6627 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2132 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1061 | 5 | 3.8 | 0 | 0 | 0 | 0 | 0 | 45 | 1061 | 300 | 44.3836 | -13.3225 | -4.8845 | 274.284 | 4.49 | 112.6501 | -25.1221 | 0 | 70.3373 | 109.6627 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9741 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1062 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 45 | 1062 | 360 | 44.3836 | -13.3225 | -4.8845 | 334.284 | 5.49 | 97.6501 | -14.8702 | 0 | 70.3373 | 109.6627 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1598 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1063 | 7 | 2.8 | 0 | 0 | 0 | 0 | 0 | 45 | 1063 | 420 | 44.3836 | -13.3225 | -4.8845 | 394.284 | 6.49 | 82.6501 | -4.7418 | 0 | 70.3373 | 109.6627 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.4294 | 135.4294 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1064 | 8 | 3 | 0 | 0 | 0 | 0 | 0 | 45 | 1064 | 480 | 44.3836 | -13.3225 | -4.8845 | 454.284 | 7.49 | 67.6501 | 4.9041 | 4.9041 | 64.5947 | 115.4053 | 68.7339 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.0988 | 138.0988 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1065 | 9 | 2.8 | 0.08 | 5.75 | 5.83 | 5.75 | 2.88 | 45 | 1065 | 540 | 44.3836 | -13.3225 | -4.8845 | 514.284 | 8.49 | 52.6501 | 13.6726 | 13.6726 | 52.7604 | 127.2396 | 54.3438 | 0.19729 | 0.19729 | 4.9079 | 5.1052 | -29.4781 | 0% | 2.3086 | 0 | 0 | 117.6824 | 117.6824 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1066 | 10 | 2.9 | 0.83 | 23.53 | 24.36 | 23.53 | 11.77 | 45 | 1066 | 600 | 44.3836 | -13.3225 | -4.8845 | 574.284 | 9.49 | 37.6501 | 21.0822 | 21.0822 | 39.5714 | 140.4286 | 40.277 | 1.7604 | 1.7604 | 20.0841 | 21.8445 | -6.262 | 0% | 9.8781 | 0 | 0 | 119.3097 | 119.3097 | 0% | 12.08% | 12.08% | 80% | 9.667% | 0.95492 | 9.3386 | 6 | 5.7295 | 2.1117 | 4.802% | 4.802%
2 | 45 | 14 | 1067 | 11 | 3.3 | 1.75 | 57.69 | 59.44 | 57.69 | 28.85 | 45 | 1067 | 660 | 44.3836 | -13.3225 | -4.8845 | 634.284 | 10.49 | 22.6501 | 26.5567 | 26.5567 | 24.7677 | 155.2323 | 27.0694 | 3.4855 | 3.4855 | 49.2415 | 52.727 | -2.105 | 0% | 23.8431 | 0 | 0 | 120.706 | 120.706 | 0% | 12.04% | 12.04% | 80% | 9.631% | 2.2963 | 9.2124 | 6 | 13.7776 | 5.078 | 11.41% | 11.41%
2 | 45 | 14 | 1068 | 12 | 3.3 | 2.78 | 121.47 | 124.25 | 121.47 | 60.74 | 45 | 1068 | 720 | 44.3836 | -13.3225 | -4.8845 | 694.284 | 11.49 | 7.6501 | 29.5082 | 29.5082 | 8.5602 | 171.4398 | 16.9 | 5.4004 | 5.4004 | 103.6811 | 109.0815 | -0.60213 | 0% | 49.3267 | 0 | 0 | 122.0084 | 122.0084 | 0% | 11.99% | 11.99% | 80% | 9.589% | 4.7301 | 9.2124 | 6 | 28.3804 | 10.4601 | 23.26% | 23.26%
2 | 45 | 14 | 1069 | 13 | 3.6 | 16.11 | 164.25 | 180.36 | 164.25 | 82.13 | 45 | 1069 | 780 | 44.3836 | -13.3225 | -4.8845 | 754.284 | 12.49 | -7.3499 | 29.5383 | 29.5383 | 8.2262 | 188.2262 | 16.7684 | 31.2877 | 31.2877 | 140.1961 | 171.4839 | -0.086206 | 0% | 77.545 | 0 | 0 | 125.2885 | 125.2885 | 0% | 11.92% | 11.92% | 80% | 9.535% | 7.394 | 9.1184 | 6 | 44.3641 | 16.3512 | 35.41% | 35.41%
2 | 45 | 14 | 1070 | 14 | 3.7 | 2.97 | 114.64 | 117.61 | 114.64 | 57.32 | 45 | 1070 | 840 | 44.3836 | -13.3225 | -4.8845 | 814.284 | 13.49 | -22.3499 | 26.6423 | 26.6423 | 24.4553 | 204.4553 | 26.8228 | 5.9106 | 5.9106 | 97.8514 | 103.762 | -0.66488 | 0% | 46.9212 | 0 | 0 | 122.5112 | 122.5112 | 0% | 11.98% | 11.98% | 80% | 9.581% | 4.4955 | 9.0873 | 6 | 26.9729 | 9.9414 | 22.02% | 22.02%
2 | 45 | 14 | 1071 | 15 | 4.8 | 10.64 | 98.89 | 109.53 | 98.89 | 49.45 | 45 | 1071 | 900 | 44.3836 | -13.3225 | -4.8845 | 874.284 | 14.49 | -37.3499 | 21.2128 | 21.2128 | 39.2912 | 219.2912 | 40.0013 | 22.5258 | 22.5258 | 84.4079 | 106.9337 | -0.5965 | 0% | 48.3554 | 0 | 0 | 143.7492 | 143.7492 | 0% | 11.93% | 11.93% | 80% | 9.545% | 4.6156 | 8.7491 | 6 | 27.6935 | 10.207 | 19.27% | 19.27%
2 | 45 | 14 | 1072 | 16 | 4 | 71.47 | 97.22 | 168.69 | 97.22 | 48.61 | 45 | 1072 | 960 | 44.3836 | -13.3225 | -4.8845 | 934.284 | 15.49 | -52.3499 | 13.836 | 13.836 | 52.5111 | 232.5111 | 54.0582 | 175.4188 | 175.4188 | 82.9825 | 258.4013 | 0.21697 | 21.7% | 116.8491 | 25.353 | 17.7471 | 103.2148 | 103.2148 | 17.19% | 11.83% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1073 | 17 | 3.3 | 43.97 | 56.31 | 100.28 | 56.31 | 28.16 | 45 | 1073 | 1020 | 44.3836 | -13.3225 | -4.8845 | 994.284 | 16.49 | -67.3499 | 5.0896 | 5.0896 | 64.3682 | 244.3682 | 68.4441 | 0 | 0 | 48.0636 | 48.0636 | -2.3872 | 0% | 21.7344 | 0 | 0 | 140.1214 | 140.1214 | 0% | 12.04% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1074 | 18 | 3.3 | 0 | 19.25 | 19.25 | 19.25 | 9.63 | 45 | 1074 | 1080 | 44.3836 | -13.3225 | -4.8845 | 1054.284 | 17.49 | -82.3499 | -4.5428 | 0 | 70.3373 | 250.3373 | 76.2357 | 0 | 0 | 16.4309 | 16.4309 | -8.531 | 0% | 7.4301 | 0 | 0 | 133.8218 | 133.8218 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1075 | 19 | 3.4 | 0 | 0 | 0 | 0 | 0 | 45 | 1075 | 1140 | 44.3836 | -13.3225 | -4.8845 | 1114.284 | 18.49 | -97.3499 | -14.6651 | 0 | 70.3373 | 250.3373 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.9367 | 130.9367 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1076 | 20 | 2.8 | 0 | 0 | 0 | 0 | 0 | 45 | 1076 | 1200 | 44.3836 | -13.3225 | -4.8845 | 1174.284 | 19.49 | -112.3499 | -24.9181 | 0 | 70.3373 | 250.3373 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.3612 | 127.3612 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1077 | 21 | 2.7 | 0 | 0 | 0 | 0 | 0 | 45 | 1077 | 1260 | 44.3836 | -13.3225 | -4.8845 | 1234.284 | 20.49 | -127.3499 | -34.9043 | 0 | 70.3373 | 250.3373 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4696 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1078 | 22 | 2.4 | 0 | 0 | 0 | 0 | 0 | 45 | 1078 | 1320 | 44.3836 | -13.3225 | -4.8845 | 1294.284 | 21.49 | -142.3499 | -44.0703 | 0 | 70.3373 | 250.3373 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5341 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1079 | 23 | 1.3 | 0 | 0 | 0 | 0 | 0 | 45 | 1079 | 1380 | 44.3836 | -13.3225 | -4.8845 | 1354.284 | 22.49 | -157.3499 | -51.5285 | 0 | 70.3373 | 250.3373 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1426 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
2 | 45 | 14 | 1080 | 24 | -0.1 | 0 | 0 | 0 | 0 | 0 | 45 | 1080 | 1440 | 44.3836 | -13.3225 | -4.8845 | 1414.284 | 23.49 | -172.3499 | -55.933 | 0 | 70.3373 | 250.3373 | 76.2357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2082 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1081 | 1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 46 | 1081 | 60 | 45.3699 | -12.9932 | -4.6641 | 34.284 | 0.49366 | 172.595 | -55.646 | 0 | 70.8338 | 109.1662 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7739 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1082 | 2 | -0.4 | 0 | 0 | 0 | 0 | 0 | 46 | 1082 | 120 | 45.3699 | -12.9932 | -4.6641 | 94.284 | 1.4937 | 157.595 | -51.3302 | 0 | 70.8338 | 109.1662 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3425 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1083 | 3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 46 | 1083 | 180 | 45.3699 | -12.9932 | -4.6641 | 154.284 | 2.4937 | 142.595 | -43.9405 | 0 | 70.8338 | 109.1662 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6251 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1084 | 4 | -0.3 | 0 | 0 | 0 | 0 | 0 | 46 | 1084 | 240 | 45.3699 | -12.9932 | -4.6641 | 214.284 | 3.4937 | 127.595 | -34.8157 | 0 | 70.8338 | 109.1662 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8443 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1085 | 5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 46 | 1085 | 300 | 45.3699 | -12.9932 | -4.6641 | 274.284 | 4.4937 | 112.595 | -24.8487 | 0 | 70.8338 | 109.1662 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1857 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1086 | 6 | 0.8 | 0 | 0 | 0 | 0 | 0 | 46 | 1086 | 360 | 45.3699 | -12.9932 | -4.6641 | 334.284 | 5.4937 | 97.595 | -14.598 | 0 | 70.8338 | 109.1662 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.6501 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1087 | 7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 46 | 1087 | 420 | 45.3699 | -12.9932 | -4.6641 | 394.284 | 6.4937 | 82.595 | -4.4642 | 0 | 70.8338 | 109.1662 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 151.6875 | 151.6875 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1088 | 8 | 0.4 | 0 | 0 | 0 | 0 | 0 | 46 | 1088 | 480 | 45.3699 | -12.9932 | -4.6641 | 454.284 | 7.4937 | 67.595 | 5.1924 | 5.1924 | 64.7633 | 115.2367 | 68.6394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 155.2185 | 155.2185 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1089 | 9 | 1.4 | 12.5 | 19.92 | 32.42 | 19.92 | 9.96 | 46 | 1089 | 540 | 45.3699 | -12.9932 | -4.6641 | 514.284 | 8.4937 | 52.595 | 13.9754 | 13.9754 | 52.9048 | 127.0952 | 54.2231 | 30.2598 | 30.2598 | 17.0028 | 47.2626 | -2.5393 | 0% | 21.3721 | 0 | 0 | 139.0931 | 139.0931 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1090 | 10 | 0.8 | 23.53 | 68.06 | 91.59 | 68.06 | 34.03 | 46 | 1090 | 600 | 45.3699 | -12.9932 | -4.6641 | 574.284 | 9.4937 | 37.595 | 21.4006 | 21.4006 | 39.6784 | 140.3216 | 40.1189 | 49.3129 | 49.3129 | 58.0928 | 107.4057 | -0.6809 | 0% | 48.5689 | 0 | 0 | 138.4561 | 138.4561 | 0% | 12.08% | 12.08% | 80% | 9.667% | 4.695 | 10.0195 | 6 | 28.1701 | 10.3826 | 20.35% | 20.35%
2 | 46 | 15 | 1091 | 11 | 0.8 | 24.72 | 112.58 | 137.3 | 112.58 | 56.29 | 46 | 1091 | 660 | 45.3699 | -12.9932 | -4.6641 | 634.284 | 10.4937 | 22.595 | 26.8872 | 26.8872 | 24.8191 | 155.1809 | 26.8494 | 48.7691 | 48.7691 | 96.093 | 144.8621 | -0.29695 | 0% | 65.5066 | 0 | 0 | 135.6024 | 135.6024 | 0% | 12.04% | 12.04% | 80% | 9.635% | 6.3116 | 10.0195 | 6 | 37.8696 | 13.9576 | 27.93% | 27.93%
2 | 46 | 15 | 1092 | 12 | 2 | 35.92 | 164.17 | 200.09 | 164.17 | 82.09 | 46 | 1092 | 720 | 45.3699 | -12.9932 | -4.6641 | 694.284 | 11.4937 | 7.595 | 29.8414 | 29.8414 | 8.5384 | 171.4616 | 16.583 | 69.184 | 69.184 | 140.1279 | 209.3119 | 0.056091 | 5.609% | 94.6508 | 5.309 | 3.7163 | 112.3459 | 112.3459 | 3.308% | 11.94% | 11.94% | 80% | 9.549% | 9.0386 | 9.6266 | 6 | 54.2317 | 19.9881 | 48.27% | 48.27%
2 | 46 | 15 | 1093 | 13 | 4.2 | 54.36 | 177.03 | 231.39 | 177.03 | 88.52 | 46 | 1093 | 780 | 45.3699 | -12.9932 | -4.6641 | 754.284 | 12.4937 | -7.405 | 29.8605 | 29.8605 | 8.3261 | 188.3261 | 16.4981 | 104.6858 | 104.6858 | 151.1046 | 255.7904 | 0.21287 | 21.29% | 115.6684 | 24.6221 | 17.2355 | 115.4182 | 115.4182 | 14.93% | 11.82% | 11.82% | 80% | 9.46% | 10.9422 | 8.9325 | 6 | 65.6529 | 24.1976 | 56.88% | 56.88%
2 | 46 | 15 | 1094 | 14 | 5.3 | 35.75 | 193.25 | 229 | 193.25 | 96.63 | 46 | 1094 | 840 | 45.3699 | -12.9932 | -4.6641 | 814.284 | 13.4937 | -22.405 | 26.9416 | 26.9416 | 24.6205 | 204.6205 | 26.6922 | 70.4954 | 70.4954 | 164.9492 | 235.4446 | 0.17302 | 17.3% | 106.468 | 18.4215 | 12.895 | 115.8176 | 115.8176 | 11.13% | 11.81% | 11.81% | 80% | 9.447% | 10.0578 | 8.5982 | 6 | 60.3466 | 22.2419 | 52.1% | 52.1%
2 | 46 | 15 | 1095 | 15 | 4.7 | 56.86 | 169.53 | 226.39 | 169.53 | 84.77 | 46 | 1095 | 900 | 45.3699 | -12.9932 | -4.6641 | 874.284 | 14.4937 | -37.405 | 21.4835 | 21.4835 | 39.5005 | 219.5005 | 39.9438 | 119.031 | 119.031 | 144.7029 | 263.7339 | 0.23524 | 23.52% | 119.2605 | 28.0549 | 19.6384 | 112.8078 | 112.8078 | 17.41% | 11.8% | 11.8% | 80% | 9.443% | 11.2613 | 8.7795 | 6 | 67.5678 | 24.9034 | 59.9% | 59.9%
2 | 46 | 15 | 1096 | 16 | 4 | 41.47 | 114.36 | 155.83 | 114.36 | 57.18 | 46 | 1096 | 960 | 45.3699 | -12.9932 | -4.6641 | 934.284 | 15.4937 | -52.405 | 14.0791 | 14.0791 | 52.7466 | 232.7466 | 54.0418 | 100.1021 | 100.1021 | 97.6124 | 197.7145 | 0.036789 | 3.679% | 89.4065 | 3.2892 | 2.3024 | 106.9966 | 106.9966 | 2.152% | 11.88% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1097 | 17 | 3.4 | 27.14 | 87.31 | 114.45 | 87.31 | 43.66 | 46 | 1097 | 1020 | 45.3699 | -12.9932 | -4.6641 | 994.284 | 16.4937 | -67.405 | 5.3101 | 5.3101 | 64.6197 | 244.6197 | 68.4556 | 0 | 0 | 74.5237 | 74.5237 | -1.2509 | 0% | 33.6996 | 0 | 0 | 144.4933 | 144.4933 | 0% | 12.01% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1098 | 18 | 2.8 | 1.03 | 35.56 | 36.59 | 35.56 | 17.78 | 46 | 1098 | 1080 | 45.3699 | -12.9932 | -4.6641 | 1054.284 | 17.4937 | -82.405 | -4.3381 | 0 | 70.8338 | 250.8338 | 76.5763 | 0 | 0 | 30.3524 | 30.3524 | -4.2894 | 0% | 13.7253 | 0 | 0 | 136.9747 | 136.9747 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1099 | 19 | 2.6 | 0 | 2.03 | 2.03 | 2.03 | 1.02 | 46 | 1099 | 1140 | 45.3699 | -12.9932 | -4.6641 | 1114.284 | 18.4937 | -97.405 | -14.4681 | 0 | 70.8338 | 250.8338 | 76.5763 | 0 | 0 | 1.7327 | 1.7327 | -88.6992 | 0% | 0.78353 | 0 | 0 | 132.4968 | 132.4968 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1100 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 46 | 1100 | 1200 | 45.3699 | -12.9932 | -4.6641 | 1174.284 | 19.4937 | -112.405 | -24.7196 | 0 | 70.8338 | 250.8338 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.6631 | 127.6631 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1101 | 21 | 1.3 | 0 | 0 | 0 | 0 | 0 | 46 | 1101 | 1260 | 45.3699 | -12.9932 | -4.6641 | 1234.284 | 20.4937 | -127.405 | -34.6932 | 0 | 70.8338 | 250.8338 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3013 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1102 | 22 | 1.2 | 0 | 0 | 0 | 0 | 0 | 46 | 1102 | 1320 | 45.3699 | -12.9932 | -4.6641 | 1294.284 | 21.4937 | -142.405 | -43.8334 | 0 | 70.8338 | 250.8338 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2873 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1103 | 23 | 1.1 | 0 | 0 | 0 | 0 | 0 | 46 | 1103 | 1380 | 45.3699 | -12.9932 | -4.6641 | 1354.284 | 22.4937 | -157.405 | -51.2526 | 0 | 70.8338 | 250.8338 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0939 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
2 | 46 | 15 | 1104 | 24 | 1.3 | 0 | 0 | 0 | 0 | 0 | 46 | 1104 | 1440 | 45.3699 | -12.9932 | -4.6641 | 1414.284 | 23.4937 | -172.405 | -55.6167 | 0 | 70.8338 | 250.8338 | 76.5763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4433 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1105 | 1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 47 | 1105 | 60 | 46.3562 | -12.6601 | -4.4337 | 34.284 | 0.49751 | 172.5374 | -55.3082 | 0 | 71.3351 | 108.6649 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5321 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1106 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 47 | 1106 | 120 | 46.3562 | -12.6601 | -4.4337 | 94.284 | 1.4975 | 157.5374 | -51.004 | 0 | 71.3351 | 108.6649 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0449 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1107 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 47 | 1107 | 180 | 46.3562 | -12.6601 | -4.4337 | 154.284 | 2.4975 | 142.5374 | -43.636 | 0 | 71.3351 | 108.6649 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.2529 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1108 | 4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 47 | 1108 | 240 | 46.3562 | -12.6601 | -4.4337 | 214.284 | 3.4975 | 127.5374 | -34.5284 | 0 | 71.3351 | 108.6649 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8625 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1109 | 5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 47 | 1109 | 300 | 46.3562 | -12.6601 | -4.4337 | 274.284 | 4.4975 | 112.5374 | -24.5705 | 0 | 71.3351 | 108.6649 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.059 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1110 | 6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 47 | 1110 | 360 | 46.3562 | -12.6601 | -4.4337 | 334.284 | 5.4975 | 97.5374 | -14.3211 | 0 | 71.3351 | 108.6649 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.837 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1111 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 47 | 1111 | 420 | 46.3562 | -12.6601 | -4.4337 | 394.284 | 6.4975 | 82.5374 | -4.1821 | 0 | 71.3351 | 108.6649 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 154.1498 | 154.1498 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1112 | 8 | 0.2 | 0 | 0 | 0 | 0 | 0 | 47 | 1112 | 480 | 46.3562 | -12.6601 | -4.4337 | 454.284 | 7.4975 | 67.5374 | 5.4852 | 5.4852 | 64.9324 | 115.0676 | 68.5425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 158.217 | 158.217 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1113 | 9 | 0.1 | 7.03 | 26.94 | 33.97 | 26.94 | 13.47 | 47 | 1113 | 540 | 46.3562 | -12.6601 | -4.4337 | 514.284 | 8.4975 | 52.5374 | 14.2826 | 14.2826 | 53.0494 | 126.9506 | 54.1002 | 16.7089 | 16.7089 | 22.9947 | 39.7036 | -3.2564 | 0% | 17.954 | 0 | 0 | 140.1789 | 140.1789 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1114 | 10 | -0.8 | 55.47 | 64.92 | 120.39 | 64.92 | 32.46 | 47 | 1114 | 600 | 46.3562 | -12.6601 | -4.4337 | 574.284 | 9.4975 | 37.5374 | 21.7234 | 21.7234 | 39.7852 | 140.2148 | 39.959 | 114.8743 | 114.8743 | 55.4127 | 170.287 | -0.15577 | 0% | 77.0038 | 0 | 0 | 142.4077 | 142.4077 | 0% | 12.07% | 12.07% | 80% | 9.658% | 7.437 | 10.559 | 6 | 44.6218 | 16.4462 | 31.33% | 31.33%
2 | 47 | 16 | 1115 | 11 | -1.7 | 104.36 | 107.86 | 212.22 | 107.86 | 53.93 | 47 | 1115 | 660 | 46.3562 | -12.6601 | -4.4337 | 634.284 | 10.4975 | 22.5374 | 27.222 | 27.222 | 24.8692 | 155.1308 | 26.6275 | 203.943 | 203.943 | 92.0643 | 296.0072 | 0.2443 | 24.43% | 133.8545 | 32.7011 | 22.8908 | 119.5441 | 119.5441 | 19.15% | 11.95% | 11.95% | 80% | 9.563% | 12.8003 | 10.8704 | 6 | 76.8015 | 28.3066 | 64.25% | 64.25%
2 | 47 | 16 | 1116 | 12 | -1.8 | 134.08 | 134.25 | 268.33 | 134.25 | 67.13 | 47 | 1116 | 720 | 46.3562 | -12.6601 | -4.4337 | 694.284 | 11.4975 | 7.5374 | 30.1785 | 30.1785 | 8.514 | 171.486 | 16.2621 | 256.0511 | 256.0511 | 114.5895 | 370.6407 | 0.35633 | 35.63% | 167.6037 | 59.7228 | 41.806 | 114.5963 | 114.5963 | 36.48% | 11.87% | 11.87% | 85% | 10.09% | 16.9058 | 10.9053 | 6 | 101.4349 | 37.3857 | 88.51% | 88.51%
2 | 47 | 16 | 1117 | 13 | -1.9 | 149.81 | 161.47 | 311.28 | 161.47 | 80.74 | 47 | 1117 | 780 | 46.3562 | -12.6601 | -4.4337 | 754.284 | 12.4975 | -7.4626 | 30.186 | 30.186 | 8.43 | 188.43 | 16.228 | 286.0752 | 286.0752 | 137.8233 | 423.8985 | 0.41199 | 41.2% | 191.6869 | 78.9729 | 55.2811 | 114.599 | 114.599 | 48.24% | 11.81% | 11.81% | 85% | 10.03% | 19.2344 | 10.9403 | 6 | 115.4062 | 42.5351 | 100.7% | 100.7%
2 | 47 | 16 | 1118 | 14 | -1.8 | 143.06 | 174.25 | 317.31 | 174.25 | 87.13 | 47 | 1118 | 840 | 46.3562 | -12.6601 | -4.4337 | 814.284 | 13.4975 | -22.4626 | 27.2435 | 27.2435 | 24.7907 | 204.7907 | 26.5651 | 279.5199 | 279.5199 | 148.7317 | 428.2515 | 0.41656 | 41.66% | 193.6553 | 80.6683 | 56.4678 | 113.7492 | 113.7492 | 49.64% | 11.8% | 11.8% | 85% | 10.03% | 19.4199 | 10.9053 | 6 | 116.5193 | 42.9454 | 102.4% | 102.4%
2 | 47 | 16 | 1119 | 15 | -1.7 | 115.36 | 161.94 | 277.3 | 161.94 | 80.97 | 47 | 1119 | 900 | 46.3562 | -12.6601 | -4.4337 | 874.284 | 14.4975 | -37.4626 | 21.7562 | 21.7562 | 39.715 | 219.715 | 39.8898 | 238.8011 | 238.8011 | 138.2244 | 377.0255 | 0.36458 | 36.46% | 170.4909 | 62.1568 | 43.5098 | 110.0354 | 110.0354 | 39.54% | 11.86% | 11.86% | 85% | 10.08% | 17.1826 | 10.8704 | 6 | 103.0955 | 37.9977 | 93.69% | 93.69%
2 | 47 | 16 | 1120 | 16 | -1.6 | 101.94 | 128.33 | 230.27 | 128.33 | 64.17 | 47 | 1120 | 960 | 46.3562 | -12.6601 | -4.4337 | 934.284 | 15.4975 | -52.4626 | 14.3236 | 14.3236 | 52.987 | 232.987 | 54.0287 | 242.0292 | 242.0292 | 109.5365 | 351.5657 | 0.33346 | 33.35% | 158.978 | 53.0131 | 37.1092 | 106.8057 | 106.8057 | 34.74% | 11.88% | 0% | 85% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1121 | 17 | -2 | 58.25 | 88.33 | 146.58 | 88.33 | 44.17 | 47 | 1121 | 1020 | 46.3562 | -12.6601 | -4.4337 | 994.284 | 16.4975 | -67.4626 | 5.5316 | 5.5316 | 64.8758 | 244.8758 | 68.47 | 0 | 0 | 75.3944 | 75.3944 | -1.4034 | 0% | 34.0933 | 0 | 0 | 142.2617 | 142.2617 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1122 | 18 | -2.2 | 1.58 | 41.03 | 42.61 | 41.03 | 20.52 | 47 | 1122 | 1080 | 46.3562 | -12.6601 | -4.4337 | 1054.284 | 17.4975 | -82.4626 | -4.1324 | 0 | 71.3351 | 251.3351 | 76.9208 | 0 | 0 | 35.0213 | 35.0213 | -3.9623 | 0% | 15.8366 | 0 | 0 | 132.9365 | 132.9365 | 0% | 12.29% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1123 | 19 | -3.1 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 47 | 1123 | 1140 | 46.3562 | -12.6601 | -4.4337 | 1114.284 | 18.4975 | -97.4626 | -14.2699 | 0 | 71.3351 | 251.3351 | 76.9208 | 0 | 0 | 1.6559 | 1.6559 | -101.3619 | 0% | 0.7488 | 0 | 0 | 126.4099 | 126.4099 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1124 | 20 | -3.6 | 0 | 0 | 0 | 0 | 0 | 47 | 1124 | 1200 | 46.3562 | -12.6601 | -4.4337 | 1174.284 | 19.4975 | -112.4626 | -24.5197 | 0 | 71.3351 | 251.3351 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.0837 | 121.0837 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1125 | 21 | -4 | 0 | 0 | 0 | 0 | 0 | 47 | 1125 | 1260 | 46.3562 | -12.6601 | -4.4337 | 1234.284 | 20.4975 | -127.4626 | -34.4803 | 0 | 71.3351 | 251.3351 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.6113 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1126 | 22 | -4.1 | 0 | 0 | 0 | 0 | 0 | 47 | 1126 | 1320 | 46.3562 | -12.6601 | -4.4337 | 1294.284 | 21.4975 | -142.4626 | -43.594 | 0 | 71.3351 | 251.3351 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.766 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1127 | 23 | -4.1 | 0 | 0 | 0 | 0 | 0 | 47 | 1127 | 1380 | 46.3562 | -12.6601 | -4.4337 | 1354.284 | 22.4975 | -157.4626 | -50.9737 | 0 | 71.3351 | 251.3351 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.4313 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
2 | 47 | 16 | 1128 | 24 | -4.1 | 0 | 0 | 0 | 0 | 0 | 47 | 1128 | 1440 | 46.3562 | -12.6601 | -4.4337 | 1414.284 | 23.4975 | -172.4626 | -55.2968 | 0 | 71.3351 | 251.3351 | 76.9208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.0965 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1129 | 1 | -4 | 0 | 0 | 0 | 0 | 0 | 48 | 1129 | 60 | 47.3425 | -12.3235 | -4.1933 | 34.284 | 0.50151 | 172.4773 | -54.9665 | 0 | 71.841 | 108.159 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6642 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1130 | 2 | -4.2 | 0 | 0 | 0 | 0 | 0 | 48 | 1130 | 120 | 47.3425 | -12.3235 | -4.1933 | 94.284 | 1.5015 | 157.4773 | -50.6734 | 0 | 71.841 | 108.159 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6407 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1131 | 3 | -4.2 | 0 | 0 | 0 | 0 | 0 | 48 | 1131 | 180 | 47.3425 | -12.3235 | -4.1933 | 154.284 | 2.5015 | 142.4773 | -43.3267 | 0 | 71.841 | 108.159 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3124 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1132 | 4 | -5.2 | 0 | 0 | 0 | 0 | 0 | 48 | 1132 | 240 | 47.3425 | -12.3235 | -4.1933 | 214.284 | 3.5015 | 127.4773 | -34.2364 | 0 | 71.841 | 108.159 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8363 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1133 | 5 | -6.6 | 0 | 0 | 0 | 0 | 0 | 48 | 1133 | 300 | 47.3425 | -12.3235 | -4.1933 | 274.284 | 4.5015 | 112.4773 | -24.2876 | 0 | 71.841 | 108.159 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7667 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.665 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1134 | 6 | -7.2 | 0 | 0 | 0 | 0 | 0 | 48 | 1134 | 360 | 47.3425 | -12.3235 | -4.1933 | 334.284 | 5.5015 | 97.4773 | -14.0397 | 0 | 71.841 | 108.159 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2067 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1135 | 7 | -7.7 | 0 | 0 | 0 | 0 | 0 | 48 | 1135 | 420 | 47.3425 | -12.3235 | -4.1933 | 394.284 | 6.5015 | 82.4773 | -3.8955 | 0 | 71.841 | 108.159 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.0414 | 148.0414 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.091 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1136 | 8 | -8.8 | 0 | 0 | 0 | 0 | 0 | 48 | 1136 | 480 | 47.3425 | -12.3235 | -4.1933 | 454.284 | 7.5015 | 67.4773 | 5.7824 | 5.7824 | 65.1021 | 114.8979 | 68.4434 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 152.7185 | 152.7185 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5254 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1137 | 9 | -6.8 | 14.25 | 27.78 | 42.03 | 27.78 | 13.89 | 48 | 1137 | 540 | 47.3425 | -12.3235 | -4.1933 | 514.284 | 8.5015 | 52.4773 | 14.5943 | 14.5943 | 53.1943 | 126.8057 | 53.9754 | 33.2611 | 33.2611 | 23.7117 | 56.9729 | -2.3301 | 0% | 25.7631 | 0 | 0 | 139.1758 | 139.1758 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.7418 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1138 | 10 | -5.6 | 63.33 | 73.14 | 136.47 | 73.14 | 36.57 | 48 | 1138 | 600 | 47.3425 | -12.3235 | -4.1933 | 574.284 | 9.5015 | 37.4773 | 22.0505 | 22.0505 | 39.8918 | 140.1082 | 39.7974 | 129.6061 | 129.6061 | 62.4289 | 192.035 | -0.10986 | 0% | 86.8382 | 0 | 0 | 144.9711 | 144.9711 | 0% | 12.21% | 12.21% | 80% | 9.766% | 8.481 | 12.2851 | 6 | 50.8859 | 18.7549 | 35.1% | 35.1%
2 | 48 | 17 | 1139 | 11 | -4.7 | 109.92 | 114.08 | 224 | 114.08 | 57.04 | 48 | 1139 | 660 | 47.3425 | -12.3235 | -4.1933 | 634.284 | 10.5015 | 22.4773 | 27.561 | 27.561 | 24.918 | 155.082 | 26.4037 | 212.7838 | 212.7838 | 97.3734 | 310.1571 | 0.24554 | 24.55% | 140.2531 | 34.438 | 24.1066 | 124.2909 | 124.2909 | 19.4% | 12.02% | 12.02% | 85% | 10.21% | 14.3266 | 11.9492 | 6 | 85.9597 | 31.682 | 69.16% | 69.16%
2 | 48 | 17 | 1140 | 12 | -3.7 | 178.97 | 156.19 | 335.16 | 156.19 | 78.1 | 48 | 1140 | 720 | 47.3425 | -12.3235 | -4.1933 | 694.284 | 11.5015 | 7.4773 | 30.5194 | 30.5194 | 8.4868 | 171.5132 | 15.9374 | 338.8747 | 338.8747 | 133.3165 | 472.1912 | 0.44253 | 44.25% | 213.5248 | 94.4904 | 66.1433 | 122.9273 | 122.9273 | 53.81% | 11.78% | 11.78% | 85% | 10.01% | 21.379 | 11.5826 | 6 | 128.2738 | 47.2777 | 104.3% | 104.3%
2 | 48 | 17 | 1141 | 13 | -2.4 | 208.14 | 203.81 | 411.95 | 203.81 | 101.91 | 48 | 1141 | 780 | 47.3425 | -12.3235 | -4.1933 | 754.284 | 12.5015 | -7.5227 | 30.5148 | 30.5148 | 8.538 | 188.538 | 15.9584 | 394.1195 | 394.1195 | 173.9627 | 568.0822 | 0.50929 | 50.93% | 256.8868 | 130.8289 | 91.5802 | 127.1654 | 127.1654 | 72.02% | 11.64% | 11.64% | 90% | 10.47% | 26.9062 | 11.1164 | 6 | 161.4372 | 59.5007 | 127% | 127%
2 | 48 | 17 | 1142 | 14 | -2.9 | 175.92 | 194.81 | 370.73 | 194.81 | 97.41 | 48 | 1142 | 840 | 47.3425 | -12.3235 | -4.1933 | 814.284 | 13.5015 | -22.5227 | 27.5479 | 27.5479 | 24.9657 | 204.9657 | 26.4418 | 340.5836 | 340.5836 | 166.2807 | 506.8644 | 0.47122 | 47.12% | 229.2041 | 108.0057 | 75.604 | 123.8025 | 123.8025 | 61.07% | 11.72% | 11.72% | 90% | 10.55% | 24.1789 | 11.2943 | 6 | 145.0736 | 53.4695 | 117.2% | 117.2%
2 | 48 | 17 | 1143 | 15 | -2 | 169.36 | 184.81 | 354.17 | 184.81 | 92.41 | 48 | 1143 | 900 | 47.3425 | -12.3235 | -4.1933 | 874.284 | 14.5015 | -37.5227 | 22.0306 | 22.0306 | 39.9345 | 219.9345 | 39.8394 | 346.684 | 346.684 | 157.7452 | 504.4292 | 0.47408 | 47.41% | 228.1029 | 108.1385 | 75.697 | 122.4772 | 122.4772 | 61.8% | 11.71% | 11.71% | 90% | 10.54% | 24.039 | 10.9754 | 6 | 144.2341 | 53.1602 | 117.8% | 117.8%
2 | 48 | 17 | 1144 | 16 | -1.7 | 146.67 | 143.53 | 290.2 | 143.53 | 71.77 | 48 | 1144 | 960 | 47.3425 | -12.3235 | -4.1933 | 934.284 | 15.5015 | -52.5227 | 14.5694 | 14.5694 | 53.2322 | 233.2322 | 54.0188 | 342.5589 | 342.5589 | 122.5105 | 465.0694 | 0.44776 | 44.78% | 210.3044 | 94.1669 | 65.9168 | 119.0367 | 119.0367 | 55.38% | 11.75% | 0% | 85% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1145 | 17 | -1.8 | 134.64 | 70.19 | 204.83 | 70.19 | 35.1 | 48 | 1145 | 1020 | 47.3425 | -12.3235 | -4.1933 | 994.284 | 16.5015 | -67.5227 | 5.7542 | 5.7542 | 65.1364 | 245.1364 | 68.4873 | 0 | 0 | 59.9109 | 59.9109 | -1.9655 | 0% | 27.0917 | 0 | 0 | 113.3495 | 113.3495 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1146 | 18 | -3.4 | 0 | 47.03 | 47.03 | 47.03 | 23.52 | 48 | 1146 | 1080 | 47.3425 | -12.3235 | -4.1933 | 1054.284 | 17.5015 | -82.5227 | -3.9257 | 0 | 71.841 | 251.841 | 77.269 | 0 | 0 | 40.1426 | 40.1426 | -3.4291 | 0% | 18.1525 | 0 | 0 | 138.6284 | 138.6284 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.4739 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1147 | 19 | -5.4 | 0 | 2.78 | 2.78 | 2.78 | 1.39 | 48 | 1147 | 1140 | 47.3425 | -12.3235 | -4.1933 | 1114.284 | 18.5015 | -97.5227 | -14.0707 | 0 | 71.841 | 251.841 | 77.269 | 0 | 0 | 2.3729 | 2.3729 | -72.94 | 0% | 1.073 | 0 | 0 | 128.6465 | 128.6465 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1148 | 20 | -6.4 | 0 | 0 | 0 | 0 | 0 | 48 | 1148 | 1200 | 47.3425 | -12.3235 | -4.1933 | 1174.284 | 19.5015 | -112.5227 | -24.3183 | 0 | 71.841 | 251.841 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.691 | 120.691 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1149 | 21 | -8 | 0 | 0 | 0 | 0 | 0 | 48 | 1149 | 1260 | 47.3425 | -12.3235 | -4.1933 | 1234.284 | 20.5015 | -127.5227 | -34.2655 | 0 | 71.841 | 251.841 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.3193 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.2086 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1150 | 22 | -9.7 | 0 | 0 | 0 | 0 | 0 | 48 | 1150 | 1320 | 47.3425 | -12.3235 | -4.1933 | 1294.284 | 21.5015 | -142.5227 | -43.3521 | 0 | 71.841 | 251.841 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -33.336 | 0 | 0% | 12.66% | 0% | 80% | 0% | 0 | 13.8872 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1151 | 23 | -9.6 | 0 | 0 | 0 | 0 | 0 | 48 | 1151 | 1380 | 47.3425 | -12.3235 | -4.1933 | 1354.284 | 22.5015 | -157.5227 | -50.6917 | 0 | 71.841 | 251.841 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.8553 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
2 | 48 | 17 | 1152 | 24 | -10.6 | 0 | 0 | 0 | 0 | 0 | 48 | 1152 | 1440 | 47.3425 | -12.3235 | -4.1933 | 1414.284 | 23.5015 | -172.5227 | -54.9734 | 0 | 71.841 | 251.841 | 77.269 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -34.0509 | 0 | 0% | 12.7% | 0% | 80% | 0% | 0 | 14.2546 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1153 | 1 | -10.3 | 0 | 0 | 0 | 0 | 0 | 49 | 1153 | 60 | 48.3288 | -11.9832 | -3.9434 | 34.284 | 0.50568 | 172.4148 | -54.6209 | 0 | 72.3514 | 107.6486 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.8301 | 0 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.1315 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1154 | 2 | -11.4 | 0 | 0 | 0 | 0 | 0 | 49 | 1154 | 120 | 48.3288 | -11.9832 | -3.9434 | 94.284 | 1.5057 | 157.4148 | -50.3383 | 0 | 72.3514 | 107.6486 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.0113 | 0 | 0% | 12.73% | 0% | 80% | 0% | 0 | 14.5859 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1155 | 3 | -12.2 | 0 | 0 | 0 | 0 | 0 | 49 | 1155 | 180 | 48.3288 | -11.9832 | -3.9434 | 154.284 | 2.5057 | 142.4148 | -43.0128 | 0 | 72.3514 | 107.6486 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.7354 | 0 | 0% | 12.77% | 0% | 80% | 0% | 0 | 14.9218 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1156 | 4 | -12.8 | 0 | 0 | 0 | 0 | 0 | 49 | 1156 | 240 | 48.3288 | -11.9832 | -3.9434 | 214.284 | 3.5057 | 127.4148 | -33.9396 | 0 | 72.3514 | 107.6486 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.6498 | 0 | 0% | 12.8% | 0% | 80% | 0% | 0 | 15.1766 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1157 | 5 | -13.5 | 0 | 0 | 0 | 0 | 0 | 49 | 1157 | 300 | 48.3288 | -11.9832 | -3.9434 | 274.284 | 4.5057 | 112.4148 | -24.0001 | 0 | 72.3514 | 107.6486 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5657 | 0 | 0% | 12.83% | 0% | 80% | 0% | 0 | 15.4771 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1158 | 6 | -14.6 | 0 | 0 | 0 | 0 | 0 | 49 | 1158 | 360 | 48.3288 | -11.9832 | -3.9434 | 334.284 | 5.5057 | 97.4148 | -13.7538 | 0 | 72.3514 | 107.6486 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5974 | 0 | 0% | 12.87% | 0% | 80% | 0% | 0 | 15.9562 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1159 | 7 | -15.3 | 0 | 0 | 0 | 0 | 0 | 49 | 1159 | 420 | 48.3288 | -11.9832 | -3.9434 | 394.284 | 6.5057 | 82.4148 | -3.6046 | 0 | 72.3514 | 107.6486 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.2047 | 146.2047 | 0% | 12.91% | 0% | 80% | 0% | 0 | 16.2655 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1160 | 8 | -15.9 | 0 | 0 | 0 | 0 | 0 | 49 | 1160 | 480 | 48.3288 | -11.9832 | -3.9434 | 454.284 | 7.5057 | 67.4148 | 6.0838 | 6.0838 | 65.2722 | 114.7278 | 68.3421 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 152.3642 | 152.3642 | 0% | 12.93% | 0% | 80% | 0% | 0 | 16.5333 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1161 | 9 | -16.1 | 16.53 | 28.19 | 44.72 | 28.19 | 14.1 | 49 | 1161 | 540 | 48.3288 | -11.9832 | -3.9434 | 514.284 | 8.5057 | 52.4148 | 14.9101 | 14.9101 | 53.3396 | 126.6604 | 53.8487 | 37.8983 | 37.8983 | 24.0617 | 61.96 | -2.4714 | 0% | 28.0183 | 0 | 0 | 135.542 | 135.542 | 0% | 12.82% | 0% | 80% | 0% | 0 | 16.6232 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1162 | 10 | -14.1 | 88.47 | 82.78 | 171.25 | 82.78 | 41.39 | 49 | 1162 | 600 | 48.3288 | -11.9832 | -3.9434 | 574.284 | 9.5057 | 37.4148 | 22.3819 | 22.3819 | 39.9982 | 140.0018 | 39.6342 | 178.9328 | 178.9328 | 70.6571 | 249.5899 | 0.012292 | 1.229% | 112.8646 | 1.3873 | 0.9711 | 143.2001 | 143.2001 | 0.6781% | 12.38% | 12.38% | 80% | 9.907% | 11.182 | 15.7374 | 6 | 67.0919 | 24.728 | 46.85% | 46.85%
2 | 49 | 18 | 1163 | 11 | -10.1 | 175.69 | 117.92 | 293.61 | 117.92 | 58.96 | 49 | 1163 | 660 | 48.3288 | -11.9832 | -3.9434 | 634.284 | 10.5057 | 22.4148 | 27.9041 | 27.9041 | 24.9656 | 155.0344 | 26.1784 | 336.9038 | 336.9038 | 100.651 | 437.5548 | 0.37645 | 37.64% | 197.8623 | 74.4847 | 52.1393 | 127.0809 | 127.0809 | 41.03% | 11.95% | 11.95% | 85% | 10.16% | 20.1013 | 14.0498 | 6 | 120.6076 | 44.4522 | 94.91% | 94.91%
2 | 49 | 18 | 1164 | 12 | -8.1 | 182.78 | 120.83 | 303.61 | 120.83 | 60.42 | 49 | 1164 | 720 | 48.3288 | -11.9832 | -3.9434 | 694.284 | 11.5057 | 7.4148 | 30.8641 | 30.8641 | 8.457 | 171.543 | 15.6092 | 343.1532 | 343.1532 | 103.1349 | 446.2881 | 0.39642 | 39.64% | 201.8115 | 80.0031 | 56.0021 | 119.8566 | 119.8566 | 46.72% | 11.9% | 11.9% | 85% | 10.11% | 20.4109 | 13.248 | 6 | 122.4656 | 45.137 | 102.2% | 102.2%
2 | 49 | 18 | 1165 | 13 | -8 | 205.92 | 155.19 | 361.11 | 155.19 | 77.6 | 49 | 1165 | 780 | 48.3288 | -11.9832 | -3.9434 | 754.284 | 12.5057 | -7.5852 | 30.8468 | 30.8468 | 8.65 | 188.65 | 15.6898 | 386.6402 | 386.6402 | 132.463 | 519.1031 | 0.45409 | 45.41% | 234.7384 | 106.5929 | 74.615 | 119.6659 | 119.6659 | 62.35% | 11.78% | 11.78% | 90% | 10.61% | 24.8966 | 13.2086 | 6 | 149.3799 | 55.0567 | 124.8% | 124.8%
2 | 49 | 18 | 1166 | 14 | -6.9 | 185.83 | 192.42 | 378.25 | 192.42 | 96.21 | 49 | 1166 | 840 | 48.3288 | -11.9832 | -3.9434 | 814.284 | 13.5057 | -22.5852 | 27.8547 | 27.8547 | 25.1456 | 205.1456 | 26.3225 | 356.4872 | 356.4872 | 164.2407 | 520.7279 | 0.46061 | 46.06% | 235.4732 | 108.4614 | 75.923 | 120.0869 | 120.0869 | 63.22% | 11.77% | 11.77% | 90% | 10.59% | 24.9335 | 12.7803 | 6 | 149.6008 | 55.1381 | 124.6% | 124.6%
2 | 49 | 18 | 1167 | 15 | -6.2 | 147.03 | 157.03 | 304.06 | 157.03 | 78.52 | 49 | 1167 | 900 | 48.3288 | -11.9832 | -3.9434 | 874.284 | 14.5057 | -37.5852 | 22.3068 | 22.3068 | 40.159 | 220.159 | 39.7928 | 297.6362 | 297.6362 | 134.0335 | 431.6697 | 0.39391 | 39.39% | 195.201 | 76.8919 | 53.8243 | 114.7368 | 114.7368 | 46.91% | 11.88% | 11.88% | 85% | 10.1% | 19.716 | 12.5122 | 6 | 118.2959 | 43.6001 | 103.1% | 103.1%
2 | 49 | 18 | 1168 | 16 | -5.3 | 103.61 | 115.83 | 219.44 | 115.83 | 57.92 | 49 | 1168 | 960 | 48.3288 | -11.9832 | -3.9434 | 934.284 | 15.5057 | -52.5852 | 14.8165 | 14.8165 | 53.4821 | 233.4821 | 54.0122 | 238.08 | 238.08 | 98.8671 | 336.9471 | 0.28543 | 28.54% | 152.3675 | 43.4899 | 30.4429 | 110.1418 | 110.1418 | 27.64% | 12% | 0% | 85% | 0% | 0 | 12.1725 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1169 | 17 | -5.2 | 58.42 | 66.75 | 125.17 | 66.75 | 33.38 | 49 | 1169 | 1020 | 48.3288 | -11.9832 | -3.9434 | 994.284 | 16.5057 | -67.5852 | 5.9778 | 5.9778 | 65.4014 | 245.4014 | 68.5075 | 0 | 0 | 56.9747 | 56.9747 | -2.2584 | 0% | 25.764 | 0 | 0 | 145.0481 | 145.0481 | 0% | 12.38% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1170 | 18 | -6 | 15 | 24.92 | 39.92 | 24.92 | 12.46 | 49 | 1170 | 1080 | 48.3288 | -11.9832 | -3.9434 | 1054.284 | 17.5057 | -82.5852 | -3.718 | 0 | 72.3514 | 252.3514 | 77.6208 | 0 | 0 | 21.2706 | 21.2706 | -7.4945 | 0% | 9.6185 | 0 | 0 | 135.6285 | 135.6285 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1171 | 19 | -7.1 | 0 | 1.67 | 1.67 | 1.67 | 0.84 | 49 | 1171 | 1140 | 48.3288 | -11.9832 | -3.9434 | 1114.284 | 18.5057 | -97.5852 | -13.8703 | 0 | 72.3514 | 252.3514 | 77.6208 | 0 | 0 | 1.4254 | 1.4254 | -124.9999 | 0% | 0.64458 | 0 | 0 | 127.6701 | 127.6701 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1172 | 20 | -7.6 | 0 | 0 | 0 | 0 | 0 | 49 | 1172 | 1200 | 48.3288 | -11.9832 | -3.9434 | 1174.284 | 19.5057 | -112.5852 | -24.1156 | 0 | 72.3514 | 252.3514 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.3342 | 121.3342 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.0519 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1173 | 21 | -9 | 0 | 0 | 0 | 0 | 0 | 49 | 1173 | 1260 | 48.3288 | -11.9832 | -3.9434 | 1234.284 | 20.5057 | -127.5852 | -34.0488 | 0 | 72.3514 | 252.3514 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.1098 | 0 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6053 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1174 | 22 | -9.2 | 0 | 0 | 0 | 0 | 0 | 49 | 1174 | 1320 | 48.3288 | -11.9832 | -3.9434 | 1294.284 | 21.5057 | -142.5852 | -43.1078 | 0 | 72.3514 | 252.3514 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.6392 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1175 | 23 | -9.6 | 0 | 0 | 0 | 0 | 0 | 49 | 1175 | 1380 | 48.3288 | -11.9832 | -3.9434 | 1354.284 | 22.5057 | -157.5852 | -50.4067 | 0 | 72.3514 | 252.3514 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.7536 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
2 | 49 | 18 | 1176 | 24 | -8.7 | 0 | 0 | 0 | 0 | 0 | 49 | 1176 | 1440 | 48.3288 | -11.9832 | -3.9434 | 1414.284 | 23.5057 | -172.5852 | -54.6467 | 0 | 72.3514 | 252.3514 | 77.6208 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.8869 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1177 | 1 | -9.1 | 0 | 0 | 0 | 0 | 0 | 50 | 1177 | 60 | 49.3151 | -11.6395 | -3.684 | 34.284 | 0.51 | 172.35 | -54.2716 | 0 | 72.8661 | 107.1339 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.4007 | 0 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6454 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1178 | 2 | -9 | 0 | 0 | 0 | 0 | 0 | 50 | 1178 | 120 | 49.3151 | -11.6395 | -3.684 | 94.284 | 1.51 | 157.35 | -49.9989 | 0 | 72.8661 | 107.1339 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.8767 | 0 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6053 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1179 | 3 | -8.9 | 0 | 0 | 0 | 0 | 0 | 50 | 1179 | 180 | 49.3151 | -11.6395 | -3.684 | 154.284 | 2.51 | 142.35 | -42.6942 | 0 | 72.8661 | 107.1339 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.3528 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5653 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1180 | 4 | -9.2 | 0 | 0 | 0 | 0 | 0 | 50 | 1180 | 240 | 49.3151 | -11.6395 | -3.684 | 214.284 | 3.51 | 127.35 | -33.6383 | 0 | 72.8661 | 107.1339 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.8099 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1181 | 5 | -9.2 | 0 | 0 | 0 | 0 | 0 | 50 | 1181 | 300 | 49.3151 | -11.6395 | -3.684 | 274.284 | 4.51 | 112.35 | -23.7082 | 0 | 72.8661 | 107.1339 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4192 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1182 | 6 | -9.2 | 0 | 0 | 0 | 0 | 0 | 50 | 1182 | 360 | 49.3151 | -11.6395 | -3.684 | 334.284 | 5.51 | 97.35 | -13.4636 | 0 | 72.8661 | 107.1339 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.65 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1183 | 7 | -9.4 | 0 | 0 | 0 | 0 | 0 | 50 | 1183 | 420 | 49.3151 | -11.6395 | -3.684 | 394.284 | 6.51 | 82.35 | -3.3094 | 0 | 72.8661 | 107.1339 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.2744 | 143.2744 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.7659 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1184 | 8 | -9.2 | 0 | 0 | 0 | 0 | 0 | 50 | 1184 | 480 | 49.3151 | -11.6395 | -3.684 | 454.284 | 7.51 | 67.35 | 6.3894 | 6.3894 | 65.4427 | 114.5573 | 68.2387 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.4284 | 149.4284 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1185 | 9 | -8.8 | 15.28 | 35.14 | 50.42 | 35.14 | 17.57 | 50 | 1185 | 540 | 49.3151 | -11.6395 | -3.684 | 514.284 | 8.51 | 52.35 | 15.2301 | 15.2301 | 53.4851 | 126.5149 | 53.7203 | 34.4185 | 34.4185 | 29.9939 | 64.4123 | -2.048 | 0% | 29.1273 | 0 | 0 | 133.6431 | 133.6431 | 0% | 12.52% | 12.52% | 80% | 10.01% | 2.9167 | 13.5254 | 6 | 17.5004 | 6.4501 | 13.09% | 13.09%
2 | 50 | 19 | 1186 | 10 | -7.4 | 61.75 | 84.72 | 146.47 | 84.72 | 42.36 | 50 | 1186 | 600 | 49.3151 | -11.6395 | -3.684 | 574.284 | 9.51 | 37.35 | 22.7174 | 22.7174 | 40.1043 | 139.8957 | 39.4695 | 123.4348 | 123.4348 | 72.313 | 195.7478 | -0.11604 | 0% | 88.5172 | 0 | 0 | 139.8883 | 139.8883 | 0% | 12.26% | 12.26% | 80% | 9.81% | 8.6836 | 12.9739 | 6 | 52.1017 | 19.203 | 37.25% | 37.25%
2 | 50 | 19 | 1187 | 11 | -6.4 | 133.97 | 119.08 | 253.05 | 119.08 | 59.54 | 50 | 1187 | 660 | 49.3151 | -11.6395 | -3.684 | 634.284 | 10.51 | 22.35 | 28.2512 | 28.2512 | 25.012 | 154.988 | 25.9517 | 254.4925 | 254.4925 | 101.6411 | 356.1337 | 0.3055 | 30.55% | 161.0436 | 49.1984 | 34.4389 | 120.6698 | 120.6698 | 28.54% | 12% | 12% | 85% | 10.2% | 16.4217 | 12.5884 | 6 | 98.5299 | 36.315 | 81.65% | 81.65%
2 | 50 | 19 | 1188 | 12 | -6.1 | 210 | 125.83 | 335.83 | 125.83 | 62.92 | 50 | 1188 | 720 | 49.3151 | -11.6395 | -3.684 | 694.284 | 11.51 | 7.35 | 31.2125 | 31.2125 | 8.4245 | 171.5755 | 15.2775 | 390.9174 | 390.9174 | 107.4026 | 498.32 | 0.44927 | 44.93% | 225.3403 | 101.2392 | 70.8675 | 117.0972 | 117.0972 | 60.52% | 11.79% | 11.79% | 85% | 10.02% | 22.573 | 12.4742 | 6 | 135.4381 | 49.9182 | 115.7% | 115.7%
2 | 50 | 19 | 1189 | 13 | -5.4 | 249.17 | 122.22 | 371.39 | 122.22 | 61.11 | 50 | 1189 | 780 | 49.3151 | -11.6395 | -3.684 | 754.284 | 12.51 | -7.65 | 31.1818 | 31.1818 | 8.7661 | 188.7661 | 15.4223 | 463.9214 | 463.9214 | 104.3213 | 568.2427 | 0.49606 | 49.61% | 256.9594 | 127.4669 | 89.2268 | 117.1951 | 117.1951 | 76.14% | 11.68% | 11.68% | 90% | 10.51% | 27.0018 | 12.2099 | 6 | 162.0106 | 59.712 | 138.2% | 138.2%
2 | 50 | 19 | 1190 | 14 | -5 | 248.06 | 148.53 | 396.59 | 148.53 | 74.27 | 50 | 1190 | 840 | 49.3151 | -11.6395 | -3.684 | 814.284 | 13.51 | -22.65 | 28.1638 | 28.1638 | 25.3304 | 205.3304 | 26.2074 | 471.5314 | 471.5314 | 126.7783 | 598.3097 | 0.51323 | 51.32% | 270.5556 | 138.8575 | 97.2003 | 117.0684 | 117.0684 | 83.03% | 11.63% | 11.63% | 90% | 10.47% | 28.3174 | 12.0605 | 6 | 169.9045 | 62.6214 | 145.1% | 145.1%
2 | 50 | 19 | 1191 | 15 | -5.1 | 192.86 | 141.67 | 334.53 | 141.67 | 70.84 | 50 | 1191 | 900 | 49.3151 | -11.6395 | -3.684 | 874.284 | 14.51 | -37.65 | 22.5846 | 22.5846 | 40.3884 | 220.3884 | 39.75 | 386.0954 | 386.0954 | 120.9229 | 507.0183 | 0.46038 | 46.04% | 229.2737 | 105.5521 | 73.8865 | 111.5552 | 111.5552 | 66.23% | 11.76% | 11.76% | 90% | 10.58% | 24.259 | 12.0978 | 6 | 145.5542 | 53.6467 | 130.5% | 130.5%
2 | 50 | 19 | 1192 | 16 | -4 | 64.08 | 150.75 | 214.83 | 150.75 | 75.38 | 50 | 1192 | 960 | 49.3151 | -11.6395 | -3.684 | 934.284 | 15.51 | -52.65 | 15.0647 | 15.0647 | 53.7368 | 233.7368 | 54.0088 | 144.8862 | 144.8862 | 128.6732 | 273.5593 | 0.1773 | 17.73% | 123.7035 | 21.9322 | 15.3525 | 105.7993 | 105.7993 | 14.51% | 12.05% | 12.05% | 80% | 9.638% | 11.922 | 11.6918 | 6 | 71.5317 | 26.3643 | 67.61% | 67.61%
2 | 50 | 19 | 1193 | 17 | -3.9 | 35.75 | 94.64 | 130.39 | 94.64 | 47.32 | 50 | 1193 | 1020 | 49.3151 | -11.6395 | -3.684 | 994.284 | 16.51 | -67.65 | 6.2024 | 6.2024 | 65.6707 | 245.6707 | 68.5306 | 0 | 0 | 80.7803 | 80.7803 | -1.3152 | 0% | 36.5288 | 0 | 0 | 141.2801 | 141.2801 | 0% | 12.3% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1194 | 18 | -3.9 | 3.42 | 38.53 | 41.95 | 38.53 | 19.27 | 50 | 1194 | 1080 | 49.3151 | -11.6395 | -3.684 | 1054.284 | 17.51 | -82.65 | -3.5093 | 0 | 72.8661 | 252.8661 | 77.9762 | 0 | 0 | 32.8874 | 32.8874 | -4.4013 | 0% | 14.8717 | 0 | 0 | 133.2852 | 133.2852 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1195 | 19 | -3.7 | 0 | 2.97 | 2.97 | 2.97 | 1.49 | 50 | 1195 | 1140 | 49.3151 | -11.6395 | -3.684 | 1114.284 | 18.51 | -97.65 | -13.6688 | 0 | 72.8661 | 252.8661 | 77.9762 | 0 | 0 | 2.5351 | 2.5351 | -66.5257 | 0% | 1.1464 | 0 | 0 | 128.457 | 128.457 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1196 | 20 | -2.9 | 0 | 0 | 0 | 0 | 0 | 50 | 1196 | 1200 | 49.3151 | -11.6395 | -3.684 | 1174.284 | 19.51 | -112.65 | -23.9114 | 0 | 72.8661 | 252.8661 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.0544 | 125.0544 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1197 | 21 | -2.9 | 0 | 0 | 0 | 0 | 0 | 50 | 1197 | 1260 | 49.3151 | -11.6395 | -3.684 | 1234.284 | 20.51 | -127.65 | -33.8302 | 0 | 72.8661 | 252.8661 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0413 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1198 | 22 | -2.9 | 0 | 0 | 0 | 0 | 0 | 50 | 1198 | 1320 | 49.3151 | -11.6395 | -3.684 | 1294.284 | 21.51 | -142.65 | -42.8611 | 0 | 72.8661 | 252.8661 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0668 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1199 | 23 | -2.9 | 0 | 0 | 0 | 0 | 0 | 50 | 1199 | 1380 | 49.3151 | -11.6395 | -3.684 | 1354.284 | 22.51 | -157.65 | -50.1188 | 0 | 72.8661 | 252.8661 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6952 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 50 | 19 | 1200 | 24 | -3 | 0 | 0 | 0 | 0 | 0 | 50 | 1200 | 1440 | 49.3151 | -11.6395 | -3.684 | 1414.284 | 23.51 | -172.65 | -54.3166 | 0 | 72.8661 | 252.8661 | 77.9762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.476 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1201 | 1 | -2.9 | 0 | 0 | 0 | 0 | 0 | 51 | 1201 | 60 | 50.3014 | -11.2925 | -3.4154 | 34.284 | 0.51448 | 172.2829 | -53.9185 | 0 | 73.3851 | 106.6149 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.3357 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1202 | 2 | -2.8 | 0 | 0 | 0 | 0 | 0 | 51 | 1202 | 120 | 50.3014 | -11.2925 | -3.4154 | 94.284 | 1.5145 | 157.2829 | -49.6553 | 0 | 73.3851 | 106.6149 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.0462 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1203 | 3 | -2.9 | 0 | 0 | 0 | 0 | 0 | 51 | 1203 | 180 | 50.3014 | -11.2925 | -3.4154 | 154.284 | 2.5145 | 142.2829 | -42.3712 | 0 | 73.3851 | 106.6149 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.0615 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1204 | 4 | -3 | 0 | 0 | 0 | 0 | 0 | 51 | 1204 | 240 | 50.3014 | -11.2925 | -3.4154 | 214.284 | 3.5145 | 127.2829 | -33.3325 | 0 | 73.3851 | 106.6149 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2139 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1205 | 5 | -3.2 | 0 | 0 | 0 | 0 | 0 | 51 | 1205 | 300 | 50.3014 | -11.2925 | -3.4154 | 274.284 | 4.5145 | 112.2829 | -23.4119 | 0 | 73.3851 | 106.6149 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3278 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1206 | 6 | -3.3 | 0 | 0 | 0 | 0 | 0 | 51 | 1206 | 360 | 50.3014 | -11.2925 | -3.4154 | 334.284 | 5.5145 | 97.2829 | -13.1692 | 0 | 73.3851 | 106.6149 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2326 | 0 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1207 | 7 | -3.3 | 0 | 0 | 0 | 0 | 0 | 51 | 1207 | 420 | 50.3014 | -11.2925 | -3.4154 | 394.284 | 6.5145 | 82.2829 | -3.0102 | 0 | 73.3851 | 106.6149 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.5103 | 135.5103 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1208 | 8 | -3.3 | 0 | 0 | 0 | 0 | 0 | 51 | 1208 | 480 | 50.3014 | -11.2925 | -3.4154 | 454.284 | 7.5145 | 67.2829 | 6.6991 | 6.6991 | 65.6138 | 114.3862 | 68.1333 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.3823 | 139.3823 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1209 | 9 | -3.6 | 0.75 | 17.97 | 18.72 | 17.97 | 8.99 | 51 | 1209 | 540 | 50.3014 | -11.2925 | -3.4154 | 514.284 | 8.5145 | 52.2829 | 15.5541 | 15.5541 | 53.631 | 126.369 | 53.5903 | 1.6602 | 1.6602 | 15.3384 | 16.9985 | -9.2223 | 0% | 7.6867 | 0 | 0 | 119.7965 | 119.7965 | 0% | 12.37% | 12.37% | 80% | 9.895% | 0.76058 | 11.5463 | 6 | 4.5635 | 1.6819 | 3.809% | 3.809%
2 | 51 | 20 | 1210 | 10 | -3.2 | 4.17 | 71.75 | 75.92 | 71.75 | 35.88 | 51 | 1210 | 600 | 50.3014 | -11.2925 | -3.4154 | 574.284 | 9.5145 | 37.2829 | 23.0568 | 23.0568 | 40.2103 | 139.7897 | 39.3036 | 8.239 | 8.239 | 61.2425 | 69.4814 | -1.6344 | 0% | 31.4195 | 0 | 0 | 123.8784 | 123.8784 | 0% | 12.28% | 12.28% | 80% | 9.827% | 3.0877 | 11.4019 | 6 | 18.5262 | 6.8282 | 14.96% | 14.96%
2 | 51 | 20 | 1211 | 11 | -1.6 | 5.75 | 105.19 | 110.94 | 105.19 | 52.6 | 51 | 1211 | 660 | 50.3014 | -11.2925 | -3.4154 | 634.284 | 10.5145 | 22.2829 | 28.6022 | 28.6022 | 25.0572 | 154.9428 | 25.7238 | 10.8207 | 10.8207 | 89.7853 | 100.606 | -0.84029 | 0% | 45.494 | 0 | 0 | 126.2954 | 126.2954 | 0% | 12.18% | 12.18% | 80% | 9.746% | 4.434 | 10.8355 | 6 | 26.6039 | 9.8054 | 21.06% | 21.06%
2 | 51 | 20 | 1212 | 12 | -0.5 | 18.61 | 174.25 | 192.86 | 174.25 | 87.13 | 51 | 1212 | 720 | 50.3014 | -11.2925 | -3.4154 | 694.284 | 11.5145 | 7.2829 | 31.5645 | 31.5645 | 8.3893 | 171.6107 | 14.9425 | 34.3499 | 34.3499 | 148.7317 | 183.0815 | -0.08464 | 0% | 82.7895 | 0 | 0 | 128.6832 | 128.6832 | 0% | 12.05% | 12.05% | 80% | 9.638% | 7.9793 | 10.4565 | 6 | 47.8758 | 17.6455 | 37.2% | 37.2%
2 | 51 | 20 | 1213 | 13 | -0.1 | 53.42 | 256.11 | 309.53 | 256.11 | 128.06 | 51 | 1213 | 780 | 50.3014 | -11.2925 | -3.4154 | 754.284 | 12.5145 | -7.7171 | 31.5198 | 31.5198 | 8.8863 | 188.8863 | 15.1565 | 98.6275 | 98.6275 | 218.6036 | 317.2311 | 0.29426 | 29.43% | 143.4519 | 42.2126 | 29.5488 | 113.6185 | 113.6185 | 26.01% | 11.89% | 11.89% | 85% | 10.1% | 14.4927 | 10.3208 | 6 | 86.9563 | 32.0494 | 76.53% | 76.53%
2 | 51 | 20 | 1214 | 14 | -0.3 | 97.69 | 266.47 | 364.16 | 266.47 | 133.24 | 51 | 1214 | 840 | 50.3014 | -11.2925 | -3.4154 | 814.284 | 13.5145 | -22.7171 | 28.4751 | 28.4751 | 25.5199 | 205.5199 | 26.0966 | 184.0082 | 184.0082 | 227.4464 | 411.4545 | 0.40979 | 40.98% | 186.0597 | 76.2457 | 53.372 | 115.2929 | 115.2929 | 46.29% | 11.79% | 11.79% | 85% | 10.02% | 18.6394 | 10.3885 | 6 | 111.8361 | 41.2193 | 97% | 97%
2 | 51 | 20 | 1215 | 15 | -0.5 | 132.31 | 213.61 | 345.92 | 213.61 | 106.81 | 51 | 1215 | 900 | 50.3014 | -11.2925 | -3.4154 | 874.284 | 14.5145 | -37.7171 | 22.864 | 22.864 | 40.6227 | 220.6227 | 39.711 | 261.9596 | 261.9596 | 182.3275 | 444.2871 | 0.43781 | 43.78% | 200.9066 | 87.9589 | 61.5712 | 112.6462 | 112.6462 | 54.66% | 11.75% | 11.75% | 85% | 9.99% | 20.0708 | 10.4565 | 6 | 120.4247 | 44.3848 | 106.9% | 106.9%
2 | 51 | 20 | 1216 | 16 | -1.1 | 107.58 | 176.67 | 284.25 | 176.67 | 88.34 | 51 | 1216 | 960 | 50.3014 | -11.2925 | -3.4154 | 934.284 | 15.5145 | -52.7171 | 15.3141 | 15.3141 | 53.996 | 233.996 | 54.0088 | 239.3726 | 239.3726 | 150.7973 | 390.1699 | 0.38321 | 38.32% | 176.4348 | 67.6107 | 47.3275 | 108.4267 | 108.4267 | 43.65% | 11.83% | 11.83% | 85% | 10.05% | 17.7378 | 10.6622 | 6 | 106.4269 | 39.2256 | 98.16% | 98.16%
2 | 51 | 20 | 1217 | 17 | -1.6 | 57.03 | 136.58 | 193.61 | 136.58 | 68.29 | 51 | 1217 | 1020 | 50.3014 | -11.2925 | -3.4154 | 994.284 | 16.5145 | -67.7171 | 6.4278 | 6.4278 | 65.9443 | 245.9443 | 68.5565 | 0 | 0 | 116.5783 | 116.5783 | -0.615 | 0% | 52.7167 | 0 | 0 | 101.8534 | 101.8534 | 0% | 12.16% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1218 | 18 | -2 | 18.14 | 50.92 | 69.06 | 50.92 | 25.46 | 51 | 1218 | 1080 | 50.3014 | -11.2925 | -3.4154 | 1054.284 | 17.5145 | -82.7171 | -3.2998 | 0 | 73.3851 | 253.3851 | 78.3351 | 0 | 0 | 43.4629 | 43.4629 | -3.0251 | 0% | 19.6539 | 0 | 0 | 134.8969 | 134.8969 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1219 | 19 | -2 | 0 | 3.89 | 3.89 | 3.89 | 1.95 | 51 | 1219 | 1140 | 50.3014 | -11.2925 | -3.4154 | 1114.284 | 18.5145 | -97.7171 | -13.4663 | 0 | 73.3851 | 253.3851 | 78.3351 | 0 | 0 | 3.3203 | 3.3203 | -49.3183 | 0% | 1.5014 | 0 | 0 | 127.74 | 127.74 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1220 | 20 | -2 | 0 | 0 | 0 | 0 | 0 | 51 | 1220 | 1200 | 50.3014 | -11.2925 | -3.4154 | 1174.284 | 19.5145 | -112.7171 | -23.7059 | 0 | 73.3851 | 253.3851 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.5608 | 123.5608 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1221 | 21 | -2 | 0 | 0 | 0 | 0 | 0 | 51 | 1221 | 1260 | 50.3014 | -11.2925 | -3.4154 | 1234.284 | 20.5145 | -127.7171 | -33.6099 | 0 | 73.3851 | 253.3851 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4574 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1222 | 22 | -2.1 | 0 | 0 | 0 | 0 | 0 | 51 | 1222 | 1320 | 50.3014 | -11.2925 | -3.4154 | 1294.284 | 21.5145 | -142.7171 | -42.612 | 0 | 73.3851 | 253.3851 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.5278 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1223 | 23 | -2.1 | 0 | 0 | 0 | 0 | 0 | 51 | 1223 | 1380 | 50.3014 | -11.2925 | -3.4154 | 1354.284 | 22.5145 | -157.7171 | -49.828 | 0 | 73.3851 | 253.3851 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.3907 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
2 | 51 | 20 | 1224 | 24 | -2.1 | 0 | 0 | 0 | 0 | 0 | 51 | 1224 | 1440 | 50.3014 | -11.2925 | -3.4154 | 1414.284 | 23.5145 | -172.7171 | -53.9832 | 0 | 73.3851 | 253.3851 | 78.3351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2536 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1225 | 1 | -2.2 | 0 | 0 | 0 | 0 | 0 | 52 | 1225 | 60 | 51.2877 | -10.9422 | -3.138 | 34.284 | 0.5191 | 172.2135 | -53.5618 | 0 | 73.9082 | 106.0918 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6726 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1226 | 2 | -2.1 | 0 | 0 | 0 | 0 | 0 | 52 | 1226 | 120 | 51.2877 | -10.9422 | -3.138 | 94.284 | 1.5191 | 157.2135 | -49.3077 | 0 | 73.9082 | 106.0918 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0464 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1227 | 3 | -1.2 | 0 | 0 | 0 | 0 | 0 | 52 | 1227 | 180 | 51.2877 | -10.9422 | -3.138 | 154.284 | 2.5191 | 142.2135 | -42.0439 | 0 | 73.9082 | 106.0918 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2011 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1228 | 4 | -0.4 | 0 | 0 | 0 | 0 | 0 | 52 | 1228 | 240 | 51.2877 | -10.9422 | -3.138 | 214.284 | 3.5191 | 127.2135 | -33.0223 | 0 | 73.9082 | 106.0918 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.9819 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1229 | 5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 52 | 1229 | 300 | 51.2877 | -10.9422 | -3.138 | 274.284 | 4.5191 | 112.2135 | -23.1114 | 0 | 73.9082 | 106.0918 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.585 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1230 | 6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 52 | 1230 | 360 | 51.2877 | -10.9422 | -3.138 | 334.284 | 5.5191 | 97.2135 | -12.8706 | 0 | 73.9082 | 106.0918 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.16462 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1231 | 7 | -1.4 | 0 | 0 | 0 | 0 | 0 | 52 | 1231 | 420 | 51.2877 | -10.9422 | -3.138 | 394.284 | 6.5191 | 82.2135 | -2.7069 | 0 | 73.9082 | 106.0918 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 159.3537 | 159.3537 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1232 | 8 | -3.4 | 0 | 1.11 | 1.11 | 1.11 | 0.56 | 52 | 1232 | 480 | 51.2877 | -10.9422 | -3.138 | 454.284 | 7.5191 | 67.2135 | 7.0127 | 7.0127 | 65.7853 | 114.2147 | 68.0261 | 0 | 0 | 0.94744 | 0.94744 | -178.5517 | 0% | 0.42843 | 0 | 0 | 163.3561 | 163.3561 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4739 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1233 | 9 | -4.6 | 13.81 | 25.47 | 39.28 | 25.47 | 12.74 | 52 | 1233 | 540 | 51.2877 | -10.9422 | -3.138 | 514.284 | 8.5191 | 52.2135 | 15.882 | 15.882 | 53.7773 | 126.2227 | 53.4587 | 30.0467 | 30.0467 | 21.74 | 51.7867 | -2.5358 | 0% | 23.4179 | 0 | 0 | 144.3333 | 144.3333 | 0% | 12.36% | 12.36% | 80% | 9.891% | 2.3164 | 11.9122 | 6 | 13.8983 | 5.1225 | 9.629% | 9.629%
2 | 52 | 21 | 1234 | 10 | -3.9 | 75 | 82.78 | 157.78 | 82.78 | 41.39 | 52 | 1234 | 600 | 51.2877 | -10.9422 | -3.138 | 574.284 | 9.5191 | 37.2135 | 23.4002 | 23.4002 | 40.3162 | 139.6838 | 39.1367 | 146.4765 | 146.4765 | 70.6571 | 217.1336 | 0.015598 | 1.56% | 98.1878 | 1.5316 | 1.0721 | 149.9969 | 149.9969 | 0.7147% | 12.12% | 12.12% | 80% | 9.695% | 9.5189 | 11.6553 | 6 | 57.1132 | 21.0501 | 38.08% | 38.08%
2 | 52 | 21 | 1235 | 11 | -2 | 141.94 | 126.31 | 268.25 | 126.31 | 63.16 | 52 | 1235 | 660 | 51.2877 | -10.9422 | -3.138 | 634.284 | 10.5191 | 22.2135 | 28.9569 | 28.9569 | 25.1013 | 154.8987 | 25.495 | 264.6242 | 264.6242 | 107.8123 | 372.4365 | 0.35715 | 35.72% | 168.4158 | 60.1501 | 42.1051 | 130.6888 | 130.6888 | 32.22% | 11.87% | 11.87% | 85% | 10.09% | 16.9914 | 10.9754 | 6 | 101.9483 | 37.5749 | 78.01% | 78.01%
2 | 52 | 21 | 1236 | 12 | -0.5 | 186.94 | 194.25 | 381.19 | 194.25 | 97.13 | 52 | 1236 | 720 | 51.2877 | -10.9422 | -3.138 | 694.284 | 11.5191 | 7.2135 | 31.9199 | 31.9199 | 8.3516 | 171.6484 | 14.6044 | 342.1386 | 342.1386 | 165.8027 | 507.9413 | 0.4837 | 48.37% | 229.6911 | 111.1015 | 77.7711 | 128.3876 | 128.3876 | 60.58% | 11.68% | 11.68% | 90% | 10.51% | 24.1478 | 10.4565 | 6 | 144.8868 | 53.4007 | 112.9% | 112.9%
2 | 52 | 21 | 1237 | 13 | 1.1 | 172.22 | 243.25 | 415.47 | 243.25 | 121.63 | 52 | 1237 | 780 | 51.2877 | -10.9422 | -3.138 | 754.284 | 12.5191 | -7.7865 | 31.8607 | 31.8607 | 9.0105 | 189.0105 | 14.8927 | 315.3041 | 315.3041 | 207.6269 | 522.931 | 0.50042 | 50.04% | 236.4694 | 118.3348 | 82.8343 | 129.599 | 129.599 | 63.92% | 11.64% | 11.64% | 90% | 10.48% | 24.7726 | 9.9203 | 6 | 148.6354 | 54.7823 | 114.7% | 114.7%
2 | 52 | 21 | 1238 | 14 | 1.4 | 197.58 | 272.97 | 470.55 | 272.97 | 136.49 | 52 | 1238 | 840 | 51.2877 | -10.9422 | -3.138 | 814.284 | 13.5191 | -22.7865 | 28.7886 | 28.7886 | 25.7143 | 205.7143 | 25.9904 | 368.7833 | 368.7833 | 232.9945 | 601.7778 | 0.54142 | 54.14% | 272.1239 | 147.3337 | 103.1336 | 130.3295 | 130.3295 | 79.13% | 11.55% | 11.55% | 90% | 10.4% | 28.299 | 9.8218 | 6 | 169.7939 | 62.5807 | 130.3% | 130.3%
2 | 52 | 21 | 1239 | 15 | -2.2 | 107.31 | 226.47 | 333.78 | 226.47 | 113.24 | 52 | 1239 | 900 | 51.2877 | -10.9422 | -3.138 | 874.284 | 14.5191 | -37.7865 | 23.1448 | 23.1448 | 40.8619 | 220.8619 | 39.6759 | 210.13 | 210.13 | 193.3042 | 403.4343 | 0.39025 | 39.02% | 182.433 | 71.1941 | 49.8359 | 115.4694 | 115.4694 | 43.16% | 11.84% | 11.84% | 85% | 10.06% | 18.3542 | 11.0458 | 6 | 110.125 | 40.5886 | 95.37% | 95.37%
2 | 52 | 21 | 1240 | 16 | -2.1 | 61.39 | 178.53 | 239.92 | 178.53 | 89.27 | 52 | 1240 | 960 | 51.2877 | -10.9422 | -3.138 | 934.284 | 15.5191 | -52.7865 | 15.5645 | 15.5645 | 54.2598 | 234.2598 | 54.012 | 134.4416 | 134.4416 | 152.3849 | 286.8265 | 0.22291 | 22.29% | 129.703 | 28.9121 | 20.2385 | 108.9373 | 108.9373 | 18.58% | 11.98% | 11.98% | 80% | 9.581% | 12.4263 | 11.0106 | 6 | 74.558 | 27.4797 | 68.44% | 68.44%
2 | 52 | 21 | 1241 | 17 | -1.8 | 25.36 | 125.56 | 150.92 | 125.56 | 62.78 | 52 | 1241 | 1020 | 51.2877 | -10.9422 | -3.138 | 994.284 | 16.5191 | -67.7865 | 6.6542 | 6.6542 | 66.222 | 246.222 | 68.5852 | 0 | 0 | 107.1722 | 107.1722 | -0.74419 | 0% | 48.4633 | 0 | 0 | 102.1454 | 102.1454 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1242 | 18 | -1.1 | 6.39 | 57.58 | 63.97 | 57.58 | 28.79 | 52 | 1242 | 1080 | 51.2877 | -10.9422 | -3.138 | 1054.284 | 17.5191 | -82.7865 | -3.0894 | 0 | 73.9082 | 253.9082 | 78.6972 | 0 | 0 | 49.1476 | 49.1476 | -2.5366 | 0% | 22.2245 | 0 | 0 | 137.3345 | 137.3345 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1243 | 19 | -0.8 | 0 | 6.94 | 6.94 | 6.94 | 3.47 | 52 | 1243 | 1140 | 51.2877 | -10.9422 | -3.138 | 1114.284 | 18.5191 | -97.7865 | -13.2627 | 0 | 73.9082 | 253.9082 | 78.6972 | 0 | 0 | 5.9237 | 5.9237 | -26.7865 | 0% | 2.6787 | 0 | 0 | 131.203 | 131.203 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1244 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 52 | 1244 | 1200 | 51.2877 | -10.9422 | -3.138 | 1174.284 | 19.5191 | -112.7865 | -23.4989 | 0 | 73.9082 | 253.9082 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.2711 | 128.2711 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1245 | 21 | 0.9 | 0 | 0 | 0 | 0 | 0 | 52 | 1245 | 1260 | 51.2877 | -10.9422 | -3.138 | 1234.284 | 20.5191 | -127.7865 | -33.3876 | 0 | 73.9082 | 253.9082 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1674 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1246 | 22 | 0.7 | 0 | 0 | 0 | 0 | 0 | 52 | 1246 | 1320 | 51.2877 | -10.9422 | -3.138 | 1294.284 | 21.5191 | -142.7865 | -42.3605 | 0 | 73.9082 | 253.9082 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6744 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1247 | 23 | 0.7 | 0 | 0 | 0 | 0 | 0 | 52 | 1247 | 1380 | 51.2877 | -10.9422 | -3.138 | 1354.284 | 22.5191 | -157.7865 | -49.5343 | 0 | 73.9082 | 253.9082 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2006 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
2 | 52 | 21 | 1248 | 24 | 0.3 | 0 | 0 | 0 | 0 | 0 | 52 | 1248 | 1440 | 51.2877 | -10.9422 | -3.138 | 1414.284 | 23.5191 | -172.7865 | -53.6466 | 0 | 73.9082 | 253.9082 | 78.6972 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3364 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1249 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 53 | 1249 | 60 | 52.274 | -10.5887 | -2.8519 | 34.284 | 0.52387 | 172.142 | -53.2017 | 0 | 74.4353 | 105.5647 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8727 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1250 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 53 | 1250 | 120 | 52.274 | -10.5887 | -2.8519 | 94.284 | 1.5239 | 157.142 | -48.9561 | 0 | 74.4353 | 105.5647 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6692 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1251 | 3 | -0.2 | 0 | 0 | 0 | 0 | 0 | 53 | 1251 | 180 | 52.274 | -10.5887 | -2.8519 | 154.284 | 2.5239 | 142.142 | -41.7124 | 0 | 74.4353 | 105.5647 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5326 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1252 | 4 | -0.7 | 0 | 0 | 0 | 0 | 0 | 53 | 1252 | 240 | 52.274 | -10.5887 | -2.8519 | 214.284 | 3.5239 | 127.142 | -32.7079 | 0 | 74.4353 | 105.5647 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2946 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1253 | 5 | -1 | 0 | 0 | 0 | 0 | 0 | 53 | 1253 | 300 | 52.274 | -10.5887 | -2.8519 | 274.284 | 4.5239 | 112.142 | -22.8067 | 0 | 74.4353 | 105.5647 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0976 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1254 | 6 | -1.1 | 0 | 0 | 0 | 0 | 0 | 53 | 1254 | 360 | 52.274 | -10.5887 | -2.8519 | 334.284 | 5.5239 | 97.142 | -12.568 | 0 | 74.4353 | 105.5647 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0257 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1255 | 7 | -1.2 | 0 | 0 | 0 | 0 | 0 | 53 | 1255 | 420 | 52.274 | -10.5887 | -2.8519 | 394.284 | 6.5239 | 82.142 | -2.3997 | 0 | 74.4353 | 105.5647 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.7227 | 137.7227 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1256 | 8 | 4.2 | 0 | 0 | 0 | 0 | 0 | 53 | 1256 | 480 | 52.274 | -10.5887 | -2.8519 | 454.284 | 7.5239 | 67.142 | 7.3301 | 7.3301 | 65.9574 | 114.0426 | 67.917 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.3519 | 149.3519 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1257 | 9 | 4.5 | 9.64 | 22.5 | 32.14 | 22.5 | 11.25 | 53 | 1257 | 540 | 52.274 | -10.5887 | -2.8519 | 514.284 | 8.5239 | 52.142 | 16.2137 | 16.2137 | 53.9239 | 126.0761 | 53.3258 | 20.6203 | 20.6203 | 19.205 | 39.8253 | -2.9746 | 0% | 18.009 | 0 | 0 | 131.4234 | 131.4234 | 0% | 12% | 12% | 80% | 9.6% | 1.7289 | 8.8405 | 6 | 10.3732 | 3.8232 | 7.893% | 7.893%
2 | 53 | 22 | 1258 | 10 | 3 | 9.72 | 73.81 | 83.53 | 73.81 | 36.91 | 53 | 1258 | 600 | 52.274 | -10.5887 | -2.8519 | 574.284 | 9.5239 | 37.142 | 23.7473 | 23.7473 | 40.4219 | 139.5781 | 38.9687 | 18.7662 | 18.7662 | 63.0008 | 81.7669 | -1.0808 | 0% | 36.975 | 0 | 0 | 130.3396 | 130.3396 | 0% | 12.02% | 12.02% | 80% | 9.619% | 3.5566 | 9.3069 | 6 | 21.3394 | 7.865 | 16.37% | 16.37%
2 | 53 | 22 | 1259 | 11 | 3.9 | 7.86 | 100.19 | 108.05 | 100.19 | 50.1 | 53 | 1259 | 660 | 52.274 | -10.5887 | -2.8519 | 634.284 | 10.5239 | 22.142 | 29.3154 | 29.3154 | 25.1442 | 154.8558 | 25.2654 | 14.5177 | 14.5177 | 85.5175 | 100.0352 | -0.71477 | 0% | 45.2359 | 0 | 0 | 129.905 | 129.905 | 0% | 11.97% | 11.97% | 80% | 9.577% | 4.3325 | 9.0252 | 6 | 25.9947 | 9.5808 | 20.01% | 20.01%
2 | 53 | 22 | 1260 | 12 | 5.4 | 9.25 | 121.19 | 130.44 | 121.19 | 60.6 | 53 | 1260 | 720 | 52.274 | -10.5887 | -2.8519 | 694.284 | 11.5239 | 7.142 | 32.2787 | 32.2787 | 8.3112 | 171.6888 | 14.2633 | 16.7869 | 16.7869 | 103.4421 | 120.2291 | -0.42965 | 0% | 54.3676 | 0 | 0 | 128.8842 | 128.8842 | 0% | 11.9% | 11.9% | 80% | 9.518% | 5.1749 | 8.5682 | 6 | 31.0492 | 11.4437 | 24.09% | 24.09%
2 | 53 | 22 | 1261 | 13 | 5.9 | 12.22 | 174.92 | 187.14 | 174.92 | 87.46 | 53 | 1261 | 780 | 52.274 | -10.5887 | -2.8519 | 754.284 | 12.5239 | -7.858 | 32.2043 | 32.2043 | 9.1387 | 189.1387 | 14.6313 | 22.1859 | 22.1859 | 149.3036 | 171.4894 | -0.053917 | 0% | 77.5475 | 0 | 0 | 131.6576 | 131.6576 | 0% | 11.84% | 11.84% | 80% | 9.472% | 7.3449 | 8.4194 | 6 | 44.0696 | 16.2427 | 33.47% | 33.47%
2 | 53 | 22 | 1262 | 14 | 6.6 | 13.89 | 179.08 | 192.97 | 179.08 | 89.54 | 53 | 1262 | 840 | 52.274 | -10.5887 | -2.8519 | 814.284 | 13.5239 | -22.858 | 29.104 | 29.104 | 25.9134 | 205.9134 | 25.889 | 25.691 | 25.691 | 152.8543 | 178.5453 | -0.010661 | 0% | 80.7382 | 0 | 0 | 132.4543 | 132.4543 | 0% | 11.81% | 11.81% | 80% | 9.448% | 7.6282 | 8.2139 | 6 | 45.7689 | 16.869 | 34.55% | 34.55%
2 | 53 | 22 | 1263 | 15 | 7.6 | 22.58 | 176.94 | 199.52 | 176.94 | 88.47 | 53 | 1263 | 900 | 52.274 | -10.5887 | -2.8519 | 874.284 | 14.5239 | -37.858 | 23.4271 | 23.4271 | 41.1059 | 221.1059 | 39.6448 | 43.7317 | 43.7317 | 151.0277 | 194.7594 | 0.06935 | 6.935% | 88.0702 | 6.1076 | 4.2753 | 111.9723 | 111.9723 | 3.818% | 11.76% | 11.76% | 80% | 9.412% | 8.289 | 7.9264 | 6 | 49.734 | 18.3304 | 44.42% | 44.42%
2 | 53 | 22 | 1264 | 16 | 7.7 | 28.61 | 144.25 | 172.86 | 144.25 | 72.13 | 53 | 1264 | 960 | 52.274 | -10.5887 | -2.8519 | 934.284 | 15.5239 | -52.858 | 15.8159 | 15.8159 | 54.528 | 234.528 | 54.0185 | 61.6739 | 61.6739 | 123.1251 | 184.799 | 0.031033 | 3.103% | 83.5661 | 2.5933 | 1.8153 | 109.9821 | 109.9821 | 1.651% | 11.77% | 11.77% | 80% | 9.415% | 7.8674 | 7.8981 | 6 | 47.2042 | 17.398 | 42.92% | 42.92%
2 | 53 | 22 | 1265 | 17 | 7.1 | 39.72 | 79.36 | 119.08 | 79.36 | 39.68 | 53 | 1265 | 1020 | 52.274 | -10.5887 | -2.8519 | 994.284 | 16.5239 | -67.858 | 6.8813 | 6.8813 | 66.5038 | 246.5038 | 68.6167 | 0 | 0 | 67.738 | 67.738 | -1.3258 | 0% | 30.6311 | 0 | 0 | 147.6343 | 147.6343 | 0% | 11.87% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1266 | 18 | 6.2 | 14.53 | 23.06 | 37.59 | 23.06 | 11.53 | 53 | 1266 | 1080 | 52.274 | -10.5887 | -2.8519 | 1054.284 | 17.5239 | -82.858 | -2.8781 | 0 | 74.4353 | 254.4353 | 79.0627 | 0 | 0 | 19.6829 | 19.6829 | -6.6343 | 0% | 8.9006 | 0 | 0 | 140.5296 | 140.5296 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1267 | 19 | 4.2 | 0 | 2.69 | 2.69 | 2.69 | 1.35 | 53 | 1267 | 1140 | 52.274 | -10.5887 | -2.8519 | 1114.284 | 18.5239 | -97.858 | -13.0581 | 0 | 74.4353 | 254.4353 | 79.0627 | 0 | 0 | 2.2961 | 2.2961 | -65.0505 | 0% | 1.0383 | 0 | 0 | 132.9192 | 132.9192 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1268 | 20 | 3.4 | 0 | 0 | 0 | 0 | 0 | 53 | 1268 | 1200 | 52.274 | -10.5887 | -2.8519 | 1174.284 | 19.5239 | -112.858 | -23.2906 | 0 | 74.4353 | 254.4353 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.3982 | 128.3982 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1269 | 21 | 3.3 | 0 | 0 | 0 | 0 | 0 | 53 | 1269 | 1260 | 52.274 | -10.5887 | -2.8519 | 1234.284 | 20.5239 | -127.858 | -33.1636 | 0 | 74.4353 | 254.4353 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5188 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1270 | 22 | 2.8 | 0 | 0 | 0 | 0 | 0 | 53 | 1270 | 1320 | 52.274 | -10.5887 | -2.8519 | 1294.284 | 21.5239 | -142.858 | -42.1067 | 0 | 74.4353 | 254.4353 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.978 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1271 | 23 | 2.2 | 0 | 0 | 0 | 0 | 0 | 53 | 1271 | 1380 | 52.274 | -10.5887 | -2.8519 | 1354.284 | 22.5239 | -157.858 | -49.2378 | 0 | 74.4353 | 254.4353 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6889 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
2 | 53 | 22 | 1272 | 24 | 2.1 | 0 | 0 | 0 | 0 | 0 | 53 | 1272 | 1440 | 52.274 | -10.5887 | -2.8519 | 1414.284 | 23.5239 | -172.858 | -53.3069 | 0 | 74.4353 | 254.4353 | 79.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6378 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1273 | 1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 54 | 1273 | 60 | 53.2603 | -10.2321 | -2.5575 | 34.284 | 0.52877 | 172.0684 | -52.8382 | 0 | 74.9662 | 105.0338 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9687 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1274 | 2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 54 | 1274 | 120 | 53.2603 | -10.2321 | -2.5575 | 94.284 | 1.5288 | 157.0684 | -48.6007 | 0 | 74.9662 | 105.0338 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0109 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1275 | 3 | 3.4 | 0 | 0 | 0 | 0 | 0 | 54 | 1275 | 180 | 53.2603 | -10.2321 | -2.5575 | 154.284 | 2.5288 | 142.0684 | -41.3768 | 0 | 74.9662 | 105.0338 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4247 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1276 | 4 | 3.9 | 0 | 0 | 0 | 0 | 0 | 54 | 1276 | 240 | 53.2603 | -10.2321 | -2.5575 | 214.284 | 3.5288 | 127.0684 | -32.3895 | 0 | 74.9662 | 105.0338 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6627 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1277 | 5 | 3.9 | 0 | 0 | 0 | 0 | 0 | 54 | 1277 | 300 | 53.2603 | -10.2321 | -2.5575 | 274.284 | 4.5288 | 112.0684 | -22.498 | 0 | 74.9662 | 105.0338 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0031 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1278 | 6 | 3.8 | 0 | 0 | 0 | 0 | 0 | 54 | 1278 | 360 | 53.2603 | -10.2321 | -2.5575 | 334.284 | 5.5288 | 97.0684 | -12.2616 | 0 | 74.9662 | 105.0338 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.2908 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1279 | 7 | 3.8 | 0 | 0 | 0 | 0 | 0 | 54 | 1279 | 420 | 53.2603 | -10.2321 | -2.5575 | 394.284 | 6.5288 | 82.0684 | -2.0888 | 0 | 74.9662 | 105.0338 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.9332 | 149.9332 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1280 | 8 | 4.6 | 0 | 1.19 | 1.19 | 1.19 | 0.6 | 54 | 1280 | 480 | 53.2603 | -10.2321 | -2.5575 | 454.284 | 7.5288 | 67.0684 | 7.6512 | 7.6512 | 66.1299 | 113.8701 | 67.8063 | 0 | 0 | 1.0157 | 1.0157 | -147.1114 | 0% | 0.45931 | 0 | 0 | 156.3214 | 156.3214 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1281 | 9 | 5.3 | 0.56 | 29.53 | 30.09 | 29.53 | 14.77 | 54 | 1281 | 540 | 53.2603 | -10.2321 | -2.5575 | 514.284 | 8.5288 | 52.0684 | 16.5491 | 16.5491 | 54.0709 | 125.9291 | 53.1916 | 1.1779 | 1.1779 | 25.2054 | 26.3834 | -4.8268 | 0% | 11.9306 | 0 | 0 | 138.8165 | 138.8165 | 0% | 11.98% | 11.98% | 80% | 9.582% | 1.1432 | 8.5982 | 6 | 6.8591 | 2.528 | 4.941% | 4.941%
2 | 54 | 23 | 1282 | 10 | 5.2 | 2.31 | 65 | 67.31 | 65 | 32.5 | 54 | 1282 | 600 | 53.2603 | -10.2321 | -2.5575 | 574.284 | 9.5288 | 37.0684 | 24.0981 | 24.0981 | 40.5276 | 139.4724 | 38.8001 | 4.4092 | 4.4092 | 55.481 | 59.8902 | -1.6805 | 0% | 27.0823 | 0 | 0 | 140.5074 | 140.5074 | 0% | 11.95% | 11.95% | 80% | 9.564% | 2.59 | 8.6282 | 6 | 15.5402 | 5.7276 | 11.06% | 11.06%
2 | 54 | 23 | 1283 | 11 | 5.3 | 65.75 | 126.86 | 192.61 | 126.86 | 63.43 | 54 | 1283 | 660 | 53.2603 | -10.2321 | -2.5575 | 634.284 | 10.5288 | 22.0684 | 29.6774 | 29.6774 | 25.1861 | 154.8139 | 25.0354 | 120.3205 | 120.3205 | 108.2818 | 228.6023 | 0.15414 | 15.41% | 103.374 | 15.9338 | 11.1537 | 143.5937 | 143.5937 | 7.768% | 11.81% | 11.81% | 80% | 9.451% | 9.7701 | 8.5982 | 6 | 58.6204 | 21.6056 | 40.82% | 40.82%
2 | 54 | 23 | 1284 | 12 | 6.1 | 119.64 | 180.83 | 300.47 | 180.83 | 90.42 | 54 | 1284 | 720 | 53.2603 | -10.2321 | -2.5575 | 694.284 | 11.5288 | 7.0684 | 32.6407 | 32.6407 | 8.2683 | 171.7317 | 13.9193 | 215.3012 | 215.3012 | 154.3481 | 369.6493 | 0.40728 | 40.73% | 167.1554 | 68.0797 | 47.6558 | 123.0784 | 123.0784 | 38.72% | 11.68% | 11.68% | 85% | 9.929% | 16.5966 | 8.3603 | 6 | 99.5797 | 36.7019 | 80.91% | 80.91%
2 | 54 | 23 | 1285 | 13 | 6.7 | 186.58 | 264.64 | 451.22 | 264.64 | 132.32 | 54 | 1285 | 780 | 53.2603 | -10.2321 | -2.5575 | 754.284 | 12.5288 | -7.9316 | 32.5506 | 32.5506 | 9.2709 | 189.2709 | 14.3728 | 335.9211 | 335.9211 | 225.8844 | 561.8055 | 0.54552 | 54.55% | 254.0484 | 138.5883 | 97.0118 | 129.2527 | 129.2527 | 75.06% | 11.53% | 11.53% | 90% | 10.37% | 26.354 | 8.1849 | 6 | 158.1241 | 58.2795 | 122.3% | 122.3%
2 | 54 | 23 | 1286 | 14 | 8.2 | 64.53 | 226.58 | 291.11 | 226.58 | 113.29 | 54 | 1286 | 840 | 53.2603 | -10.2321 | -2.5575 | 814.284 | 13.5288 | -22.9316 | 29.4215 | 29.4215 | 26.1172 | 206.1172 | 25.7925 | 118.277 | 118.277 | 193.3981 | 311.6752 | 0.34948 | 34.95% | 140.9395 | 49.2557 | 34.479 | 123.2583 | 123.2583 | 27.97% | 11.67% | 11.67% | 85% | 9.919% | 13.9792 | 7.7573 | 6 | 83.8752 | 30.9138 | 68.05% | 68.05%
2 | 54 | 23 | 1287 | 15 | 8.9 | 102.31 | 236.11 | 338.42 | 236.11 | 118.06 | 54 | 1287 | 900 | 53.2603 | -10.2321 | -2.5575 | 874.284 | 14.5288 | -37.9316 | 23.7107 | 23.7107 | 41.3546 | 221.3546 | 39.6178 | 195.9894 | 195.9894 | 201.5325 | 397.5219 | 0.45178 | 45.18% | 179.7594 | 81.2122 | 56.8485 | 123.784 | 123.784 | 45.93% | 11.6% | 11.6% | 85% | 9.858% | 17.7208 | 7.5632 | 6 | 106.3247 | 39.1879 | 85.9% | 85.9%
2 | 54 | 23 | 1288 | 16 | 10 | 55 | 164.17 | 219.17 | 164.17 | 82.09 | 54 | 1288 | 960 | 53.2603 | -10.2321 | -2.5575 | 934.284 | 15.5288 | -52.9316 | 16.0682 | 16.0682 | 54.8006 | 234.8006 | 54.0284 | 116.7205 | 116.7205 | 140.1279 | 256.8484 | 0.26891 | 26.89% | 116.1469 | 31.2328 | 21.863 | 118.3531 | 118.3531 | 18.47% | 11.65% | 11.65% | 80% | 9.321% | 10.8256 | 7.265 | 6 | 64.9534 | 23.9398 | 54.88% | 54.88%
2 | 54 | 23 | 1289 | 17 | 10.3 | 10.75 | 69.08 | 79.83 | 69.08 | 34.54 | 54 | 1289 | 1020 | 53.2603 | -10.2321 | -2.5575 | 994.284 | 16.5288 | -67.9316 | 7.1092 | 7.1092 | 66.7895 | 246.7895 | 68.651 | 0 | 0 | 58.9635 | 58.9635 | -1.515 | 0% | 26.6633 | 0 | 0 | 151.6787 | 151.6787 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1290 | 18 | 10.4 | 1.11 | 28.89 | 30 | 28.89 | 14.45 | 54 | 1290 | 1080 | 53.2603 | -10.2321 | -2.5575 | 1054.284 | 17.5288 | -82.9316 | -2.666 | 0 | 74.9662 | 254.9662 | 79.4312 | 0 | 0 | 24.6592 | 24.6592 | -4.7317 | 0% | 11.1509 | 0 | 0 | 146.5825 | 146.5825 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1291 | 19 | 8.3 | 0 | 3.61 | 3.61 | 3.61 | 1.81 | 54 | 1291 | 1140 | 53.2603 | -10.2321 | -2.5575 | 1114.284 | 18.5288 | -97.9316 | -12.8525 | 0 | 74.9662 | 254.9662 | 79.4312 | 0 | 0 | 3.0813 | 3.0813 | -45.0939 | 0% | 1.3934 | 0 | 0 | 139.1051 | 139.1051 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1292 | 20 | 5.8 | 0 | 0 | 0 | 0 | 0 | 54 | 1292 | 1200 | 53.2603 | -10.2321 | -2.5575 | 1174.284 | 19.5288 | -112.9316 | -23.081 | 0 | 74.9662 | 254.9662 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.8415 | 130.8415 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1293 | 21 | 4.8 | 0 | 0 | 0 | 0 | 0 | 54 | 1293 | 1260 | 53.2603 | -10.2321 | -2.5575 | 1234.284 | 20.5288 | -127.9316 | -32.9377 | 0 | 74.9662 | 254.9662 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.73 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1294 | 22 | 3.9 | 0 | 0 | 0 | 0 | 0 | 54 | 1294 | 1320 | 53.2603 | -10.2321 | -2.5575 | 1294.284 | 21.5288 | -142.9316 | -41.8505 | 0 | 74.9662 | 254.9662 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0698 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1295 | 23 | 4 | 0 | 0 | 0 | 0 | 0 | 54 | 1295 | 1380 | 53.2603 | -10.2321 | -2.5575 | 1354.284 | 22.5288 | -157.9316 | -48.9385 | 0 | 74.9662 | 254.9662 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.636 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
2 | 54 | 23 | 1296 | 24 | 3.9 | 0 | 0 | 0 | 0 | 0 | 54 | 1296 | 1440 | 53.2603 | -10.2321 | -2.5575 | 1414.284 | 23.5288 | -172.9316 | -52.9641 | 0 | 74.9662 | 254.9662 | 79.4312 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5069 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1297 | 1 | 3.3 | 0 | 0 | 0 | 0 | 0 | 55 | 1297 | 60 | 54.2466 | -9.8726 | -2.2551 | 34.284 | 0.53381 | 171.9928 | -52.4715 | 0 | 75.5008 | 104.4992 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7575 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1298 | 2 | 2.6 | 0 | 0 | 0 | 0 | 0 | 55 | 1298 | 120 | 54.2466 | -9.8726 | -2.2551 | 94.284 | 1.5338 | 156.9928 | -48.2416 | 0 | 75.5008 | 104.4992 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2438 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1299 | 3 | 1.9 | 0 | 0 | 0 | 0 | 0 | 55 | 1299 | 180 | 54.2466 | -9.8726 | -2.2551 | 154.284 | 2.5338 | 141.9928 | -41.0372 | 0 | 75.5008 | 104.4992 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7301 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1300 | 4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 55 | 1300 | 240 | 54.2466 | -9.8726 | -2.2551 | 214.284 | 3.5338 | 126.9928 | -32.067 | 0 | 75.5008 | 104.4992 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0349 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1301 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 55 | 1301 | 300 | 54.2466 | -9.8726 | -2.2551 | 274.284 | 4.5338 | 111.9928 | -22.1854 | 0 | 75.5008 | 104.4992 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.8218 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1302 | 6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 55 | 1302 | 360 | 54.2466 | -9.8726 | -2.2551 | 334.284 | 5.5338 | 96.9928 | -11.9514 | 0 | 75.5008 | 104.4992 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.8803 | 3.8803 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1303 | 7 | 0.9 | 0 | 0 | 0 | 0 | 0 | 55 | 1303 | 420 | 54.2466 | -9.8726 | -2.2551 | 394.284 | 6.5338 | 81.9928 | -1.7741 | 0 | 75.5008 | 104.4992 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 168.7435 | 168.7435 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1304 | 8 | 0.4 | 0 | 1.86 | 1.86 | 1.86 | 0.93 | 55 | 1304 | 480 | 54.2466 | -9.8726 | -2.2551 | 454.284 | 7.5338 | 66.9928 | 7.9759 | 7.9759 | 66.3029 | 113.6971 | 67.6939 | 0 | 0 | 1.5876 | 1.5876 | -100.2731 | 0% | 0.71792 | 0 | 0 | 176.19 | 176.19 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1305 | 9 | 0.6 | 28.81 | 37.97 | 66.78 | 37.97 | 18.99 | 55 | 1305 | 540 | 54.2466 | -9.8726 | -2.2551 | 514.284 | 8.5338 | 51.9928 | 16.8881 | 16.8881 | 54.2183 | 125.7817 | 53.0563 | 59.6059 | 59.6059 | 32.4094 | 92.0153 | -0.93461 | 0% | 41.6093 | 0 | 0 | 161.2418 | 161.2418 | 0% | 12.11% | 12.11% | 80% | 9.686% | 4.0303 | 10.0859 | 6 | 24.1815 | 8.9125 | 15% | 15%
2 | 55 | 24 | 1306 | 10 | 1.9 | 115.08 | 75.56 | 190.64 | 75.56 | 37.78 | 55 | 1306 | 600 | 54.2466 | -9.8726 | -2.2551 | 574.284 | 9.5338 | 36.9928 | 24.4524 | 24.4524 | 40.6332 | 139.3668 | 38.6308 | 217.1798 | 217.1798 | 64.4945 | 281.6743 | 0.24736 | 24.74% | 127.3731 | 31.5073 | 22.0551 | 166.7949 | 166.7949 | 13.22% | 11.87% | 11.87% | 80% | 9.494% | 12.0933 | 9.659 | 6 | 72.5598 | 26.7433 | 43.5% | 43.5%
2 | 55 | 24 | 1307 | 11 | 3.2 | 181.67 | 120.19 | 301.86 | 120.19 | 60.1 | 55 | 1307 | 660 | 54.2466 | -9.8726 | -2.2551 | 634.284 | 10.5338 | 21.9928 | 30.0428 | 30.0428 | 25.2269 | 154.7731 | 24.805 | 329.3919 | 329.3919 | 102.5886 | 431.9805 | 0.44837 | 44.84% | 195.3416 | 87.5853 | 61.3097 | 144.386 | 144.386 | 42.46% | 11.69% | 11.69% | 85% | 9.938% | 19.4135 | 9.2438 | 6 | 116.4811 | 42.9313 | 80.67% | 80.67%
2 | 55 | 24 | 1308 | 12 | 5 | 160.08 | 170.64 | 330.72 | 170.64 | 85.32 | 55 | 1308 | 720 | 54.2466 | -9.8726 | -2.2551 | 694.284 | 11.5338 | 6.9928 | 33.0059 | 33.0059 | 8.2228 | 171.7772 | 13.5728 | 285.666 | 285.666 | 145.6504 | 431.3163 | 0.4579 | 45.79% | 195.0412 | 89.3087 | 62.5161 | 135.9983 | 135.9983 | 45.97% | 11.66% | 11.66% | 85% | 9.908% | 19.3242 | 8.6885 | 6 | 115.9451 | 42.7337 | 85.25% | 85.25%
2 | 55 | 24 | 1309 | 13 | 5.8 | 148.06 | 214.25 | 362.31 | 214.25 | 107.13 | 55 | 1309 | 780 | 54.2466 | -9.8726 | -2.2551 | 754.284 | 12.5338 | -8.0072 | 32.8994 | 32.8994 | 9.4071 | 189.4071 | 14.1177 | 264.3542 | 264.3542 | 182.8738 | 447.228 | 0.4745 | 47.45% | 202.2365 | 95.9607 | 67.1725 | 135.6355 | 135.6355 | 49.52% | 11.63% | 11.63% | 85% | 9.883% | 19.9878 | 8.449 | 6 | 119.9269 | 44.2013 | 88.42% | 88.42%
2 | 55 | 24 | 1310 | 14 | 7.1 | 165.08 | 245.08 | 410.16 | 245.08 | 122.54 | 55 | 1310 | 840 | 54.2466 | -9.8726 | -2.2551 | 814.284 | 13.5338 | -23.0072 | 29.7407 | 29.7407 | 26.3258 | 206.3258 | 25.7011 | 299.85 | 299.85 | 209.1889 | 509.0388 | 0.52059 | 52.06% | 230.1874 | 119.8338 | 83.8837 | 137.5311 | 137.5311 | 60.99% | 11.56% | 11.56% | 90% | 10.4% | 23.9455 | 8.0693 | 6 | 143.6727 | 52.9532 | 104.5% | 104.5%
2 | 55 | 24 | 1311 | 15 | 8.3 | 152.42 | 212.86 | 365.28 | 212.86 | 106.43 | 55 | 1311 | 900 | 54.2466 | -9.8726 | -2.2551 | 874.284 | 14.5338 | -38.0072 | 23.9955 | 23.9955 | 41.6079 | 221.6079 | 39.5948 | 288.8138 | 288.8138 | 181.6874 | 470.5012 | 0.50341 | 50.34% | 212.7606 | 107.1066 | 74.9746 | 133.9678 | 133.9678 | 55.96% | 11.56% | 11.56% | 85% | 9.829% | 20.9132 | 7.7294 | 6 | 125.4789 | 46.2476 | 93.66% | 93.66%
2 | 55 | 24 | 1312 | 16 | 8.7 | 136.31 | 179.08 | 315.39 | 179.08 | 89.54 | 55 | 1312 | 960 | 54.2466 | -9.8726 | -2.2551 | 934.284 | 15.5338 | -53.0072 | 16.3214 | 16.3214 | 55.0774 | 235.0774 | 54.0415 | 284.8173 | 284.8173 | 152.8543 | 437.6716 | 0.48302 | 48.3% | 197.9151 | 95.5967 | 66.9177 | 130.0794 | 130.0794 | 51.44% | 11.58% | 11.58% | 85% | 9.841% | 19.4761 | 7.6183 | 6 | 116.8563 | 43.0696 | 89.83% | 89.83%
2 | 55 | 24 | 1313 | 17 | 9.7 | 76.31 | 123.42 | 199.73 | 123.42 | 61.71 | 55 | 1313 | 1020 | 54.2466 | -9.8726 | -2.2551 | 994.284 | 16.5338 | -68.0072 | 7.3379 | 7.3379 | 67.0791 | 247.0791 | 68.688 | 0 | 0 | 105.3456 | 105.3456 | -0.50729 | 0% | 47.6373 | 0 | 0 | 123.1214 | 123.1214 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1314 | 18 | 9.2 | 26.94 | 59.53 | 86.47 | 59.53 | 29.77 | 55 | 1314 | 1080 | 54.2466 | -9.8726 | -2.2551 | 1054.284 | 17.5338 | -83.0072 | -2.4532 | 0 | 75.5008 | 255.5008 | 79.8029 | 0 | 0 | 50.812 | 50.812 | -1.9377 | 0% | 22.9772 | 0 | 0 | 154.5123 | 154.5123 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1315 | 19 | 7.4 | 0 | 8.81 | 8.81 | 8.81 | 4.41 | 55 | 1315 | 1140 | 54.2466 | -9.8726 | -2.2551 | 1114.284 | 18.5338 | -98.0072 | -12.6459 | 0 | 75.5008 | 255.5008 | 79.8029 | 0 | 0 | 7.5198 | 7.5198 | -18.2861 | 0% | 3.4005 | 0 | 0 | 142.6393 | 142.6393 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1316 | 20 | 6.7 | 0 | 0 | 0 | 0 | 0 | 55 | 1316 | 1200 | 54.2466 | -9.8726 | -2.2551 | 1174.284 | 19.5338 | -113.0072 | -22.87 | 0 | 75.5008 | 255.5008 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.6518 | 134.6518 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1317 | 21 | 5.9 | 0 | 0 | 0 | 0 | 0 | 55 | 1317 | 1260 | 54.2466 | -9.8726 | -2.2551 | 1234.284 | 20.5338 | -128.0072 | -32.71 | 0 | 75.5008 | 255.5008 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1049 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1318 | 22 | 2.7 | 0 | 0 | 0 | 0 | 0 | 55 | 1318 | 1320 | 54.2466 | -9.8726 | -2.2551 | 1294.284 | 21.5338 | -143.0072 | -41.592 | 0 | 75.5008 | 255.5008 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4132 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1319 | 23 | 1.1 | 0 | 0 | 0 | 0 | 0 | 55 | 1319 | 1380 | 54.2466 | -9.8726 | -2.2551 | 1354.284 | 22.5338 | -158.0072 | -48.6365 | 0 | 75.5008 | 255.5008 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2711 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
2 | 55 | 24 | 1320 | 24 | 0.7 | 0 | 0 | 0 | 0 | 0 | 55 | 1320 | 1440 | 54.2466 | -9.8726 | -2.2551 | 1414.284 | 23.5338 | -173.0072 | -52.6184 | 0 | 75.5008 | 255.5008 | 79.8029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3003 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1321 | 1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 56 | 1321 | 60 | 55.2329 | -9.5101 | -1.945 | 34.284 | 0.53898 | 171.9152 | -52.1015 | 0 | 76.039 | 103.961 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5924 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1322 | 2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 56 | 1322 | 120 | 55.2329 | -9.5101 | -1.945 | 94.284 | 1.539 | 156.9152 | -47.879 | 0 | 76.039 | 103.961 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6699 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1323 | 3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 56 | 1323 | 180 | 55.2329 | -9.5101 | -1.945 | 154.284 | 2.539 | 141.9152 | -40.6938 | 0 | 76.039 | 103.961 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5094 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1324 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1324 | 240 | 55.2329 | -9.5101 | -1.945 | 214.284 | 3.539 | 126.9152 | -31.7406 | 0 | 76.039 | 103.961 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8142 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1325 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1325 | 300 | 55.2329 | -9.5101 | -1.945 | 274.284 | 4.539 | 111.9152 | -21.8691 | 0 | 76.039 | 103.961 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.2319 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1326 | 6 | -0.4 | 0 | 0 | 0 | 0 | 0 | 56 | 1326 | 360 | 55.2329 | -9.5101 | -1.945 | 334.284 | 5.539 | 96.9152 | -11.6375 | 0 | 76.039 | 103.961 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.0301 | 4.0301 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1327 | 7 | -0.7 | 0 | 0 | 0 | 0 | 0 | 56 | 1327 | 420 | 55.2329 | -9.5101 | -1.945 | 394.284 | 6.539 | 81.9152 | -1.456 | 0 | 76.039 | 103.961 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 170.4129 | 170.4129 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1328 | 8 | -0.6 | 0.08 | 1.47 | 1.55 | 1.47 | 0.74 | 56 | 1328 | 480 | 55.2329 | -9.5101 | -1.945 | 454.284 | 7.539 | 66.9152 | 8.3041 | 8.3041 | 66.4764 | 113.5236 | 67.5801 | 0 | 0 | 1.2547 | 1.2547 | -129.0583 | 0% | 0.56739 | 0 | 0 | 179.4712 | 179.4712 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1329 | 9 | -1 | 41.03 | 29.36 | 70.39 | 29.36 | 14.68 | 56 | 1329 | 540 | 55.2329 | -9.5101 | -1.945 | 514.284 | 8.539 | 51.9152 | 17.2304 | 17.2304 | 54.3662 | 125.6338 | 52.92 | 83.5142 | 83.5142 | 25.0603 | 108.5746 | -0.70587 | 0% | 49.0974 | 0 | 0 | 164.5272 | 164.5272 | 0% | 12.15% | 12.15% | 80% | 9.72% | 4.7725 | 10.6277 | 6 | 28.635 | 10.554 | 17.4% | 17.4%
2 | 56 | 25 | 1330 | 10 | 0.8 | 148.89 | 61.19 | 210.08 | 61.19 | 30.6 | 56 | 1330 | 600 | 55.2329 | -9.5101 | -1.945 | 574.284 | 9.539 | 36.9152 | 24.8101 | 24.8101 | 40.7388 | 139.2612 | 38.4611 | 277.8405 | 277.8405 | 52.2289 | 330.0695 | 0.32081 | 32.08% | 149.2574 | 47.8831 | 33.5182 | 150.6003 | 150.6003 | 22.26% | 11.85% | 11.85% | 85% | 10.07% | 15.0317 | 10.0195 | 6 | 90.1904 | 33.2413 | 59.89% | 59.89%
2 | 56 | 25 | 1331 | 11 | 3.5 | 233.33 | 93.06 | 326.39 | 93.06 | 46.53 | 56 | 1331 | 660 | 55.2329 | -9.5101 | -1.945 | 634.284 | 10.539 | 21.9152 | 30.4116 | 30.4116 | 25.2667 | 154.7333 | 24.5747 | 419.1843 | 419.1843 | 79.4317 | 498.6159 | 0.49736 | 49.74% | 225.4741 | 112.1407 | 78.4985 | 150.7331 | 150.7331 | 52.08% | 11.63% | 11.63% | 85% | 9.882% | 22.2806 | 9.1497 | 6 | 133.6838 | 49.2716 | 88.69% | 88.69%
2 | 56 | 25 | 1332 | 12 | 5.1 | 286.31 | 128.53 | 414.84 | 128.53 | 64.27 | 56 | 1332 | 720 | 55.2329 | -9.5101 | -1.945 | 694.284 | 11.539 | 6.9152 | 33.3741 | 33.3741 | 8.1749 | 171.8251 | 13.2238 | 506.6653 | 506.6653 | 109.7072 | 616.3725 | 0.5622 | 56.22% | 278.7236 | 156.698 | 109.6886 | 143.4928 | 143.4928 | 76.44% | 11.5% | 11.5% | 90% | 10.35% | 28.8541 | 8.6583 | 6 | 173.1248 | 63.8083 | 120.7% | 120.7%
2 | 56 | 25 | 1333 | 13 | 7.2 | 299.17 | 148.14 | 447.31 | 148.14 | 74.07 | 56 | 1333 | 780 | 55.2329 | -9.5101 | -1.945 | 754.284 | 12.539 | -8.0848 | 33.2507 | 33.2507 | 9.5472 | 189.5472 | 13.8663 | 529.7273 | 529.7273 | 126.4454 | 656.1727 | 0.5845 | 58.45% | 296.7213 | 173.4345 | 121.4041 | 144.6203 | 144.6203 | 83.95% | 11.45% | 11.45% | 90% | 10.31% | 30.5858 | 8.0406 | 6 | 183.5149 | 67.6378 | 126.9% | 126.9%
2 | 56 | 25 | 1334 | 14 | 9.4 | 306.94 | 130.83 | 437.77 | 130.83 | 65.42 | 56 | 1334 | 840 | 55.2329 | -9.5101 | -1.945 | 814.284 | 13.539 | -23.0848 | 30.0618 | 30.0618 | 26.5389 | 206.5389 | 25.615 | 552.5163 | 552.5163 | 111.6704 | 664.1866 | 0.59496 | 59.5% | 300.3452 | 178.6937 | 125.0856 | 145.1115 | 145.1115 | 86.2% | 11.43% | 11.43% | 90% | 10.29% | 30.8997 | 7.4266 | 6 | 185.3982 | 68.3319 | 127.8% | 127.8%
2 | 56 | 25 | 1335 | 15 | 11.6 | 277.03 | 107.42 | 384.45 | 107.42 | 53.71 | 56 | 1335 | 900 | 55.2329 | -9.5101 | -1.945 | 874.284 | 14.539 | -38.0848 | 24.2815 | 24.2815 | 41.8659 | 221.8659 | 39.5759 | 519.2585 | 519.2585 | 91.6887 | 610.9472 | 0.58513 | 58.51% | 276.2703 | 161.6538 | 113.1576 | 142.8913 | 142.8913 | 79.19% | 11.44% | 11.44% | 90% | 10.3% | 28.4432 | 6.8464 | 6 | 170.659 | 62.8995 | 119.4% | 119.4%
2 | 56 | 25 | 1336 | 16 | 12.7 | 210 | 94.53 | 304.53 | 94.53 | 47.27 | 56 | 1336 | 960 | 55.2329 | -9.5101 | -1.945 | 934.284 | 15.539 | -53.0848 | 16.5755 | 16.5755 | 55.3585 | 235.3585 | 54.058 | 432.08 | 432.08 | 80.6864 | 512.7664 | 0.54817 | 54.82% | 231.873 | 127.1054 | 88.9738 | 138.9306 | 138.9306 | 64.04% | 11.47% | 11.47% | 90% | 10.32% | 23.9307 | 6.5691 | 6 | 143.584 | 52.9205 | 103.3% | 103.3%
2 | 56 | 25 | 1337 | 17 | 12.5 | 135.83 | 61.94 | 197.77 | 61.94 | 30.97 | 56 | 1337 | 1020 | 55.2329 | -9.5101 | -1.945 | 994.284 | 16.539 | -68.0848 | 7.5673 | 7.5673 | 67.3724 | 247.3724 | 68.7277 | 0 | 0 | 52.8691 | 52.8691 | -1.686 | 0% | 23.9074 | 0 | 0 | 130.5118 | 130.5118 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1338 | 18 | 12.1 | 46.11 | 35 | 81.11 | 35 | 17.5 | 56 | 1338 | 1080 | 55.2329 | -9.5101 | -1.945 | 1054.284 | 17.539 | -83.0848 | -2.2396 | 0 | 76.039 | 256.039 | 80.1774 | 0 | 0 | 29.8744 | 29.8744 | -3.6334 | 0% | 13.5092 | 0 | 0 | 160.9045 | 160.9045 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1339 | 19 | 11 | 0 | 4.92 | 4.92 | 4.92 | 2.46 | 56 | 1339 | 1140 | 55.2329 | -9.5101 | -1.945 | 1114.284 | 18.539 | -98.0848 | -12.4382 | 0 | 76.039 | 256.039 | 80.1774 | 0 | 0 | 4.1995 | 4.1995 | -31.3688 | 0% | 1.899 | 0 | 0 | 148.6855 | 148.6855 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1340 | 20 | 7.4 | 0 | 0 | 0 | 0 | 0 | 56 | 1340 | 1200 | 55.2329 | -9.5101 | -1.945 | 1174.284 | 19.539 | -113.0848 | -22.6576 | 0 | 76.039 | 256.039 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.7245 | 135.7245 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1341 | 21 | 6.3 | 0 | 0 | 0 | 0 | 0 | 56 | 1341 | 1260 | 55.2329 | -9.5101 | -1.945 | 1234.284 | 20.539 | -128.0848 | -32.4805 | 0 | 76.039 | 256.039 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6884 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1342 | 22 | 5.6 | 0 | 0 | 0 | 0 | 0 | 56 | 1342 | 1320 | 55.2329 | -9.5101 | -1.945 | 1294.284 | 21.539 | -143.0848 | -41.3311 | 0 | 76.039 | 256.039 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3684 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1343 | 23 | 5.5 | 0 | 0 | 0 | 0 | 0 | 56 | 1343 | 1380 | 55.2329 | -9.5101 | -1.945 | 1354.284 | 22.539 | -158.0848 | -48.3317 | 0 | 76.039 | 256.039 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9031 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
2 | 56 | 25 | 1344 | 24 | 5.7 | 0 | 0 | 0 | 0 | 0 | 56 | 1344 | 1440 | 55.2329 | -9.5101 | -1.945 | 1414.284 | 23.539 | -173.0848 | -52.2697 | 0 | 76.039 | 256.039 | 80.1774 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9806 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1345 | 1 | 6.5 | 0 | 0 | 0 | 0 | 0 | 57 | 1345 | 60 | 56.2192 | -9.1449 | -1.6275 | 34.284 | 0.54428 | 171.8359 | -51.7285 | 0 | 76.5807 | 103.4193 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8774 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1346 | 2 | 5.1 | 0 | 0 | 0 | 0 | 0 | 57 | 1346 | 120 | 56.2192 | -9.1449 | -1.6275 | 94.284 | 1.5443 | 156.8359 | -47.5129 | 0 | 76.5807 | 103.4193 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6403 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1347 | 3 | 3.8 | 0 | 0 | 0 | 0 | 0 | 57 | 1347 | 180 | 56.2192 | -9.1449 | -1.6275 | 154.284 | 2.5443 | 141.8359 | -40.3468 | 0 | 76.5807 | 103.4193 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2508 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1348 | 4 | 3.2 | 0 | 0 | 0 | 0 | 0 | 57 | 1348 | 240 | 56.2192 | -9.1449 | -1.6275 | 214.284 | 3.5443 | 126.8359 | -31.4106 | 0 | 76.5807 | 103.4193 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.1652 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1349 | 5 | 3.6 | 0 | 0 | 0 | 0 | 0 | 57 | 1349 | 300 | 56.2192 | -9.1449 | -1.6275 | 274.284 | 4.5443 | 111.8359 | -21.5491 | 0 | 76.5807 | 103.4193 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5955 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1350 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 57 | 1350 | 360 | 56.2192 | -9.1449 | -1.6275 | 334.284 | 5.5443 | 96.8359 | -11.3201 | 0 | 76.5807 | 103.4193 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.1833 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1351 | 7 | 3.6 | 0 | 0 | 0 | 0 | 0 | 57 | 1351 | 420 | 56.2192 | -9.1449 | -1.6275 | 394.284 | 6.5443 | 81.8359 | -1.1345 | 0 | 76.5807 | 103.4193 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 156.2615 | 156.2615 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1352 | 8 | 4.2 | 0.14 | 2.08 | 2.22 | 2.08 | 1.04 | 57 | 1352 | 480 | 56.2192 | -9.1449 | -1.6275 | 454.284 | 7.5443 | 66.8359 | 8.6356 | 8.6356 | 66.6505 | 113.3495 | 67.465 | 0 | 0 | 1.7754 | 1.7754 | -84.3637 | 0% | 0.80283 | 0 | 0 | 163.3701 | 163.3701 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1353 | 9 | 2.5 | 16.31 | 38.89 | 55.2 | 38.89 | 19.45 | 57 | 1353 | 540 | 56.2192 | -9.1449 | -1.6275 | 514.284 | 8.5443 | 51.8359 | 17.5761 | 17.5761 | 54.5145 | 125.4855 | 52.7829 | 32.6682 | 32.6682 | 33.1947 | 65.8629 | -1.5543 | 0% | 29.7832 | 0 | 0 | 144.1238 | 144.1238 | 0% | 12.06% | 12.06% | 80% | 9.647% | 2.8732 | 9.4659 | 6 | 17.2389 | 6.3537 | 11.96% | 11.96%
2 | 57 | 26 | 1354 | 10 | 3.4 | 66.03 | 97.03 | 163.06 | 97.03 | 48.52 | 57 | 1354 | 600 | 56.2192 | -9.1449 | -1.6275 | 574.284 | 9.5443 | 36.8359 | 25.1712 | 25.1712 | 40.8445 | 139.1555 | 38.2912 | 121.8484 | 121.8484 | 82.8203 | 204.6687 | 0.055765 | 5.576% | 92.5512 | 5.1611 | 3.6128 | 149.8404 | 149.8404 | 2.411% | 11.9% | 11.9% | 80% | 9.516% | 8.8076 | 9.181 | 6 | 52.8454 | 19.4772 | 35.27% | 35.27%
2 | 57 | 26 | 1355 | 11 | 6.3 | 127.58 | 160.92 | 288.5 | 160.92 | 80.46 | 57 | 1355 | 660 | 56.2192 | -9.1449 | -1.6275 | 634.284 | 10.5443 | 21.8359 | 30.7837 | 30.7837 | 25.3056 | 154.6944 | 24.3447 | 227.1127 | 227.1127 | 137.3538 | 364.4666 | 0.40295 | 40.3% | 164.8118 | 66.4112 | 46.4878 | 133.9467 | 133.9467 | 34.71% | 11.68% | 11.68% | 85% | 9.928% | 16.3628 | 8.3016 | 6 | 98.1765 | 36.1848 | 73.3% | 73.3%
2 | 57 | 26 | 1356 | 12 | 7.9 | 137.69 | 192.31 | 330 | 192.31 | 96.16 | 57 | 1356 | 720 | 56.2192 | -9.1449 | -1.6275 | 694.284 | 11.5443 | 6.8359 | 33.7453 | 33.7453 | 8.1244 | 171.8756 | 12.8726 | 241.6368 | 241.6368 | 164.1469 | 405.7837 | 0.45315 | 45.31% | 183.4954 | 83.1503 | 58.2052 | 130.1315 | 130.1315 | 44.73% | 11.61% | 11.61% | 85% | 9.872% | 18.115 | 7.8416 | 6 | 108.6902 | 40.0598 | 83.52% | 83.52%
2 | 57 | 26 | 1357 | 13 | 8.9 | 189.53 | 235.92 | 425.45 | 235.92 | 117.96 | 57 | 1357 | 780 | 56.2192 | -9.1449 | -1.6275 | 754.284 | 12.5443 | -8.1641 | 33.6044 | 33.6044 | 9.6911 | 189.6911 | 13.6192 | 332.8195 | 332.8195 | 201.3703 | 534.1899 | 0.54189 | 54.19% | 241.5607 | 130.9004 | 91.6303 | 134.0785 | 134.0785 | 68.34% | 11.51% | 11.51% | 90% | 10.36% | 25.0326 | 7.5632 | 6 | 150.1954 | 55.3573 | 112% | 112%
2 | 57 | 26 | 1358 | 14 | 9 | 175.64 | 242.97 | 418.61 | 242.97 | 121.49 | 57 | 1358 | 840 | 56.2192 | -9.1449 | -1.6275 | 814.284 | 13.5443 | -23.1641 | 30.3845 | 30.3845 | 26.7566 | 206.7566 | 25.5343 | 313.3351 | 313.3351 | 207.3879 | 520.7229 | 0.53557 | 53.56% | 235.4709 | 126.1105 | 88.2773 | 132.5614 | 132.5614 | 66.59% | 11.52% | 11.52% | 90% | 10.37% | 24.4157 | 7.5357 | 6 | 146.494 | 53.9931 | 110.5% | 110.5%
2 | 57 | 26 | 1359 | 15 | 9.8 | 143.14 | 218.69 | 361.83 | 218.69 | 109.35 | 57 | 1359 | 900 | 56.2192 | -9.1449 | -1.6275 | 874.284 | 14.5443 | -38.1641 | 24.5686 | 24.5686 | 42.1283 | 222.1283 | 39.5611 | 265.4108 | 265.4108 | 186.6636 | 452.0744 | 0.49895 | 49.9% | 204.428 | 101.9996 | 71.3997 | 128.8433 | 128.8433 | 55.42% | 11.55% | 11.55% | 85% | 9.815% | 20.0648 | 7.3186 | 6 | 120.389 | 44.3716 | 93.44% | 93.44%
2 | 57 | 26 | 1360 | 16 | 10.2 | 82.78 | 179.92 | 262.7 | 179.92 | 89.96 | 57 | 1360 | 960 | 56.2192 | -9.1449 | -1.6275 | 934.284 | 15.5443 | -53.1641 | 16.8303 | 16.8303 | 55.6437 | 235.6437 | 54.0777 | 167.7367 | 167.7367 | 153.5713 | 321.3081 | 0.37771 | 37.77% | 145.2955 | 54.8794 | 38.4156 | 123.2337 | 123.2337 | 31.17% | 11.61% | 11.61% | 85% | 9.869% | 14.3385 | 7.2117 | 6 | 86.031 | 31.7083 | 69.81% | 69.81%
2 | 57 | 26 | 1361 | 17 | 10.6 | 72.5 | 114.81 | 187.31 | 114.81 | 57.41 | 57 | 1361 | 1020 | 56.2192 | -9.1449 | -1.6275 | 994.284 | 16.5443 | -68.1641 | 7.7973 | 7.7973 | 67.6694 | 247.6694 | 68.77 | 0 | 0 | 97.9965 | 97.9965 | -0.5842 | 0% | 44.314 | 0 | 0 | 118.1832 | 118.1832 | 0% | 11.71% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1362 | 18 | 10.7 | 17.22 | 51.67 | 68.89 | 51.67 | 25.84 | 57 | 1362 | 1080 | 56.2192 | -9.1449 | -1.6275 | 1054.284 | 17.5443 | -83.1641 | -2.0252 | 0 | 76.5807 | 256.5807 | 80.5549 | 0 | 0 | 44.1031 | 44.1031 | -2.2753 | 0% | 19.9434 | 0 | 0 | 150.8477 | 150.8477 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1363 | 19 | 9.9 | 0 | 7.22 | 7.22 | 7.22 | 3.61 | 57 | 1363 | 1140 | 56.2192 | -9.1449 | -1.6275 | 1114.284 | 18.5443 | -98.1641 | -12.2296 | 0 | 76.5807 | 256.5807 | 80.5549 | 0 | 0 | 6.1627 | 6.1627 | -21.5356 | 0% | 2.7868 | 0 | 0 | 142.298 | 142.298 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1364 | 20 | 8.4 | 0 | 0 | 0 | 0 | 0 | 57 | 1364 | 1200 | 56.2192 | -9.1449 | -1.6275 | 1174.284 | 19.5443 | -113.1641 | -22.4439 | 0 | 76.5807 | 256.5807 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.3729 | 134.3729 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1365 | 21 | 8.2 | 0 | 0 | 0 | 0 | 0 | 57 | 1365 | 1260 | 56.2192 | -9.1449 | -1.6275 | 1234.284 | 20.5443 | -128.1641 | -32.2491 | 0 | 76.5807 | 256.5807 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2161 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1366 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 57 | 1366 | 1320 | 56.2192 | -9.1449 | -1.6275 | 1294.284 | 21.5443 | -143.1641 | -41.0679 | 0 | 76.5807 | 256.5807 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7034 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1367 | 23 | 8.6 | 0 | 0 | 0 | 0 | 0 | 57 | 1367 | 1380 | 56.2192 | -9.1449 | -1.6275 | 1354.284 | 22.5443 | -158.1641 | -48.0242 | 0 | 76.5807 | 256.5807 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4183 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
2 | 57 | 26 | 1368 | 24 | 8.8 | 0 | 0 | 0 | 0 | 0 | 57 | 1368 | 1440 | 56.2192 | -9.1449 | -1.6275 | 1414.284 | 23.5443 | -173.1641 | -51.9182 | 0 | 76.5807 | 256.5807 | 80.5549 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7429 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1369 | 1 | 7.8 | 0 | 0 | 0 | 0 | 0 | 58 | 1369 | 60 | 57.2055 | -8.777 | -1.3029 | 34.284 | 0.54969 | 171.7547 | -51.3526 | 0 | 77.1256 | 102.8744 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1722 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1370 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 58 | 1370 | 120 | 57.2055 | -8.777 | -1.3029 | 94.284 | 1.5497 | 156.7547 | -47.1435 | 0 | 77.1256 | 102.8744 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6907 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1371 | 3 | 7.8 | 0 | 0 | 0 | 0 | 0 | 58 | 1371 | 180 | 57.2055 | -8.777 | -1.3029 | 154.284 | 2.5497 | 141.7547 | -39.9961 | 0 | 77.1256 | 102.8744 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8188 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1372 | 4 | 7.6 | 0 | 0 | 0 | 0 | 0 | 58 | 1372 | 240 | 57.2055 | -8.777 | -1.3029 | 214.284 | 3.5497 | 126.7547 | -31.0769 | 0 | 77.1256 | 102.8744 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1236 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1373 | 5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 58 | 1373 | 300 | 57.2055 | -8.777 | -1.3029 | 274.284 | 4.5497 | 111.7547 | -21.2256 | 0 | 77.1256 | 102.8744 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4963 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1374 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 58 | 1374 | 360 | 57.2055 | -8.777 | -1.3029 | 334.284 | 5.5497 | 96.7547 | -10.9994 | 0 | 77.1256 | 102.8744 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.4732 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1375 | 7 | 5.7 | 0 | 0 | 0 | 0 | 0 | 58 | 1375 | 420 | 57.2055 | -8.777 | -1.3029 | 394.284 | 6.5497 | 81.7547 | -0.80967 | 0 | 77.1256 | 102.8744 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.907 | 143.907 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1376 | 8 | 4.6 | 0 | 1.67 | 1.67 | 1.67 | 0.84 | 58 | 1376 | 480 | 57.2055 | -8.777 | -1.3029 | 454.284 | 7.5497 | 66.7547 | 8.9703 | 8.9703 | 66.8251 | 113.1749 | 67.3485 | 0 | 0 | 1.4254 | 1.4254 | -104.5968 | 0% | 0.64458 | 0 | 0 | 145.7255 | 145.7255 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1377 | 9 | 4.9 | 0.75 | 24.92 | 25.67 | 24.92 | 12.46 | 58 | 1377 | 540 | 57.2055 | -8.777 | -1.3029 | 514.284 | 8.5497 | 51.7547 | 17.925 | 17.925 | 54.6634 | 125.3366 | 52.645 | 1.4786 | 1.4786 | 21.2706 | 22.7491 | -5.7686 | 0% | 10.2872 | 0 | 0 | 127.0254 | 127.0254 | 0% | 12% | 12% | 80% | 9.598% | 0.98736 | 8.7188 | 6 | 5.9242 | 2.1835 | 4.664% | 4.664%
2 | 58 | 27 | 1378 | 10 | 6 | 2.22 | 64.81 | 67.03 | 64.81 | 32.41 | 58 | 1378 | 600 | 57.2055 | -8.777 | -1.3029 | 574.284 | 9.5497 | 36.7547 | 25.5354 | 25.5354 | 40.9503 | 139.0497 | 38.1212 | 4.0515 | 4.0515 | 55.3188 | 59.3703 | -1.67 | 0% | 26.8473 | 0 | 0 | 130.5995 | 130.5995 | 0% | 11.92% | 11.92% | 80% | 9.538% | 2.5606 | 8.3898 | 6 | 15.3639 | 5.6626 | 11.76% | 11.76%
2 | 58 | 27 | 1379 | 11 | 6.3 | 22.5 | 139.36 | 161.86 | 139.36 | 69.68 | 58 | 1379 | 660 | 57.2055 | -8.777 | -1.3029 | 634.284 | 10.5497 | 21.7547 | 31.1588 | 31.1588 | 25.3436 | 154.6564 | 24.1151 | 39.6905 | 39.6905 | 118.9512 | 158.6417 | -0.11738 | 0% | 71.7378 | 0 | 0 | 133.4448 | 133.4448 | 0% | 11.84% | 11.84% | 80% | 9.468% | 6.7923 | 8.3016 | 6 | 40.7537 | 15.0205 | 30.54% | 30.54%
2 | 58 | 27 | 1380 | 12 | 7.4 | 50.08 | 192.5 | 242.58 | 192.5 | 96.25 | 58 | 1380 | 720 | 57.2055 | -8.777 | -1.3029 | 694.284 | 11.5497 | 6.7547 | 34.1192 | 34.1192 | 8.0716 | 171.9284 | 12.5193 | 87.1595 | 87.1595 | 164.309 | 251.4685 | 0.23314 | 23.31% | 113.7141 | 26.5111 | 18.5578 | 114.2453 | 114.2453 | 16.24% | 11.73% | 11.73% | 80% | 9.386% | 10.6729 | 7.9834 | 6 | 64.0372 | 23.6021 | 56.05% | 56.05%
2 | 58 | 27 | 1381 | 13 | 8 | 90.28 | 209.17 | 299.45 | 209.17 | 104.59 | 58 | 1381 | 780 | 57.2055 | -8.777 | -1.3029 | 754.284 | 12.5497 | -8.2453 | 33.9603 | 33.9603 | 9.839 | 189.839 | 13.377 | 157.2281 | 157.2281 | 178.5378 | 335.7659 | 0.38069 | 38.07% | 151.8333 | 57.8009 | 40.4606 | 116.9024 | 116.9024 | 34.61% | 11.66% | 11.66% | 85% | 9.91% | 15.0461 | 7.8134 | 6 | 90.2768 | 33.2732 | 77.22% | 77.22%
2 | 58 | 27 | 1382 | 14 | 8 | 83.81 | 229.92 | 313.73 | 229.92 | 114.96 | 58 | 1382 | 840 | 57.2055 | -8.777 | -1.3029 | 814.284 | 13.5497 | -23.2453 | 30.7087 | 30.7087 | 26.9788 | 206.9788 | 25.4591 | 148.1795 | 148.1795 | 196.249 | 344.4285 | 0.39133 | 39.13% | 155.7505 | 60.9503 | 42.6652 | 116.8867 | 116.8867 | 36.5% | 11.65% | 11.65% | 85% | 9.905% | 15.4267 | 7.8134 | 6 | 92.5605 | 34.1149 | 79.19% | 79.19%
2 | 58 | 27 | 1383 | 15 | 8.2 | 17.86 | 166.58 | 184.44 | 166.58 | 83.29 | 58 | 1383 | 900 | 57.2055 | -8.777 | -1.3029 | 874.284 | 14.5497 | -38.2453 | 24.8567 | 24.8567 | 42.3952 | 222.3952 | 39.5506 | 32.7612 | 32.7612 | 142.1849 | 174.9461 | -0.0057476 | 0% | 79.1106 | 0 | 0 | 109.7793 | 109.7793 | 0% | 11.76% | 11.76% | 80% | 9.406% | 7.4412 | 7.7573 | 6 | 44.6475 | 16.4557 | 40.67% | 40.67%
2 | 58 | 27 | 1384 | 16 | 8.5 | 10.28 | 139.36 | 149.64 | 139.36 | 69.68 | 58 | 1384 | 960 | 57.2055 | -8.777 | -1.3029 | 934.284 | 15.5497 | -53.2453 | 17.0857 | 17.0857 | 55.9329 | 235.9329 | 54.1006 | 20.5166 | 20.5166 | 118.9512 | 139.4678 | -0.20666 | 0% | 63.0673 | 0 | 0 | 149.519 | 149.519 | 0% | 11.77% | 11.77% | 80% | 9.416% | 5.9383 | 7.6737 | 6 | 35.6299 | 13.132 | 23.83% | 23.83%
2 | 58 | 27 | 1385 | 17 | 8 | 20.08 | 73.33 | 93.41 | 73.33 | 36.67 | 58 | 1385 | 1020 | 57.2055 | -8.777 | -1.3029 | 994.284 | 16.5497 | -68.2453 | 8.0279 | 8.0279 | 67.9699 | 247.9699 | 68.8148 | 0 | 0 | 62.5911 | 62.5911 | -1.4668 | 0% | 28.3037 | 0 | 0 | 144.8281 | 144.8281 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1386 | 18 | 8 | 2.31 | 26.67 | 28.98 | 26.67 | 13.34 | 58 | 1386 | 1080 | 57.2055 | -8.777 | -1.3029 | 1054.284 | 17.5497 | -83.2453 | -1.8101 | 0 | 77.1256 | 257.1256 | 80.9351 | 0 | 0 | 22.7643 | 22.7643 | -5.4397 | 0% | 10.294 | 0 | 0 | 139.7794 | 139.7794 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1387 | 19 | 6.3 | 0 | 4.72 | 4.72 | 4.72 | 2.36 | 58 | 1387 | 1140 | 57.2055 | -8.777 | -1.3029 | 1114.284 | 18.5497 | -98.2453 | -12.0201 | 0 | 77.1256 | 257.1256 | 80.9351 | 0 | 0 | 4.0288 | 4.0288 | -35.4772 | 0% | 1.8218 | 0 | 0 | 133.7755 | 133.7755 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1388 | 20 | 4.5 | 0 | 0 | 0 | 0 | 0 | 58 | 1388 | 1200 | 57.2055 | -8.777 | -1.3029 | 1174.284 | 19.5497 | -113.2453 | -22.2289 | 0 | 77.1256 | 257.1256 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.7152 | 127.7152 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1389 | 21 | 3.7 | 0 | 0 | 0 | 0 | 0 | 58 | 1389 | 1260 | 57.2055 | -8.777 | -1.3029 | 1234.284 | 20.5497 | -128.2453 | -32.016 | 0 | 77.1256 | 257.1256 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2595 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1390 | 22 | 3.8 | 0 | 0 | 0 | 0 | 0 | 58 | 1390 | 1320 | 57.2055 | -8.777 | -1.3029 | 1294.284 | 21.5497 | -143.2453 | -40.8025 | 0 | 77.1256 | 257.1256 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7983 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1391 | 23 | 3 | 0 | 0 | 0 | 0 | 0 | 58 | 1391 | 1380 | 57.2055 | -8.777 | -1.3029 | 1354.284 | 22.5497 | -158.2453 | -47.7141 | 0 | 77.1256 | 257.1256 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8408 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
2 | 58 | 27 | 1392 | 24 | 3 | 0 | 0 | 0 | 0 | 0 | 58 | 1392 | 1440 | 57.2055 | -8.777 | -1.3029 | 1414.284 | 23.5497 | -173.2453 | -51.5639 | 0 | 77.1256 | 257.1256 | 80.9351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6641 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1393 | 1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 59 | 1393 | 60 | 58.1918 | -8.4065 | -0.97157 | 34.284 | 0.55521 | 171.6719 | -50.9738 | 0 | 77.6738 | 102.3262 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.3296 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1394 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 59 | 1394 | 120 | 58.1918 | -8.4065 | -0.97157 | 94.284 | 1.5552 | 156.6719 | -46.7709 | 0 | 77.6738 | 102.3262 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3875 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1395 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 59 | 1395 | 180 | 58.1918 | -8.4065 | -0.97157 | 154.284 | 2.5552 | 141.6719 | -39.642 | 0 | 77.6738 | 102.3262 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6834 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1396 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 59 | 1396 | 240 | 58.1918 | -8.4065 | -0.97157 | 214.284 | 3.5552 | 126.6719 | -30.7397 | 0 | 77.6738 | 102.3262 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4454 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1397 | 5 | -0.3 | 0 | 0 | 0 | 0 | 0 | 59 | 1397 | 300 | 58.1918 | -8.4065 | -0.97157 | 274.284 | 4.5552 | 111.6719 | -20.8987 | 0 | 77.6738 | 102.3262 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.199 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1398 | 6 | 0.4 | 0 | 0 | 0 | 0 | 0 | 59 | 1398 | 360 | 58.1918 | -8.4065 | -0.97157 | 334.284 | 5.5552 | 96.6719 | -10.6754 | 0 | 77.6738 | 102.3262 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.108 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1399 | 7 | -1.3 | 0 | 0 | 0 | 0 | 0 | 59 | 1399 | 420 | 58.1918 | -8.4065 | -0.97157 | 394.284 | 6.5552 | 81.6719 | -0.48172 | 0 | 77.6738 | 102.3262 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 150.2564 | 150.2564 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1400 | 8 | -1.3 | 0.28 | 3.19 | 3.47 | 3.19 | 1.6 | 59 | 1400 | 480 | 58.1918 | -8.4065 | -0.97157 | 454.284 | 7.5552 | 66.6719 | 9.308 | 9.308 | 67.0002 | 112.9998 | 67.231 | 0 | 0 | 2.7228 | 2.7228 | -59.6765 | 0% | 1.2313 | 0 | 0 | 156.5509 | 156.5509 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1401 | 9 | -0.5 | 3.25 | 46.19 | 49.44 | 46.19 | 23.1 | 59 | 1401 | 540 | 58.1918 | -8.4065 | -0.97157 | 514.284 | 8.5552 | 51.6719 | 18.2768 | 18.2768 | 54.8128 | 125.1872 | 52.5066 | 6.3078 | 6.3078 | 39.4256 | 45.7334 | -2.7534 | 0% | 20.6807 | 0 | 0 | 140.3839 | 140.3839 | 0% | 12.2% | 12.2% | 80% | 9.762% | 2.0188 | 10.4565 | 6 | 12.113 | 4.4645 | 8.628% | 8.628%
2 | 59 | 28 | 1402 | 10 | 1.9 | 47.69 | 106.11 | 153.8 | 106.11 | 53.06 | 59 | 1402 | 600 | 58.1918 | -8.4065 | -0.97157 | 574.284 | 9.5552 | 36.6719 | 25.9027 | 25.9027 | 41.0562 | 138.9438 | 37.9514 | 86.0838 | 86.0838 | 90.5706 | 176.6543 | -0.083556 | 0% | 79.8831 | 0 | 0 | 149.576 | 149.576 | 0% | 11.97% | 11.97% | 80% | 9.578% | 7.6512 | 9.659 | 6 | 45.9074 | 16.92 | 30.69% | 30.69%
2 | 59 | 28 | 1403 | 11 | 2.9 | 126.67 | 149.92 | 276.59 | 149.92 | 74.96 | 59 | 1403 | 660 | 58.1918 | -8.4065 | -0.97157 | 634.284 | 10.5552 | 21.6719 | 31.5369 | 31.5369 | 25.3807 | 154.6193 | 23.8863 | 221.4343 | 221.4343 | 127.9647 | 349.399 | 0.36223 | 36.22% | 157.9982 | 57.2318 | 40.0623 | 131.7184 | 131.7184 | 30.42% | 11.78% | 11.78% | 85% | 10.01% | 15.8147 | 9.3386 | 6 | 94.8883 | 34.9728 | 72.04% | 72.04%
2 | 59 | 28 | 1404 | 12 | 4.3 | 148.42 | 200.47 | 348.89 | 200.47 | 100.24 | 59 | 1404 | 720 | 58.1918 | -8.4065 | -0.97157 | 694.284 | 11.5552 | 6.6719 | 34.4959 | 34.4959 | 8.0164 | 171.9836 | 12.1643 | 256.181 | 256.181 | 171.1118 | 427.2929 | 0.4507 | 45.07% | 193.2218 | 87.0841 | 60.9589 | 129.8998 | 129.8998 | 46.93% | 11.67% | 11.67% | 85% | 9.923% | 19.1729 | 8.9018 | 6 | 115.0376 | 42.3992 | 88.56% | 88.56%
2 | 59 | 28 | 1405 | 13 | 4.9 | 285.28 | 211.58 | 496.86 | 211.58 | 105.79 | 59 | 1405 | 780 | 58.1918 | -8.4065 | -0.97157 | 754.284 | 12.5552 | -8.3281 | 34.3184 | 34.3184 | 9.9906 | 189.9906 | 13.1402 | 492.7536 | 492.7536 | 180.5948 | 673.3484 | 0.58195 | 58.19% | 304.4882 | 177.1954 | 124.0368 | 135.8603 | 135.8603 | 91.3% | 11.46% | 11.46% | 90% | 10.31% | 31.3972 | 8.7188 | 6 | 188.3831 | 69.4321 | 138.7% | 138.7%
2 | 59 | 28 | 1406 | 14 | 5.5 | 203.89 | 194.36 | 398.25 | 194.36 | 97.18 | 59 | 1406 | 840 | 58.1918 | -8.4065 | -0.97157 | 814.284 | 13.5552 | -23.3281 | 31.0345 | 31.0345 | 27.2055 | 207.2055 | 25.3896 | 357.2793 | 357.2793 | 165.8966 | 523.176 | 0.52096 | 52.1% | 236.5802 | 123.2484 | 86.2739 | 131.4429 | 131.4429 | 65.64% | 11.57% | 11.57% | 90% | 10.42% | 24.641 | 8.5383 | 6 | 147.8459 | 54.4913 | 112.5% | 112.5%
2 | 59 | 28 | 1407 | 15 | 5.5 | 178.06 | 123.33 | 301.39 | 123.33 | 61.67 | 59 | 1407 | 900 | 58.1918 | -8.4065 | -0.97157 | 874.284 | 14.5552 | -38.3281 | 25.1458 | 25.1458 | 42.6665 | 222.6665 | 39.5442 | 323.137 | 323.137 | 105.2687 | 428.4057 | 0.45834 | 45.83% | 193.7251 | 88.7929 | 62.155 | 124.5637 | 124.5637 | 49.9% | 11.65% | 11.65% | 85% | 9.901% | 19.1809 | 8.5383 | 6 | 115.0854 | 42.4169 | 92.39% | 92.39%
2 | 59 | 28 | 1408 | 16 | 6 | 108.97 | 158.53 | 267.5 | 158.53 | 79.27 | 59 | 1408 | 960 | 58.1918 | -8.4065 | -0.97157 | 934.284 | 15.5552 | -53.3281 | 17.3419 | 17.3419 | 56.226 | 236.226 | 54.1267 | 214.229 | 214.229 | 135.3138 | 349.5428 | 0.38378 | 38.38% | 158.0632 | 60.6616 | 42.4631 | 122.452 | 122.452 | 34.68% | 11.7% | 11.7% | 85% | 9.944% | 15.7178 | 8.3898 | 6 | 94.3071 | 34.7586 | 77.02% | 77.02%
2 | 59 | 28 | 1409 | 17 | 5.76 | 92.69 | 112.14 | 204.83 | 112.14 | 56.07 | 59 | 1409 | 1020 | 58.1918 | -8.4065 | -0.97157 | 994.284 | 16.5552 | -68.3281 | 8.2591 | 8.2591 | 68.2739 | 248.2739 | 68.8623 | 0 | 0 | 95.7175 | 95.7175 | -0.73656 | 0% | 43.2834 | 0 | 0 | 116.8425 | 116.8425 | 0% | 11.9% | 0% | 80% | 0% | 0 | 8.4608 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1410 | 18 | 5.53 | 55.75 | 51.47 | 107.22 | 51.47 | 25.74 | 59 | 1410 | 1080 | 58.1918 | -8.4065 | -0.97157 | 1054.284 | 17.5552 | -83.3281 | -1.5943 | 0 | 77.6738 | 257.6738 | 81.3179 | 0 | 0 | 43.9324 | 43.9324 | -2.565 | 0% | 19.8662 | 0 | 0 | 150.7179 | 150.7179 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.5293 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1411 | 19 | 4.51 | 0 | 8.61 | 8.61 | 8.61 | 4.31 | 59 | 1411 | 1140 | 58.1918 | -8.4065 | -0.97157 | 1114.284 | 18.5552 | -98.3281 | -11.8095 | 0 | 77.6738 | 257.6738 | 81.3179 | 0 | 0 | 7.3491 | 7.3491 | -19.6691 | 0% | 3.3233 | 0 | 0 | 138.0118 | 138.0118 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8374 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1412 | 20 | 2.8 | 0 | 0 | 0 | 0 | 0 | 59 | 1412 | 1200 | 58.1918 | -8.4065 | -0.97157 | 1174.284 | 19.5552 | -113.3281 | -22.0125 | 0 | 77.6738 | 257.6738 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.2379 | 129.2379 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1413 | 21 | 0.86 | 0 | 0 | 0 | 0 | 0 | 59 | 1413 | 1260 | 58.1918 | -8.4065 | -0.97157 | 1234.284 | 20.5552 | -128.3281 | -31.7811 | 0 | 77.6738 | 257.6738 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1541 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9996 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1414 | 22 | -0.27 | 0 | 0 | 0 | 0 | 0 | 59 | 1414 | 1320 | 58.1918 | -8.4065 | -0.97157 | 1294.284 | 21.5552 | -143.3281 | -40.5348 | 0 | 77.6738 | 257.6738 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.1874 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3783 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1415 | 23 | -1 | 0 | 0 | 0 | 0 | 0 | 59 | 1415 | 1380 | 58.1918 | -8.4065 | -0.97157 | 1354.284 | 22.5552 | -158.3281 | -47.4015 | 0 | 77.6738 | 257.6738 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9862 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
2 | 59 | 28 | 1416 | 24 | -1.61 | 0 | 0 | 0 | 0 | 0 | 59 | 1416 | 1440 | 58.1918 | -8.4065 | -0.97157 | 1414.284 | 23.5552 | -173.3281 | -51.207 | 0 | 77.6738 | 257.6738 | 81.3179 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.6022 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.839 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1417 | 1 | -2.04 | 0 | 0 | 0 | 0 | 0 | 60 | 1417 | 60 | 59.1781 | -8.0335 | -0.63389 | 34.284 | 0.56084 | 171.5875 | -50.5923 | 0 | 78.225 | 101.775 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5019 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9895 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1418 | 2 | -2.72 | 0 | 0 | 0 | 0 | 0 | 60 | 1418 | 120 | 59.1781 | -8.0335 | -0.63389 | 94.284 | 1.5608 | 156.5875 | -46.3952 | 0 | 78.225 | 101.775 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.1863 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.2301 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1419 | 3 | -3.33 | 0 | 0 | 0 | 0 | 0 | 60 | 1419 | 180 | 59.1781 | -8.0335 | -0.63389 | 154.284 | 2.5608 | 141.5875 | -39.2846 | 0 | 78.225 | 101.775 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.7641 | 0 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4487 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1420 | 4 | -3.9 | 0 | 0 | 0 | 0 | 0 | 60 | 1420 | 240 | 59.1781 | -8.0335 | -0.63389 | 214.284 | 3.5608 | 126.5875 | -30.3993 | 0 | 78.225 | 101.775 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.6328 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1421 | 5 | -4.15 | 0 | 0 | 0 | 0 | 0 | 60 | 1421 | 300 | 59.1781 | -8.0335 | -0.63389 | 274.284 | 4.5608 | 111.5875 | -20.5685 | 0 | 78.225 | 101.775 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4288 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7467 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1422 | 6 | -4.65 | 0 | 0 | 0 | 0 | 0 | 60 | 1422 | 360 | 59.1781 | -8.0335 | -0.63389 | 334.284 | 5.5608 | 96.5875 | -10.3482 | 0 | 78.225 | 101.775 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9197 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9307 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1423 | 7 | -4.93 | 0 | 0 | 0 | 0 | 0 | 60 | 1423 | 420 | 59.1781 | -8.0335 | -0.63389 | 394.284 | 6.5608 | 81.5875 | -0.15077 | 0 | 78.225 | 101.775 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.5334 | 142.5334 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0345 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1424 | 8 | -5 | 0.28 | 3.69 | 3.97 | 3.69 | 1.85 | 60 | 1424 | 480 | 59.1781 | -8.0335 | -0.63389 | 454.284 | 7.5608 | 66.5875 | 9.6487 | 9.6487 | 67.176 | 112.824 | 67.1125 | 0 | 0 | 3.1496 | 3.1496 | -54.4314 | 0% | 1.4243 | 0 | 0 | 147.8057 | 147.8057 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1425 | 9 | -2.9 | 19.25 | 41.11 | 60.36 | 41.11 | 20.56 | 60 | 1425 | 540 | 59.1781 | -8.0335 | -0.63389 | 514.284 | 8.5608 | 51.5875 | 18.6316 | 18.6316 | 54.9627 | 125.0373 | 52.3679 | 36.7903 | 36.7903 | 35.0896 | 71.8799 | -1.5426 | 0% | 32.5041 | 0 | 0 | 134.3507 | 134.3507 | 0% | 12.27% | 12.27% | 80% | 9.815% | 3.1904 | 11.2943 | 6 | 19.1421 | 7.0552 | 14.25% | 14.25%
3 | 60 | 1 | 1426 | 10 | 0.6 | 63.25 | 112.97 | 176.22 | 112.97 | 56.49 | 60 | 1426 | 600 | 59.1781 | -8.0335 | -0.63389 | 574.284 | 9.5608 | 36.5875 | 26.2728 | 26.2728 | 41.1623 | 138.8377 | 37.7818 | 112.9335 | 112.9335 | 96.4259 | 209.3595 | 0.039867 | 3.987% | 94.6723 | 3.7743 | 2.642 | 144.2998 | 144.2998 | 1.831% | 11.98% | 11.98% | 80% | 9.586% | 9.0751 | 10.0859 | 6 | 54.4504 | 20.0687 | 37.73% | 37.73%
3 | 60 | 1 | 1427 | 11 | 4.3 | 119.64 | 153.61 | 273.25 | 153.61 | 76.81 | 60 | 1427 | 660 | 59.1781 | -8.0335 | -0.63389 | 634.284 | 10.5608 | 21.5875 | 31.9179 | 31.9179 | 25.417 | 154.583 | 23.6586 | 207.2701 | 207.2701 | 131.1143 | 338.3845 | 0.35787 | 35.79% | 153.0175 | 54.7598 | 38.3319 | 128.8532 | 128.8532 | 29.75% | 11.75% | 11.75% | 85% | 9.988% | 15.2834 | 8.9018 | 6 | 91.7004 | 33.7979 | 71.17% | 71.17%
3 | 60 | 1 | 1428 | 12 | 4.9 | 87.97 | 193.33 | 281.3 | 193.33 | 96.67 | 60 | 1428 | 720 | 59.1781 | -8.0335 | -0.63389 | 694.284 | 11.5608 | 6.5875 | 34.8752 | 34.8752 | 7.9589 | 172.0411 | 11.8078 | 150.5942 | 150.5942 | 165.0175 | 315.6117 | 0.33025 | 33.03% | 142.7196 | 47.1335 | 32.9935 | 122.9601 | 122.9601 | 26.83% | 11.75% | 11.75% | 85% | 9.991% | 14.2593 | 8.7188 | 6 | 85.5559 | 31.5332 | 69.58% | 69.58%
3 | 60 | 1 | 1429 | 13 | 5.8 | 180.92 | 146.58 | 327.5 | 146.58 | 73.29 | 60 | 1429 | 780 | 59.1781 | -8.0335 | -0.63389 | 754.284 | 12.5608 | -8.4125 | 34.6786 | 34.6786 | 10.146 | 190.146 | 12.9093 | 309.9399 | 309.9399 | 125.1139 | 435.0538 | 0.46528 | 46.53% | 196.7313 | 91.5346 | 64.0742 | 124.0504 | 124.0504 | 51.65% | 11.64% | 11.64% | 85% | 9.891% | 19.4596 | 8.449 | 6 | 116.7577 | 43.0332 | 94.12% | 94.12%
3 | 60 | 1 | 1430 | 14 | 7 | 92.5 | 200.36 | 292.86 | 200.36 | 100.18 | 60 | 1430 | 840 | 59.1781 | -8.0335 | -0.63389 | 814.284 | 13.5608 | -23.4125 | 31.3617 | 31.3617 | 27.4367 | 207.4367 | 25.326 | 160.6524 | 160.6524 | 171.018 | 331.6704 | 0.36832 | 36.83% | 149.9814 | 55.2408 | 38.6686 | 123.0496 | 123.0496 | 31.43% | 11.69% | 11.69% | 85% | 9.934% | 14.8989 | 8.0981 | 6 | 89.3933 | 32.9476 | 72.65% | 72.65%
3 | 60 | 1 | 1431 | 15 | 7.2 | 80.64 | 173.33 | 253.97 | 173.33 | 86.67 | 60 | 1431 | 900 | 59.1781 | -8.0335 | -0.63389 | 874.284 | 14.5608 | -38.4125 | 25.4357 | 25.4357 | 42.942 | 222.942 | 39.542 | 144.7883 | 144.7883 | 147.9464 | 292.7347 | 0.31199 | 31.2% | 132.3747 | 41.2997 | 28.9098 | 118.8778 | 118.8778 | 24.32% | 11.71% | 11.71% | 80% | 9.367% | 12.3999 | 8.0406 | 6 | 74.3995 | 27.4213 | 62.58% | 62.58%
3 | 60 | 1 | 1432 | 16 | 9 | 18.97 | 141.58 | 160.55 | 141.58 | 70.79 | 60 | 1432 | 960 | 59.1781 | -8.0335 | -0.63389 | 934.284 | 15.5608 | -53.4125 | 17.5986 | 17.5986 | 56.5229 | 236.5229 | 54.156 | 36.7407 | 36.7407 | 120.8461 | 157.5868 | -0.082998 | 0% | 71.2608 | 0 | 0 | 115.3708 | 115.3708 | 0% | 11.74% | 11.74% | 80% | 9.393% | 6.6932 | 7.5357 | 6 | 40.1591 | 14.8014 | 34.81% | 34.81%
3 | 60 | 1 | 1433 | 17 | 8.4 | 6.47 | 94.72 | 101.19 | 94.72 | 47.36 | 60 | 1433 | 1020 | 59.1781 | -8.0335 | -0.63389 | 994.284 | 16.5608 | -68.4125 | 8.4909 | 8.4909 | 68.5811 | 248.5811 | 68.9121 | 0 | 0 | 80.8486 | 80.8486 | -0.94236 | 0% | 36.5597 | 0 | 0 | 151.2783 | 151.2783 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1434 | 18 | 7.4 | 1.67 | 47.31 | 48.98 | 47.31 | 23.66 | 60 | 1434 | 1080 | 59.1781 | -8.0335 | -0.63389 | 1054.284 | 17.5608 | -83.4125 | -1.3778 | 0 | 78.225 | 258.225 | 81.7033 | 0 | 0 | 40.3816 | 40.3816 | -2.7509 | 0% | 18.2606 | 0 | 0 | 144.5473 | 144.5473 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1435 | 19 | 5.6 | 0 | 7.22 | 7.22 | 7.22 | 3.61 | 60 | 1435 | 1140 | 59.1781 | -8.0335 | -0.63389 | 1114.284 | 18.5608 | -98.4125 | -11.598 | 0 | 78.225 | 258.225 | 81.7033 | 0 | 0 | 6.1627 | 6.1627 | -23.1859 | 0% | 2.7868 | 0 | 0 | 137.2113 | 137.2113 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1436 | 20 | 4.5 | 0 | 0 | 0 | 0 | 0 | 60 | 1436 | 1200 | 59.1781 | -8.0335 | -0.63389 | 1174.284 | 19.5608 | -113.4125 | -21.7947 | 0 | 78.225 | 258.225 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.2342 | 131.2342 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1437 | 21 | 2.1 | 0 | 0 | 0 | 0 | 0 | 60 | 1437 | 1260 | 59.1781 | -8.0335 | -0.63389 | 1234.284 | 20.5608 | -128.4125 | -31.5444 | 0 | 78.225 | 258.225 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.3652 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1438 | 22 | 1.5 | 0 | 0 | 0 | 0 | 0 | 60 | 1438 | 1320 | 59.1781 | -8.0335 | -0.63389 | 1294.284 | 21.5608 | -143.4125 | -40.2649 | 0 | 78.225 | 258.225 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1625 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1439 | 23 | 1.2 | 0 | 0 | 0 | 0 | 0 | 60 | 1439 | 1380 | 59.1781 | -8.0335 | -0.63389 | 1354.284 | 22.5608 | -158.4125 | -47.0863 | 0 | 78.225 | 258.225 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2678 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
3 | 60 | 1 | 1440 | 24 | 0.8 | 0 | 0 | 0 | 0 | 0 | 60 | 1440 | 1440 | 59.1781 | -8.0335 | -0.63389 | 1414.284 | 23.5608 | -173.4125 | -50.8474 | 0 | 78.225 | 258.225 | 81.7033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5256 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1441 | 1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 61 | 1441 | 60 | 60.1644 | -7.6581 | -0.29022 | 34.284 | 0.56656 | 171.5016 | -50.2082 | 0 | 78.7792 | 101.2208 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4053 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1442 | 2 | -0.5 | 0 | 0 | 0 | 0 | 0 | 61 | 1442 | 120 | 60.1644 | -7.6581 | -0.29022 | 94.284 | 1.5666 | 156.5016 | -46.0166 | 0 | 78.7792 | 101.2208 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.19 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1443 | 3 | -1 | 0 | 0 | 0 | 0 | 0 | 61 | 1443 | 180 | 60.1644 | -7.6581 | -0.29022 | 154.284 | 2.5666 | 141.5016 | -38.9241 | 0 | 78.7792 | 101.2208 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5176 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1444 | 4 | -1.4 | 0 | 0 | 0 | 0 | 0 | 61 | 1444 | 240 | 60.1644 | -7.6581 | -0.29022 | 214.284 | 3.5666 | 126.5016 | -30.0556 | 0 | 78.7792 | 101.2208 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.1272 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1445 | 5 | -2.1 | 0 | 0 | 0 | 0 | 0 | 61 | 1445 | 300 | 60.1644 | -7.6581 | -0.29022 | 274.284 | 4.5666 | 111.5016 | -20.2353 | 0 | 78.7792 | 101.2208 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1873 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1446 | 6 | -2.2 | 0 | 0 | 0 | 0 | 0 | 61 | 1446 | 360 | 60.1644 | -7.6581 | -0.29022 | 334.284 | 5.5666 | 96.5016 | -10.0181 | 0 | 78.7792 | 101.2208 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1219 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1447 | 7 | -2.3 | 0 | 0 | 0 | 0 | 0 | 61 | 1447 | 420 | 60.1644 | -7.6581 | -0.29022 | 394.284 | 6.5666 | 81.5016 | 0.18304 | 0.18304 | 78.5805 | 101.4195 | 81.8214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 150.48 | 150.48 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1448 | 8 | -2.9 | 0.56 | 4.64 | 5.2 | 4.64 | 2.32 | 61 | 1448 | 480 | 60.1644 | -7.6581 | -0.29022 | 454.284 | 7.5666 | 66.5016 | 9.9922 | 9.9922 | 67.3524 | 112.6476 | 66.993 | 0 | 0 | 3.9605 | 3.9605 | -41.7852 | 0% | 1.7909 | 0 | 0 | 155.5463 | 155.5463 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1449 | 9 | -1.6 | 25.64 | 40.92 | 66.56 | 40.92 | 20.46 | 61 | 1449 | 540 | 60.1644 | -7.6581 | -0.29022 | 514.284 | 8.5666 | 51.5016 | 18.9892 | 18.9892 | 55.1133 | 124.8867 | 52.2288 | 48.2644 | 48.2644 | 34.9274 | 83.1918 | -1.1845 | 0% | 37.6193 | 0 | 0 | 141.2434 | 141.2434 | 0% | 12.2% | 12.2% | 80% | 9.763% | 3.6727 | 10.8355 | 6 | 22.0363 | 8.1219 | 15.6% | 15.6%
3 | 61 | 2 | 1450 | 10 | 0.9 | 80.36 | 132.31 | 212.67 | 132.31 | 66.16 | 61 | 1450 | 600 | 60.1644 | -7.6581 | -0.29022 | 574.284 | 9.5666 | 36.5016 | 26.6458 | 26.6458 | 41.2686 | 138.7314 | 37.6128 | 141.9423 | 141.9423 | 112.9336 | 254.876 | 0.17922 | 17.92% | 115.2549 | 20.6563 | 14.4594 | 129.1873 | 129.1873 | 11.19% | 11.92% | 11.92% | 80% | 9.54% | 10.995 | 9.9864 | 6 | 65.97 | 24.3145 | 51.07% | 51.07%
3 | 61 | 2 | 1451 | 11 | 3.4 | 131.11 | 149.25 | 280.36 | 149.25 | 74.63 | 61 | 1451 | 660 | 60.1644 | -7.6581 | -0.29022 | 634.284 | 10.5666 | 21.5016 | 32.3017 | 32.3017 | 25.4527 | 154.5473 | 23.4323 | 225.1171 | 225.1171 | 127.3928 | 352.51 | 0.36957 | 36.96% | 159.405 | 58.9116 | 41.2381 | 130.2067 | 130.2067 | 31.67% | 11.76% | 11.76% | 85% | 9.996% | 15.9349 | 9.181 | 6 | 95.6093 | 35.2386 | 73.43% | 73.43%
3 | 61 | 2 | 1452 | 12 | 4.3 | 126.03 | 205.75 | 331.78 | 205.75 | 102.88 | 61 | 1452 | 720 | 60.1644 | -7.6581 | -0.29022 | 694.284 | 11.5666 | 6.5016 | 35.2571 | 35.2571 | 7.8991 | 172.1009 | 11.45 | 213.9847 | 213.9847 | 175.6186 | 389.6034 | 0.41652 | 41.65% | 176.1786 | 73.3814 | 51.367 | 125.2554 | 125.2554 | 41.01% | 11.71% | 11.71% | 85% | 9.95% | 17.5305 | 8.9018 | 6 | 105.1831 | 38.7672 | 83.97% | 83.97%
3 | 61 | 2 | 1453 | 13 | 7.6 | 82.97 | 226.11 | 309.08 | 226.11 | 113.06 | 61 | 1453 | 780 | 60.1644 | -7.6581 | -0.29022 | 754.284 | 12.5666 | -8.4984 | 35.0407 | 35.0407 | 10.3051 | 190.3051 | 12.685 | 140.9801 | 140.9801 | 192.997 | 333.977 | 0.37559 | 37.56% | 151.0244 | 56.7228 | 39.706 | 126.7346 | 126.7346 | 31.33% | 11.67% | 11.67% | 85% | 9.919% | 14.9806 | 7.9264 | 6 | 89.8839 | 33.1284 | 70.92% | 70.92%
3 | 61 | 2 | 1454 | 14 | 9 | 24.72 | 187.86 | 212.58 | 187.86 | 93.93 | 61 | 1454 | 840 | 60.1644 | -7.6581 | -0.29022 | 814.284 | 13.5666 | -23.4984 | 31.6901 | 31.6901 | 27.6721 | 207.6721 | 25.2683 | 42.5542 | 42.5542 | 160.3485 | 202.9027 | 0.1151 | 11.51% | 91.7526 | 10.5609 | 7.3927 | 122.6452 | 122.6452 | 6.028% | 11.71% | 11.71% | 80% | 9.371% | 8.5978 | 7.5357 | 6 | 51.5866 | 19.0132 | 42.06% | 42.06%
3 | 61 | 2 | 1455 | 15 | 10.4 | 3.97 | 111.94 | 115.91 | 111.94 | 55.97 | 61 | 1455 | 900 | 60.1644 | -7.6581 | -0.29022 | 874.284 | 14.5666 | -38.4984 | 25.7264 | 25.7264 | 43.2217 | 223.2217 | 39.5439 | 7.0527 | 7.0527 | 95.5468 | 102.5995 | -0.52646 | 0% | 46.3955 | 0 | 0 | 159.1154 | 159.1154 | 0% | 11.72% | 11.72% | 80% | 9.376% | 4.3501 | 7.1587 | 6 | 26.1008 | 9.6199 | 16.4% | 16.4%
3 | 61 | 2 | 1456 | 16 | 11.5 | 3.06 | 84.44 | 87.5 | 84.44 | 42.22 | 61 | 1456 | 960 | 60.1644 | -7.6581 | -0.29022 | 934.284 | 15.5666 | -53.4984 | 17.8559 | 17.8559 | 56.8235 | 236.8235 | 54.1885 | 5.8393 | 5.8393 | 72.074 | 77.9133 | -0.91522 | 0% | 35.2324 | 0 | 0 | 157.1393 | 157.1393 | 0% | 11.69% | 11.69% | 80% | 9.352% | 3.2948 | 6.8721 | 6 | 19.7689 | 7.2862 | 12.58% | 12.58%
3 | 61 | 2 | 1457 | 17 | 11.7 | 1.11 | 37.14 | 38.25 | 37.14 | 18.57 | 61 | 1457 | 1020 | 60.1644 | -7.6581 | -0.29022 | 994.284 | 16.5666 | -68.4984 | 8.7232 | 8.7232 | 68.8916 | 248.8916 | 68.9644 | 0 | 0 | 31.701 | 31.701 | -3.4068 | 0% | 14.3352 | 0 | 0 | 152.6867 | 152.6867 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1458 | 18 | 11.2 | 0.36 | 18.25 | 18.61 | 18.25 | 9.13 | 61 | 1458 | 1080 | 60.1644 | -7.6581 | -0.29022 | 1054.284 | 17.5666 | -83.4984 | -1.1607 | 0 | 78.7792 | 258.7792 | 82.0912 | 0 | 0 | 15.5773 | 15.5773 | -7.8396 | 0% | 7.0441 | 0 | 0 | 148.2368 | 148.2368 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1459 | 19 | 9.4 | 0 | 2.08 | 2.08 | 2.08 | 1.04 | 61 | 1459 | 1140 | 60.1644 | -7.6581 | -0.29022 | 1114.284 | 18.5666 | -98.4984 | -11.3856 | 0 | 78.7792 | 258.7792 | 82.0912 | 0 | 0 | 1.7754 | 1.7754 | -77.399 | 0% | 0.80283 | 0 | 0 | 142.2376 | 142.2376 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1460 | 20 | 7 | 0 | 0 | 0 | 0 | 0 | 61 | 1460 | 1200 | 60.1644 | -7.6581 | -0.29022 | 1174.284 | 19.5666 | -113.4984 | -21.5757 | 0 | 78.7792 | 258.7792 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.3571 | 134.3571 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1461 | 21 | 3.6 | 0 | 0 | 0 | 0 | 0 | 61 | 1461 | 1260 | 60.1644 | -7.6581 | -0.29022 | 1234.284 | 20.5666 | -128.4984 | -31.3058 | 0 | 78.7792 | 258.7792 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7777 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1462 | 22 | 2.3 | 0 | 0 | 0 | 0 | 0 | 61 | 1462 | 1320 | 60.1644 | -7.6581 | -0.29022 | 1294.284 | 21.5666 | -143.4984 | -39.9927 | 0 | 78.7792 | 258.7792 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6606 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1463 | 23 | 1.6 | 0 | 0 | 0 | 0 | 0 | 61 | 1463 | 1380 | 60.1644 | -7.6581 | -0.29022 | 1354.284 | 22.5666 | -158.4984 | -46.7686 | 0 | 78.7792 | 258.7792 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.293 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
3 | 61 | 2 | 1464 | 24 | 0.7 | 0 | 0 | 0 | 0 | 0 | 61 | 1464 | 1440 | 60.1644 | -7.6581 | -0.29022 | 1414.284 | 23.5666 | -173.4984 | -50.4854 | 0 | 78.7792 | 258.7792 | 82.0912 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2301 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1465 | 1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 62 | 1465 | 60 | 61.1507 | -7.2804 | 0.059101 | 34.284 | 0.57239 | 171.4142 | -49.8215 | 0 | 79.3361 | 100.6639 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.566 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1466 | 2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 62 | 1466 | 120 | 61.1507 | -7.2804 | 0.059101 | 94.284 | 1.5724 | 156.4142 | -45.6353 | 0 | 79.3361 | 100.6639 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4287 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1467 | 3 | -0.2 | 0 | 0 | 0 | 0 | 0 | 62 | 1467 | 180 | 61.1507 | -7.2804 | 0.059101 | 154.284 | 2.5724 | 141.4142 | -38.5606 | 0 | 79.3361 | 100.6639 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4626 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1468 | 4 | -0.7 | 0 | 0 | 0 | 0 | 0 | 62 | 1468 | 240 | 61.1507 | -7.2804 | 0.059101 | 214.284 | 3.5724 | 126.4142 | -29.7089 | 0 | 79.3361 | 100.6639 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2246 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1469 | 5 | -0.6 | 0 | 0 | 0 | 0 | 0 | 62 | 1469 | 300 | 61.1507 | -7.2804 | 0.059101 | 274.284 | 4.5724 | 111.4142 | -19.8991 | 0 | 79.3361 | 100.6639 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4425 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1470 | 6 | -1.6 | 0 | 0 | 0 | 0 | 0 | 62 | 1470 | 360 | 61.1507 | -7.2804 | 0.059101 | 334.284 | 5.5724 | 96.4142 | -9.6852 | 0 | 79.3361 | 100.6639 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.3974 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1471 | 7 | -1.2 | 0 | 0 | 0 | 0 | 0 | 62 | 1471 | 420 | 61.1507 | -7.2804 | 0.059101 | 394.284 | 6.5724 | 81.4142 | 0.51958 | 0.51958 | 78.7726 | 101.2274 | 81.7158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 162.2821 | 162.2821 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1472 | 8 | -1.2 | 0.36 | 2.78 | 3.14 | 2.78 | 1.39 | 62 | 1472 | 480 | 61.1507 | -7.2804 | 0.059101 | 454.284 | 7.5724 | 66.4142 | 10.3383 | 10.3383 | 67.5294 | 112.4706 | 66.8729 | 0.78791 | 0.78791 | 2.3729 | 3.1608 | -51.2178 | 0% | 1.4293 | 0 | 0 | 170.2028 | 170.2028 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1473 | 9 | 1.3 | 26.75 | 23.69 | 50.44 | 23.69 | 11.85 | 62 | 1473 | 540 | 61.1507 | -7.2804 | 0.059101 | 514.284 | 8.5724 | 51.4142 | 19.3494 | 19.3494 | 55.2646 | 124.7354 | 52.0897 | 49.6063 | 49.6063 | 20.2207 | 69.8269 | -1.4624 | 0% | 31.5757 | 0 | 0 | 157.39 | 157.39 | 0% | 12.1% | 12.1% | 80% | 9.682% | 3.0573 | 9.8546 | 6 | 18.3437 | 6.7609 | 11.65% | 11.65%
3 | 62 | 3 | 1474 | 10 | 3.6 | 139.25 | 39.44 | 178.69 | 39.44 | 19.72 | 62 | 1474 | 600 | 61.1507 | -7.2804 | 0.059101 | 574.284 | 9.5724 | 36.4142 | 27.0214 | 27.0214 | 41.3753 | 138.6247 | 37.4445 | 243.343 | 243.343 | 33.6641 | 277.0071 | 0.25291 | 25.29% | 125.2626 | 31.6801 | 22.1761 | 165.5449 | 165.5449 | 13.4% | 11.82% | 11.82% | 80% | 9.459% | 11.8486 | 9.1184 | 6 | 71.0915 | 26.2021 | 42.94% | 42.94%
3 | 62 | 3 | 1475 | 11 | 5.8 | 252.58 | 42.5 | 295.08 | 42.5 | 21.25 | 62 | 1475 | 660 | 61.1507 | -7.2804 | 0.059101 | 634.284 | 10.5724 | 21.4142 | 32.688 | 32.688 | 25.4876 | 154.5124 | 23.2076 | 429.8411 | 429.8411 | 36.276 | 466.1171 | 0.48785 | 48.79% | 210.7781 | 102.8282 | 71.9798 | 145.211 | 145.211 | 49.57% | 11.61% | 11.61% | 85% | 9.871% | 20.8056 | 8.449 | 6 | 124.8335 | 46.0097 | 85.97% | 85.97%
3 | 62 | 3 | 1476 | 12 | 7.4 | 265.83 | 92.58 | 358.41 | 92.58 | 46.29 | 62 | 1476 | 720 | 61.1507 | -7.2804 | 0.059101 | 694.284 | 11.5724 | 6.4142 | 35.6413 | 35.6413 | 7.8371 | 172.1629 | 11.0912 | 447.6766 | 447.6766 | 79.022 | 526.6986 | 0.53145 | 53.14% | 238.1731 | 126.5762 | 88.6033 | 138.3494 | 138.3494 | 64.04% | 11.54% | 11.54% | 90% | 10.39% | 24.7397 | 7.9834 | 6 | 148.4379 | 54.7095 | 107.3% | 107.3%
3 | 62 | 3 | 1477 | 13 | 10.1 | 178.69 | 136.47 | 315.16 | 136.47 | 68.24 | 62 | 1477 | 780 | 61.1507 | -7.2804 | 0.059101 | 754.284 | 12.5724 | -8.5858 | 35.4047 | 35.4047 | 10.4678 | 190.4678 | 12.4678 | 301.1594 | 301.1594 | 116.4844 | 417.6438 | 0.47548 | 47.55% | 188.8585 | 89.7986 | 62.859 | 137.1837 | 137.1837 | 45.82% | 11.56% | 11.56% | 85% | 9.826% | 18.5576 | 7.2383 | 6 | 111.3453 | 41.0384 | 81.17% | 81.17%
3 | 62 | 3 | 1478 | 14 | 12.8 | 291.86 | 136.31 | 428.17 | 136.31 | 68.16 | 62 | 1478 | 840 | 61.1507 | -7.2804 | 0.059101 | 814.284 | 13.5724 | -23.5858 | 32.0198 | 32.0198 | 27.9118 | 207.9118 | 25.2166 | 498.0018 | 498.0018 | 116.3479 | 614.3496 | 0.59084 | 59.08% | 277.8089 | 164.1418 | 114.8993 | 143.3968 | 143.3968 | 80.13% | 11.43% | 11.43% | 90% | 10.28% | 28.567 | 6.5443 | 6 | 171.402 | 63.1734 | 119.5% | 119.5%
3 | 62 | 3 | 1479 | 15 | 14 | 159.64 | 167.42 | 327.06 | 167.42 | 83.71 | 62 | 1479 | 900 | 61.1507 | -7.2804 | 0.059101 | 874.284 | 14.5724 | -38.5858 | 26.0179 | 26.0179 | 43.5055 | 223.5055 | 39.5501 | 280.6177 | 280.6177 | 142.9019 | 423.5196 | 0.50129 | 50.13% | 191.5156 | 96.0044 | 67.203 | 137.4686 | 137.4686 | 48.89% | 11.48% | 11.48% | 85% | 9.755% | 18.682 | 6.2522 | 6 | 112.0918 | 41.3135 | 81.54% | 81.54%
3 | 62 | 3 | 1480 | 16 | 14.3 | 82.31 | 167.03 | 249.34 | 167.03 | 83.52 | 62 | 1480 | 960 | 61.1507 | -7.2804 | 0.059101 | 934.284 | 15.5724 | -53.5858 | 18.1137 | 18.1137 | 57.1276 | 237.1276 | 54.224 | 154.7744 | 154.7744 | 142.569 | 297.3434 | 0.37513 | 37.51% | 134.4587 | 50.4398 | 35.3079 | 131.7474 | 131.7474 | 26.8% | 11.51% | 11.51% | 80% | 9.208% | 12.3805 | 6.1808 | 6 | 74.283 | 27.3784 | 56.38% | 56.38%
3 | 62 | 3 | 1481 | 17 | 14.7 | 28.53 | 110.28 | 138.81 | 110.28 | 55.14 | 62 | 1481 | 1020 | 61.1507 | -7.2804 | 0.059101 | 994.284 | 16.5724 | -68.5858 | 8.9559 | 8.9559 | 69.2051 | 249.2051 | 69.019 | 0 | 0 | 94.1299 | 94.1299 | -0.54107 | 0% | 42.5655 | 0 | 0 | 165.6104 | 165.6104 | 0% | 11.56% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1482 | 18 | 14.3 | 31.11 | 40.56 | 71.67 | 40.56 | 20.28 | 62 | 1482 | 1080 | 61.1507 | -7.2804 | 0.059101 | 1054.284 | 17.5724 | -83.5858 | -0.94291 | 0 | 79.3361 | 259.3361 | 82.4814 | 0 | 0 | 34.6201 | 34.6201 | -2.8794 | 0% | 15.6552 | 0 | 0 | 158.274 | 158.274 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1483 | 19 | 12.8 | 0 | 5.19 | 5.19 | 5.19 | 2.6 | 62 | 1483 | 1140 | 61.1507 | -7.2804 | 0.059101 | 1114.284 | 18.5724 | -98.5858 | -11.1722 | 0 | 79.3361 | 259.3361 | 82.4814 | 0 | 0 | 4.4299 | 4.4299 | -28.7567 | 0% | 2.0032 | 0 | 0 | 148.0814 | 148.0814 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1484 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 62 | 1484 | 1200 | 61.1507 | -7.2804 | 0.059101 | 1174.284 | 19.5724 | -113.5858 | -21.3553 | 0 | 79.3361 | 259.3361 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.8789 | 140.8789 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1485 | 21 | 11.5 | 0 | 0 | 0 | 0 | 0 | 62 | 1485 | 1260 | 61.1507 | -7.2804 | 0.059101 | 1234.284 | 20.5724 | -128.5858 | -31.0656 | 0 | 79.3361 | 259.3361 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2355 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1486 | 22 | 9.9 | 0 | 0 | 0 | 0 | 0 | 62 | 1486 | 1320 | 61.1507 | -7.2804 | 0.059101 | 1294.284 | 21.5724 | -143.5858 | -39.7184 | 0 | 79.3361 | 259.3361 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9488 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1487 | 23 | 6.7 | 0 | 0 | 0 | 0 | 0 | 62 | 1487 | 1380 | 61.1507 | -7.2804 | 0.059101 | 1354.284 | 22.5724 | -158.5858 | -46.4485 | 0 | 79.3361 | 259.3361 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2499 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
3 | 62 | 3 | 1488 | 24 | 5.8 | 0 | 0 | 0 | 0 | 0 | 62 | 1488 | 1440 | 61.1507 | -7.2804 | 0.059101 | 1414.284 | 23.5724 | -173.5858 | -50.1209 | 0 | 79.3361 | 259.3361 | 82.4814 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0458 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1489 | 1 | 5.8 | 0 | 0 | 0 | 0 | 0 | 63 | 1489 | 60 | 62.137 | -6.9005 | 0.41368 | 34.284 | 0.57829 | 171.3256 | -49.4325 | 0 | 79.8958 | 100.1042 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3704 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1490 | 2 | 5.6 | 0 | 0 | 0 | 0 | 0 | 63 | 1490 | 120 | 62.137 | -6.9005 | 0.41368 | 94.284 | 1.5783 | 156.3256 | -45.2512 | 0 | 79.8958 | 100.1042 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5872 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1491 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 63 | 1491 | 180 | 62.137 | -6.9005 | 0.41368 | 154.284 | 2.5783 | 141.3256 | -38.1942 | 0 | 79.8958 | 100.1042 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9377 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1492 | 4 | 2.4 | 0 | 0 | 0 | 0 | 0 | 63 | 1492 | 240 | 62.137 | -6.9005 | 0.41368 | 214.284 | 3.5783 | 126.3256 | -29.3593 | 0 | 79.8958 | 100.1042 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3761 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1493 | 5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 63 | 1493 | 300 | 62.137 | -6.9005 | 0.41368 | 274.284 | 4.5783 | 111.3256 | -19.5601 | 0 | 79.8958 | 100.1042 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4885 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1494 | 6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 63 | 1494 | 360 | 62.137 | -6.9005 | 0.41368 | 334.284 | 5.5783 | 96.3256 | -9.3495 | 0 | 79.8958 | 100.1042 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6129 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1495 | 7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 63 | 1495 | 420 | 62.137 | -6.9005 | 0.41368 | 394.284 | 6.5783 | 81.3256 | 0.85869 | 0.85869 | 78.9651 | 101.0349 | 81.609 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.3765 | 134.3765 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1496 | 8 | 1.3 | 0 | 3.53 | 3.53 | 3.53 | 1.77 | 63 | 1496 | 480 | 62.137 | -6.9005 | 0.41368 | 454.284 | 7.5783 | 66.3256 | 10.6869 | 10.6869 | 67.707 | 112.293 | 66.7521 | 0 | 0 | 3.013 | 3.013 | -51.7207 | 0% | 1.3625 | 0 | 0 | 136.3625 | 136.3625 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1497 | 9 | 1.3 | 1.94 | 39.25 | 41.19 | 39.25 | 19.63 | 63 | 1497 | 540 | 62.137 | -6.9005 | 0.41368 | 514.284 | 8.5783 | 51.3256 | 19.7121 | 19.7121 | 55.4165 | 124.5835 | 51.9506 | 3.545 | 3.545 | 33.502 | 37.047 | -3.4679 | 0% | 16.7526 | 0 | 0 | 117.9666 | 117.9666 | 0% | 12.14% | 12.14% | 80% | 9.709% | 1.6266 | 9.8546 | 6 | 9.7594 | 3.597 | 8.273% | 8.273%
3 | 63 | 4 | 1498 | 10 | 2.8 | 5.36 | 85 | 90.36 | 85 | 42.5 | 63 | 1498 | 600 | 62.137 | -6.9005 | 0.41368 | 574.284 | 9.5783 | 36.3256 | 27.3996 | 27.3996 | 41.4824 | 138.5176 | 37.2772 | 9.2679 | 9.2679 | 72.552 | 81.82 | -1.0855 | 0% | 36.999 | 0 | 0 | 123.3406 | 123.3406 | 0% | 12.03% | 12.03% | 80% | 9.625% | 3.5612 | 9.3703 | 6 | 21.3672 | 7.8753 | 17.32% | 17.32%
3 | 63 | 4 | 1499 | 11 | 5.3 | 7.5 | 123.69 | 131.19 | 123.69 | 61.85 | 63 | 1499 | 660 | 62.137 | -6.9005 | 0.41368 | 634.284 | 10.5783 | 21.3256 | 33.0769 | 33.0769 | 25.522 | 154.478 | 22.9848 | 12.6512 | 12.6512 | 105.576 | 118.2272 | -0.45256 | 0% | 53.4623 | 0 | 0 | 128.0576 | 128.0576 | 0% | 11.9% | 11.9% | 80% | 9.523% | 5.091 | 8.5982 | 6 | 30.5459 | 11.2583 | 23.85% | 23.85%
3 | 63 | 4 | 1500 | 12 | 6.5 | 13.97 | 152.58 | 166.55 | 152.58 | 76.29 | 63 | 1500 | 720 | 62.137 | -6.9005 | 0.41368 | 694.284 | 11.5783 | 6.3256 | 36.0277 | 36.0277 | 7.773 | 172.227 | 10.7318 | 23.3359 | 23.3359 | 130.2352 | 153.5711 | -0.14469 | 0% | 69.4449 | 0 | 0 | 129.4713 | 129.4713 | 0% | 11.83% | 11.83% | 80% | 9.466% | 6.5734 | 8.2431 | 6 | 39.4401 | 14.5364 | 30.46% | 30.46%
3 | 63 | 4 | 1501 | 13 | 8.2 | 50.56 | 176.86 | 227.42 | 176.86 | 88.43 | 63 | 1501 | 780 | 62.137 | -6.9005 | 0.41368 | 754.284 | 12.5783 | -8.6744 | 35.7704 | 35.7704 | 10.6341 | 190.6341 | 12.2583 | 84.5235 | 84.5235 | 150.9595 | 235.4829 | 0.20242 | 20.24% | 106.4854 | 21.5546 | 15.0882 | 113.8141 | 113.8141 | 13.26% | 11.72% | 11.72% | 80% | 9.375% | 9.9827 | 7.7573 | 6 | 59.8961 | 22.0758 | 52.63% | 52.63%
3 | 63 | 4 | 1502 | 14 | 8 | 114.36 | 106.58 | 220.94 | 106.58 | 53.29 | 63 | 1502 | 840 | 62.137 | -6.9005 | 0.41368 | 814.284 | 13.5783 | -23.6744 | 32.3507 | 32.3507 | 28.1557 | 208.1557 | 25.171 | 193.4232 | 193.4232 | 90.9717 | 284.3949 | 0.30422 | 30.42% | 128.6034 | 39.124 | 27.3868 | 112.5978 | 112.5978 | 24.32% | 11.69% | 11.69% | 80% | 9.354% | 12.0294 | 7.8134 | 6 | 72.1761 | 26.6018 | 64.1% | 64.1%
3 | 63 | 4 | 1503 | 15 | 9.1 | 140.36 | 103.81 | 244.17 | 103.81 | 51.91 | 63 | 1503 | 900 | 62.137 | -6.9005 | 0.41368 | 874.284 | 14.5783 | -38.6744 | 26.31 | 26.31 | 43.7933 | 223.7933 | 39.5604 | 244.1433 | 244.1433 | 88.6074 | 332.7507 | 0.38463 | 38.46% | 150.4699 | 57.8758 | 40.513 | 114.3436 | 114.3436 | 35.43% | 11.63% | 11.63% | 85% | 9.887% | 14.8774 | 7.5083 | 6 | 89.2644 | 32.9001 | 78.07% | 78.07%
3 | 63 | 4 | 1504 | 16 | 9 | 98.89 | 100 | 198.89 | 100 | 50 | 63 | 1504 | 960 | 62.137 | -6.9005 | 0.41368 | 934.284 | 15.5783 | -53.6744 | 18.3719 | 18.3719 | 57.4353 | 237.4353 | 54.2626 | 183.2543 | 183.2543 | 85.3553 | 268.6097 | 0.28362 | 28.36% | 121.4653 | 34.4499 | 24.115 | 111.8779 | 111.8779 | 21.55% | 11.67% | 11.67% | 80% | 9.339% | 11.3434 | 7.5357 | 6 | 68.0604 | 25.0849 | 60.83% | 60.83%
3 | 63 | 4 | 1505 | 17 | 8.8 | 55.56 | 75.56 | 131.12 | 75.56 | 37.78 | 63 | 1505 | 1020 | 62.137 | -6.9005 | 0.41368 | 994.284 | 16.5783 | -68.6744 | 9.1892 | 9.1892 | 69.5215 | 249.5215 | 69.0759 | 0 | 0 | 64.4945 | 64.4945 | -1.3706 | 0% | 29.1644 | 0 | 0 | 149.27 | 149.27 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1506 | 18 | 7.6 | 15.75 | 44.72 | 60.47 | 44.72 | 22.36 | 63 | 1506 | 1080 | 62.137 | -6.9005 | 0.41368 | 1054.284 | 17.5783 | -83.6744 | -0.72448 | 0 | 79.8958 | 259.8958 | 82.8739 | 0 | 0 | 38.1709 | 38.1709 | -2.9444 | 0% | 17.2609 | 0 | 0 | 142.1241 | 142.1241 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1507 | 19 | 5.5 | 0 | 7.03 | 7.03 | 7.03 | 3.52 | 63 | 1507 | 1140 | 62.137 | -6.9005 | 0.41368 | 1114.284 | 18.5783 | -98.6744 | -10.9579 | 0 | 79.8958 | 259.8958 | 82.8739 | 0 | 0 | 6.0005 | 6.0005 | -23.8741 | 0% | 2.7134 | 0 | 0 | 133.5609 | 133.5609 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1508 | 20 | 3.8 | 0 | 0 | 0 | 0 | 0 | 63 | 1508 | 1200 | 62.137 | -6.9005 | 0.41368 | 1174.284 | 19.5783 | -113.6744 | -21.1336 | 0 | 79.8958 | 259.8958 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.7287 | 127.7287 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1509 | 21 | 2.1 | 0 | 0 | 0 | 0 | 0 | 63 | 1509 | 1260 | 62.137 | -6.9005 | 0.41368 | 1234.284 | 20.5783 | -128.6744 | -30.8235 | 0 | 79.8958 | 259.8958 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6041 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1510 | 22 | 1.4 | 0 | 0 | 0 | 0 | 0 | 63 | 1510 | 1320 | 62.137 | -6.9005 | 0.41368 | 1294.284 | 21.5783 | -143.6744 | -39.4418 | 0 | 79.8958 | 259.8958 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3397 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1511 | 23 | 0.5 | 0 | 0 | 0 | 0 | 0 | 63 | 1511 | 1380 | 62.137 | -6.9005 | 0.41368 | 1354.284 | 22.5783 | -158.6744 | -46.126 | 0 | 79.8958 | 259.8958 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6233 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 63 | 4 | 1512 | 24 | 0.7 | 0 | 0 | 0 | 0 | 0 | 63 | 1512 | 1440 | 62.137 | -6.9005 | 0.41368 | 1414.284 | 23.5783 | -173.6744 | -49.754 | 0 | 79.8958 | 259.8958 | 82.8739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2306 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1513 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 64 | 1513 | 60 | 63.1233 | -6.5185 | 0.77314 | 34.284 | 0.58429 | 171.2357 | -49.0412 | 0 | 80.458 | 99.542 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3914 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1514 | 2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 64 | 1514 | 120 | 63.1233 | -6.5185 | 0.77314 | 94.284 | 1.5843 | 156.2357 | -44.8647 | 0 | 80.458 | 99.542 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0464 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1515 | 3 | -0.9 | 0 | 0 | 0 | 0 | 0 | 64 | 1515 | 180 | 63.1233 | -6.5185 | 0.77314 | 154.284 | 2.5843 | 141.2357 | -37.8251 | 0 | 80.458 | 99.542 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4635 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1516 | 4 | -0.9 | 0 | 0 | 0 | 0 | 0 | 64 | 1516 | 240 | 63.1233 | -6.5185 | 0.77314 | 214.284 | 3.5843 | 126.2357 | -29.007 | 0 | 80.458 | 99.542 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4635 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1517 | 5 | -1.7 | 0 | 0 | 0 | 0 | 0 | 64 | 1517 | 300 | 63.1233 | -6.5185 | 0.77314 | 274.284 | 4.5843 | 111.2357 | -19.2184 | 0 | 80.458 | 99.542 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0473 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1518 | 6 | -1.7 | 0 | 0 | 0 | 0 | 0 | 64 | 1518 | 360 | 63.1233 | -6.5185 | 0.77314 | 334.284 | 5.5843 | 96.2357 | -9.0113 | 0 | 80.458 | 99.542 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2476 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1519 | 7 | -0.9 | 0 | 0 | 0 | 0 | 0 | 64 | 1519 | 420 | 63.1233 | -6.5185 | 0.77314 | 394.284 | 6.5843 | 81.2357 | 1.2002 | 1.2002 | 79.158 | 100.842 | 81.5012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.1266 | 134.1266 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1520 | 8 | -0.8 | 0.08 | 2.78 | 2.86 | 2.78 | 1.39 | 64 | 1520 | 480 | 63.1233 | -6.5185 | 0.77314 | 454.284 | 7.5843 | 66.2357 | 11.0379 | 11.0379 | 67.8854 | 112.1146 | 66.6308 | 0.16574 | 0.16574 | 2.3729 | 2.5386 | -63.5763 | 0% | 1.148 | 0 | 0 | 137.9347 | 137.9347 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1521 | 9 | 1.3 | 1.47 | 37.86 | 39.33 | 37.86 | 18.93 | 64 | 1521 | 540 | 63.1233 | -6.5185 | 0.77314 | 514.284 | 8.5843 | 51.2357 | 20.0771 | 20.0771 | 55.5693 | 124.4307 | 51.8117 | 2.6474 | 2.6474 | 32.3155 | 34.963 | -3.7225 | 0% | 15.8103 | 0 | 0 | 122.8056 | 122.8056 | 0% | 12.14% | 12.14% | 80% | 9.711% | 1.5353 | 9.8546 | 6 | 9.2121 | 3.3953 | 7.501% | 7.501%
3 | 64 | 5 | 1522 | 10 | 4.7 | 4.08 | 80.28 | 84.36 | 80.28 | 40.14 | 64 | 1522 | 600 | 63.1233 | -6.5185 | 0.77314 | 574.284 | 9.5843 | 36.2357 | 27.7801 | 27.7801 | 41.5899 | 138.4101 | 37.1109 | 6.9809 | 6.9809 | 68.5233 | 75.5042 | -1.1827 | 0% | 34.143 | 0 | 0 | 130.9786 | 130.9786 | 0% | 11.96% | 11.96% | 80% | 9.569% | 3.2673 | 8.7795 | 6 | 19.6035 | 7.2252 | 14.97% | 14.97%
3 | 64 | 5 | 1523 | 11 | 5.9 | 8.25 | 141.31 | 149.56 | 141.31 | 70.66 | 64 | 1523 | 660 | 63.1233 | -6.5185 | 0.77314 | 634.284 | 10.5843 | 21.2357 | 33.4682 | 33.4682 | 25.5559 | 154.4441 | 22.7643 | 13.7946 | 13.7946 | 120.6156 | 134.4102 | -0.29059 | 0% | 60.7803 | 0 | 0 | 134.5331 | 134.5331 | 0% | 11.87% | 11.87% | 80% | 9.495% | 5.7708 | 8.4194 | 6 | 34.6248 | 12.7616 | 25.74% | 25.74%
3 | 64 | 5 | 1524 | 12 | 6.4 | 24.17 | 229.17 | 253.34 | 229.17 | 114.59 | 64 | 1524 | 720 | 63.1233 | -6.5185 | 0.77314 | 694.284 | 11.5843 | 6.2357 | 36.4163 | 36.4163 | 7.7068 | 172.2932 | 10.3721 | 40.049 | 40.049 | 195.6088 | 235.6579 | 0.18475 | 18.48% | 106.5645 | 19.6881 | 13.7817 | 116.4578 | 116.4578 | 11.83% | 11.77% | 11.77% | 80% | 9.419% | 10.0376 | 8.2723 | 6 | 60.2258 | 22.1973 | 51.71% | 51.71%
3 | 64 | 5 | 1525 | 13 | 6.1 | 15.69 | 213.75 | 229.44 | 213.75 | 106.88 | 64 | 1525 | 780 | 63.1233 | -6.5185 | 0.77314 | 754.284 | 12.5843 | -8.7643 | 36.1378 | 36.1378 | 10.804 | 190.804 | 12.0573 | 26.0185 | 26.0185 | 182.447 | 208.4655 | 0.10055 | 10.05% | 94.2681 | 9.4783 | 6.6348 | 115.1327 | 115.1327 | 5.763% | 11.8% | 11.8% | 80% | 9.443% | 8.9021 | 8.3603 | 6 | 53.4126 | 19.6862 | 46.39% | 46.39%
3 | 64 | 5 | 1526 | 14 | 7.4 | 160 | 143.14 | 303.14 | 143.14 | 71.57 | 64 | 1526 | 840 | 63.1233 | -6.5185 | 0.77314 | 814.284 | 13.5843 | -23.7643 | 32.6825 | 32.6825 | 28.4038 | 208.4038 | 25.1317 | 268.2553 | 268.2553 | 122.1776 | 390.433 | 0.43632 | 43.63% | 176.5538 | 77.0342 | 53.924 | 119.6261 | 119.6261 | 45.08% | 11.64% | 11.64% | 85% | 9.89% | 17.462 | 7.9834 | 6 | 104.7718 | 38.6156 | 87.58% | 87.58%
3 | 64 | 5 | 1527 | 15 | 7.7 | 163.53 | 86.58 | 250.11 | 86.58 | 43.29 | 64 | 1527 | 900 | 63.1233 | -6.5185 | 0.77314 | 874.284 | 14.5843 | -38.7643 | 26.6027 | 26.6027 | 44.085 | 224.085 | 39.5749 | 281.4813 | 281.4813 | 73.9007 | 355.3819 | 0.40206 | 40.21% | 160.7037 | 64.612 | 45.2284 | 116.5816 | 116.5816 | 38.8% | 11.65% | 11.65% | 85% | 9.905% | 15.9175 | 7.8981 | 6 | 95.5049 | 35.2001 | 81.92% | 81.92%
3 | 64 | 5 | 1528 | 16 | 8 | 131.31 | 73.97 | 205.28 | 73.97 | 36.99 | 64 | 1528 | 960 | 63.1233 | -6.5185 | 0.77314 | 934.284 | 15.5843 | -53.7643 | 18.6305 | 18.6305 | 57.7463 | 237.7463 | 54.3042 | 239.8297 | 239.8297 | 63.1373 | 302.967 | 0.33486 | 33.49% | 137.0017 | 45.8762 | 32.1134 | 114.7706 | 114.7706 | 27.98% | 11.68% | 11.68% | 85% | 9.928% | 13.6016 | 7.8134 | 6 | 81.6094 | 30.0787 | 71.11% | 71.11%
3 | 64 | 5 | 1529 | 17 | 8.7 | 84.36 | 66.11 | 150.47 | 66.11 | 33.06 | 64 | 1529 | 1020 | 63.1233 | -6.5185 | 0.77314 | 994.284 | 16.5843 | -68.7643 | 9.4228 | 9.4228 | 69.8408 | 249.8408 | 69.1349 | 0 | 0 | 56.4284 | 56.4284 | -1.6856 | 0% | 25.5169 | 0 | 0 | 112.0338 | 112.0338 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1530 | 18 | 8.2 | 32.86 | 29.81 | 62.67 | 29.81 | 14.91 | 64 | 1530 | 1080 | 63.1233 | -6.5185 | 0.77314 | 1054.284 | 17.5843 | -83.7643 | -0.50543 | 0 | 80.458 | 260.458 | 83.2685 | 0 | 0 | 25.4444 | 25.4444 | -4.7635 | 0% | 11.506 | 0 | 0 | 146.7864 | 146.7864 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1531 | 19 | 6.5 | 0 | 4.81 | 4.81 | 4.81 | 2.41 | 64 | 1531 | 1140 | 63.1233 | -6.5185 | 0.77314 | 1114.284 | 18.5843 | -98.7643 | -10.7427 | 0 | 80.458 | 260.458 | 83.2685 | 0 | 0 | 4.1056 | 4.1056 | -34.6823 | 0% | 1.8565 | 0 | 0 | 137.2668 | 137.2668 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1532 | 20 | 4.6 | 0 | 0 | 0 | 0 | 0 | 64 | 1532 | 1200 | 63.1233 | -6.5185 | 0.77314 | 1174.284 | 19.5843 | -113.7643 | -20.9105 | 0 | 80.458 | 260.458 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.2615 | 130.2615 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1533 | 21 | 3.6 | 0 | 0 | 0 | 0 | 0 | 64 | 1533 | 1260 | 63.1233 | -6.5185 | 0.77314 | 1234.284 | 20.5843 | -128.7643 | -30.5797 | 0 | 80.458 | 260.458 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2523 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1534 | 22 | 2.6 | 0 | 0 | 0 | 0 | 0 | 64 | 1534 | 1320 | 63.1233 | -6.5185 | 0.77314 | 1294.284 | 21.5843 | -143.7643 | -39.1631 | 0 | 80.458 | 260.458 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6642 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1535 | 23 | 2.4 | 0 | 0 | 0 | 0 | 0 | 64 | 1535 | 1380 | 63.1233 | -6.5185 | 0.77314 | 1354.284 | 22.5843 | -158.7643 | -45.8012 | 0 | 80.458 | 260.458 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8621 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 64 | 5 | 1536 | 24 | 2.4 | 0 | 0 | 0 | 0 | 0 | 64 | 1536 | 1440 | 63.1233 | -6.5185 | 0.77314 | 1414.284 | 23.5843 | -173.7643 | -49.3849 | 0 | 80.458 | 260.458 | 83.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7551 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1537 | 1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 65 | 1537 | 60 | 64.1096 | -6.1345 | 1.1371 | 34.284 | 0.59035 | 171.1447 | -48.6477 | 0 | 81.0226 | 98.9774 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5939 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1538 | 2 | 2.3 | 0 | 0 | 0 | 0 | 0 | 65 | 1538 | 120 | 64.1096 | -6.1345 | 1.1371 | 94.284 | 1.5904 | 156.1447 | -44.4758 | 0 | 81.0226 | 98.9774 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4247 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1539 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 65 | 1539 | 180 | 64.1096 | -6.1345 | 1.1371 | 154.284 | 2.5904 | 141.1447 | -37.4534 | 0 | 81.0226 | 98.9774 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0843 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1540 | 4 | 0.3 | 0 | 0 | 0 | 0 | 0 | 65 | 1540 | 240 | 64.1096 | -6.1345 | 1.1371 | 214.284 | 3.5904 | 126.1447 | -28.652 | 0 | 81.0226 | 98.9774 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1511 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1541 | 5 | -0.1 | 0 | 0 | 0 | 0 | 0 | 65 | 1541 | 300 | 64.1096 | -6.1345 | 1.1371 | 274.284 | 4.5904 | 111.1447 | -18.8742 | 0 | 81.0226 | 98.9774 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8734 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1542 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1542 | 360 | 64.1096 | -6.1345 | 1.1371 | 334.284 | 5.5904 | 96.1447 | -8.6708 | 0 | 81.0226 | 98.9774 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1967 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1543 | 7 | -0.7 | 0 | 0 | 0 | 0 | 0 | 65 | 1543 | 420 | 64.1096 | -6.1345 | 1.1371 | 394.284 | 6.5904 | 81.1447 | 1.5441 | 1.5441 | 79.3515 | 100.6485 | 81.3923 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.0281 | 148.0281 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1544 | 8 | -0.4 | 0.47 | 4.72 | 5.19 | 4.72 | 2.36 | 65 | 1544 | 480 | 64.1096 | -6.1345 | 1.1371 | 454.284 | 7.5904 | 66.1447 | 11.3911 | 11.3911 | 68.0645 | 111.9355 | 66.5092 | 0.94855 | 0.94855 | 4.0288 | 4.9773 | -31.8333 | 0% | 2.2507 | 0 | 0 | 154.3056 | 154.3056 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1545 | 9 | 2.3 | 24.25 | 42.31 | 66.56 | 42.31 | 21.16 | 65 | 1545 | 540 | 64.1096 | -6.1345 | 1.1371 | 514.284 | 8.5904 | 51.1447 | 20.4444 | 20.4444 | 55.7228 | 124.2772 | 51.6731 | 43.0537 | 43.0537 | 36.1138 | 79.1676 | -1.1642 | 0% | 35.7996 | 0 | 0 | 142.1469 | 142.1469 | 0% | 12.05% | 12.05% | 80% | 9.643% | 3.4521 | 9.53 | 6 | 20.7129 | 7.6341 | 14.57% | 14.57%
3 | 65 | 6 | 1546 | 10 | 4.6 | 74.64 | 108.25 | 182.89 | 108.25 | 54.13 | 65 | 1546 | 600 | 64.1096 | -6.1345 | 1.1371 | 574.284 | 9.5904 | 36.1447 | 28.1629 | 28.1629 | 41.6979 | 138.3021 | 36.9459 | 126.388 | 126.388 | 92.3972 | 218.7851 | 0.11729 | 11.73% | 98.9346 | 11.6041 | 8.1229 | 150.7491 | 150.7491 | 5.388% | 11.84% | 11.84% | 80% | 9.475% | 9.3745 | 8.8099 | 6 | 56.2469 | 20.7308 | 37.31% | 37.31%
3 | 65 | 6 | 1547 | 11 | 5.5 | 109.36 | 151.94 | 261.3 | 151.94 | 75.97 | 65 | 1547 | 660 | 64.1096 | -6.1345 | 1.1371 | 634.284 | 10.5904 | 21.1447 | 33.8617 | 33.8617 | 25.5894 | 154.4106 | 22.5464 | 181.2696 | 181.2696 | 129.6889 | 310.9585 | 0.32779 | 32.78% | 140.6154 | 46.0927 | 32.2649 | 130.2248 | 130.2248 | 24.78% | 11.74% | 11.74% | 85% | 9.981% | 14.0344 | 8.5383 | 6 | 84.2065 | 31.0359 | 64.66% | 64.66%
3 | 65 | 6 | 1548 | 12 | 6.8 | 65.75 | 173.33 | 239.08 | 173.33 | 86.67 | 65 | 1548 | 720 | 64.1096 | -6.1345 | 1.1371 | 694.284 | 11.5904 | 6.1447 | 36.807 | 36.807 | 7.6386 | 172.3614 | 10.0125 | 108.0726 | 108.0726 | 147.9464 | 256.019 | 0.23772 | 23.77% | 115.7718 | 27.5214 | 19.265 | 124.1844 | 124.1844 | 15.51% | 11.75% | 11.75% | 80% | 9.398% | 10.8797 | 8.1559 | 6 | 65.2782 | 24.0595 | 52.57% | 52.57%
3 | 65 | 6 | 1549 | 13 | 7.3 | 88.53 | 167.58 | 256.11 | 167.58 | 83.79 | 65 | 1549 | 780 | 64.1096 | -6.1345 | 1.1371 | 754.284 | 12.5904 | -8.8553 | 36.5067 | 36.5067 | 10.9773 | 190.9773 | 11.8653 | 145.631 | 145.631 | 143.0385 | 288.6695 | 0.30588 | 30.59% | 130.5364 | 39.929 | 27.9503 | 124.3504 | 124.3504 | 22.48% | 11.71% | 11.71% | 80% | 9.367% | 12.2278 | 8.012 | 6 | 73.3666 | 27.0406 | 59% | 59%
3 | 65 | 6 | 1550 | 14 | 8.4 | 247.22 | 192.22 | 439.44 | 192.22 | 96.11 | 65 | 1550 | 840 | 64.1096 | -6.1345 | 1.1371 | 814.284 | 13.5904 | -23.8553 | 33.0154 | 33.0154 | 28.6558 | 208.6558 | 25.0986 | 410.8868 | 410.8868 | 164.07 | 574.9569 | 0.55843 | 55.84% | 259.9955 | 145.19 | 101.633 | 132.5367 | 132.5367 | 76.68% | 11.5% | 11.5% | 90% | 10.35% | 26.8992 | 7.7015 | 6 | 161.3951 | 59.4851 | 121.8% | 121.8%
3 | 65 | 6 | 1551 | 15 | 9.1 | 233.97 | 168.06 | 402.03 | 168.06 | 84.03 | 65 | 1551 | 900 | 64.1096 | -6.1345 | 1.1371 | 874.284 | 14.5904 | -38.8553 | 26.896 | 26.896 | 44.3804 | 224.3804 | 39.5935 | 398.5525 | 398.5525 | 143.4482 | 542.0007 | 0.54654 | 54.65% | 245.0927 | 133.9525 | 93.7668 | 129.9078 | 129.9078 | 72.18% | 11.51% | 11.51% | 90% | 10.36% | 25.3818 | 7.5083 | 6 | 152.2909 | 56.1296 | 117.2% | 117.2%
3 | 65 | 6 | 1552 | 16 | 9.4 | 115 | 104.64 | 219.64 | 104.64 | 52.32 | 65 | 1552 | 960 | 64.1096 | -6.1345 | 1.1371 | 934.284 | 15.5904 | -53.8553 | 18.8895 | 18.8895 | 58.0606 | 238.0606 | 54.3486 | 207.0396 | 207.0396 | 89.3158 | 296.3554 | 0.33551 | 33.55% | 134.0119 | 44.9617 | 31.4732 | 120.6679 | 120.6679 | 26.08% | 11.65% | 11.65% | 80% | 9.316% | 12.4852 | 7.4266 | 6 | 74.9113 | 27.6099 | 62.08% | 62.08%
3 | 65 | 6 | 1553 | 17 | 9.6 | 88.61 | 116.31 | 204.92 | 116.31 | 58.16 | 65 | 1553 | 1020 | 64.1096 | -6.1345 | 1.1371 | 994.284 | 16.5904 | -68.8553 | 9.6569 | 9.6569 | 70.1628 | 250.1628 | 69.1961 | 0 | 0 | 99.2768 | 99.2768 | -0.58981 | 0% | 44.893 | 0 | 0 | 118.2533 | 118.2533 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1554 | 18 | 8.8 | 43.14 | 58.61 | 101.75 | 58.61 | 29.31 | 65 | 1554 | 1080 | 64.1096 | -6.1345 | 1.1371 | 1054.284 | 17.5904 | -83.8553 | -0.28577 | 0 | 81.0226 | 261.0226 | 83.6651 | 0 | 0 | 50.0268 | 50.0268 | -1.9995 | 0% | 22.6221 | 0 | 0 | 151.0885 | 151.0885 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1555 | 19 | 7.3 | 0 | 11.67 | 11.67 | 11.67 | 5.84 | 65 | 1555 | 1140 | 64.1096 | -6.1345 | 1.1371 | 1114.284 | 18.5904 | -98.8553 | -10.5265 | 0 | 81.0226 | 261.0226 | 83.6651 | 0 | 0 | 9.961 | 9.961 | -13.6314 | 0% | 4.5043 | 0 | 0 | 139.6404 | 139.6404 | 0% | 11.9% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1556 | 20 | 5.8 | 0 | 0 | 0 | 0 | 0 | 65 | 1556 | 1200 | 64.1096 | -6.1345 | 1.1371 | 1174.284 | 19.5904 | -113.8553 | -20.6862 | 0 | 81.0226 | 261.0226 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.9217 | 131.9217 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1557 | 21 | 4.2 | 0 | 0 | 0 | 0 | 0 | 65 | 1557 | 1260 | 64.1096 | -6.1345 | 1.1371 | 1234.284 | 20.5904 | -128.8553 | -30.3341 | 0 | 81.0226 | 261.0226 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7138 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1558 | 22 | 2.4 | 0 | 0 | 0 | 0 | 0 | 65 | 1558 | 1320 | 64.1096 | -6.1345 | 1.1371 | 1294.284 | 21.5904 | -143.8553 | -38.8823 | 0 | 81.0226 | 261.0226 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5587 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1559 | 23 | 1.8 | 0 | 0 | 0 | 0 | 0 | 65 | 1559 | 1380 | 64.1096 | -6.1345 | 1.1371 | 1354.284 | 22.5904 | -158.8553 | -45.4741 | 0 | 81.0226 | 261.0226 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1515 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
3 | 65 | 6 | 1560 | 24 | 1.9 | 0 | 0 | 0 | 0 | 0 | 65 | 1560 | 1440 | 64.1096 | -6.1345 | 1.1371 | 1414.284 | 23.5904 | -173.8553 | -49.0136 | 0 | 81.0226 | 261.0226 | 83.6651 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6775 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1561 | 1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 66 | 1561 | 60 | 65.0959 | -5.7487 | 1.5051 | 34.284 | 0.59649 | 171.0527 | -48.2522 | 0 | 81.5896 | 98.4104 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5305 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1562 | 2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 66 | 1562 | 120 | 65.0959 | -5.7487 | 1.5051 | 94.284 | 1.5965 | 156.0527 | -44.0846 | 0 | 81.5896 | 98.4104 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0967 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1563 | 3 | 0.7 | 0 | 0 | 0 | 0 | 0 | 66 | 1563 | 180 | 65.0959 | -5.7487 | 1.5051 | 154.284 | 2.5965 | 141.0527 | -37.0792 | 0 | 81.5896 | 98.4104 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8822 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1564 | 4 | 1.1 | 0 | 0 | 0 | 0 | 0 | 66 | 1564 | 240 | 65.0959 | -5.7487 | 1.5051 | 214.284 | 3.5965 | 126.0527 | -28.2946 | 0 | 81.5896 | 98.4104 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2726 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1565 | 5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 66 | 1565 | 300 | 65.0959 | -5.7487 | 1.5051 | 274.284 | 4.5965 | 111.0527 | -18.5276 | 0 | 81.5896 | 98.4104 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9601 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1566 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 66 | 1566 | 360 | 65.0959 | -5.7487 | 1.5051 | 334.284 | 5.5965 | 96.0527 | -8.3279 | 0 | 81.5896 | 98.4104 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.75085 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1567 | 7 | 2.3 | 0 | 0 | 0 | 0 | 0 | 66 | 1567 | 420 | 65.0959 | -5.7487 | 1.5051 | 394.284 | 6.5965 | 81.0527 | 1.8901 | 1.8901 | 79.5454 | 100.4546 | 81.2826 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 160.2424 | 160.2424 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1568 | 8 | 2.4 | 1.31 | 5.83 | 7.14 | 5.83 | 2.92 | 66 | 1568 | 480 | 65.0959 | -5.7487 | 1.5051 | 454.284 | 7.5965 | 66.0527 | 11.7464 | 11.7464 | 68.2444 | 111.7556 | 66.3873 | 2.5775 | 2.5775 | 4.9762 | 7.5537 | -19.7913 | 0% | 3.4158 | 0 | 0 | 167.3767 | 167.3767 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1569 | 9 | 2.3 | 30.28 | 52.22 | 82.5 | 52.22 | 26.11 | 66 | 1569 | 540 | 65.0959 | -5.7487 | 1.5051 | 514.284 | 8.5965 | 51.0527 | 20.8137 | 20.8137 | 55.8772 | 124.1228 | 51.5351 | 53.0077 | 53.0077 | 44.5726 | 97.5802 | -0.79278 | 0% | 44.1258 | 0 | 0 | 151.8232 | 151.8232 | 0% | 12.04% | 12.04% | 80% | 9.629% | 4.2487 | 9.53 | 6 | 25.4923 | 9.3957 | 16.79% | 16.79%
3 | 66 | 7 | 1570 | 10 | 5.4 | 111.19 | 76.39 | 187.58 | 76.39 | 38.2 | 66 | 1570 | 600 | 65.0959 | -5.7487 | 1.5051 | 574.284 | 9.5965 | 36.0527 | 28.5477 | 28.5477 | 41.8065 | 138.1935 | 36.7825 | 186.3474 | 186.3474 | 65.2029 | 251.5503 | 0.21438 | 21.44% | 113.7511 | 24.3854 | 17.0698 | 160.5618 | 160.5618 | 10.63% | 11.79% | 11.79% | 80% | 9.434% | 10.7312 | 8.5682 | 6 | 64.3871 | 23.7311 | 40.1% | 40.1%
3 | 66 | 7 | 1571 | 11 | 5.9 | 181.03 | 105.92 | 286.95 | 105.92 | 52.96 | 66 | 1571 | 660 | 65.0959 | -5.7487 | 1.5051 | 634.284 | 10.5965 | 21.0527 | 34.2573 | 34.2573 | 25.6226 | 154.3774 | 22.3314 | 297.4776 | 297.4776 | 90.4084 | 387.8859 | 0.4247 | 42.47% | 175.402 | 74.4939 | 52.1457 | 138.7169 | 138.7169 | 37.59% | 11.67% | 11.67% | 85% | 9.921% | 17.4014 | 8.4194 | 6 | 104.4083 | 38.4816 | 75.27% | 75.27%
3 | 66 | 7 | 1572 | 12 | 6.7 | 222.69 | 116.94 | 339.63 | 116.94 | 58.47 | 66 | 1572 | 720 | 65.0959 | -5.7487 | 1.5051 | 694.284 | 11.5965 | 6.0527 | 37.1996 | 37.1996 | 7.5685 | 172.4315 | 9.6535 | 363.1145 | 363.1145 | 99.8145 | 462.929 | 0.49031 | 49.03% | 209.3365 | 102.6399 | 71.8479 | 132.8444 | 132.8444 | 54.08% | 11.6% | 11.6% | 85% | 9.859% | 20.638 | 8.1849 | 6 | 123.8282 | 45.6392 | 93.21% | 93.21%
3 | 66 | 7 | 1573 | 13 | 6.5 | 232.42 | 151.67 | 384.09 | 151.67 | 75.84 | 66 | 1573 | 780 | 65.0959 | -5.7487 | 1.5051 | 754.284 | 12.5965 | -8.9473 | 36.8771 | 36.8771 | 11.154 | 191.154 | 11.683 | 379.2777 | 379.2777 | 129.4584 | 508.7361 | 0.51762 | 51.76% | 230.0505 | 119.0786 | 83.355 | 132.1228 | 132.1228 | 63.09% | 11.57% | 11.57% | 90% | 10.41% | 23.9516 | 8.2431 | 6 | 143.7094 | 52.9667 | 108.8% | 108.8%
3 | 66 | 7 | 1574 | 14 | 7.1 | 279.17 | 177.42 | 456.59 | 177.42 | 88.71 | 66 | 1574 | 840 | 65.0959 | -5.7487 | 1.5051 | 814.284 | 13.5965 | -23.9473 | 33.3491 | 33.3491 | 28.9118 | 208.9118 | 25.0718 | 459.9751 | 459.9751 | 151.4374 | 611.4125 | 0.56805 | 56.8% | 276.4807 | 157.0537 | 109.9376 | 134.4332 | 134.4332 | 81.78% | 11.49% | 11.49% | 90% | 10.34% | 28.5804 | 8.0693 | 6 | 171.4826 | 63.2031 | 127.6% | 127.6%
3 | 66 | 7 | 1575 | 15 | 7.1 | 211.58 | 179.17 | 390.75 | 179.17 | 89.59 | 66 | 1575 | 900 | 65.0959 | -5.7487 | 1.5051 | 874.284 | 14.5965 | -38.9473 | 27.1897 | 27.1897 | 44.6796 | 224.6796 | 39.6162 | 356.6944 | 356.6944 | 152.9312 | 509.6255 | 0.52092 | 52.09% | 230.4527 | 120.0472 | 84.033 | 129.0258 | 129.0258 | 65.13% | 11.56% | 11.56% | 90% | 10.4% | 23.9722 | 8.0693 | 6 | 143.8331 | 53.0124 | 111.5% | 111.5%
3 | 66 | 7 | 1576 | 16 | 7.4 | 166.86 | 159.36 | 326.22 | 159.36 | 79.68 | 66 | 1576 | 960 | 65.0959 | -5.7487 | 1.5051 | 934.284 | 15.5965 | -53.9473 | 19.1488 | 19.1488 | 58.3779 | 238.3779 | 54.396 | 296.1453 | 296.1453 | 136.0223 | 432.1676 | 0.47183 | 47.18% | 195.4262 | 92.2076 | 64.5453 | 124.9828 | 124.9828 | 51.64% | 11.61% | 11.61% | 85% | 9.866% | 19.2805 | 7.9834 | 6 | 115.683 | 42.6371 | 92.56% | 92.56%
3 | 66 | 7 | 1577 | 17 | 7.1 | 54.92 | 107.78 | 162.7 | 107.78 | 53.89 | 66 | 1577 | 1020 | 65.0959 | -5.7487 | 1.5051 | 994.284 | 16.5965 | -68.9473 | 9.8913 | 9.8913 | 70.4874 | 250.4874 | 69.2592 | 0 | 0 | 91.996 | 91.996 | -0.76417 | 0% | 41.6006 | 0 | 0 | 113.7653 | 113.7653 | 0% | 11.85% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1578 | 18 | 6.3 | 24.25 | 73.69 | 97.94 | 73.69 | 36.85 | 66 | 1578 | 1080 | 65.0959 | -5.7487 | 1.5051 | 1054.284 | 17.5965 | -83.9473 | -0.065504 | 0 | 81.5896 | 261.5896 | 84.0637 | 0 | 0 | 62.8983 | 62.8983 | -1.5199 | 0% | 28.4426 | 0 | 0 | 147.6602 | 147.6602 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1579 | 19 | 6.2 | 0 | 13.33 | 13.33 | 13.33 | 6.67 | 66 | 1579 | 1140 | 65.0959 | -5.7487 | 1.5051 | 1114.284 | 18.5965 | -98.9473 | -10.3094 | 0 | 81.5896 | 261.5896 | 84.0637 | 0 | 0 | 11.3779 | 11.3779 | -12.0637 | 0% | 5.1451 | 0 | 0 | 138.9748 | 138.9748 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1580 | 20 | 4.8 | 0 | 0 | 0 | 0 | 0 | 66 | 1580 | 1200 | 65.0959 | -5.7487 | 1.5051 | 1174.284 | 19.5965 | -113.9473 | -20.4605 | 0 | 81.5896 | 261.5896 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.7431 | 130.7431 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1581 | 21 | 3.5 | 0 | 0 | 0 | 0 | 0 | 66 | 1581 | 1260 | 65.0959 | -5.7487 | 1.5051 | 1234.284 | 20.5965 | -128.9473 | -30.0868 | 0 | 81.5896 | 261.5896 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5585 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1582 | 22 | 2.8 | 0 | 0 | 0 | 0 | 0 | 66 | 1582 | 1320 | 65.0959 | -5.7487 | 1.5051 | 1294.284 | 21.5965 | -143.9473 | -38.5995 | 0 | 81.5896 | 261.5896 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8505 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1583 | 23 | 2.8 | 0 | 0 | 0 | 0 | 0 | 66 | 1583 | 1380 | 65.0959 | -5.7487 | 1.5051 | 1354.284 | 22.5965 | -158.9473 | -45.1448 | 0 | 81.5896 | 261.5896 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4168 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
3 | 66 | 7 | 1584 | 24 | 2.1 | 0 | 0 | 0 | 0 | 0 | 66 | 1584 | 1440 | 65.0959 | -5.7487 | 1.5051 | 1414.284 | 23.5965 | -173.9473 | -48.6402 | 0 | 81.5896 | 261.5896 | 84.0637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0498 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1585 | 1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 67 | 1585 | 60 | 66.0822 | -5.361 | 1.8768 | 34.284 | 0.60268 | 170.9598 | -47.8547 | 0 | 82.1587 | 97.8413 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.592 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1586 | 2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 67 | 1586 | 120 | 66.0822 | -5.361 | 1.8768 | 94.284 | 1.6027 | 155.9598 | -43.6913 | 0 | 82.1587 | 97.8413 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7222 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1587 | 3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 67 | 1587 | 180 | 66.0822 | -5.361 | 1.8768 | 154.284 | 2.6027 | 140.9598 | -36.7028 | 0 | 82.1587 | 97.8413 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.986 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1588 | 4 | -0.3 | 0 | 0 | 0 | 0 | 0 | 67 | 1588 | 240 | 66.0822 | -5.361 | 1.8768 | 214.284 | 3.6027 | 125.9598 | -27.9348 | 0 | 82.1587 | 97.8413 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2052 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1589 | 5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 67 | 1589 | 300 | 66.0822 | -5.361 | 1.8768 | 274.284 | 4.6027 | 110.9598 | -18.1788 | 0 | 82.1587 | 97.8413 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.287 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1590 | 6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 67 | 1590 | 360 | 66.0822 | -5.361 | 1.8768 | 334.284 | 5.6027 | 95.9598 | -7.983 | 0 | 82.1587 | 97.8413 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2942 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1591 | 7 | -0.2 | 0 | 0 | 0 | 0 | 0 | 67 | 1591 | 420 | 66.0822 | -5.361 | 1.8768 | 394.284 | 6.6027 | 80.9598 | 2.238 | 2.238 | 79.7398 | 100.2602 | 81.1722 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.2102 | 142.2102 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1592 | 8 | 0.3 | 1.31 | 4.81 | 6.12 | 4.81 | 2.41 | 67 | 1592 | 480 | 66.0822 | -5.361 | 1.8768 | 454.284 | 7.6027 | 65.9598 | 12.1036 | 12.1036 | 68.425 | 111.575 | 66.2653 | 2.5147 | 2.5147 | 4.1056 | 6.6203 | -23.4725 | 0% | 2.9937 | 0 | 0 | 147.6421 | 147.6421 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1593 | 9 | 1.3 | 24.25 | 21.86 | 46.11 | 21.86 | 10.93 | 67 | 1593 | 540 | 66.0822 | -5.361 | 1.8768 | 514.284 | 8.6027 | 50.9598 | 21.1849 | 21.1849 | 56.0326 | 123.9674 | 51.3978 | 41.8669 | 41.8669 | 18.6587 | 60.5256 | -1.8107 | 0% | 27.3697 | 0 | 0 | 131.4347 | 131.4347 | 0% | 12.11% | 12.11% | 80% | 9.69% | 2.6521 | 9.8546 | 6 | 15.9128 | 5.865 | 12.11% | 12.11%
3 | 67 | 8 | 1594 | 10 | 2.7 | 67.14 | 47.03 | 114.17 | 47.03 | 23.52 | 67 | 1594 | 600 | 66.0822 | -5.361 | 1.8768 | 574.284 | 9.6027 | 35.9598 | 28.9346 | 28.9346 | 41.9158 | 138.0842 | 36.6207 | 111.3797 | 111.3797 | 40.1426 | 151.5223 | -0.2179 | 0% | 68.5184 | 0 | 0 | 136.5793 | 136.5793 | 0% | 11.97% | 11.97% | 80% | 9.575% | 6.5608 | 9.4021 | 6 | 39.3647 | 14.5086 | 28.82% | 28.82%
3 | 67 | 8 | 1595 | 11 | 4.1 | 102.97 | 72.86 | 175.83 | 72.86 | 36.43 | 67 | 1595 | 660 | 66.0822 | -5.361 | 1.8768 | 634.284 | 10.6027 | 20.9598 | 34.6549 | 34.6549 | 25.6554 | 154.3446 | 22.1195 | 167.756 | 167.756 | 62.1899 | 229.9459 | 0.14538 | 14.54% | 103.9815 | 15.1167 | 10.5817 | 138.1276 | 138.1276 | 7.661% | 11.85% | 11.85% | 80% | 9.48% | 9.8579 | 8.9633 | 6 | 59.1473 | 21.7998 | 42.82% | 42.82%
3 | 67 | 8 | 1596 | 12 | 5.6 | 139.72 | 90.83 | 230.55 | 90.83 | 45.42 | 67 | 1596 | 720 | 66.0822 | -5.361 | 1.8768 | 694.284 | 11.6027 | 5.9598 | 37.594 | 37.594 | 7.4966 | 172.5034 | 9.2954 | 226.0183 | 226.0183 | 77.5283 | 303.5466 | 0.31695 | 31.7% | 137.2638 | 43.5063 | 30.4544 | 116.4546 | 116.4546 | 26.15% | 11.75% | 11.75% | 85% | 9.983% | 13.7036 | 8.5084 | 6 | 82.2216 | 30.3043 | 70.6% | 70.6%
3 | 67 | 8 | 1597 | 13 | 7.1 | 241.94 | 106.25 | 348.19 | 106.25 | 53.13 | 67 | 1597 | 780 | 66.0822 | -5.361 | 1.8768 | 754.284 | 12.6027 | -9.0402 | 37.2489 | 37.2489 | 11.3341 | 191.3341 | 11.5111 | 391.6771 | 391.6771 | 90.69 | 482.3672 | 0.50492 | 50.49% | 218.1264 | 110.1369 | 77.0958 | 122.162 | 122.162 | 63.11% | 11.58% | 11.58% | 85% | 9.841% | 21.4653 | 8.0693 | 6 | 128.7917 | 47.4686 | 105.4% | 105.4%
3 | 67 | 8 | 1598 | 14 | 7.5 | 238.06 | 102.92 | 340.98 | 102.92 | 51.46 | 67 | 1598 | 840 | 66.0822 | -5.361 | 1.8768 | 814.284 | 13.6027 | -24.0402 | 33.6836 | 33.6836 | 29.1717 | 209.1717 | 25.0514 | 388.8625 | 388.8625 | 87.8477 | 476.7102 | 0.50336 | 50.34% | 215.5684 | 108.5091 | 75.9563 | 121.1613 | 121.1613 | 62.69% | 11.57% | 11.57% | 85% | 9.838% | 21.2079 | 7.9549 | 6 | 127.2473 | 46.8993 | 105% | 105%
3 | 67 | 8 | 1599 | 15 | 9.4 | 136.11 | 76.19 | 212.3 | 76.19 | 38.1 | 67 | 1599 | 900 | 66.0822 | -5.361 | 1.8768 | 874.284 | 14.6027 | -39.0402 | 27.4838 | 27.4838 | 44.9823 | 224.9823 | 39.6429 | 227.1074 | 227.1074 | 65.0322 | 292.1396 | 0.32874 | 32.87% | 132.1055 | 43.429 | 30.4003 | 116.4975 | 116.4975 | 26.1% | 11.65% | 11.65% | 80% | 9.318% | 12.3102 | 7.4266 | 6 | 73.8613 | 27.2229 | 63.4% | 63.4%
3 | 67 | 8 | 1600 | 16 | 8.3 | 91.03 | 66.67 | 157.7 | 66.67 | 33.34 | 67 | 1600 | 960 | 66.0822 | -5.361 | 1.8768 | 934.284 | 15.6027 | -54.0402 | 19.4084 | 19.4084 | 58.6983 | 238.6983 | 54.4461 | 159.2872 | 159.2872 | 56.9064 | 216.1936 | 0.14983 | 14.98% | 97.7627 | 14.6482 | 10.2538 | 111.1769 | 111.1769 | 9.223% | 11.73% | 11.73% | 80% | 9.382% | 9.1722 | 7.7294 | 6 | 55.0334 | 20.2836 | 49.5% | 49.5%
3 | 67 | 8 | 1601 | 17 | 8.2 | 51.39 | 55.47 | 106.86 | 55.47 | 27.74 | 67 | 1601 | 1020 | 66.0822 | -5.361 | 1.8768 | 994.284 | 16.6027 | -69.0402 | 10.1262 | 10.1262 | 70.8143 | 250.8143 | 69.3243 | 103.2025 | 103.2025 | 47.3466 | 150.5491 | -0.13697 | 0% | 68.0783 | 0 | 0 | 148.7644 | 148.7644 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1602 | 18 | 7.5 | 9.25 | 42.5 | 51.75 | 42.5 | 21.25 | 67 | 1602 | 1080 | 66.0822 | -5.361 | 1.8768 | 1054.284 | 17.6027 | -84.0402 | 0.15535 | 0.15535 | 81.9918 | 261.9918 | 84.2362 | 0 | 0 | 36.276 | 36.276 | -3.1467 | 0% | 16.404 | 0 | 0 | 142.2895 | 142.2895 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1603 | 19 | 7 | 0 | 10.28 | 10.28 | 10.28 | 5.14 | 67 | 1603 | 1140 | 66.0822 | -5.361 | 1.8768 | 1114.284 | 18.6027 | -99.0402 | -10.0913 | 0 | 82.1587 | 262.1587 | 84.464 | 0 | 0 | 8.7745 | 8.7745 | -15.6644 | 0% | 3.9678 | 0 | 0 | 136.9822 | 136.9822 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1604 | 20 | 5.6 | 0 | 0 | 0 | 0 | 0 | 67 | 1604 | 1200 | 66.0822 | -5.361 | 1.8768 | 1174.284 | 19.6027 | -114.0402 | -20.2335 | 0 | 82.1587 | 262.1587 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.0514 | 131.0514 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1605 | 21 | 4.4 | 0 | 0 | 0 | 0 | 0 | 67 | 1605 | 1260 | 66.0822 | -5.361 | 1.8768 | 1234.284 | 20.6027 | -129.0402 | -29.8378 | 0 | 82.1587 | 262.1587 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5871 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1606 | 22 | 4.3 | 0 | 0 | 0 | 0 | 0 | 67 | 1606 | 1320 | 66.0822 | -5.361 | 1.8768 | 1294.284 | 21.6027 | -144.0402 | -38.3145 | 0 | 82.1587 | 262.1587 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4957 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1607 | 23 | 3.5 | 0 | 0 | 0 | 0 | 0 | 67 | 1607 | 1380 | 66.0822 | -5.361 | 1.8768 | 1354.284 | 22.6027 | -159.0402 | -44.8133 | 0 | 82.1587 | 262.1587 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4547 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
3 | 67 | 8 | 1608 | 24 | 2.6 | 0 | 0 | 0 | 0 | 0 | 67 | 1608 | 1440 | 66.0822 | -5.361 | 1.8768 | 1414.284 | 23.6027 | -174.0402 | -48.2648 | 0 | 82.1587 | 262.1587 | 84.464 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5661 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1609 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 68 | 1609 | 60 | 67.0685 | -4.9717 | 2.2518 | 34.284 | 0.60893 | 170.866 | -47.4554 | 0 | 82.7298 | 97.2702 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8105 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1610 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 68 | 1610 | 120 | 67.0685 | -4.9717 | 2.2518 | 94.284 | 1.6089 | 155.866 | -43.2961 | 0 | 82.7298 | 97.2702 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8481 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1611 | 3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 68 | 1611 | 180 | 67.0685 | -4.9717 | 2.2518 | 154.284 | 2.6089 | 140.866 | -36.3243 | 0 | 82.7298 | 97.2702 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4954 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1612 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 68 | 1612 | 240 | 67.0685 | -4.9717 | 2.2518 | 214.284 | 3.6089 | 125.866 | -27.5729 | 0 | 82.7298 | 97.2702 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9526 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1613 | 5 | -0.9 | 0 | 0 | 0 | 0 | 0 | 68 | 1613 | 300 | 67.0685 | -4.9717 | 2.2518 | 274.284 | 4.6089 | 110.866 | -17.8279 | 0 | 82.7298 | 97.2702 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9521 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1614 | 6 | -2.6 | 0 | 0 | 0 | 0 | 0 | 68 | 1614 | 360 | 67.0685 | -4.9717 | 2.2518 | 334.284 | 5.6089 | 95.866 | -7.6361 | 0 | 82.7298 | 97.2702 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1657 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1615 | 7 | -2.5 | 0 | 0 | 0 | 0 | 0 | 68 | 1615 | 420 | 67.0685 | -4.9717 | 2.2518 | 394.284 | 6.6089 | 80.866 | 2.5878 | 2.5878 | 79.9348 | 100.0652 | 81.0611 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.6834 | 139.6834 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1616 | 8 | -2.8 | 0.83 | 8.14 | 8.97 | 8.14 | 4.07 | 68 | 1616 | 480 | 67.0685 | -4.9717 | 2.2518 | 454.284 | 7.6089 | 65.866 | 12.4625 | 12.4625 | 68.6066 | 111.3934 | 66.1435 | 1.5556 | 1.5556 | 6.9479 | 8.5035 | -19.0024 | 0% | 3.8453 | 0 | 0 | 144.2797 | 144.2797 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1617 | 9 | -1.4 | 13.81 | 44.25 | 58.06 | 44.25 | 22.13 | 68 | 1617 | 540 | 67.0685 | -4.9717 | 2.2518 | 514.284 | 8.6089 | 50.866 | 21.5578 | 21.5578 | 56.1889 | 123.8111 | 51.2613 | 23.5191 | 23.5191 | 37.7697 | 61.2889 | -1.887 | 0% | 27.7148 | 0 | 0 | 128.8197 | 128.8197 | 0% | 12.22% | 12.22% | 80% | 9.777% | 2.7097 | 10.7659 | 6 | 16.2584 | 5.9923 | 12.62% | 12.62%
3 | 68 | 9 | 1618 | 10 | 1.3 | 36.31 | 74.25 | 110.56 | 74.25 | 37.13 | 68 | 1618 | 600 | 67.0685 | -4.9717 | 2.2518 | 574.284 | 9.6089 | 35.866 | 29.3232 | 29.3232 | 42.0259 | 137.9741 | 36.4609 | 59.6296 | 59.6296 | 63.3763 | 123.0059 | -0.4826 | 0% | 55.6233 | 0 | 0 | 134.9165 | 134.9165 | 0% | 12.05% | 12.05% | 80% | 9.639% | 5.3613 | 9.8546 | 6 | 32.1679 | 11.8561 | 23.84% | 23.84%
3 | 68 | 9 | 1619 | 11 | 4.3 | 67.69 | 92.78 | 160.47 | 92.78 | 46.39 | 68 | 1619 | 660 | 67.0685 | -4.9717 | 2.2518 | 634.284 | 10.6089 | 20.866 | 35.0544 | 35.0544 | 25.6882 | 154.3118 | 21.9112 | 109.3408 | 109.3408 | 79.1927 | 188.5335 | 0.0032687 | 0.3269% | 85.2549 | 0.27868 | 0.19507 | 138.322 | 138.322 | 0.141% | 11.88% | 11.88% | 80% | 9.504% | 8.1026 | 8.9018 | 6 | 48.6157 | 17.9182 | 35.15% | 35.15%
3 | 68 | 9 | 1620 | 12 | 6.5 | 153.75 | 162.22 | 315.97 | 162.22 | 81.11 | 68 | 1620 | 720 | 67.0685 | -4.9717 | 2.2518 | 694.284 | 11.6089 | 5.866 | 37.9901 | 37.9901 | 7.4229 | 172.5771 | 8.9388 | 246.7528 | 246.7528 | 138.4634 | 385.2162 | 0.42579 | 42.58% | 174.1948 | 74.1706 | 51.9195 | 122.2349 | 122.2349 | 42.48% | 11.66% | 11.66% | 85% | 9.911% | 17.2644 | 8.2431 | 6 | 103.5865 | 38.1787 | 84.74% | 84.74%
3 | 68 | 9 | 1621 | 13 | 7.6 | 126.67 | 204.17 | 330.84 | 204.17 | 102.09 | 68 | 1621 | 780 | 67.0685 | -4.9717 | 2.2518 | 754.284 | 12.6089 | -9.134 | 37.6219 | 37.6219 | 11.5174 | 191.5174 | 11.3501 | 203.4454 | 203.4454 | 174.27 | 377.7154 | 0.4252 | 42.52% | 170.8029 | 72.6247 | 50.8373 | 123.2545 | 123.2545 | 41.25% | 11.64% | 11.64% | 85% | 9.894% | 16.8992 | 7.9264 | 6 | 101.3954 | 37.3712 | 82.27% | 82.27%
3 | 68 | 9 | 1622 | 14 | 8.6 | 136.03 | 228.33 | 364.36 | 228.33 | 114.17 | 68 | 1622 | 840 | 67.0685 | -4.9717 | 2.2518 | 814.284 | 13.6089 | -24.134 | 34.0187 | 34.0187 | 29.4353 | 209.4353 | 25.0374 | 220.2957 | 220.2957 | 194.8918 | 415.1875 | 0.46507 | 46.51% | 187.7478 | 87.3158 | 61.1211 | 125.2045 | 125.2045 | 48.82% | 11.59% | 11.59% | 85% | 9.854% | 18.5012 | 7.6459 | 6 | 111.0072 | 40.9138 | 88.66% | 88.66%
3 | 68 | 9 | 1623 | 15 | 9.5 | 122.31 | 205.47 | 327.78 | 205.47 | 102.74 | 68 | 1623 | 900 | 67.0685 | -4.9717 | 2.2518 | 874.284 | 14.6089 | -39.134 | 27.7782 | 27.7782 | 45.2885 | 225.2885 | 39.6737 | 201.9977 | 201.9977 | 175.3796 | 377.3773 | 0.43671 | 43.67% | 170.65 | 74.5247 | 52.1673 | 123.0168 | 123.0168 | 42.41% | 11.6% | 11.6% | 85% | 9.857% | 16.8204 | 7.3995 | 6 | 100.9223 | 37.1968 | 82.04% | 82.04%
3 | 68 | 9 | 1624 | 16 | 9 | 55.56 | 126.86 | 182.42 | 126.86 | 63.43 | 68 | 1624 | 960 | 67.0685 | -4.9717 | 2.2518 | 934.284 | 15.6089 | -54.134 | 19.6682 | 19.6682 | 59.0215 | 239.0215 | 54.4989 | 95.8624 | 95.8624 | 108.2818 | 204.1441 | 0.11929 | 11.93% | 92.314 | 11.0123 | 7.7086 | 114.218 | 114.218 | 6.749% | 11.71% | 11.71% | 80% | 9.37% | 8.6498 | 7.5357 | 6 | 51.8989 | 19.1283 | 45.44% | 45.44%
3 | 68 | 9 | 1625 | 17 | 8.5 | 36.94 | 84.92 | 121.86 | 84.92 | 42.46 | 68 | 1625 | 1020 | 67.0685 | -4.9717 | 2.2518 | 994.284 | 16.6089 | -69.134 | 10.3613 | 10.3613 | 71.1436 | 251.1436 | 69.3913 | 72.2934 | 72.2934 | 72.4838 | 144.7771 | -0.1696 | 0% | 65.4682 | 0 | 0 | 150.8052 | 150.8052 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1626 | 18 | 7.8 | 6.11 | 35.64 | 41.75 | 35.64 | 17.82 | 68 | 1626 | 1080 | 67.0685 | -4.9717 | 2.2518 | 1054.284 | 17.6089 | -84.134 | 0.37678 | 0.37678 | 82.3253 | 262.3253 | 84.3138 | 0 | 0 | 30.4206 | 30.4206 | -3.8838 | 0% | 13.7562 | 0 | 0 | 143.2692 | 143.2692 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1627 | 19 | 7.1 | 0 | 7.97 | 7.97 | 7.97 | 3.99 | 68 | 1627 | 1140 | 67.0685 | -4.9717 | 2.2518 | 1114.284 | 18.6089 | -99.134 | -9.8724 | 0 | 82.7298 | 262.7298 | 84.8661 | 0 | 0 | 6.8028 | 6.8028 | -20.4027 | 0% | 3.0762 | 0 | 0 | 137.7825 | 137.7825 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1628 | 20 | 6.6 | 0 | 0 | 0 | 0 | 0 | 68 | 1628 | 1200 | 67.0685 | -4.9717 | 2.2518 | 1174.284 | 19.6089 | -114.134 | -20.0052 | 0 | 82.7298 | 262.7298 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.7972 | 132.7972 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1629 | 21 | 5.5 | 0 | 0 | 0 | 0 | 0 | 68 | 1629 | 1260 | 67.0685 | -4.9717 | 2.2518 | 1234.284 | 20.6089 | -129.134 | -29.587 | 0 | 82.7298 | 262.7298 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8098 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1630 | 22 | 4.9 | 0 | 0 | 0 | 0 | 0 | 68 | 1630 | 1320 | 67.0685 | -4.9717 | 2.2518 | 1294.284 | 21.6089 | -144.134 | -38.0276 | 0 | 82.7298 | 262.7298 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5827 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1631 | 23 | 4.7 | 0 | 0 | 0 | 0 | 0 | 68 | 1631 | 1380 | 67.0685 | -4.9717 | 2.2518 | 1354.284 | 22.6089 | -159.134 | -44.4798 | 0 | 82.7298 | 262.7298 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6204 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
3 | 68 | 9 | 1632 | 24 | 4.7 | 0 | 0 | 0 | 0 | 0 | 68 | 1632 | 1440 | 67.0685 | -4.9717 | 2.2518 | 1414.284 | 23.6089 | -174.134 | -47.8875 | 0 | 82.7298 | 262.7298 | 84.8661 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3532 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1633 | 1 | 4.6 | 0 | 0 | 0 | 0 | 0 | 69 | 1633 | 60 | 68.0548 | -4.5808 | 2.6297 | 34.284 | 0.61523 | 170.7716 | -47.0545 | 0 | 83.3029 | 96.6971 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.3677 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1634 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 69 | 1634 | 120 | 68.0548 | -4.5808 | 2.6297 | 94.284 | 1.6152 | 155.7716 | -42.899 | 0 | 83.3029 | 96.6971 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5417 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1635 | 3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 69 | 1635 | 180 | 68.0548 | -4.5808 | 2.6297 | 154.284 | 2.6152 | 140.7716 | -35.9438 | 0 | 83.3029 | 96.6971 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5446 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1636 | 4 | 2.4 | 0 | 0 | 0 | 0 | 0 | 69 | 1636 | 240 | 68.0548 | -4.5808 | 2.6297 | 214.284 | 3.6152 | 125.7716 | -27.209 | 0 | 83.3029 | 96.6971 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2878 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1637 | 5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 69 | 1637 | 300 | 68.0548 | -4.5808 | 2.6297 | 274.284 | 4.6152 | 110.7716 | -17.4751 | 0 | 83.3029 | 96.6971 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2556 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1638 | 6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 69 | 1638 | 360 | 68.0548 | -4.5808 | 2.6297 | 334.284 | 5.6152 | 95.7716 | -7.2874 | 0 | 83.3029 | 96.6971 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9845 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1639 | 7 | -0.1 | 0 | 0 | 0 | 0 | 0 | 69 | 1639 | 420 | 68.0548 | -4.5808 | 2.6297 | 394.284 | 6.6152 | 80.7716 | 2.9393 | 2.9393 | 80.1303 | 99.8697 | 80.9496 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.9359 | 137.9359 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1640 | 8 | -0.6 | 0.19 | 6.03 | 6.22 | 6.03 | 3.02 | 69 | 1640 | 480 | 68.0548 | -4.5808 | 2.6297 | 454.284 | 7.6152 | 65.7716 | 12.823 | 12.823 | 68.7889 | 111.2111 | 66.0218 | 0.3479 | 0.3479 | 5.1469 | 5.4948 | -28.8496 | 0% | 2.4848 | 0 | 0 | 141.138 | 141.138 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1641 | 9 | 0.7 | 3.25 | 39.53 | 42.78 | 39.53 | 19.77 | 69 | 1641 | 540 | 68.0548 | -4.5808 | 2.6297 | 514.284 | 8.6152 | 50.7716 | 21.9324 | 21.9324 | 56.3462 | 123.6538 | 51.1258 | 5.461 | 5.461 | 33.741 | 39.2019 | -3.2706 | 0% | 17.7271 | 0 | 0 | 124.5055 | 124.5055 | 0% | 12.16% | 12.16% | 80% | 9.728% | 1.7244 | 10.0527 | 6 | 10.3466 | 3.8134 | 8.31% | 8.31%
3 | 69 | 10 | 1642 | 10 | 3.7 | 14.53 | 81.11 | 95.64 | 81.11 | 40.56 | 69 | 1642 | 600 | 68.0548 | -4.5808 | 2.6297 | 574.284 | 9.6152 | 35.7716 | 29.7136 | 29.7136 | 42.1367 | 137.8633 | 36.3032 | 23.6242 | 23.6242 | 69.2317 | 92.8559 | -0.8374 | 0% | 41.9894 | 0 | 0 | 131.0745 | 131.0745 | 0% | 11.99% | 11.99% | 80% | 9.589% | 4.0263 | 9.0873 | 6 | 24.1576 | 8.9037 | 18.43% | 18.43%
3 | 69 | 10 | 1643 | 11 | 6.4 | 52.22 | 120.83 | 173.05 | 120.83 | 60.42 | 69 | 1643 | 660 | 68.0548 | -4.5808 | 2.6297 | 634.284 | 10.6152 | 20.7716 | 35.4556 | 35.4556 | 25.7208 | 154.2792 | 21.7068 | 83.6397 | 83.6397 | 103.1349 | 186.7746 | 0.022682 | 2.268% | 84.4595 | 1.9157 | 1.341 | 136.0515 | 136.0515 | 0.9857% | 11.81% | 11.81% | 80% | 9.449% | 7.9802 | 8.2723 | 6 | 47.8812 | 17.6475 | 35.19% | 35.19%
3 | 69 | 10 | 1644 | 12 | 6.7 | 76.75 | 171.11 | 247.86 | 171.11 | 85.56 | 69 | 1644 | 720 | 68.0548 | -4.5808 | 2.6297 | 694.284 | 11.6152 | 5.7716 | 38.3878 | 38.3878 | 7.3475 | 172.6525 | 8.5844 | 122.2101 | 122.2101 | 146.0515 | 268.2616 | 0.26268 | 26.27% | 121.3079 | 31.8649 | 22.3054 | 114.4658 | 114.4658 | 19.49% | 11.74% | 11.74% | 80% | 9.393% | 11.3942 | 8.1849 | 6 | 68.3651 | 25.1972 | 59.73% | 59.73%
3 | 69 | 10 | 1645 | 13 | 8.5 | 82.22 | 214.92 | 297.14 | 214.92 | 107.46 | 69 | 1645 | 780 | 68.0548 | -4.5808 | 2.6297 | 754.284 | 12.6152 | -9.2284 | 37.996 | 37.996 | 11.7038 | 191.7038 | 11.2009 | 131.0154 | 131.0154 | 183.4457 | 314.4611 | 0.35576 | 35.58% | 142.1993 | 50.5884 | 35.4119 | 118.4358 | 118.4358 | 29.9% | 11.66% | 11.66% | 85% | 9.91% | 14.0923 | 7.6737 | 6 | 84.5537 | 31.1638 | 71.39% | 71.39%
3 | 69 | 10 | 1646 | 14 | 9.3 | 43.53 | 225.64 | 269.17 | 225.64 | 112.82 | 69 | 1646 | 840 | 68.0548 | -4.5808 | 2.6297 | 814.284 | 13.6152 | -24.2284 | 34.3546 | 34.3546 | 29.7026 | 209.7026 | 25.0298 | 69.8939 | 69.8939 | 192.5958 | 262.4897 | 0.27417 | 27.42% | 118.6978 | 32.5432 | 22.7803 | 117.7422 | 117.7422 | 19.35% | 11.67% | 11.67% | 80% | 9.335% | 11.08 | 7.4538 | 6 | 66.4802 | 24.5025 | 56.46% | 56.46%
3 | 69 | 10 | 1647 | 15 | 9.5 | 40.28 | 221.47 | 261.75 | 221.47 | 110.74 | 69 | 1647 | 900 | 68.0548 | -4.5808 | 2.6297 | 874.284 | 14.6152 | -39.2284 | 28.073 | 28.073 | 45.5981 | 225.5981 | 39.7083 | 65.8478 | 65.8478 | 189.0365 | 254.8842 | 0.2602 | 26.02% | 115.2586 | 29.99 | 20.993 | 116.0915 | 116.0915 | 18.08% | 11.67% | 11.67% | 80% | 9.333% | 10.7576 | 7.3995 | 6 | 64.5456 | 23.7895 | 55.6% | 55.6%
3 | 69 | 10 | 1648 | 16 | 10 | 32.31 | 181.39 | 213.7 | 181.39 | 90.7 | 69 | 1648 | 960 | 68.0548 | -4.5808 | 2.6297 | 934.284 | 15.6152 | -54.2284 | 19.9282 | 19.9282 | 59.3475 | 239.3475 | 54.5544 | 54.9741 | 54.9741 | 154.826 | 209.8002 | 0.14891 | 14.89% | 94.8716 | 14.1276 | 9.8893 | 113.515 | 113.515 | 8.712% | 11.68% | 11.68% | 80% | 9.341% | 8.8622 | 7.265 | 6 | 53.1734 | 19.598 | 46.84% | 46.84%
3 | 69 | 10 | 1649 | 17 | 9.7 | 18.69 | 121.67 | 140.36 | 121.67 | 60.84 | 69 | 1649 | 1020 | 68.0548 | -4.5808 | 2.6297 | 994.284 | 16.6152 | -69.2284 | 10.5968 | 10.5968 | 71.4751 | 251.4751 | 69.4599 | 35.6594 | 35.6594 | 103.8518 | 139.5113 | -0.18616 | 0% | 63.087 | 0 | 0 | 150.1864 | 150.1864 | 0% | 11.73% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1650 | 18 | 9.6 | 9.53 | 77.14 | 86.67 | 77.14 | 38.57 | 69 | 1650 | 1080 | 68.0548 | -4.5808 | 2.6297 | 1054.284 | 17.6152 | -84.2284 | 0.59877 | 0.59877 | 82.6606 | 262.6606 | 84.3924 | 0 | 0 | 65.8431 | 65.8431 | -1.2975 | 0% | 29.7743 | 0 | 0 | 145.7128 | 145.7128 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1651 | 19 | 8.5 | 0 | 22.5 | 22.5 | 22.5 | 11.25 | 69 | 1651 | 1140 | 68.0548 | -4.5808 | 2.6297 | 1114.284 | 18.6152 | -99.2284 | -9.6526 | 0 | 83.3029 | 263.3029 | 85.2699 | 0 | 0 | 19.205 | 19.205 | -6.5355 | 0% | 8.6845 | 0 | 0 | 138.5998 | 138.5998 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1652 | 20 | 7.1 | 0 | 0 | 0 | 0 | 0 | 69 | 1652 | 1200 | 68.0548 | -4.5808 | 2.6297 | 1174.284 | 19.6152 | -114.2284 | -19.7755 | 0 | 83.3029 | 263.3029 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.2471 | 132.2471 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1653 | 21 | 5.1 | 0 | 0 | 0 | 0 | 0 | 69 | 1653 | 1260 | 68.0548 | -4.5808 | 2.6297 | 1234.284 | 20.6152 | -129.2284 | -29.3345 | 0 | 83.3029 | 263.3029 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5583 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1654 | 22 | 4.2 | 0 | 0 | 0 | 0 | 0 | 69 | 1654 | 1320 | 68.0548 | -4.5808 | 2.6297 | 1294.284 | 21.6152 | -144.2284 | -37.7386 | 0 | 83.3029 | 263.3029 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.6263 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1655 | 23 | 3.3 | 0 | 0 | 0 | 0 | 0 | 69 | 1655 | 1380 | 68.0548 | -4.5808 | 2.6297 | 1354.284 | 22.6152 | -159.2284 | -44.1442 | 0 | 83.3029 | 263.3029 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7816 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
3 | 69 | 10 | 1656 | 24 | 2.8 | 0 | 0 | 0 | 0 | 0 | 69 | 1656 | 1440 | 68.0548 | -4.5808 | 2.6297 | 1414.284 | 23.6152 | -174.2284 | -47.5084 | 0 | 83.3029 | 263.3029 | 85.2699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3272 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1657 | 1 | 2.5 | 0 | 0 | 0 | 0 | 0 | 70 | 1657 | 60 | 69.0411 | -4.1884 | 3.01 | 34.284 | 0.62157 | 170.6765 | -46.6519 | 0 | 83.8778 | 96.1222 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5226 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1658 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 70 | 1658 | 120 | 69.0411 | -4.1884 | 3.01 | 94.284 | 1.6216 | 155.6765 | -42.5002 | 0 | 83.8778 | 96.1222 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5475 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1659 | 3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 70 | 1659 | 180 | 69.0411 | -4.1884 | 3.01 | 154.284 | 2.6216 | 140.6765 | -35.5615 | 0 | 83.8778 | 96.1222 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3532 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1660 | 4 | -0.9 | 0 | 0 | 0 | 0 | 0 | 70 | 1660 | 240 | 69.0411 | -4.1884 | 3.01 | 214.284 | 3.6216 | 125.6765 | -26.8433 | 0 | 83.8778 | 96.1222 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.182 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1661 | 5 | -2 | 0 | 0 | 0 | 0 | 0 | 70 | 1661 | 300 | 69.0411 | -4.1884 | 3.01 | 274.284 | 4.6216 | 110.6765 | -17.1205 | 0 | 83.8778 | 96.1222 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7399 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1662 | 6 | -2.8 | 0 | 0 | 0 | 0 | 0 | 70 | 1662 | 360 | 69.0411 | -4.1884 | 3.01 | 334.284 | 5.6216 | 95.6765 | -6.937 | 0 | 83.8778 | 96.1222 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.741 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1663 | 7 | -3.8 | 0 | 0 | 0 | 0 | 0 | 70 | 1663 | 420 | 69.0411 | -4.1884 | 3.01 | 394.284 | 6.6216 | 80.6765 | 3.2923 | 3.2923 | 80.3264 | 99.6736 | 80.8377 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.4587 | 140.4587 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1664 | 8 | -3.8 | 0.92 | 12.14 | 13.06 | 12.14 | 6.07 | 70 | 1664 | 480 | 69.0411 | -4.1884 | 3.01 | 454.284 | 7.6216 | 65.6765 | 13.185 | 13.185 | 68.9723 | 111.0277 | 65.9004 | 1.6469 | 1.6469 | 10.3621 | 12.0091 | -13.43 | 0% | 5.4305 | 0 | 0 | 146.4614 | 146.4614 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1665 | 9 | -1.9 | 12.14 | 68.53 | 80.67 | 68.53 | 34.27 | 70 | 1665 | 540 | 69.0411 | -4.1884 | 3.01 | 514.284 | 8.6216 | 50.6765 | 22.3084 | 22.3084 | 56.5047 | 123.4953 | 50.9915 | 20.1304 | 20.1304 | 58.494 | 78.6244 | -1.3095 | 0% | 35.554 | 0 | 0 | 132.7758 | 132.7758 | 0% | 12.22% | 12.22% | 80% | 9.777% | 3.476 | 10.9403 | 6 | 20.8561 | 7.6869 | 15.71% | 15.71%
3 | 70 | 11 | 1666 | 10 | 1.6 | 27.69 | 110.47 | 138.16 | 110.47 | 55.24 | 70 | 1666 | 600 | 69.0411 | -4.1884 | 3.01 | 574.284 | 9.6216 | 35.6765 | 30.1054 | 30.1054 | 42.2485 | 137.7515 | 36.1479 | 44.5772 | 44.5772 | 94.292 | 138.8692 | -0.33034 | 0% | 62.7967 | 0 | 0 | 140.525 | 140.525 | 0% | 12.02% | 12.02% | 80% | 9.617% | 6.0391 | 9.7564 | 6 | 36.2344 | 13.3548 | 25.79% | 25.79%
3 | 70 | 11 | 1667 | 11 | 4.6 | 44.81 | 160.56 | 205.37 | 160.56 | 80.28 | 70 | 1667 | 660 | 69.0411 | -4.1884 | 3.01 | 634.284 | 10.6216 | 20.6765 | 35.8583 | 35.8583 | 25.7535 | 154.2465 | 21.5067 | 71.1698 | 71.1698 | 137.0465 | 208.2164 | 0.082434 | 8.243% | 94.1554 | 7.7616 | 5.4331 | 123.587 | 123.587 | 4.396% | 11.85% | 11.85% | 80% | 9.483% | 8.9284 | 8.8099 | 6 | 53.5703 | 19.7443 | 43.35% | 43.35%
3 | 70 | 11 | 1668 | 12 | 7.5 | 153.97 | 225.64 | 379.61 | 225.64 | 112.82 | 70 | 1668 | 720 | 69.0411 | -4.1884 | 3.01 | 694.284 | 11.6216 | 5.6765 | 38.787 | 38.787 | 7.2706 | 172.7294 | 8.2327 | 243.258 | 243.258 | 192.5958 | 435.8538 | 0.47518 | 47.52% | 197.0931 | 93.655 | 65.5585 | 130.0319 | 130.0319 | 50.42% | 11.6% | 11.6% | 85% | 9.862% | 19.4373 | 7.9549 | 6 | 116.6239 | 42.9839 | 89.69% | 89.69%
3 | 70 | 11 | 1669 | 13 | 7.8 | 138.97 | 284.64 | 423.61 | 284.64 | 142.32 | 70 | 1669 | 780 | 69.0411 | -4.1884 | 3.01 | 754.284 | 12.6216 | -9.3235 | 38.3711 | 38.3711 | 11.8933 | 191.8933 | 11.0638 | 219.7123 | 219.7123 | 242.9554 | 462.6678 | 0.49577 | 49.58% | 209.2184 | 103.7247 | 72.6073 | 131.6924 | 131.6924 | 55.13% | 11.58% | 11.58% | 85% | 9.842% | 20.5904 | 7.8698 | 6 | 123.5426 | 45.5339 | 93.81% | 93.81%
3 | 70 | 11 | 1670 | 14 | 8.6 | 181.67 | 256.19 | 437.86 | 256.19 | 128.1 | 70 | 1670 | 840 | 69.0411 | -4.1884 | 3.01 | 814.284 | 13.6216 | -24.3235 | 34.6909 | 34.6909 | 29.9735 | 209.9735 | 25.0285 | 289.2224 | 289.2224 | 218.6718 | 507.8942 | 0.52694 | 52.69% | 229.6698 | 121.0211 | 84.7147 | 132.6572 | 132.6572 | 63.86% | 11.54% | 11.54% | 90% | 10.38% | 23.8435 | 7.6459 | 6 | 143.0609 | 52.7277 | 107.8% | 107.8%
3 | 70 | 11 | 1671 | 15 | 10.2 | 161.11 | 189.44 | 350.55 | 189.44 | 94.72 | 70 | 1671 | 900 | 69.0411 | -4.1884 | 3.01 | 874.284 | 14.6216 | -39.3235 | 28.3679 | 28.3679 | 45.9108 | 225.9108 | 39.7469 | 260.7145 | 260.7145 | 161.6972 | 422.4117 | 0.47974 | 47.97% | 191.0146 | 91.6375 | 64.1463 | 129.3844 | 129.3844 | 49.58% | 11.56% | 11.56% | 85% | 9.822% | 18.7618 | 7.2117 | 6 | 112.5709 | 41.4901 | 87.01% | 87.01%
3 | 70 | 11 | 1672 | 16 | 11.8 | 135.47 | 151.86 | 287.33 | 151.86 | 75.93 | 70 | 1672 | 960 | 69.0411 | -4.1884 | 3.01 | 934.284 | 15.6216 | -54.3235 | 20.1884 | 20.1884 | 59.6761 | 239.6761 | 54.6124 | 227.3239 | 227.3239 | 129.6206 | 356.9445 | 0.43068 | 43.07% | 161.4103 | 69.5154 | 48.6608 | 127.9997 | 127.9997 | 38.02% | 11.55% | 11.55% | 85% | 9.819% | 15.849 | 6.7954 | 6 | 95.0937 | 35.0485 | 74.29% | 74.29%
3 | 70 | 11 | 1673 | 17 | 10.8 | 100 | 124.81 | 224.81 | 124.81 | 62.41 | 70 | 1673 | 1020 | 69.0411 | -4.1884 | 3.01 | 994.284 | 16.6216 | -69.3235 | 10.8325 | 10.8325 | 71.8086 | 251.8086 | 69.5303 | 186.0782 | 186.0782 | 106.532 | 292.6102 | 0.34067 | 34.07% | 132.3183 | 45.0775 | 31.5542 | 121.8138 | 121.8138 | 25.9% | 11.61% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1674 | 18 | 10 | 40.83 | 67.69 | 108.52 | 67.69 | 33.85 | 70 | 1674 | 1080 | 69.0411 | -4.1884 | 3.01 | 1054.284 | 17.6216 | -84.3235 | 0.82133 | 0.82133 | 82.9974 | 262.9974 | 84.4719 | 0 | 0 | 57.777 | 57.777 | -1.5748 | 0% | 26.1268 | 0 | 0 | 153.9286 | 153.9286 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1675 | 19 | 8.3 | 0 | 17.78 | 17.78 | 17.78 | 8.89 | 70 | 1675 | 1140 | 69.0411 | -4.1884 | 3.01 | 1114.284 | 18.6216 | -99.3235 | -9.4318 | 0 | 83.8778 | 263.8778 | 85.6751 | 0 | 0 | 15.1762 | 15.1762 | -8.515 | 0% | 6.8627 | 0 | 0 | 142.0328 | 142.0328 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1676 | 20 | 6.3 | 0 | 0 | 0 | 0 | 0 | 70 | 1676 | 1200 | 69.0411 | -4.1884 | 3.01 | 1174.284 | 19.6216 | -114.3235 | -19.5446 | 0 | 83.8778 | 263.8778 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.9378 | 132.9378 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1677 | 21 | 4.2 | 0 | 0 | 0 | 0 | 0 | 70 | 1677 | 1260 | 69.0411 | -4.1884 | 3.01 | 1234.284 | 20.6216 | -129.3235 | -29.0804 | 0 | 83.8778 | 263.8778 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5486 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1678 | 22 | 2.6 | 0 | 0 | 0 | 0 | 0 | 70 | 1678 | 1320 | 69.0411 | -4.1884 | 3.01 | 1294.284 | 21.6216 | -144.3235 | -37.4477 | 0 | 83.8778 | 263.8778 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1534 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1679 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 70 | 1679 | 1380 | 69.0411 | -4.1884 | 3.01 | 1354.284 | 22.6216 | -159.3235 | -43.8067 | 0 | 83.8778 | 263.8778 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8067 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
3 | 70 | 11 | 1680 | 24 | 2.3 | 0 | 0 | 0 | 0 | 0 | 70 | 1680 | 1440 | 69.0411 | -4.1884 | 3.01 | 1414.284 | 23.6216 | -174.3235 | -47.1276 | 0 | 83.8778 | 263.8778 | 85.6751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0884 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1681 | 1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 71 | 1681 | 60 | 70.0274 | -3.7947 | 3.3923 | 34.284 | 0.62794 | 170.5809 | -46.248 | 0 | 84.4543 | 95.5457 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5998 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1682 | 2 | -0.2 | 0 | 0 | 0 | 0 | 0 | 71 | 1682 | 120 | 70.0274 | -3.7947 | 3.3923 | 94.284 | 1.6279 | 155.5809 | -42.1 | 0 | 84.4543 | 95.5457 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2856 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1683 | 3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 71 | 1683 | 180 | 70.0274 | -3.7947 | 3.3923 | 154.284 | 2.6279 | 140.5809 | -35.1775 | 0 | 84.4543 | 95.5457 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0758 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1684 | 4 | 0.1 | 0 | 0 | 0 | 0 | 0 | 71 | 1684 | 240 | 70.0274 | -3.7947 | 3.3923 | 214.284 | 3.6279 | 125.5809 | -26.4759 | 0 | 84.4543 | 95.5457 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3806 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1685 | 5 | -0.9 | 0 | 0 | 0 | 0 | 0 | 71 | 1685 | 300 | 70.0274 | -3.7947 | 3.3923 | 274.284 | 4.6279 | 110.5809 | -16.7644 | 0 | 84.4543 | 95.5457 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7027 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1686 | 6 | -0.8 | 0 | 0 | 0 | 0 | 0 | 71 | 1686 | 360 | 70.0274 | -3.7947 | 3.3923 | 334.284 | 5.6279 | 95.5809 | -6.5852 | 0 | 84.4543 | 95.5457 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.4205 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1687 | 7 | -1.7 | 0 | 0 | 0 | 0 | 0 | 71 | 1687 | 420 | 70.0274 | -3.7947 | 3.3923 | 394.284 | 6.6279 | 80.5809 | 3.6466 | 3.6466 | 80.5231 | 99.4769 | 80.7256 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 153.4389 | 153.4389 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1688 | 8 | -1.3 | 2.5 | 14.53 | 17.03 | 14.53 | 7.27 | 71 | 1688 | 480 | 70.0274 | -3.7947 | 3.3923 | 454.284 | 7.6279 | 65.5809 | 13.5483 | 13.5483 | 69.1565 | 110.8435 | 65.7795 | 4.378 | 4.378 | 12.4021 | 16.7802 | -9.0099 | 0% | 7.588 | 0 | 0 | 161.7016 | 161.7016 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1689 | 9 | 0.1 | 9.72 | 62.69 | 72.41 | 62.69 | 31.35 | 71 | 1689 | 540 | 70.0274 | -3.7947 | 3.3923 | 514.284 | 8.6279 | 50.5809 | 22.6858 | 22.6858 | 56.6643 | 123.3357 | 50.8585 | 15.9087 | 15.9087 | 53.5093 | 69.418 | -1.5183 | 0% | 31.3908 | 0 | 0 | 146.3919 | 146.3919 | 0% | 12.15% | 12.15% | 80% | 9.721% | 3.0516 | 10.2533 | 6 | 18.3096 | 6.7483 | 12.51% | 12.51%
3 | 71 | 12 | 1690 | 10 | 4.1 | 105.28 | 125.75 | 231.03 | 125.75 | 62.88 | 71 | 1690 | 600 | 70.0274 | -3.7947 | 3.3923 | 574.284 | 9.6279 | 35.5809 | 30.4987 | 30.4987 | 42.3613 | 137.6387 | 35.9951 | 167.8336 | 167.8336 | 107.3343 | 275.1679 | 0.25362 | 25.36% | 124.4309 | 31.558 | 22.0906 | 138.0161 | 138.0161 | 16.01% | 11.81% | 11.81% | 80% | 9.449% | 11.7572 | 8.9633 | 6 | 70.5432 | 26 | 51.11% | 51.11%
3 | 71 | 12 | 1691 | 11 | 7.7 | 149.25 | 175.64 | 324.89 | 175.64 | 87.82 | 71 | 1691 | 660 | 70.0274 | -3.7947 | 3.3923 | 634.284 | 10.6279 | 20.5809 | 36.2626 | 36.2626 | 25.7863 | 154.2137 | 21.3111 | 235.0762 | 235.0762 | 149.9181 | 384.9943 | 0.43297 | 43.3% | 174.0944 | 75.3781 | 52.7647 | 141.4452 | 141.4452 | 37.3% | 11.63% | 11.63% | 85% | 9.888% | 17.2142 | 7.8981 | 6 | 103.2851 | 38.0676 | 73.02% | 73.02%
3 | 71 | 12 | 1692 | 12 | 9.9 | 103.14 | 200.19 | 303.33 | 200.19 | 100.1 | 71 | 1692 | 720 | 70.0274 | -3.7947 | 3.3923 | 694.284 | 11.6279 | 5.5809 | 39.1875 | 39.1875 | 7.1922 | 172.8078 | 7.8846 | 161.6893 | 161.6893 | 170.8729 | 332.5621 | 0.39003 | 39% | 150.3846 | 58.6544 | 41.058 | 134.4551 | 134.4551 | 30.54% | 11.61% | 11.61% | 85% | 9.87% | 14.8428 | 7.2918 | 6 | 89.057 | 32.8236 | 66.24% | 66.24%
3 | 71 | 12 | 1693 | 13 | 10 | 50.83 | 197.5 | 248.33 | 197.5 | 98.75 | 71 | 1693 | 780 | 70.0274 | -3.7947 | 3.3923 | 754.284 | 12.6279 | -9.4191 | 38.7473 | 38.7473 | 12.0858 | 192.0858 | 10.9397 | 79.737 | 79.737 | 168.5768 | 248.3138 | 0.25052 | 25.05% | 112.2875 | 28.1299 | 19.6909 | 130.0764 | 130.0764 | 15.14% | 11.66% | 11.66% | 80% | 9.324% | 10.4701 | 7.265 | 6 | 62.8204 | 23.1536 | 48.3% | 48.3%
3 | 71 | 12 | 1694 | 14 | 12 | 61.47 | 253.97 | 315.44 | 253.97 | 126.99 | 71 | 1694 | 840 | 70.0274 | -3.7947 | 3.3923 | 814.284 | 13.6279 | -24.4191 | 35.0277 | 35.0277 | 30.2479 | 210.2479 | 25.0337 | 97.035 | 97.035 | 216.777 | 313.812 | 0.38083 | 38.08% | 141.9058 | 54.0427 | 37.8299 | 134.5082 | 134.5082 | 28.12% | 11.57% | 11.57% | 85% | 9.831% | 13.9508 | 6.7446 | 6 | 83.7048 | 30.851 | 62.23% | 62.23%
3 | 71 | 12 | 1695 | 15 | 14.1 | 202.03 | 178.97 | 381 | 178.97 | 89.49 | 71 | 1695 | 900 | 70.0274 | -3.7947 | 3.3923 | 874.284 | 14.6279 | -39.4191 | 28.663 | 28.663 | 46.2267 | 226.2267 | 39.7892 | 323.649 | 323.649 | 152.7605 | 476.4094 | 0.53537 | 53.54% | 215.4324 | 115.3366 | 80.7356 | 137.3846 | 137.3846 | 58.77% | 11.46% | 11.46% | 85% | 9.738% | 20.9798 | 6.2283 | 6 | 125.8787 | 46.3949 | 91.63% | 91.63%
3 | 71 | 12 | 1696 | 16 | 14.3 | 82.03 | 190.19 | 272.22 | 190.19 | 95.1 | 71 | 1696 | 960 | 70.0274 | -3.7947 | 3.3923 | 934.284 | 15.6279 | -54.4191 | 20.4487 | 20.4487 | 60.0071 | 240.0071 | 54.6729 | 135.769 | 135.769 | 162.3373 | 298.1063 | 0.37623 | 37.62% | 134.8037 | 50.7172 | 35.5021 | 130.8256 | 130.8256 | 27.14% | 11.51% | 11.51% | 80% | 9.207% | 12.412 | 6.1808 | 6 | 74.4721 | 27.4481 | 56.92% | 56.92%
3 | 71 | 12 | 1697 | 17 | 14.5 | 54.72 | 131.31 | 186.03 | 131.31 | 65.66 | 71 | 1697 | 1020 | 70.0274 | -3.7947 | 3.3923 | 994.284 | 16.6279 | -69.4191 | 11.0685 | 11.0685 | 72.1439 | 252.1439 | 69.6021 | 99.342 | 99.342 | 112.0801 | 211.4221 | 0.203 | 20.3% | 95.6051 | 19.4074 | 13.5852 | 124.5588 | 124.5588 | 10.91% | 11.53% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1698 | 18 | 13.6 | 3.42 | 62.69 | 66.11 | 62.69 | 31.35 | 71 | 1698 | 1080 | 70.0274 | -3.7947 | 3.3923 | 1054.284 | 17.6279 | -84.4191 | 1.0444 | 1.0444 | 83.3356 | 263.3356 | 84.5522 | 0 | 0 | 53.5093 | 53.5093 | -1.609 | 0% | 24.1969 | 0 | 0 | 155.4786 | 155.4786 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1699 | 19 | 11 | 0 | 14.92 | 14.92 | 14.92 | 7.46 | 71 | 1699 | 1140 | 70.0274 | -3.7947 | 3.3923 | 1114.284 | 18.6279 | -99.4191 | -9.2101 | 0 | 84.4543 | 264.4543 | 86.0817 | 0 | 0 | 12.735 | 12.735 | -9.8053 | 0% | 5.7588 | 0 | 0 | 145.4795 | 145.4795 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1700 | 20 | 8.1 | 0 | 0 | 0 | 0 | 0 | 71 | 1700 | 1200 | 70.0274 | -3.7947 | 3.3923 | 1174.284 | 19.6279 | -114.4191 | -19.3124 | 0 | 84.4543 | 264.4543 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.0179 | 135.0179 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1701 | 21 | 6.3 | 0 | 0 | 0 | 0 | 0 | 71 | 1701 | 1260 | 70.0274 | -3.7947 | 3.3923 | 1234.284 | 20.6279 | -129.4191 | -28.8246 | 0 | 84.4543 | 264.4543 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9931 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1702 | 22 | 3.8 | 0 | 0 | 0 | 0 | 0 | 71 | 1702 | 1320 | 70.0274 | -3.7947 | 3.3923 | 1294.284 | 21.6279 | -144.4191 | -37.1549 | 0 | 84.4543 | 264.4543 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.9808 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1703 | 23 | 2.2 | 0 | 0 | 0 | 0 | 0 | 71 | 1703 | 1380 | 70.0274 | -3.7947 | 3.3923 | 1354.284 | 22.6279 | -159.4191 | -43.4673 | 0 | 84.4543 | 264.4543 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9714 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
3 | 71 | 12 | 1704 | 24 | 2.4 | 0 | 0 | 0 | 0 | 0 | 71 | 1704 | 1440 | 70.0274 | -3.7947 | 3.3923 | 1414.284 | 23.6279 | -174.4191 | -46.7452 | 0 | 84.4543 | 264.4543 | 86.0817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2188 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1705 | 1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 72 | 1705 | 60 | 71.0137 | -3.3997 | 3.7762 | 34.284 | 0.63434 | 170.4849 | -45.8427 | 0 | 85.0324 | 94.9676 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.54 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1706 | 2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 72 | 1706 | 120 | 71.0137 | -3.3997 | 3.7762 | 94.284 | 1.6343 | 155.4849 | -41.6983 | 0 | 85.0324 | 94.9676 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.7734 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1707 | 3 | -0.6 | 0 | 0 | 0 | 0 | 0 | 72 | 1707 | 180 | 71.0137 | -3.3997 | 3.7762 | 154.284 | 2.6343 | 140.4849 | -34.7919 | 0 | 85.0324 | 94.9676 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4641 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1708 | 4 | -0.7 | 0 | 0 | 0 | 0 | 0 | 72 | 1708 | 240 | 71.0137 | -3.3997 | 3.7762 | 214.284 | 3.6343 | 125.4849 | -26.1069 | 0 | 85.0324 | 94.9676 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.6165 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1709 | 5 | -0.7 | 0 | 0 | 0 | 0 | 0 | 72 | 1709 | 300 | 71.0137 | -3.3997 | 3.7762 | 274.284 | 4.6343 | 110.4849 | -16.4067 | 0 | 85.0324 | 94.9676 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5621 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1710 | 6 | -1.4 | 0 | 0 | 0 | 0 | 0 | 72 | 1710 | 360 | 71.0137 | -3.3997 | 3.7762 | 334.284 | 5.6343 | 95.4849 | -6.2321 | 0 | 85.0324 | 94.9676 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.813 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1711 | 7 | -3.1 | 0 | 0 | 0 | 0 | 0 | 72 | 1711 | 420 | 71.0137 | -3.3997 | 3.7762 | 394.284 | 6.6343 | 80.4849 | 4.0022 | 4.0022 | 80.7204 | 99.2796 | 80.6133 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.7862 | 143.7862 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1712 | 8 | -1.6 | 2.22 | 14.53 | 16.75 | 14.53 | 7.27 | 72 | 1712 | 480 | 71.0137 | -3.3997 | 3.7762 | 454.284 | 7.6343 | 65.4849 | 13.9127 | 13.9127 | 69.3418 | 110.6582 | 65.6592 | 3.8055 | 3.8055 | 12.4021 | 16.2076 | -9.4026 | 0% | 7.3291 | 0 | 0 | 153.0095 | 153.0095 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1713 | 9 | -0.4 | 5.83 | 66.58 | 72.41 | 66.58 | 33.29 | 72 | 1713 | 540 | 71.0137 | -3.3997 | 3.7762 | 514.284 | 8.6343 | 50.4849 | 23.0642 | 23.0642 | 56.8251 | 123.1749 | 50.7271 | 9.4202 | 9.4202 | 56.8296 | 66.2498 | -1.648 | 0% | 29.9582 | 0 | 0 | 137.5857 | 137.5857 | 0% | 12.18% | 12.18% | 80% | 9.74% | 2.918 | 10.4224 | 6 | 17.5079 | 6.4529 | 12.73% | 12.73%
3 | 72 | 13 | 1714 | 10 | 3.7 | 12.78 | 122.58 | 135.36 | 122.58 | 61.29 | 72 | 1714 | 600 | 71.0137 | -3.3997 | 3.7762 | 574.284 | 9.6343 | 35.4849 | 30.8931 | 30.8931 | 42.4752 | 137.5248 | 35.845 | 20.1768 | 20.1768 | 104.6286 | 124.8053 | -0.41721 | 0% | 56.437 | 0 | 0 | 146.8263 | 146.8263 | 0% | 11.96% | 11.96% | 80% | 9.566% | 5.3987 | 9.0873 | 6 | 32.3921 | 11.9387 | 22.06% | 22.06%
3 | 72 | 13 | 1715 | 11 | 6.7 | 123.61 | 196.31 | 319.92 | 196.31 | 98.16 | 72 | 1715 | 660 | 71.0137 | -3.3997 | 3.7762 | 634.284 | 10.6343 | 20.4849 | 36.6681 | 36.6681 | 25.8193 | 154.1807 | 21.1204 | 193.0853 | 193.0853 | 167.5611 | 360.6464 | 0.40135 | 40.13% | 163.0843 | 65.4531 | 45.8172 | 135.3409 | 135.3409 | 33.85% | 11.67% | 11.67% | 85% | 9.922% | 16.1818 | 8.1849 | 6 | 97.0911 | 35.7847 | 71.74% | 71.74%
3 | 72 | 13 | 1716 | 12 | 8.9 | 156.94 | 164.53 | 321.47 | 164.53 | 82.27 | 72 | 1716 | 720 | 71.0137 | -3.3997 | 3.7762 | 694.284 | 11.6343 | 5.4849 | 39.5892 | 39.5892 | 7.1123 | 172.8877 | 7.541 | 244.136 | 244.136 | 140.4351 | 384.5712 | 0.43992 | 43.99% | 173.9031 | 76.5037 | 53.5526 | 131.8299 | 131.8299 | 40.62% | 11.61% | 11.61% | 85% | 9.865% | 17.1551 | 7.5632 | 6 | 102.9309 | 37.9371 | 78.08% | 78.08%
3 | 72 | 13 | 1717 | 13 | 10.7 | 142.03 | 217.5 | 359.53 | 217.5 | 108.75 | 72 | 1717 | 780 | 71.0137 | -3.3997 | 3.7762 | 754.284 | 12.6343 | -9.5151 | 39.1242 | 39.1242 | 12.2812 | 192.2812 | 10.8289 | 221.0777 | 221.0777 | 185.6479 | 406.7256 | 0.4701 | 47.01% | 183.9213 | 86.4611 | 60.5228 | 135.4509 | 135.4509 | 44.68% | 11.55% | 11.55% | 85% | 9.82% | 18.0614 | 7.0797 | 6 | 108.3685 | 39.9412 | 80.01% | 80.01%
3 | 72 | 13 | 1718 | 14 | 12.6 | 123.25 | 248.89 | 372.14 | 248.89 | 124.45 | 72 | 1718 | 840 | 71.0137 | -3.3997 | 3.7762 | 814.284 | 13.6343 | -24.5151 | 35.3649 | 35.3649 | 30.5256 | 210.5256 | 25.0452 | 192.9247 | 192.9247 | 212.4409 | 405.3656 | 0.47982 | 47.98% | 183.3063 | 87.9539 | 61.5677 | 138.2569 | 138.2569 | 44.53% | 11.51% | 11.51% | 85% | 9.786% | 17.9378 | 6.5939 | 6 | 107.6271 | 39.668 | 77.85% | 77.85%
3 | 72 | 13 | 1719 | 15 | 13.2 | 284.72 | 146.75 | 431.47 | 146.75 | 73.38 | 72 | 1719 | 900 | 71.0137 | -3.3997 | 3.7762 | 874.284 | 14.6343 | -39.5151 | 28.9582 | 28.9582 | 46.5455 | 226.5455 | 39.8353 | 451.5614 | 451.5614 | 125.259 | 576.8203 | 0.57857 | 57.86% | 260.8382 | 150.9125 | 105.6387 | 139.1958 | 139.1958 | 75.89% | 11.44% | 11.44% | 90% | 10.29% | 26.8453 | 6.4458 | 6 | 161.0716 | 59.3659 | 115.7% | 115.7%
3 | 72 | 13 | 1720 | 16 | 13.8 | 207.31 | 114.25 | 321.56 | 114.25 | 57.13 | 72 | 1720 | 960 | 71.0137 | -3.3997 | 3.7762 | 934.284 | 15.6343 | -54.5151 | 20.709 | 20.709 | 60.3405 | 240.3405 | 54.7357 | 338.4693 | 338.4693 | 97.5185 | 435.9877 | 0.5089 | 50.89% | 197.1537 | 100.3309 | 70.2316 | 134.2967 | 134.2967 | 52.3% | 11.48% | 11.48% | 85% | 9.755% | 19.2318 | 6.3002 | 6 | 115.3906 | 42.5293 | 85.92% | 85.92%
3 | 72 | 13 | 1721 | 17 | 14.2 | 134.72 | 76.19 | 210.91 | 76.19 | 38.1 | 72 | 1721 | 1020 | 71.0137 | -3.3997 | 3.7762 | 994.284 | 16.6343 | -69.5151 | 11.3048 | 11.3048 | 72.481 | 252.481 | 69.6755 | 238.707 | 238.707 | 65.0322 | 303.7393 | 0.38341 | 38.34% | 137.3509 | 52.6622 | 36.8635 | 127.6389 | 127.6389 | 28.88% | 11.51% | 0% | 85% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1722 | 18 | 13.5 | 66.39 | 46.58 | 112.97 | 46.58 | 23.29 | 72 | 1722 | 1080 | 71.0137 | -3.3997 | 3.7762 | 1054.284 | 17.6343 | -84.5151 | 1.2681 | 1.2681 | 83.675 | 263.675 | 84.6333 | 0 | 0 | 39.7585 | 39.7585 | -2.4493 | 0% | 17.9788 | 0 | 0 | 160.4993 | 160.4993 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1723 | 19 | 12 | 0 | 11.75 | 11.75 | 11.75 | 5.88 | 72 | 1723 | 1140 | 71.0137 | -3.3997 | 3.7762 | 1114.284 | 18.6343 | -99.5151 | -8.9876 | 0 | 85.0324 | 265.0324 | 86.4896 | 0 | 0 | 10.0293 | 10.0293 | -12.4367 | 0% | 4.5352 | 0 | 0 | 147.3138 | 147.3138 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1724 | 20 | 8.8 | 0 | 0 | 0 | 0 | 0 | 72 | 1724 | 1200 | 71.0137 | -3.3997 | 3.7762 | 1174.284 | 19.6343 | -114.5151 | -19.0789 | 0 | 85.0324 | 265.0324 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.1385 | 136.1385 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1725 | 21 | 6.9 | 0 | 0 | 0 | 0 | 0 | 72 | 1725 | 1260 | 71.0137 | -3.3997 | 3.7762 | 1234.284 | 20.6343 | -129.5151 | -28.5672 | 0 | 85.0324 | 265.0324 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1868 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1726 | 22 | 4.9 | 0 | 0 | 0 | 0 | 0 | 72 | 1726 | 1320 | 71.0137 | -3.3997 | 3.7762 | 1294.284 | 21.6343 | -144.5151 | -36.8602 | 0 | 85.0324 | 265.0324 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5348 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1727 | 23 | 3.7 | 0 | 0 | 0 | 0 | 0 | 72 | 1727 | 1380 | 71.0137 | -3.3997 | 3.7762 | 1354.284 | 22.6343 | -159.5151 | -43.126 | 0 | 85.0324 | 265.0324 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.073 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
3 | 72 | 13 | 1728 | 24 | 2.3 | 0 | 0 | 0 | 0 | 0 | 72 | 1728 | 1440 | 71.0137 | -3.3997 | 3.7762 | 1414.284 | 23.6343 | -174.5151 | -46.3612 | 0 | 85.0324 | 265.0324 | 86.4896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9161 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1729 | 1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 73 | 1729 | 60 | 72 | -3.0036 | 4.1613 | 34.284 | 0.64076 | 170.3887 | -45.4362 | 0 | 85.6118 | 94.3882 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0603 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1730 | 2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 73 | 1730 | 120 | 72 | -3.0036 | 4.1613 | 94.284 | 1.6408 | 155.3887 | -41.2953 | 0 | 85.6118 | 94.3882 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5797 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1731 | 3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 73 | 1731 | 180 | 72 | -3.0036 | 4.1613 | 154.284 | 2.6408 | 140.3887 | -34.4051 | 0 | 85.6118 | 94.3882 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4038 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1732 | 4 | 0.3 | 0 | 0 | 0 | 0 | 0 | 73 | 1732 | 240 | 72 | -3.0036 | 4.1613 | 214.284 | 3.6408 | 125.3887 | -25.7366 | 0 | 85.6118 | 94.3882 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.861 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1733 | 5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 73 | 1733 | 300 | 72 | -3.0036 | 4.1613 | 274.284 | 4.6408 | 110.3887 | -16.0478 | 0 | 85.6118 | 94.3882 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.767 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1734 | 6 | 1.4 | 0 | 0 | 0 | 0 | 0 | 73 | 1734 | 360 | 72 | -3.0036 | 4.1613 | 334.284 | 5.6408 | 95.3887 | -5.8778 | 0 | 85.6118 | 94.3882 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.0267 | 9.0267 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1735 | 7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 73 | 1735 | 420 | 72 | -3.0036 | 4.1613 | 394.284 | 6.6408 | 80.3887 | 4.3588 | 4.3588 | 80.9184 | 99.0816 | 80.5011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 180.8974 | 180.8974 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1736 | 8 | 2.6 | 12.86 | 15.83 | 28.69 | 15.83 | 7.92 | 73 | 1736 | 480 | 72 | -3.0036 | 4.1613 | 454.284 | 7.6408 | 65.3887 | 14.2781 | 14.2781 | 69.5281 | 110.4719 | 65.5397 | 21.5905 | 21.5905 | 13.5118 | 35.1023 | -3.614 | 0% | 15.8732 | 0 | 0 | 193.6917 | 193.6917 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1737 | 9 | 4 | 99.25 | 66.19 | 165.44 | 66.19 | 33.1 | 73 | 1737 | 540 | 72 | -3.0036 | 4.1613 | 514.284 | 8.6408 | 50.3887 | 23.4436 | 23.4436 | 56.9873 | 123.0127 | 50.5972 | 158.3543 | 158.3543 | 56.4967 | 214.851 | 0.097982 | 9.798% | 97.1556 | 9.5195 | 6.6636 | 183.9612 | 183.9612 | 3.622% | 11.87% | 11.87% | 80% | 9.494% | 9.2235 | 8.9942 | 6 | 55.3411 | 20.397 | 30.08% | 30.08%
3 | 73 | 14 | 1738 | 10 | 7 | 234.72 | 89.53 | 324.25 | 89.53 | 44.77 | 73 | 1738 | 600 | 72 | -3.0036 | 4.1613 | 574.284 | 9.6408 | 35.3887 | 31.2887 | 31.2887 | 42.5902 | 137.4098 | 35.6979 | 367.0303 | 367.0303 | 76.4186 | 443.449 | 0.47814 | 47.81% | 200.5276 | 95.88 | 67.116 | 172.5753 | 172.5753 | 38.89% | 11.61% | 11.61% | 85% | 9.866% | 19.7838 | 8.0981 | 6 | 118.7031 | 43.7502 | 68.78% | 68.78%
3 | 73 | 14 | 1739 | 11 | 10.7 | 357.14 | 101.47 | 458.61 | 101.47 | 50.74 | 73 | 1739 | 660 | 72 | -3.0036 | 4.1613 | 634.284 | 10.6408 | 20.3887 | 37.0749 | 37.0749 | 25.8526 | 154.1474 | 20.9349 | 553.3041 | 553.3041 | 86.6101 | 639.9142 | 0.59177 | 59.18% | 289.3692 | 171.2412 | 119.8689 | 174.0193 | 174.0193 | 68.88% | 11.43% | 11.43% | 90% | 10.29% | 29.7775 | 7.0797 | 6 | 178.6651 | 65.8503 | 102.7% | 102.7%
3 | 73 | 14 | 1740 | 12 | 11.4 | 408.53 | 125.75 | 534.28 | 125.75 | 62.88 | 73 | 1740 | 720 | 72 | -3.0036 | 4.1613 | 694.284 | 11.6408 | 5.3887 | 39.992 | 39.992 | 7.0312 | 172.9688 | 7.2029 | 630.649 | 630.649 | 107.3343 | 737.9834 | 0.62218 | 62.22% | 333.7161 | 207.6308 | 145.3416 | 162.9827 | 162.9827 | 89.18% | 11.38% | 11.38% | 90% | 10.24% | 34.1832 | 6.8978 | 6 | 205.0992 | 75.5931 | 125.8% | 125.8%
3 | 73 | 14 | 1741 | 13 | 12.3 | 544.25 | 122.42 | 666.67 | 122.42 | 61.21 | 73 | 1741 | 780 | 72 | -3.0036 | 4.1613 | 754.284 | 12.6408 | -9.6113 | 39.5019 | 39.5019 | 12.4794 | 192.4794 | 10.732 | 840.6342 | 840.6342 | 104.492 | 945.1262 | 0.66423 | 66.42% | 427.3861 | 283.8817 | 198.7172 | 165.7338 | 165.7338 | 119.9% | 11.29% | 11.29% | 95% | 10.73% | 45.8415 | 6.669 | 6 | 275.0489 | 101.3743 | 166% | 166%
3 | 73 | 14 | 1742 | 14 | 12 | 499.25 | 147.03 | 646.28 | 147.03 | 73.52 | 73 | 1742 | 840 | 72 | -3.0036 | 4.1613 | 814.284 | 13.6408 | -24.6113 | 35.7024 | 35.7024 | 30.8065 | 210.8065 | 25.0631 | 774.9506 | 774.9506 | 125.498 | 900.4485 | 0.65652 | 65.65% | 407.1828 | 267.3254 | 187.1278 | 161.8666 | 161.8666 | 115.6% | 11.31% | 11.31% | 95% | 10.74% | 43.7413 | 6.7446 | 6 | 262.4475 | 96.7299 | 162.1% | 162.1%
3 | 73 | 14 | 1743 | 15 | 12.6 | 426.75 | 141.86 | 568.61 | 141.86 | 70.93 | 73 | 1743 | 900 | 72 | -3.0036 | 4.1613 | 874.284 | 14.6408 | -39.6113 | 29.2535 | 29.2535 | 46.8672 | 226.8672 | 39.885 | 670.0972 | 670.0972 | 121.0851 | 791.1823 | 0.6379 | 63.79% | 357.7726 | 228.2248 | 159.7574 | 155.5904 | 155.5904 | 102.7% | 11.36% | 11.36% | 90% | 10.22% | 36.5645 | 6.5939 | 6 | 219.3868 | 80.8591 | 141% | 141%
3 | 73 | 14 | 1744 | 16 | 12.8 | 223.53 | 125.56 | 349.09 | 125.56 | 62.78 | 73 | 1744 | 960 | 72 | -3.0036 | 4.1613 | 934.284 | 15.6408 | -54.6113 | 20.9694 | 20.9694 | 60.676 | 240.676 | 54.8008 | 360.0399 | 360.0399 | 107.1722 | 467.2121 | 0.52372 | 52.37% | 211.2733 | 110.6472 | 77.4531 | 143.294 | 143.294 | 54.05% | 11.48% | 11.48% | 85% | 9.761% | 20.6228 | 6.5443 | 6 | 123.7371 | 45.6056 | 86.35% | 86.35%
3 | 73 | 14 | 1745 | 17 | 12.4 | 197.86 | 98.69 | 296.55 | 98.69 | 49.35 | 73 | 1745 | 1020 | 72 | -3.0036 | 4.1613 | 994.284 | 16.6408 | -69.6113 | 11.5413 | 11.5413 | 72.8198 | 252.8198 | 69.7501 | 342.2849 | 342.2849 | 84.2372 | 426.5221 | 0.49482 | 49.48% | 192.8733 | 95.4376 | 66.8063 | 136.6072 | 136.6072 | 48.9% | 11.51% | 0% | 85% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1746 | 18 | 11.8 | 98.61 | 65.19 | 163.8 | 65.19 | 32.6 | 73 | 1746 | 1080 | 72 | -3.0036 | 4.1613 | 1054.284 | 17.6408 | -84.6113 | 1.4923 | 1.4923 | 84.0155 | 264.0155 | 84.7149 | 0 | 0 | 55.6431 | 55.6431 | -1.5908 | 0% | 25.1618 | 0 | 0 | 123.5831 | 123.5831 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1747 | 19 | 10.5 | 0 | 20.08 | 20.08 | 20.08 | 10.04 | 73 | 1747 | 1140 | 72 | -3.0036 | 4.1613 | 1114.284 | 18.6408 | -99.6113 | -8.7641 | 0 | 85.6118 | 265.6118 | 86.8986 | 0 | 0 | 17.1394 | 17.1394 | -7.1468 | 0% | 7.7504 | 0 | 0 | 148.4046 | 148.4046 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1748 | 20 | 8.2 | 0 | 0 | 0 | 0 | 0 | 73 | 1748 | 1200 | 72 | -3.0036 | 4.1613 | 1174.284 | 19.6408 | -114.6113 | -18.8441 | 0 | 85.6118 | 265.6118 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.5842 | 135.5842 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1749 | 21 | 6.5 | 0 | 0 | 0 | 0 | 0 | 73 | 1749 | 1260 | 72 | -3.0036 | 4.1613 | 1234.284 | 20.6408 | -129.6113 | -28.3081 | 0 | 85.6118 | 265.6118 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0294 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1750 | 22 | 5.2 | 0 | 0 | 0 | 0 | 0 | 73 | 1750 | 1320 | 72 | -3.0036 | 4.1613 | 1294.284 | 21.6408 | -144.6113 | -36.5637 | 0 | 85.6118 | 265.6118 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.8927 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1751 | 23 | 3.9 | 0 | 0 | 0 | 0 | 0 | 73 | 1751 | 1380 | 72 | -3.0036 | 4.1613 | 1354.284 | 22.6408 | -159.6113 | -42.7831 | 0 | 85.6118 | 265.6118 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.174 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
3 | 73 | 14 | 1752 | 24 | 3 | 0 | 0 | 0 | 0 | 0 | 73 | 1752 | 1440 | 72 | -3.0036 | 4.1613 | 1414.284 | 23.6408 | -174.6113 | -45.9758 | 0 | 85.6118 | 265.6118 | 86.8986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8458 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1753 | 1 | 2.5 | 0 | 0 | 0 | 0 | 0 | 74 | 1753 | 60 | 72.9863 | -2.6064 | 4.5471 | 34.284 | 0.64719 | 170.2922 | -45.0286 | 0 | 86.1926 | 93.8074 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4075 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1754 | 2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 74 | 1754 | 120 | 72.9863 | -2.6064 | 4.5471 | 94.284 | 1.6472 | 155.2922 | -40.8913 | 0 | 86.1926 | 93.8074 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0025 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1755 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 74 | 1755 | 180 | 72.9863 | -2.6064 | 4.5471 | 154.284 | 2.6472 | 140.2922 | -34.017 | 0 | 86.1926 | 93.8074 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9878 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1756 | 4 | 2.4 | 0 | 0 | 0 | 0 | 0 | 74 | 1756 | 240 | 72.9863 | -2.6064 | 4.5471 | 214.284 | 3.6472 | 125.2922 | -25.3651 | 0 | 86.1926 | 93.8074 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6163 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1757 | 5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 74 | 1757 | 300 | 72.9863 | -2.6064 | 4.5471 | 274.284 | 4.6472 | 110.2922 | -15.6878 | 0 | 86.1926 | 93.8074 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4469 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1758 | 6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 74 | 1758 | 360 | 72.9863 | -2.6064 | 4.5471 | 334.284 | 5.6472 | 95.2922 | -5.5226 | 0 | 86.1926 | 93.8074 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.2578 | 1.2578 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1759 | 7 | 1.2 | 0 | 0 | 0 | 0 | 0 | 74 | 1759 | 420 | 72.9863 | -2.6064 | 4.5471 | 394.284 | 6.6472 | 80.2922 | 4.7162 | 4.7162 | 81.1171 | 98.8829 | 80.3891 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 164.1375 | 164.1375 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1760 | 8 | 1.6 | 6.31 | 16.94 | 23.25 | 16.94 | 8.47 | 74 | 1760 | 480 | 72.9863 | -2.6064 | 4.5471 | 454.284 | 7.6472 | 65.2922 | 14.6443 | 14.6443 | 69.7155 | 110.2845 | 65.4211 | 10.3815 | 10.3815 | 14.4592 | 24.8407 | -5.5374 | 0% | 11.233 | 0 | 0 | 174.5852 | 174.5852 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1761 | 9 | 2.4 | 63.33 | 69.17 | 132.5 | 69.17 | 34.59 | 74 | 1761 | 540 | 72.9863 | -2.6064 | 4.5471 | 514.284 | 8.6472 | 50.2922 | 23.8239 | 23.8239 | 57.1508 | 122.8492 | 50.4692 | 99.7932 | 99.7932 | 59.0403 | 158.8335 | -0.17546 | 0% | 71.8245 | 0 | 0 | 162.2319 | 162.2319 | 0% | 11.97% | 11.97% | 80% | 9.578% | 6.8794 | 9.4979 | 6 | 41.2766 | 15.2133 | 25.44% | 25.44%
3 | 74 | 15 | 1762 | 10 | 4.5 | 162.69 | 114.53 | 277.22 | 114.53 | 57.27 | 74 | 1762 | 600 | 72.9863 | -2.6064 | 4.5471 | 574.284 | 9.6472 | 35.2922 | 31.6851 | 31.6851 | 42.7065 | 137.2935 | 35.554 | 251.9928 | 251.9928 | 97.7575 | 349.7503 | 0.37374 | 37.37% | 158.1571 | 59.11 | 41.377 | 150.2891 | 150.2891 | 27.53% | 11.74% | 11.74% | 85% | 9.975% | 15.7769 | 8.8405 | 6 | 94.6614 | 34.8892 | 62.99% | 62.99%
3 | 74 | 15 | 1763 | 11 | 7.5 | 257.22 | 164.25 | 421.47 | 164.25 | 82.13 | 74 | 1763 | 660 | 72.9863 | -2.6064 | 4.5471 | 634.284 | 10.6472 | 20.2922 | 37.4827 | 37.4827 | 25.8864 | 154.1136 | 20.7551 | 395.2651 | 395.2651 | 140.1961 | 535.4613 | 0.53635 | 53.63% | 242.1356 | 129.8691 | 90.9084 | 154.377 | 154.377 | 58.89% | 11.53% | 11.53% | 90% | 10.38% | 25.1348 | 7.9549 | 6 | 150.8091 | 55.5835 | 97.69% | 97.69%
3 | 74 | 15 | 1764 | 12 | 10.8 | 272.5 | 133.42 | 405.92 | 133.42 | 66.71 | 74 | 1764 | 720 | 72.9863 | -2.6064 | 4.5471 | 694.284 | 11.6472 | 5.2922 | 40.3958 | 40.3958 | 6.9489 | 173.0511 | 6.8714 | 417.4627 | 417.4627 | 113.8811 | 531.3438 | 0.54885 | 54.88% | 240.2736 | 131.8735 | 92.3115 | 147.5261 | 147.5261 | 62.57% | 11.49% | 11.49% | 90% | 10.34% | 24.8422 | 7.0535 | 6 | 149.0535 | 54.9364 | 101% | 101%
3 | 74 | 15 | 1765 | 13 | 11.9 | 452.86 | 153.61 | 606.47 | 153.61 | 76.81 | 74 | 1765 | 780 | 72.9863 | -2.6064 | 4.5471 | 754.284 | 12.6472 | -9.7078 | 39.8802 | 39.8802 | 12.6802 | 192.6802 | 10.6496 | 694.1214 | 694.1214 | 131.1143 | 825.2357 | 0.6428 | 64.28% | 373.1716 | 239.876 | 167.9132 | 155.4612 | 155.4612 | 108% | 11.34% | 11.34% | 95% | 10.77% | 40.2045 | 6.77 | 6 | 241.2268 | 88.9086 | 155.2% | 155.2%
3 | 74 | 15 | 1766 | 14 | 12.4 | 360.19 | 151.03 | 511.22 | 151.03 | 75.52 | 74 | 1766 | 840 | 72.9863 | -2.6064 | 4.5471 | 814.284 | 13.6472 | -24.7078 | 36.04 | 36.04 | 31.0906 | 211.0906 | 25.0872 | 554.4501 | 554.4501 | 128.9122 | 683.3622 | 0.61102 | 61.1% | 309.0164 | 188.8166 | 132.1716 | 150.8435 | 150.8435 | 87.62% | 11.4% | 11.4% | 90% | 10.26% | 31.7072 | 6.6439 | 6 | 190.2431 | 70.1176 | 126.1% | 126.1%
3 | 74 | 15 | 1767 | 15 | 12.6 | 249.92 | 140.47 | 390.39 | 140.47 | 70.24 | 74 | 1767 | 900 | 72.9863 | -2.6064 | 4.5471 | 874.284 | 14.6472 | -39.7078 | 29.5487 | 29.5487 | 47.1916 | 227.1916 | 39.9383 | 388.5582 | 388.5582 | 119.8986 | 508.4569 | 0.54555 | 54.55% | 229.9242 | 125.4346 | 87.8042 | 143.0135 | 143.0135 | 61.4% | 11.47% | 11.47% | 90% | 10.32% | 23.7364 | 6.5939 | 6 | 142.4186 | 52.491 | 99.58% | 99.58%
3 | 74 | 15 | 1768 | 16 | 12.1 | 289.53 | 130.08 | 419.61 | 130.08 | 65.04 | 74 | 1768 | 960 | 72.9863 | -2.6064 | 4.5471 | 934.284 | 15.6472 | -54.7078 | 21.2298 | 21.2298 | 61.0136 | 241.0136 | 54.8681 | 460.1178 | 460.1178 | 111.0302 | 571.1481 | 0.5719 | 57.19% | 258.2732 | 147.7064 | 103.3945 | 142.2542 | 142.2542 | 72.68% | 11.45% | 11.45% | 90% | 10.31% | 26.6184 | 6.7193 | 6 | 159.7103 | 58.8642 | 112.3% | 112.3%
3 | 74 | 15 | 1769 | 17 | 10.1 | 214.44 | 102.22 | 316.66 | 102.22 | 51.11 | 74 | 1769 | 1020 | 72.9863 | -2.6064 | 4.5471 | 994.284 | 16.6472 | -69.7078 | 11.778 | 11.778 | 73.1599 | 253.1599 | 69.826 | 362.3077 | 362.3077 | 87.2502 | 449.5579 | 0.4988 | 49.88% | 203.2901 | 101.4016 | 70.9811 | 131.7111 | 131.7111 | 53.89% | 11.54% | 0% | 85% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1770 | 18 | 9.4 | 100.83 | 63.33 | 164.16 | 63.33 | 31.67 | 74 | 1770 | 1080 | 72.9863 | -2.6064 | 4.5471 | 1054.284 | 17.6472 | -84.7078 | 1.717 | 1.717 | 84.357 | 264.357 | 84.797 | 0 | 0 | 54.0555 | 54.0555 | -1.7645 | 0% | 24.4439 | 0 | 0 | 118.441 | 118.441 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1771 | 19 | 8.2 | 0 | 23.97 | 23.97 | 23.97 | 11.99 | 74 | 1771 | 1140 | 72.9863 | -2.6064 | 4.5471 | 1114.284 | 18.6472 | -99.7078 | -8.5398 | 0 | 86.1926 | 266.1926 | 87.3087 | 0 | 0 | 20.4597 | 20.4597 | -6.12 | 0% | 9.2519 | 0 | 0 | 143.9074 | 143.9074 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1772 | 20 | 7.6 | 0 | 0 | 0 | 0 | 0 | 74 | 1772 | 1200 | 72.9863 | -2.6064 | 4.5471 | 1174.284 | 19.6472 | -114.7078 | -18.6081 | 0 | 86.1926 | 266.1926 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.4548 | 134.4548 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1773 | 21 | 6.9 | 0 | 0 | 0 | 0 | 0 | 74 | 1773 | 1260 | 72.9863 | -2.6064 | 4.5471 | 1234.284 | 20.6472 | -129.7078 | -28.0474 | 0 | 86.1926 | 266.1926 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4408 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1774 | 22 | 5.9 | 0 | 0 | 0 | 0 | 0 | 74 | 1774 | 1320 | 72.9863 | -2.6064 | 4.5471 | 1294.284 | 21.6472 | -144.7078 | -36.2654 | 0 | 86.1926 | 266.1926 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6414 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1775 | 23 | 5.1 | 0 | 0 | 0 | 0 | 0 | 74 | 1775 | 1380 | 72.9863 | -2.6064 | 4.5471 | 1354.284 | 22.6472 | -159.7078 | -42.4384 | 0 | 86.1926 | 266.1926 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.3888 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
3 | 74 | 15 | 1776 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 74 | 1776 | 1440 | 72.9863 | -2.6064 | 4.5471 | 1414.284 | 23.6472 | -174.7078 | -45.5891 | 0 | 86.1926 | 266.1926 | 87.3087 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0693 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1777 | 1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 75 | 1777 | 60 | 73.9726 | -2.2083 | 4.9333 | 34.284 | 0.65362 | 170.1957 | -44.6201 | 0 | 86.7744 | 93.2256 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9545 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1778 | 2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 75 | 1778 | 120 | 73.9726 | -2.2083 | 4.9333 | 94.284 | 1.6536 | 155.1957 | -40.4863 | 0 | 86.7744 | 93.2256 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8402 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1779 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 75 | 1779 | 180 | 73.9726 | -2.2083 | 4.9333 | 154.284 | 2.6536 | 140.1957 | -33.6279 | 0 | 86.7744 | 93.2256 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4879 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1780 | 4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 75 | 1780 | 240 | 73.9726 | -2.2083 | 4.9333 | 214.284 | 3.6536 | 125.1957 | -24.9926 | 0 | 86.7744 | 93.2256 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0975 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1781 | 5 | 4.4 | 0 | 0 | 0 | 0 | 0 | 75 | 1781 | 300 | 73.9726 | -2.2083 | 4.9333 | 274.284 | 4.6536 | 110.1957 | -15.3268 | 0 | 86.7744 | 93.2256 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.2463 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1782 | 6 | 4.1 | 0 | 0 | 0 | 0 | 0 | 75 | 1782 | 360 | 73.9726 | -2.2083 | 4.9333 | 334.284 | 5.6536 | 95.1957 | -5.1665 | 0 | 86.7744 | 93.2256 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.87289 | 0.87289 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1783 | 7 | 5.4 | 0 | 0 | 0 | 0 | 0 | 75 | 1783 | 420 | 73.9726 | -2.2083 | 4.9333 | 394.284 | 6.6536 | 80.1957 | 5.0744 | 5.0744 | 81.3166 | 98.6834 | 80.2773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 162.6551 | 162.6551 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1784 | 8 | 5.4 | 6.86 | 16.75 | 23.61 | 16.75 | 8.38 | 75 | 1784 | 480 | 73.9726 | -2.2083 | 4.9333 | 454.284 | 7.6536 | 65.1957 | 15.0111 | 15.0111 | 69.904 | 110.096 | 65.3035 | 11.0661 | 11.0661 | 14.297 | 25.3631 | -5.0439 | 0% | 11.4692 | 0 | 0 | 170.5035 | 170.5035 | 0% | 11.97% | 11.97% | 80% | 9.579% | 1.0987 | 8.5682 | 6 | 6.592 | 2.4296 | 3.866% | 3.866%
3 | 75 | 16 | 1785 | 9 | 5.2 | 61.67 | 70.83 | 132.5 | 70.83 | 35.42 | 75 | 1785 | 540 | 73.9726 | -2.2083 | 4.9333 | 514.284 | 8.6536 | 50.1957 | 24.2048 | 24.2048 | 57.3156 | 122.6844 | 50.3431 | 95.9931 | 95.9931 | 60.4572 | 156.4503 | -0.1471 | 0% | 70.7468 | 0 | 0 | 155.8194 | 155.8194 | 0% | 11.88% | 11.88% | 80% | 9.501% | 6.7214 | 8.6282 | 6 | 40.3286 | 14.8638 | 25.88% | 25.88%
3 | 75 | 16 | 1786 | 10 | 6.3 | 102.31 | 121.75 | 224.06 | 121.75 | 60.88 | 75 | 1786 | 600 | 73.9726 | -2.2083 | 4.9333 | 574.284 | 9.6536 | 35.1957 | 32.0824 | 32.0824 | 42.8241 | 137.1759 | 35.4134 | 156.9874 | 156.9874 | 103.9201 | 260.9075 | 0.24377 | 24.38% | 117.9824 | 28.7603 | 20.1322 | 138.4911 | 138.4911 | 14.54% | 11.76% | 11.76% | 80% | 9.407% | 11.0981 | 8.3016 | 6 | 66.5885 | 24.5424 | 48.08% | 48.08%
3 | 75 | 16 | 1787 | 11 | 7 | 152.97 | 150.64 | 303.61 | 150.64 | 75.32 | 75 | 1787 | 660 | 73.9726 | -2.2083 | 4.9333 | 634.284 | 10.6536 | 20.1957 | 37.8914 | 37.8914 | 25.9208 | 154.0792 | 20.5812 | 233.1724 | 233.1724 | 128.5793 | 361.7517 | 0.40455 | 40.45% | 163.5841 | 66.1775 | 46.3242 | 137.0221 | 137.0221 | 33.81% | 11.67% | 11.67% | 85% | 9.916% | 16.2203 | 8.0981 | 6 | 97.3215 | 35.8697 | 71.03% | 71.03%
3 | 75 | 16 | 1788 | 12 | 7.3 | 170.28 | 141.19 | 311.47 | 141.19 | 70.6 | 75 | 1788 | 720 | 73.9726 | -2.2083 | 4.9333 | 694.284 | 11.6536 | 5.1957 | 40.8005 | 40.8005 | 6.8655 | 173.1345 | 6.5479 | 258.8953 | 258.8953 | 120.5132 | 379.4085 | 0.42501 | 42.5% | 171.5685 | 72.9189 | 51.0432 | 128.6762 | 128.6762 | 39.67% | 11.65% | 11.65% | 85% | 9.899% | 16.9834 | 8.012 | 6 | 101.9005 | 37.5573 | 79.19% | 79.19%
3 | 75 | 16 | 1789 | 13 | 9.1 | 198.33 | 183.06 | 381.39 | 183.06 | 91.53 | 75 | 1789 | 780 | 73.9726 | -2.2083 | 4.9333 | 754.284 | 12.6536 | -9.8043 | 40.2591 | 40.2591 | 12.8837 | 192.8837 | 10.5818 | 301.677 | 301.677 | 156.2515 | 457.9285 | 0.49927 | 49.93% | 207.0753 | 103.3865 | 72.3706 | 132.3681 | 132.3681 | 54.67% | 11.56% | 11.56% | 85% | 9.824% | 20.3421 | 7.5083 | 6 | 122.0524 | 44.9847 | 92.21% | 92.21%
3 | 75 | 16 | 1790 | 14 | 6 | 193.81 | 133.06 | 326.87 | 133.06 | 66.53 | 75 | 1790 | 840 | 73.9726 | -2.2083 | 4.9333 | 814.284 | 13.6536 | -24.8043 | 36.3779 | 36.3779 | 31.3777 | 211.3777 | 25.1175 | 295.8707 | 295.8707 | 113.5738 | 409.4445 | 0.44526 | 44.53% | 185.1508 | 82.44 | 57.708 | 123.6716 | 123.6716 | 46.66% | 11.65% | 11.65% | 85% | 9.905% | 18.3389 | 8.3898 | 6 | 110.0331 | 40.5547 | 88.97% | 88.97%
3 | 75 | 16 | 1791 | 15 | 8.3 | 171.86 | 111.94 | 283.8 | 111.94 | 55.97 | 75 | 1791 | 900 | 73.9726 | -2.2083 | 4.9333 | 874.284 | 14.6536 | -39.8043 | 29.8439 | 29.8439 | 47.5185 | 227.5185 | 39.9951 | 264.5735 | 264.5735 | 95.5468 | 360.1203 | 0.41128 | 41.13% | 162.8464 | 66.9755 | 46.8828 | 123.0797 | 123.0797 | 38.09% | 11.64% | 11.64% | 85% | 9.89% | 16.1052 | 7.7294 | 6 | 96.6311 | 35.6152 | 78.51% | 78.51%
3 | 75 | 16 | 1792 | 16 | 8.1 | 146.75 | 122.69 | 269.44 | 122.69 | 61.35 | 75 | 1792 | 960 | 73.9726 | -2.2083 | 4.9333 | 934.284 | 15.6536 | -54.8043 | 21.4902 | 21.4902 | 61.3531 | 241.3531 | 54.9375 | 230.1224 | 230.1224 | 104.7225 | 334.8449 | 0.38023 | 38.02% | 151.4169 | 57.5728 | 40.301 | 120.7243 | 120.7243 | 33.38% | 11.66% | 11.66% | 85% | 9.908% | 15.0023 | 7.7853 | 6 | 90.0141 | 33.1764 | 74.56% | 74.56%
3 | 75 | 16 | 1793 | 17 | 8 | 92.86 | 62.31 | 155.17 | 62.31 | 31.16 | 75 | 1793 | 1020 | 73.9726 | -2.2083 | 4.9333 | 994.284 | 16.6536 | -69.8043 | 12.0149 | 12.0149 | 73.5014 | 253.5014 | 69.9031 | 153.2794 | 153.2794 | 53.1849 | 206.4643 | 0.11558 | 11.56% | 93.3631 | 10.7908 | 7.5536 | 113.1 | 113.1 | 6.679% | 11.74% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1794 | 18 | 6.4 | 41.19 | 33.14 | 74.33 | 33.14 | 16.57 | 75 | 1794 | 1080 | 73.9726 | -2.2083 | 4.9333 | 1054.284 | 17.6536 | -84.8043 | 1.9422 | 1.9422 | 84.6993 | 264.6993 | 84.8795 | 0 | 0 | 28.2868 | 28.2868 | -4.355 | 0% | 12.7913 | 0 | 0 | 145.4678 | 145.4678 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1795 | 19 | 3.9 | 0 | 13.53 | 13.53 | 13.53 | 6.77 | 75 | 1795 | 1140 | 73.9726 | -2.2083 | 4.9333 | 1114.284 | 18.6536 | -99.8043 | -8.3146 | 0 | 86.7744 | 266.7744 | 87.7198 | 0 | 0 | 11.5486 | 11.5486 | -12.3518 | 0% | 5.2223 | 0 | 0 | 134.3181 | 134.3181 | 0% | 12.05% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1796 | 20 | 3 | 0 | 0 | 0 | 0 | 0 | 75 | 1796 | 1200 | 73.9726 | -2.2083 | 4.9333 | 1174.284 | 19.6536 | -114.8043 | -18.3708 | 0 | 86.7744 | 266.7744 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.224 | 127.224 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1797 | 21 | 2 | 0 | 0 | 0 | 0 | 0 | 75 | 1797 | 1260 | 73.9726 | -2.2083 | 4.9333 | 1234.284 | 20.6536 | -129.8043 | -27.7852 | 0 | 86.7744 | 266.7744 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.511 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1798 | 22 | 1.1 | 0 | 0 | 0 | 0 | 0 | 75 | 1798 | 1320 | 73.9726 | -2.2083 | 4.9333 | 1294.284 | 21.6536 | -144.8043 | -35.9654 | 0 | 86.7744 | 266.7744 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0031 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1799 | 23 | 1.1 | 0 | 0 | 0 | 0 | 0 | 75 | 1799 | 1380 | 73.9726 | -2.2083 | 4.9333 | 1354.284 | 22.6536 | -159.8043 | -42.0922 | 0 | 86.7744 | 266.7744 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.584 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
3 | 75 | 16 | 1800 | 24 | 0.5 | 0 | 0 | 0 | 0 | 0 | 75 | 1800 | 1440 | 73.9726 | -2.2083 | 4.9333 | 1414.284 | 23.6536 | -174.8043 | -45.2012 | 0 | 86.7744 | 266.7744 | 87.7198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0792 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1801 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 76 | 1801 | 60 | 74.9589 | -1.8094 | 5.3193 | 34.284 | 0.66005 | 170.0992 | -44.2108 | 0 | 87.3573 | 92.6427 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.631 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1802 | 2 | -0.1 | 0 | 0 | 0 | 0 | 0 | 76 | 1802 | 120 | 74.9589 | -1.8094 | 5.3193 | 94.284 | 1.6601 | 155.0992 | -40.0805 | 0 | 87.3573 | 92.6427 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4078 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1803 | 3 | -0.3 | 0 | 0 | 0 | 0 | 0 | 76 | 1803 | 180 | 74.9589 | -1.8094 | 5.3193 | 154.284 | 2.6601 | 140.0992 | -33.2379 | 0 | 87.3573 | 92.6427 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4227 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1804 | 4 | -1.2 | 0 | 0 | 0 | 0 | 0 | 76 | 1804 | 240 | 74.9589 | -1.8094 | 5.3193 | 214.284 | 3.6601 | 125.0992 | -24.6191 | 0 | 87.3573 | 92.6427 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.7943 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1805 | 5 | -1.4 | 0 | 0 | 0 | 0 | 0 | 76 | 1805 | 300 | 74.9589 | -1.8094 | 5.3193 | 274.284 | 4.6601 | 110.0992 | -14.9651 | 0 | 87.3573 | 92.6427 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.282 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1806 | 6 | -1.5 | 0 | 0 | 0 | 0 | 0 | 76 | 1806 | 360 | 74.9589 | -1.8094 | 5.3193 | 334.284 | 5.6601 | 95.0992 | -4.8097 | 0 | 87.3573 | 92.6427 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6202 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1807 | 7 | -1.4 | 0 | 0 | 0 | 0 | 0 | 76 | 1807 | 420 | 74.9589 | -1.8094 | 5.3193 | 394.284 | 6.6601 | 80.0992 | 5.4331 | 5.4331 | 81.5168 | 98.4832 | 80.1659 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.1871 | 146.1871 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1808 | 8 | -2.1 | 0.28 | 7.97 | 8.25 | 7.97 | 3.99 | 76 | 1808 | 480 | 74.9589 | -1.8094 | 5.3193 | 454.284 | 7.6601 | 65.0992 | 15.3784 | 15.3784 | 70.0937 | 109.9063 | 65.1871 | 0.44309 | 0.44309 | 6.8028 | 7.2459 | -22.1982 | 0% | 3.2766 | 0 | 0 | 150.3268 | 150.3268 | 0% | 12.32% | 12.32% | 80% | 9.852% | 0.32283 | 11.0106 | 6 | 1.937 | 0.7139 | 1.288% | 1.288%
3 | 76 | 17 | 1809 | 9 | -1 | 10 | 52.03 | 62.03 | 52.03 | 26.02 | 76 | 1809 | 540 | 74.9589 | -1.8094 | 5.3193 | 514.284 | 8.6601 | 50.0992 | 24.5862 | 24.5862 | 57.482 | 122.518 | 50.2192 | 15.3788 | 15.3788 | 44.4104 | 59.7892 | -1.9379 | 0% | 27.0367 | 0 | 0 | 134.488 | 134.488 | 0% | 12.21% | 12.21% | 80% | 9.766% | 2.6403 | 10.6277 | 6 | 15.8417 | 5.8387 | 11.78% | 11.78%
3 | 76 | 17 | 1810 | 10 | 0 | 65.56 | 116.58 | 182.14 | 116.58 | 58.29 | 76 | 1810 | 600 | 74.9589 | -1.8094 | 5.3193 | 574.284 | 9.6601 | 35.0992 | 32.4802 | 32.4802 | 42.9432 | 137.0568 | 35.2763 | 99.6664 | 99.6664 | 99.5073 | 199.1737 | -0.0066368 | 0% | 90.0663 | 0 | 0 | 141.1123 | 141.1123 | 0% | 12.01% | 12.01% | 80% | 9.61% | 8.6557 | 10.287 | 6 | 51.934 | 19.1412 | 36.8% | 36.8%
3 | 76 | 17 | 1811 | 11 | 0.5 | 96.31 | 140.75 | 237.06 | 140.75 | 70.38 | 76 | 1811 | 660 | 74.9589 | -1.8094 | 5.3193 | 634.284 | 10.6601 | 20.0992 | 38.3008 | 38.3008 | 25.9558 | 154.0442 | 20.4136 | 145.6325 | 145.6325 | 120.1376 | 265.7702 | 0.20113 | 20.11% | 120.1813 | 24.1721 | 16.9205 | 119.267 | 119.267 | 14.19% | 11.92% | 11.92% | 80% | 9.54% | 11.4653 | 10.1193 | 6 | 68.7915 | 25.3544 | 57.68% | 57.68%
3 | 76 | 17 | 1812 | 12 | 0.4 | 101.75 | 181.39 | 283.14 | 181.39 | 90.7 | 76 | 1812 | 720 | 74.9589 | -1.8094 | 5.3193 | 694.284 | 11.6601 | 5.0992 | 41.2059 | 41.2059 | 6.7812 | 173.2188 | 6.234 | 153.5418 | 153.5418 | 154.826 | 308.3679 | 0.28361 | 28.36% | 139.4439 | 39.548 | 27.6836 | 114.9847 | 114.9847 | 24.08% | 11.88% | 11.88% | 85% | 10.1% | 14.0834 | 10.1527 | 6 | 84.5004 | 31.1442 | 73.49% | 73.49%
3 | 76 | 17 | 1813 | 13 | 1 | 129.81 | 195 | 324.81 | 195 | 97.5 | 76 | 1813 | 780 | 74.9589 | -1.8094 | 5.3193 | 754.284 | 12.6601 | -9.9008 | 40.6383 | 40.6383 | 13.0896 | 193.0896 | 10.5292 | 195.9585 | 195.9585 | 166.4429 | 362.4014 | 0.36527 | 36.53% | 163.8779 | 59.8602 | 41.9021 | 116.3752 | 116.3752 | 36.01% | 11.81% | 11.81% | 85% | 10.04% | 16.4499 | 9.9533 | 6 | 98.6994 | 36.3775 | 84.81% | 84.81%
3 | 76 | 17 | 1814 | 14 | 1.4 | 154.36 | 203.33 | 357.69 | 203.33 | 101.67 | 76 | 1814 | 840 | 74.9589 | -1.8094 | 5.3193 | 814.284 | 13.6601 | -24.9008 | 36.7157 | 36.7157 | 31.6676 | 211.6676 | 25.1539 | 233.7093 | 233.7093 | 173.553 | 407.2623 | 0.41601 | 41.6% | 184.164 | 76.6139 | 53.6298 | 117.4007 | 117.4007 | 45.68% | 11.75% | 11.75% | 85% | 9.991% | 18.3993 | 9.8218 | 6 | 110.3957 | 40.6884 | 94.03% | 94.03%
3 | 76 | 17 | 1815 | 15 | 1.6 | 107.22 | 226.03 | 333.25 | 226.03 | 113.02 | 76 | 1815 | 900 | 74.9589 | -1.8094 | 5.3193 | 874.284 | 14.6601 | -39.9008 | 30.1389 | 30.1389 | 47.8479 | 227.8479 | 40.0552 | 163.4519 | 163.4519 | 192.9287 | 356.3805 | 0.36199 | 36.2% | 161.1553 | 58.3364 | 40.8355 | 114.9663 | 114.9663 | 35.52% | 11.8% | 11.8% | 85% | 10.03% | 16.1652 | 9.7564 | 6 | 96.991 | 35.7478 | 84.36% | 84.36%
3 | 76 | 17 | 1816 | 16 | 1.7 | 60.56 | 146.19 | 206.75 | 146.19 | 73.1 | 76 | 1816 | 960 | 74.9589 | -1.8094 | 5.3193 | 934.284 | 15.6601 | -54.9008 | 21.7505 | 21.7505 | 61.6944 | 241.6944 | 55.0088 | 93.7167 | 93.7167 | 124.781 | 218.4976 | 0.084177 | 8.418% | 98.8046 | 8.3171 | 5.822 | 107.9398 | 107.9398 | 5.394% | 11.94% | 11.94% | 80% | 9.55% | 9.4357 | 9.7239 | 6 | 56.614 | 20.8661 | 52.45% | 52.45%
3 | 76 | 17 | 1817 | 17 | 1.9 | 61.47 | 118.61 | 180.08 | 118.61 | 59.31 | 76 | 1817 | 1020 | 74.9589 | -1.8094 | 5.3193 | 994.284 | 16.6601 | -69.9008 | 12.252 | 12.252 | 73.844 | 253.844 | 69.9811 | 99.1605 | 99.1605 | 101.24 | 200.4005 | 0.021614 | 2.161% | 90.6211 | 1.9587 | 1.3711 | 105.3466 | 105.3466 | 1.301% | 11.95% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1818 | 18 | 1 | 28.81 | 68.89 | 97.7 | 68.89 | 34.45 | 76 | 1818 | 1080 | 74.9589 | -1.8094 | 5.3193 | 1054.284 | 17.6601 | -84.9008 | 2.1679 | 2.1679 | 85.0423 | 265.0423 | 84.9622 | 0 | 0 | 58.8013 | 58.8013 | -1.8999 | 0% | 26.5899 | 0 | 0 | 139.518 | 139.518 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1819 | 19 | 0.1 | 0 | 13.42 | 13.42 | 13.42 | 6.71 | 76 | 1819 | 1140 | 74.9589 | -1.8094 | 5.3193 | 1114.284 | 18.6601 | -99.9008 | -8.0885 | 0 | 87.3573 | 267.3573 | 88.1317 | 0 | 0 | 11.4547 | 11.4547 | -13.2698 | 0% | 5.1798 | 0 | 0 | 130.54 | 130.54 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1820 | 20 | -0.8 | 0 | 0 | 0 | 0 | 0 | 76 | 1820 | 1200 | 74.9589 | -1.8094 | 5.3193 | 1174.284 | 19.6601 | -114.9008 | -18.1322 | 0 | 87.3573 | 267.3573 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.318 | 124.318 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1821 | 21 | -2.5 | 0 | 0 | 0 | 0 | 0 | 76 | 1821 | 1260 | 74.9589 | -1.8094 | 5.3193 | 1234.284 | 20.6601 | -129.9008 | -27.5214 | 0 | 87.3573 | 267.3573 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2904 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1822 | 22 | -2.7 | 0 | 0 | 0 | 0 | 0 | 76 | 1822 | 1320 | 74.9589 | -1.8094 | 5.3193 | 1294.284 | 21.6601 | -144.9008 | -35.6637 | 0 | 87.3573 | 267.3573 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.5299 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1823 | 23 | -4.3 | 0 | 0 | 0 | 0 | 0 | 76 | 1823 | 1380 | 74.9589 | -1.8094 | 5.3193 | 1354.284 | 22.6601 | -159.9008 | -41.7444 | 0 | 87.3573 | 267.3573 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.6783 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
3 | 76 | 17 | 1824 | 24 | -4.3 | 0 | 0 | 0 | 0 | 0 | 76 | 1824 | 1440 | 74.9589 | -1.8094 | 5.3193 | 1414.284 | 23.6601 | -174.9008 | -44.8122 | 0 | 87.3573 | 267.3573 | 88.1317 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.3884 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1825 | 1 | -4.3 | 0 | 0 | 0 | 0 | 0 | 77 | 1825 | 60 | 75.9452 | -1.4099 | 5.7048 | 34.284 | 0.66648 | 170.0028 | -43.8008 | 0 | 87.9411 | 92.0589 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.7688 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1826 | 2 | -4.3 | 0 | 0 | 0 | 0 | 0 | 77 | 1826 | 120 | 75.9452 | -1.4099 | 5.7048 | 94.284 | 1.6665 | 155.0028 | -39.6741 | 0 | 87.9411 | 92.0589 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4144 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1827 | 3 | -4.3 | 0 | 0 | 0 | 0 | 0 | 77 | 1827 | 180 | 75.9452 | -1.4099 | 5.7048 | 154.284 | 2.6665 | 140.0028 | -32.8472 | 0 | 87.9411 | 92.0589 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.0599 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1828 | 4 | -4.7 | 0 | 0 | 0 | 0 | 0 | 77 | 1828 | 240 | 75.9452 | -1.4099 | 5.7048 | 214.284 | 3.6665 | 125.0028 | -24.2449 | 0 | 87.9411 | 92.0589 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.6695 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1829 | 5 | -4.8 | 0 | 0 | 0 | 0 | 0 | 77 | 1829 | 300 | 75.9452 | -1.4099 | 5.7048 | 274.284 | 4.6665 | 110.0028 | -14.6027 | 0 | 87.9411 | 92.0589 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3849 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1830 | 6 | -5.2 | 0 | 0 | 0 | 0 | 0 | 77 | 1830 | 360 | 75.9452 | -1.4099 | 5.7048 | 334.284 | 5.6665 | 95.0028 | -4.4524 | 0 | 87.9411 | 92.0589 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1111 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1831 | 7 | -6.3 | 0 | 0 | 0 | 0 | 0 | 77 | 1831 | 420 | 75.9452 | -1.4099 | 5.7048 | 394.284 | 6.6665 | 80.0028 | 5.7922 | 5.7922 | 81.7177 | 98.2823 | 80.0551 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.0596 | 146.0596 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5503 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1832 | 8 | -5.8 | 0.36 | 11.67 | 12.03 | 11.67 | 5.84 | 77 | 1832 | 480 | 75.9452 | -1.4099 | 5.7048 | 454.284 | 7.6665 | 65.0028 | 15.746 | 15.746 | 70.2846 | 109.7154 | 65.072 | 0.55913 | 0.55913 | 9.961 | 10.5201 | -15.9262 | 0% | 4.7572 | 0 | 0 | 152.8629 | 152.8629 | 0% | 12.47% | 12.47% | 80% | 9.978% | 0.47466 | 12.3605 | 6 | 2.848 | 1.0497 | 1.863% | 1.863%
3 | 77 | 18 | 1833 | 9 | -4.4 | 26.58 | 64.08 | 90.66 | 64.08 | 32.04 | 77 | 1833 | 540 | 75.9452 | -1.4099 | 5.7048 | 514.284 | 8.6665 | 50.0028 | 24.9679 | 24.9679 | 57.65 | 122.35 | 50.0975 | 40.3937 | 40.3937 | 54.6957 | 95.0894 | -1.0096 | 0% | 42.9994 | 0 | 0 | 138.9099 | 138.9099 | 0% | 12.3% | 12.3% | 80% | 9.838% | 4.2305 | 11.8384 | 6 | 25.3827 | 9.3553 | 18.27% | 18.27%
3 | 77 | 18 | 1834 | 10 | -3.4 | 91.31 | 121.67 | 212.98 | 121.67 | 60.84 | 77 | 1834 | 600 | 75.9452 | -1.4099 | 5.7048 | 574.284 | 9.6665 | 35.0028 | 32.8785 | 32.8785 | 43.0639 | 136.9361 | 35.143 | 137.5419 | 137.5419 | 103.8518 | 241.3937 | 0.10005 | 10% | 109.1582 | 10.9211 | 7.6448 | 123.6077 | 123.6077 | 6.185% | 12.07% | 12.07% | 80% | 9.657% | 10.5411 | 11.4739 | 6 | 63.2468 | 23.3108 | 51.17% | 51.17%
3 | 77 | 18 | 1835 | 11 | -2.7 | 104.81 | 148.61 | 253.42 | 148.61 | 74.31 | 77 | 1835 | 660 | 75.9452 | -1.4099 | 5.7048 | 634.284 | 10.6665 | 20.0028 | 38.7109 | 38.7109 | 25.9916 | 154.0084 | 20.2526 | 157.2299 | 157.2299 | 126.8466 | 284.0764 | 0.212 | 21.2% | 128.4594 | 27.2337 | 19.0636 | 121.0224 | 121.0224 | 15.75% | 12% | 12% | 80% | 9.597% | 12.3281 | 11.223 | 6 | 73.9687 | 27.2625 | 61.12% | 61.12%
3 | 77 | 18 | 1836 | 12 | -1 | 93.14 | 227.03 | 320.17 | 227.03 | 113.52 | 77 | 1836 | 720 | 75.9452 | -1.4099 | 5.7048 | 694.284 | 11.6665 | 5.0028 | 41.612 | 41.612 | 6.696 | 173.304 | 5.9316 | 139.5028 | 139.5028 | 193.7822 | 333.285 | 0.31213 | 31.21% | 150.7115 | 47.0414 | 32.929 | 118.9376 | 118.9376 | 27.69% | 11.89% | 11.89% | 85% | 10.11% | 15.233 | 10.6277 | 6 | 91.398 | 33.6864 | 76.85% | 76.85%
3 | 77 | 18 | 1837 | 13 | -2.3 | 27.69 | 238.33 | 266.02 | 238.33 | 119.17 | 77 | 1837 | 780 | 75.9452 | -1.4099 | 5.7048 | 754.284 | 12.6665 | -9.9972 | 41.0179 | 41.0179 | 13.298 | 193.298 | 10.4919 | 41.486 | 41.486 | 203.4274 | 244.9133 | 0.12143 | 12.14% | 110.7498 | 13.4478 | 9.4135 | 113.3307 | 113.3307 | 8.306% | 12.03% | 12.03% | 80% | 9.626% | 10.6611 | 11.0811 | 6 | 63.9663 | 23.576 | 56.44% | 56.44%
3 | 77 | 18 | 1838 | 14 | 0.4 | 18.53 | 204.92 | 223.45 | 204.92 | 102.46 | 77 | 1838 | 840 | 75.9452 | -1.4099 | 5.7048 | 814.284 | 13.6665 | -24.9972 | 37.0535 | 37.0535 | 31.9604 | 211.9604 | 25.1963 | 27.8261 | 27.8261 | 174.9102 | 202.7363 | 0.012474 | 1.247% | 91.6774 | 1.1436 | 0.80054 | 114.5477 | 114.5477 | 0.6989% | 12% | 12% | 80% | 9.597% | 8.798 | 10.1527 | 6 | 52.7879 | 19.456 | 46.08% | 46.08%
3 | 77 | 18 | 1839 | 15 | 0.5 | 23.25 | 169.92 | 193.17 | 169.92 | 84.96 | 77 | 1839 | 900 | 75.9452 | -1.4099 | 5.7048 | 874.284 | 14.6665 | -39.9972 | 30.4337 | 30.4337 | 48.1795 | 228.1795 | 40.1186 | 35.0999 | 35.0999 | 145.0358 | 180.1357 | -0.085467 | 0% | 81.4574 | 0 | 0 | 111.1679 | 111.1679 | 0% | 12.02% | 12.02% | 80% | 9.613% | 7.8309 | 10.1193 | 6 | 46.9851 | 17.3172 | 42.27% | 42.27%
3 | 77 | 18 | 1840 | 16 | -0.7 | 41.67 | 187.14 | 228.81 | 187.14 | 93.57 | 77 | 1840 | 960 | 75.9452 | -1.4099 | 5.7048 | 934.284 | 15.6665 | -54.9972 | 22.0107 | 22.0107 | 62.0373 | 242.0373 | 55.082 | 63.6428 | 63.6428 | 159.734 | 223.3768 | 0.073445 | 7.344% | 101.011 | 7.4187 | 5.1931 | 109.4271 | 109.4271 | 4.746% | 12.01% | 12.01% | 80% | 9.607% | 9.7039 | 10.5248 | 6 | 58.2235 | 21.4593 | 53.21% | 53.21%
3 | 77 | 18 | 1841 | 17 | -0.1 | 88.61 | 151.94 | 240.55 | 151.94 | 75.97 | 77 | 1841 | 1020 | 75.9452 | -1.4099 | 5.7048 | 994.284 | 16.6665 | -69.9972 | 12.4892 | 12.4892 | 74.1876 | 254.1876 | 70.0601 | 139.7375 | 139.7375 | 129.6889 | 269.4264 | 0.20382 | 20.38% | 121.8346 | 24.8323 | 17.3826 | 109.4297 | 109.4297 | 15.88% | 11.94% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1842 | 18 | -0.4 | 23.97 | 91.94 | 115.91 | 91.94 | 45.97 | 77 | 1842 | 1080 | 75.9452 | -1.4099 | 5.7048 | 1054.284 | 17.6665 | -84.9972 | 2.3941 | 2.3941 | 85.3857 | 265.3857 | 85.045 | 0 | 0 | 78.4757 | 78.4757 | -1.266 | 0% | 35.4867 | 0 | 0 | 141.7283 | 141.7283 | 0% | 12.16% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1843 | 19 | -1.6 | 0 | 27.86 | 27.86 | 27.86 | 13.93 | 77 | 1843 | 1140 | 75.9452 | -1.4099 | 5.7048 | 1114.284 | 18.6665 | -99.9972 | -7.8615 | 0 | 87.9411 | 267.9411 | 88.5443 | 0 | 0 | 23.78 | 23.78 | -6.1525 | 0% | 10.7533 | 0 | 0 | 131.778 | 131.778 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1844 | 20 | -3 | 0 | 0 | 0 | 0 | 0 | 77 | 1844 | 1200 | 75.9452 | -1.4099 | 5.7048 | 1174.284 | 19.6665 | -114.9972 | -17.8925 | 0 | 87.9411 | 267.9411 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.4025 | 123.4025 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1845 | 21 | -3.7 | 0 | 0 | 0 | 0 | 0 | 77 | 1845 | 1260 | 75.9452 | -1.4099 | 5.7048 | 1234.284 | 20.6665 | -129.9972 | -27.2561 | 0 | 87.9411 | 267.9411 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8409 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1846 | 22 | -5 | 0 | 0 | 0 | 0 | 0 | 77 | 1846 | 1320 | 75.9452 | -1.4099 | 5.7048 | 1294.284 | 21.6665 | -144.9972 | -35.3604 | 0 | 87.9411 | 267.9411 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.8991 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1847 | 23 | -5.5 | 0 | 0 | 0 | 0 | 0 | 77 | 1847 | 1380 | 75.9452 | -1.4099 | 5.7048 | 1354.284 | 22.6665 | -159.9972 | -41.3953 | 0 | 87.9411 | 267.9411 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.3066 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
3 | 77 | 18 | 1848 | 24 | -5.9 | 0 | 0 | 0 | 0 | 0 | 77 | 1848 | 1440 | 75.9452 | -1.4099 | 5.7048 | 1414.284 | 23.6665 | -174.9972 | -44.4222 | 0 | 87.9411 | 267.9411 | 88.5443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.5617 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1849 | 1 | -6.5 | 0 | 0 | 0 | 0 | 0 | 78 | 1849 | 60 | 76.9315 | -1.0097 | 6.0892 | 34.284 | 0.67289 | 169.9067 | -43.3903 | 0 | 88.5256 | 91.4744 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.0101 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1850 | 2 | -7.8 | 0 | 0 | 0 | 0 | 0 | 78 | 1850 | 120 | 76.9315 | -1.0097 | 6.0892 | 94.284 | 1.6729 | 154.9067 | -39.2671 | 0 | 88.5256 | 91.4744 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.5016 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1851 | 3 | -8.2 | 0 | 0 | 0 | 0 | 0 | 78 | 1851 | 180 | 76.9315 | -1.0097 | 6.0892 | 154.284 | 2.6729 | 139.9067 | -32.4559 | 0 | 88.5256 | 91.4744 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.6215 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.2874 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1852 | 4 | -8.6 | 0 | 0 | 0 | 0 | 0 | 78 | 1852 | 240 | 76.9315 | -1.0097 | 6.0892 | 214.284 | 3.6729 | 124.9067 | -23.8702 | 0 | 88.5256 | 91.4744 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.2311 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4458 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1853 | 5 | -8.1 | 0 | 0 | 0 | 0 | 0 | 78 | 1853 | 300 | 76.9315 | -1.0097 | 6.0892 | 274.284 | 4.6729 | 109.9067 | -14.2398 | 0 | 88.5256 | 91.4744 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7138 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.248 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1854 | 6 | -8 | 0 | 0 | 0 | 0 | 0 | 78 | 1854 | 360 | 76.9315 | -1.0097 | 6.0892 | 334.284 | 5.6729 | 94.9067 | -4.0948 | 0 | 88.5256 | 91.4744 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4026 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.2086 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1855 | 7 | -6.2 | 0 | 0 | 0 | 0 | 0 | 78 | 1855 | 420 | 76.9315 | -1.0097 | 6.0892 | 394.284 | 6.6729 | 79.9067 | 6.1515 | 6.1515 | 81.9195 | 98.0805 | 79.945 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 156.7301 | 156.7301 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1856 | 8 | -4 | 10.83 | 20.64 | 31.47 | 20.64 | 10.32 | 78 | 1856 | 480 | 76.9315 | -1.0097 | 6.0892 | 454.284 | 7.6729 | 64.9067 | 16.1137 | 16.1137 | 70.4768 | 109.5232 | 64.9584 | 16.5166 | 16.5166 | 17.6173 | 34.1339 | -4.2186 | 0% | 15.4354 | 0 | 0 | 169.9109 | 169.9109 | 0% | 12.36% | 12.36% | 80% | 9.89% | 1.5266 | 11.6918 | 6 | 9.1597 | 3.376 | 5.391% | 5.391%
3 | 78 | 19 | 1857 | 9 | -2.7 | 64.72 | 71.94 | 136.66 | 71.94 | 35.97 | 78 | 1857 | 540 | 76.9315 | -1.0097 | 6.0892 | 514.284 | 8.6729 | 49.9067 | 25.3498 | 25.3498 | 57.8195 | 122.1805 | 49.9783 | 97.2105 | 97.2105 | 61.4046 | 158.6151 | -0.25626 | 0% | 71.7258 | 0 | 0 | 157.0499 | 157.0499 | 0% | 12.15% | 12.15% | 80% | 9.722% | 6.9733 | 11.223 | 6 | 41.84 | 15.4209 | 26.64% | 26.64%
3 | 78 | 19 | 1858 | 10 | -1.7 | 144.72 | 141.19 | 285.91 | 141.19 | 70.6 | 78 | 1858 | 600 | 76.9315 | -1.0097 | 6.0892 | 574.284 | 9.6729 | 34.9067 | 33.2771 | 33.2771 | 43.1862 | 136.8138 | 35.0136 | 216.0206 | 216.0206 | 120.5132 | 336.5338 | 0.3117 | 31.17% | 152.1806 | 47.4353 | 33.2047 | 142.1927 | 142.1927 | 23.35% | 11.91% | 11.91% | 85% | 10.12% | 15.3997 | 10.8704 | 6 | 92.3984 | 34.0551 | 64.98% | 64.98%
3 | 78 | 19 | 1859 | 11 | -0.6 | 151.39 | 195.92 | 347.31 | 195.92 | 97.96 | 78 | 1859 | 660 | 76.9315 | -1.0097 | 6.0892 | 634.284 | 10.6729 | 19.9067 | 39.1215 | 39.1215 | 26.0283 | 153.9717 | 20.0985 | 225.3222 | 225.3222 | 167.2282 | 392.5504 | 0.38892 | 38.89% | 177.5113 | 69.037 | 48.3259 | 139.1388 | 139.1388 | 34.73% | 11.81% | 11.81% | 85% | 10.04% | 17.825 | 10.4906 | 6 | 106.9498 | 39.4183 | 76.87% | 76.87%
3 | 78 | 19 | 1860 | 12 | -0.4 | 169.25 | 227.5 | 396.75 | 227.5 | 113.75 | 78 | 1860 | 720 | 76.9315 | -1.0097 | 6.0892 | 694.284 | 11.6729 | 4.9067 | 42.0185 | 42.0185 | 6.6101 | 173.3899 | 5.6428 | 251.6242 | 251.6242 | 194.1834 | 445.8076 | 0.43961 | 43.96% | 201.5942 | 88.6236 | 62.0365 | 130.9962 | 130.9962 | 47.36% | 11.75% | 11.75% | 85% | 9.987% | 20.1332 | 10.4224 | 6 | 120.7992 | 44.5228 | 92.22% | 92.22%
3 | 78 | 19 | 1861 | 13 | 0 | 217.69 | 250 | 467.69 | 250 | 125 | 78 | 1861 | 780 | 76.9315 | -1.0097 | 6.0892 | 754.284 | 12.6729 | -10.0933 | 41.3978 | 41.3978 | 13.5085 | 193.5085 | 10.47 | 323.7124 | 323.7124 | 213.3883 | 537.1008 | 0.50339 | 50.34% | 242.877 | 122.262 | 85.5834 | 132.3684 | 132.3684 | 64.66% | 11.64% | 11.64% | 90% | 10.48% | 25.4464 | 10.287 | 6 | 152.6783 | 56.2724 | 115.3% | 115.3%
3 | 78 | 19 | 1862 | 14 | -0.1 | 202.78 | 235.83 | 438.61 | 235.83 | 117.92 | 78 | 1862 | 840 | 76.9315 | -1.0097 | 6.0892 | 814.284 | 13.6729 | -25.0933 | 37.3913 | 37.3913 | 32.2557 | 212.2557 | 25.2446 | 302.0371 | 302.0371 | 201.2935 | 503.3306 | 0.48273 | 48.27% | 227.6061 | 109.8725 | 76.9108 | 129.4533 | 129.4533 | 59.41% | 11.68% | 11.68% | 90% | 10.51% | 23.9259 | 10.3208 | 6 | 143.5553 | 52.91 | 110.9% | 110.9%
3 | 78 | 19 | 1863 | 15 | -0.5 | 200 | 172.58 | 372.58 | 172.58 | 86.29 | 78 | 1863 | 900 | 76.9315 | -1.0097 | 6.0892 | 874.284 | 14.6729 | -40.0933 | 30.7283 | 30.7283 | 48.5133 | 228.5133 | 40.1852 | 299.0256 | 299.0256 | 147.3062 | 446.3318 | 0.43949 | 43.95% | 201.8312 | 88.7022 | 62.0916 | 123.2777 | 123.2777 | 50.37% | 11.75% | 11.75% | 85% | 9.988% | 20.1592 | 10.4565 | 6 | 120.9552 | 44.5803 | 98.12% | 98.12%
3 | 78 | 19 | 1864 | 16 | -1.9 | 216.67 | 186.67 | 403.34 | 186.67 | 93.34 | 78 | 1864 | 960 | 76.9315 | -1.0097 | 6.0892 | 934.284 | 15.6729 | -55.0933 | 22.2708 | 22.2708 | 62.3816 | 242.3816 | 55.1569 | 326.6362 | 326.6362 | 159.3328 | 485.969 | 0.46206 | 46.21% | 219.7552 | 101.5398 | 71.0779 | 121.094 | 121.094 | 58.7% | 11.73% | 11.73% | 85% | 9.971% | 21.9112 | 10.9403 | 6 | 131.4669 | 48.4546 | 108.6% | 108.6%
3 | 78 | 19 | 1865 | 17 | -2.5 | 89.08 | 134.17 | 223.25 | 134.17 | 67.09 | 78 | 1865 | 1020 | 76.9315 | -1.0097 | 6.0892 | 994.284 | 16.6729 | -70.0933 | 12.7266 | 12.7266 | 74.5321 | 254.5321 | 70.1398 | 137.3712 | 137.3712 | 114.5213 | 251.8924 | 0.13835 | 13.84% | 113.9057 | 15.759 | 11.0313 | 108.9355 | 108.9355 | 10.13% | 12.03% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1866 | 18 | -2.4 | 54.92 | 75.92 | 130.84 | 75.92 | 37.96 | 78 | 1866 | 1080 | 76.9315 | -1.0097 | 6.0892 | 1054.284 | 17.6729 | -85.0933 | 2.6208 | 2.6208 | 85.7296 | 265.7296 | 85.1279 | 0 | 0 | 64.8018 | 64.8018 | -1.7796 | 0% | 29.3034 | 0 | 0 | 142.915 | 142.915 | 0% | 12.26% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1867 | 19 | -2.3 | 0 | 24.25 | 24.25 | 24.25 | 12.13 | 78 | 1867 | 1140 | 76.9315 | -1.0097 | 6.0892 | 1114.284 | 18.6729 | -100.0933 | -7.6337 | 0 | 88.5256 | 268.5256 | 88.9575 | 0 | 0 | 20.6987 | 20.6987 | -7.2724 | 0% | 9.3599 | 0 | 0 | 132.3735 | 132.3735 | 0% | 12.31% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1868 | 20 | -2.2 | 0 | 0 | 0 | 0 | 0 | 78 | 1868 | 1200 | 76.9315 | -1.0097 | 6.0892 | 1174.284 | 19.6729 | -115.0933 | -17.6515 | 0 | 88.5256 | 268.5256 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.0023 | 125.0023 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1869 | 21 | -2.1 | 0 | 0 | 0 | 0 | 0 | 78 | 1869 | 1260 | 76.9315 | -1.0097 | 6.0892 | 1234.284 | 20.6729 | -130.0933 | -26.9893 | 0 | 88.5256 | 268.5256 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3701 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1870 | 22 | -2.1 | 0 | 0 | 0 | 0 | 0 | 78 | 1870 | 1320 | 76.9315 | -1.0097 | 6.0892 | 1294.284 | 21.6729 | -145.0933 | -35.0555 | 0 | 88.5256 | 268.5256 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.7735 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1871 | 23 | -1.8 | 0 | 0 | 0 | 0 | 0 | 78 | 1871 | 1380 | 76.9315 | -1.0097 | 6.0892 | 1354.284 | 22.6729 | -160.0933 | -41.0447 | 0 | 88.5256 | 268.5256 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8266 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
3 | 78 | 19 | 1872 | 24 | -2.2 | 0 | 0 | 0 | 0 | 0 | 78 | 1872 | 1440 | 76.9315 | -1.0097 | 6.0892 | 1414.284 | 23.6729 | -175.0933 | -44.0314 | 0 | 88.5256 | 268.5256 | 88.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9466 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1873 | 1 | -2.2 | 0 | 0 | 0 | 0 | 0 | 79 | 1873 | 60 | 77.9178 | -0.60903 | 6.4723 | 34.284 | 0.67927 | 169.8109 | -42.9793 | 0 | 89.1107 | 90.8893 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3884 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1874 | 2 | -2.2 | 0 | 0 | 0 | 0 | 0 | 79 | 1874 | 120 | 77.9178 | -0.60903 | 6.4723 | 94.284 | 1.6793 | 154.8109 | -38.8598 | 0 | 89.1107 | 90.8893 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8082 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1875 | 3 | -2.3 | 0 | 0 | 0 | 0 | 0 | 79 | 1875 | 180 | 77.9178 | -0.60903 | 6.4723 | 154.284 | 2.6793 | 139.8109 | -32.0642 | 0 | 89.1107 | 90.8893 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3805 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1876 | 4 | -2.3 | 0 | 0 | 0 | 0 | 0 | 79 | 1876 | 240 | 77.9178 | -0.60903 | 6.4723 | 214.284 | 3.6793 | 124.8109 | -23.4951 | 0 | 89.1107 | 90.8893 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3805 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1877 | 5 | -2.4 | 0 | 0 | 0 | 0 | 0 | 79 | 1877 | 300 | 77.9178 | -0.60903 | 6.4723 | 274.284 | 4.6793 | 109.8109 | -13.8766 | 0 | 89.1107 | 90.8893 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8924 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1878 | 6 | -2.4 | 0 | 0 | 0 | 0 | 0 | 79 | 1878 | 360 | 77.9178 | -0.60903 | 6.4723 | 334.284 | 5.6793 | 94.8109 | -3.737 | 0 | 89.1107 | 90.8893 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.72411 | 0.72411 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1879 | 7 | -2.1 | 0 | 0 | 0 | 0 | 0 | 79 | 1879 | 420 | 77.9178 | -0.60903 | 6.4723 | 394.284 | 6.6793 | 79.8109 | 6.5108 | 6.5108 | 82.1221 | 97.8779 | 79.8357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 164.9809 | 164.9809 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1880 | 8 | -1.8 | 16.58 | 26.75 | 43.33 | 26.75 | 13.38 | 79 | 1880 | 480 | 77.9178 | -0.60903 | 6.4723 | 454.284 | 7.6793 | 64.8109 | 16.4814 | 16.4814 | 70.6703 | 109.3297 | 64.8463 | 24.8402 | 24.8402 | 22.8326 | 47.6728 | -2.6765 | 0% | 21.5576 | 0 | 0 | 176.4321 | 176.4321 | 0% | 12.25% | 12.25% | 80% | 9.803% | 2.1133 | 10.9053 | 6 | 12.6801 | 4.6735 | 7.187% | 7.187%
3 | 79 | 20 | 1881 | 9 | -1.8 | 86.94 | 82.69 | 169.63 | 82.69 | 41.35 | 79 | 1881 | 540 | 77.9178 | -0.60903 | 6.4723 | 514.284 | 8.6793 | 49.8109 | 25.7316 | 25.7316 | 57.9907 | 122.0093 | 49.8617 | 129.0884 | 129.0884 | 70.5803 | 199.6688 | -0.026993 | 0% | 90.2902 | 0 | 0 | 162.3272 | 162.3272 | 0% | 12.07% | 12.07% | 80% | 9.657% | 8.7197 | 10.9053 | 6 | 52.3183 | 19.2829 | 32.23% | 32.23%
3 | 79 | 20 | 1882 | 10 | -1.1 | 171.94 | 113.69 | 285.63 | 113.69 | 56.85 | 79 | 1882 | 600 | 77.9178 | -0.60903 | 6.4723 | 574.284 | 9.6793 | 34.8109 | 33.6758 | 33.6758 | 43.3102 | 136.6898 | 34.8883 | 254.3531 | 254.3531 | 97.0405 | 351.3935 | 0.33677 | 33.68% | 158.9002 | 53.5129 | 37.459 | 144.3387 | 144.3387 | 25.95% | 11.87% | 11.87% | 85% | 10.09% | 16.0358 | 10.6622 | 6 | 96.2145 | 35.4616 | 66.66% | 66.66%
3 | 79 | 20 | 1883 | 11 | -0.2 | 185.64 | 174.72 | 360.36 | 174.72 | 87.36 | 79 | 1883 | 660 | 77.9178 | -0.60903 | 6.4723 | 634.284 | 10.6793 | 19.8109 | 39.5324 | 39.5324 | 26.066 | 153.934 | 19.9518 | 274.1462 | 274.1462 | 149.1328 | 423.279 | 0.42139 | 42.14% | 191.4068 | 80.6565 | 56.4596 | 140.462 | 140.462 | 40.2% | 11.77% | 11.77% | 85% | 10% | 19.1502 | 10.3546 | 6 | 114.901 | 42.3489 | 81.8% | 81.8%
3 | 79 | 20 | 1884 | 12 | 0.1 | 101.75 | 199.81 | 301.56 | 199.81 | 99.91 | 79 | 1884 | 720 | 77.9178 | -0.60903 | 6.4723 | 694.284 | 11.6793 | 4.8109 | 42.4254 | 42.4254 | 6.5236 | 173.4764 | 5.37 | 150.1614 | 150.1614 | 170.5485 | 320.71 | 0.30133 | 30.13% | 145.025 | 43.7007 | 30.5905 | 126.3741 | 126.3741 | 24.21% | 11.88% | 11.88% | 85% | 10.1% | 14.6404 | 10.2533 | 6 | 87.8425 | 32.376 | 69.51% | 69.51%
3 | 79 | 20 | 1885 | 13 | 0.7 | 151.67 | 218.97 | 370.64 | 218.97 | 109.49 | 79 | 1885 | 780 | 77.9178 | -0.60903 | 6.4723 | 754.284 | 12.6793 | -10.1891 | 41.7778 | 41.7778 | 13.7212 | 193.7212 | 10.4637 | 223.8639 | 223.8639 | 186.9026 | 410.7664 | 0.41514 | 41.51% | 185.7486 | 77.1108 | 53.9776 | 127.1726 | 127.1726 | 42.44% | 11.77% | 11.77% | 85% | 10% | 18.5756 | 10.0527 | 6 | 111.4536 | 41.0783 | 87.64% | 87.64%
3 | 79 | 20 | 1886 | 14 | 0.8 | 149.53 | 209.08 | 358.61 | 209.08 | 104.54 | 79 | 1886 | 840 | 77.9178 | -0.60903 | 6.4723 | 814.284 | 13.6793 | -25.1891 | 37.7288 | 37.7288 | 32.5536 | 212.5536 | 25.2988 | 220.9239 | 220.9239 | 178.4609 | 399.3848 | 0.40467 | 40.47% | 180.6018 | 73.084 | 51.1588 | 124.5844 | 124.5844 | 41.06% | 11.78% | 11.78% | 85% | 10.01% | 18.0761 | 10.0195 | 6 | 108.4564 | 39.9736 | 87.05% | 87.05%
3 | 79 | 20 | 1887 | 15 | 0.5 | 85.83 | 226.94 | 312.77 | 226.94 | 113.47 | 79 | 1887 | 900 | 77.9178 | -0.60903 | 6.4723 | 874.284 | 14.6793 | -40.1891 | 31.0227 | 31.0227 | 48.8491 | 228.8491 | 40.2548 | 127.0984 | 127.0984 | 193.7054 | 320.8038 | 0.30455 | 30.46% | 145.0675 | 44.1806 | 30.9265 | 119.0851 | 119.0851 | 25.97% | 11.87% | 11.87% | 85% | 10.09% | 14.6316 | 10.1193 | 6 | 87.7894 | 32.3564 | 73.72% | 73.72%
3 | 79 | 20 | 1888 | 16 | 0.8 | 106.19 | 163.69 | 269.88 | 163.69 | 81.85 | 79 | 1888 | 960 | 77.9178 | -0.60903 | 6.4723 | 934.284 | 15.6793 | -55.1891 | 22.5308 | 22.5308 | 62.7273 | 242.7273 | 55.2335 | 158.0279 | 158.0279 | 139.7182 | 297.7461 | 0.26835 | 26.84% | 134.6408 | 36.1314 | 25.2919 | 115.1234 | 115.1234 | 21.97% | 11.88% | 11.88% | 80% | 9.506% | 12.7988 | 10.0195 | 6 | 76.7929 | 28.3035 | 66.7% | 66.7%
3 | 79 | 20 | 1889 | 17 | 0 | 26.03 | 141.58 | 167.61 | 141.58 | 70.79 | 79 | 1889 | 1020 | 77.9178 | -0.60903 | 6.4723 | 994.284 | 16.6793 | -70.1891 | 12.9641 | 12.9641 | 74.8773 | 254.8773 | 70.2203 | 39.2647 | 39.2647 | 120.8461 | 160.1108 | -0.20441 | 0% | 72.4021 | 0 | 0 | 106.0611 | 106.0611 | 0% | 12.06% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1890 | 18 | -0.7 | 8.69 | 82.97 | 91.66 | 82.97 | 41.49 | 79 | 1890 | 1080 | 77.9178 | -0.60903 | 6.4723 | 1054.284 | 17.6793 | -85.1891 | 2.848 | 2.848 | 86.0736 | 266.0736 | 85.2106 | 0 | 0 | 70.8193 | 70.8193 | -1.5003 | 0% | 32.0245 | 0 | 0 | 139.4717 | 139.4717 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1891 | 19 | -0.6 | 0 | 26.94 | 26.94 | 26.94 | 13.47 | 79 | 1891 | 1140 | 77.9178 | -0.60903 | 6.4723 | 1114.284 | 18.6793 | -100.1891 | -7.405 | 0 | 89.1107 | 269.1107 | 89.3712 | 0 | 0 | 22.9947 | 22.9947 | -6.282 | 0% | 10.3982 | 0 | 0 | 132.8354 | 132.8354 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1892 | 20 | -0.8 | 0 | 0 | 0 | 0 | 0 | 79 | 1892 | 1200 | 77.9178 | -0.60903 | 6.4723 | 1174.284 | 19.6793 | -115.1891 | -17.4093 | 0 | 89.1107 | 269.1107 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.5598 | 125.5598 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1893 | 21 | -1 | 0 | 0 | 0 | 0 | 0 | 79 | 1893 | 1260 | 77.9178 | -0.60903 | 6.4723 | 1234.284 | 20.6793 | -130.1891 | -26.7211 | 0 | 89.1107 | 269.1107 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0638 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1894 | 22 | -1 | 0 | 0 | 0 | 0 | 0 | 79 | 1894 | 1320 | 77.9178 | -0.60903 | 6.4723 | 1294.284 | 21.6793 | -145.1891 | -34.7491 | 0 | 89.1107 | 269.1107 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1895 | 23 | -1.1 | 0 | 0 | 0 | 0 | 0 | 79 | 1895 | 1380 | 77.9178 | -0.60903 | 6.4723 | 1354.284 | 22.6793 | -160.1891 | -40.693 | 0 | 89.1107 | 269.1107 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8723 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
3 | 79 | 20 | 1896 | 24 | -1 | 0 | 0 | 0 | 0 | 0 | 79 | 1896 | 1440 | 77.9178 | -0.60903 | 6.4723 | 1414.284 | 23.6793 | -175.1891 | -43.6397 | 0 | 89.1107 | 269.1107 | 89.3712 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1397 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1897 | 1 | -2 | 0 | 0 | 0 | 0 | 0 | 80 | 1897 | 60 | 78.9041 | -0.20802 | 6.8535 | 34.284 | 0.68562 | 169.7156 | -42.5681 | 0 | 89.6962 | 90.3038 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6143 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1898 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 80 | 1898 | 120 | 78.9041 | -0.20802 | 6.8535 | 94.284 | 1.6856 | 154.7156 | -38.4522 | 0 | 89.6962 | 90.3038 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5167 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1899 | 3 | -4 | 0 | 0 | 0 | 0 | 0 | 80 | 1899 | 180 | 78.9041 | -0.20802 | 6.8535 | 154.284 | 2.6856 | 139.7156 | -31.6722 | 0 | 89.6962 | 90.3038 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.419 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1900 | 4 | -4.7 | 0 | 0 | 0 | 0 | 0 | 80 | 1900 | 240 | 78.9041 | -0.20802 | 6.8535 | 214.284 | 3.6856 | 124.7156 | -23.1198 | 0 | 89.6962 | 90.3038 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4858 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1901 | 5 | -5.5 | 0 | 0 | 0 | 0 | 0 | 80 | 1901 | 300 | 78.9041 | -0.20802 | 6.8535 | 274.284 | 4.6856 | 109.7156 | -13.5134 | 0 | 89.6962 | 90.3038 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1661 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1902 | 6 | -5.5 | 0 | 0 | 0 | 0 | 0 | 80 | 1902 | 360 | 78.9041 | -0.20802 | 6.8535 | 334.284 | 5.6856 | 94.7156 | -3.3793 | 0 | 89.6962 | 90.3038 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.18906 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1903 | 7 | -6.2 | 0 | 0 | 0 | 0 | 0 | 80 | 1903 | 420 | 78.9041 | -0.20802 | 6.8535 | 394.284 | 6.6856 | 79.7156 | 6.8701 | 6.8701 | 82.3256 | 97.6744 | 79.7273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 165.2078 | 165.2078 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1904 | 8 | -6 | 19.81 | 23.14 | 42.95 | 23.14 | 11.57 | 80 | 1904 | 480 | 78.9041 | -0.20802 | 6.8535 | 454.284 | 7.6856 | 64.7156 | 16.849 | 16.849 | 70.8651 | 109.1349 | 64.736 | 29.1693 | 29.1693 | 19.7512 | 48.9205 | -2.8042 | 0% | 22.1219 | 0 | 0 | 178.0802 | 178.0802 | 0% | 12.43% | 12.43% | 80% | 9.941% | 2.1991 | 12.4362 | 6 | 13.1946 | 4.8631 | 7.409% | 7.409%
3 | 80 | 21 | 1905 | 9 | -4.8 | 88.33 | 57.03 | 145.36 | 57.03 | 28.52 | 80 | 1905 | 540 | 78.9041 | -0.20802 | 6.8535 | 514.284 | 8.6856 | 49.7156 | 26.1133 | 26.1133 | 58.1637 | 121.8363 | 49.7478 | 129.6717 | 129.6717 | 48.6781 | 178.3498 | -0.1686 | 0% | 80.6498 | 0 | 0 | 164.9845 | 164.9845 | 0% | 12.2% | 12.2% | 80% | 9.76% | 7.8714 | 11.9862 | 6 | 47.2283 | 17.4068 | 28.63% | 28.63%
3 | 80 | 21 | 1906 | 10 | -3.1 | 207.69 | 108.81 | 316.5 | 108.81 | 54.41 | 80 | 1906 | 600 | 78.9041 | -0.20802 | 6.8535 | 574.284 | 9.6856 | 34.7156 | 34.0745 | 34.0745 | 43.4361 | 136.5639 | 34.7673 | 304.5173 | 304.5173 | 92.8751 | 397.3924 | 0.37829 | 37.83% | 179.7009 | 67.9782 | 47.5847 | 152.0934 | 152.0934 | 31.29% | 11.86% | 11.86% | 85% | 10.08% | 18.121 | 11.366 | 6 | 108.7261 | 40.073 | 71.49% | 71.49%
3 | 80 | 21 | 1907 | 11 | -1.8 | 337.31 | 116.86 | 454.17 | 116.86 | 58.43 | 80 | 1907 | 660 | 78.9041 | -0.20802 | 6.8535 | 634.284 | 10.6856 | 19.7156 | 39.9435 | 39.9435 | 26.1048 | 153.8952 | 19.8126 | 494.2801 | 494.2801 | 99.7462 | 594.0264 | 0.52468 | 52.47% | 268.6187 | 140.9389 | 98.6572 | 151.2235 | 151.2235 | 65.24% | 11.6% | 11.6% | 90% | 10.44% | 28.0413 | 10.9053 | 6 | 168.2477 | 62.0108 | 111.3% | 111.3%
3 | 80 | 21 | 1908 | 12 | -1.2 | 403.97 | 149.81 | 553.78 | 149.81 | 74.91 | 80 | 1908 | 720 | 78.9041 | -0.20802 | 6.8535 | 694.284 | 11.6856 | 4.7156 | 42.8326 | 42.8326 | 6.4366 | 173.5634 | 5.1162 | 591.8297 | 591.8297 | 127.8708 | 719.7005 | 0.57553 | 57.55% | 325.4486 | 187.3054 | 131.1138 | 142.9512 | 142.9512 | 91.72% | 11.45% | 11.45% | 90% | 10.3% | 33.5247 | 10.6967 | 6 | 201.148 | 74.1368 | 140.7% | 140.7%
3 | 80 | 21 | 1909 | 13 | 0.7 | 389.81 | 154.64 | 544.45 | 154.64 | 77.32 | 80 | 1909 | 780 | 78.9041 | -0.20802 | 6.8535 | 754.284 | 12.6856 | -10.2844 | 42.1578 | 42.1578 | 13.936 | 193.936 | 10.4729 | 571.1126 | 571.1126 | 131.9935 | 703.1061 | 0.57682 | 57.68% | 317.9446 | 183.3964 | 128.3775 | 141.741 | 141.741 | 90.57% | 11.45% | 11.45% | 90% | 10.31% | 32.7781 | 10.0527 | 6 | 196.6685 | 72.4858 | 138.8% | 138.8%
3 | 80 | 21 | 1910 | 14 | 0.8 | 252.03 | 206.67 | 458.7 | 206.67 | 103.34 | 80 | 1910 | 840 | 78.9041 | -0.20802 | 6.8535 | 814.284 | 13.6856 | -25.2844 | 38.0661 | 38.0661 | 32.8538 | 212.8538 | 25.3586 | 369.3751 | 369.3751 | 176.4039 | 545.779 | 0.51178 | 51.18% | 246.8013 | 126.3084 | 88.4159 | 136.4294 | 136.4294 | 64.81% | 11.62% | 11.62% | 90% | 10.46% | 25.8115 | 10.0195 | 6 | 154.869 | 57.0798 | 113.5% | 113.5%
3 | 80 | 21 | 1911 | 15 | 1.5 | 182.69 | 210.92 | 393.61 | 210.92 | 105.46 | 80 | 1911 | 900 | 78.9041 | -0.20802 | 6.8535 | 874.284 | 14.6856 | -40.2844 | 31.3167 | 31.3167 | 49.1867 | 229.1867 | 40.3273 | 267.9573 | 267.9573 | 180.0315 | 447.9888 | 0.45183 | 45.18% | 202.5805 | 91.5316 | 64.0721 | 130.9141 | 130.9141 | 48.94% | 11.71% | 11.71% | 85% | 9.954% | 20.1641 | 9.7891 | 6 | 120.9849 | 44.5912 | 92.42% | 92.42%
3 | 80 | 21 | 1912 | 16 | 1 | 122.31 | 192.42 | 314.73 | 192.42 | 96.21 | 80 | 1912 | 960 | 78.9041 | -0.20802 | 6.8535 | 934.284 | 15.6856 | -55.2844 | 22.7905 | 22.7905 | 63.074 | 243.074 | 55.3116 | 179.6975 | 179.6975 | 164.2407 | 343.9383 | 0.34172 | 34.17% | 155.5289 | 53.1476 | 37.2033 | 123.869 | 123.869 | 30.03% | 11.83% | 11.83% | 85% | 10.05% | 15.6373 | 9.9533 | 6 | 93.824 | 34.5806 | 75.74% | 75.74%
3 | 80 | 21 | 1913 | 17 | 0.8 | 118.69 | 134.17 | 252.86 | 134.17 | 67.09 | 80 | 1913 | 1020 | 78.9041 | -0.20802 | 6.8535 | 994.284 | 16.6856 | -70.2844 | 13.2018 | 13.2018 | 75.2231 | 255.2231 | 70.3012 | 175.1786 | 175.1786 | 114.5213 | 289.6999 | 0.25348 | 25.35% | 131.0023 | 33.206 | 23.2442 | 117.3685 | 117.3685 | 19.8% | 11.89% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1914 | 18 | 0.8 | 77.97 | 72.97 | 150.94 | 72.97 | 36.49 | 80 | 1914 | 1080 | 78.9041 | -0.20802 | 6.8535 | 1054.284 | 17.6856 | -85.2844 | 3.0756 | 3.0756 | 86.4176 | 266.4176 | 85.2931 | 0 | 0 | 62.2838 | 62.2838 | -1.7566 | 0% | 28.1647 | 0 | 0 | 108.035 | 108.035 | 0% | 12.13% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1915 | 19 | 0.1 | 0 | 24.81 | 24.81 | 24.81 | 12.41 | 80 | 1915 | 1140 | 78.9041 | -0.20802 | 6.8535 | 1114.284 | 18.6856 | -100.2844 | -7.1755 | 0 | 89.6962 | 269.6962 | 89.7852 | 0 | 0 | 21.1767 | 21.1767 | -6.8087 | 0% | 9.5761 | 0 | 0 | 136.4196 | 136.4196 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1916 | 20 | -0.1 | 0 | 0 | 0 | 0 | 0 | 80 | 1916 | 1200 | 78.9041 | -0.20802 | 6.8535 | 1174.284 | 19.6856 | -115.2844 | -17.166 | 0 | 89.6962 | 269.6962 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.7385 | 127.7385 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1917 | 21 | -0.6 | 0 | 0 | 0 | 0 | 0 | 80 | 1917 | 1260 | 78.9041 | -0.20802 | 6.8535 | 1234.284 | 20.6856 | -130.2844 | -26.4514 | 0 | 89.6962 | 269.6962 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7445 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1918 | 22 | -0.8 | 0 | 0 | 0 | 0 | 0 | 80 | 1918 | 1320 | 78.9041 | -0.20802 | 6.8535 | 1294.284 | 21.6856 | -145.2844 | -34.4413 | 0 | 89.6962 | 269.6962 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6505 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1919 | 23 | -1.4 | 0 | 0 | 0 | 0 | 0 | 80 | 1919 | 1380 | 78.9041 | -0.20802 | 6.8535 | 1354.284 | 22.6856 | -160.2844 | -40.3401 | 0 | 89.6962 | 269.6962 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9433 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
3 | 80 | 21 | 1920 | 24 | -1.9 | 0 | 0 | 0 | 0 | 0 | 80 | 1920 | 1440 | 78.9041 | -0.20802 | 6.8535 | 1414.284 | 23.6856 | -175.2844 | -43.2474 | 0 | 89.6962 | 269.6962 | 89.7852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0836 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1921 | 1 | -2.2 | 0 | 0 | 0 | 0 | 0 | 81 | 1921 | 60 | 79.8904 | 0.19323 | 7.2324 | 34.284 | 0.69194 | 169.6209 | -42.1566 | 0 | 90.2822 | 89.7178 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.4009 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1922 | 2 | -3 | 0 | 0 | 0 | 0 | 0 | 81 | 1922 | 120 | 79.8904 | 0.19323 | 7.2324 | 94.284 | 1.6919 | 154.6209 | -38.0446 | 0 | 90.2822 | 89.7178 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.18 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1923 | 3 | -2.9 | 0 | 0 | 0 | 0 | 0 | 81 | 1923 | 180 | 79.8904 | 0.19323 | 7.2324 | 154.284 | 2.6919 | 139.6209 | -31.2802 | 0 | 90.2822 | 89.7178 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.5875 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1924 | 4 | -3.1 | 0 | 0 | 0 | 0 | 0 | 81 | 1924 | 240 | 79.8904 | 0.19323 | 7.2324 | 214.284 | 3.6919 | 124.6209 | -22.7444 | 0 | 90.2822 | 89.7178 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8923 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1925 | 5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 81 | 1925 | 300 | 79.8904 | 0.19323 | 7.2324 | 274.284 | 4.6919 | 109.6209 | -13.1501 | 0 | 90.2822 | 89.7178 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1314 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1926 | 6 | -3.9 | 0 | 0 | 0 | 0 | 0 | 81 | 1926 | 360 | 79.8904 | 0.19323 | 7.2324 | 334.284 | 5.6919 | 94.6209 | -3.0217 | 0 | 90.2822 | 89.7178 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7131 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1927 | 7 | -4.7 | 0 | 0 | 0 | 0 | 0 | 81 | 1927 | 420 | 79.8904 | 0.19323 | 7.2324 | 394.284 | 6.6919 | 79.6209 | 7.229 | 7.229 | 82.53 | 97.47 | 79.6199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 155.9346 | 155.9346 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1928 | 8 | -3.8 | 9.81 | 20.92 | 30.73 | 20.92 | 10.46 | 81 | 1928 | 480 | 79.8904 | 0.19323 | 7.2324 | 454.284 | 7.6919 | 64.6209 | 17.2161 | 17.2161 | 71.0612 | 108.9388 | 64.6275 | 14.2025 | 14.2025 | 17.8563 | 32.0588 | -4.528 | 0% | 14.497 | 0 | 0 | 167.2424 | 167.2424 | 0% | 12.36% | 12.36% | 80% | 9.886% | 1.4331 | 11.6189 | 6 | 8.5989 | 3.1693 | 5.142% | 5.142%
3 | 81 | 22 | 1929 | 9 | -3 | 62.78 | 70.92 | 133.7 | 70.92 | 35.46 | 81 | 1929 | 540 | 79.8904 | 0.19323 | 7.2324 | 514.284 | 8.6919 | 49.6209 | 26.4947 | 26.4947 | 58.3384 | 121.6616 | 49.6368 | 91.1386 | 91.1386 | 60.534 | 151.6726 | -0.30975 | 0% | 68.5864 | 0 | 0 | 154.1113 | 154.1113 | 0% | 12.17% | 12.17% | 80% | 9.738% | 6.6787 | 11.3301 | 6 | 40.0724 | 14.7694 | 26% | 26%
3 | 81 | 22 | 1930 | 10 | -0.1 | 127.03 | 133.89 | 260.92 | 133.89 | 66.95 | 81 | 1930 | 600 | 79.8904 | 0.19323 | 7.2324 | 574.284 | 9.6919 | 34.6209 | 34.473 | 34.473 | 43.5639 | 136.4361 | 34.6508 | 184.6213 | 184.6213 | 114.2823 | 298.9036 | 0.26301 | 26.3% | 135.1642 | 35.5492 | 24.8845 | 142.7579 | 142.7579 | 17.43% | 11.91% | 11.91% | 80% | 9.525% | 12.8741 | 10.3208 | 6 | 77.2445 | 28.4699 | 54.11% | 54.11%
3 | 81 | 22 | 1931 | 11 | 0.8 | 242.78 | 191.94 | 434.72 | 191.94 | 95.97 | 81 | 1931 | 660 | 79.8904 | 0.19323 | 7.2324 | 634.284 | 10.6919 | 19.6209 | 40.3546 | 40.3546 | 26.145 | 153.855 | 19.6813 | 353.0366 | 353.0366 | 163.831 | 516.8676 | 0.49544 | 49.54% | 233.7275 | 115.7971 | 81.058 | 145.9892 | 145.9892 | 55.52% | 11.65% | 11.65% | 90% | 10.49% | 24.5084 | 10.0195 | 6 | 147.0505 | 54.1982 | 100.7% | 100.7%
3 | 81 | 22 | 1932 | 12 | 0.7 | 209.36 | 220.56 | 429.92 | 220.56 | 110.28 | 81 | 1932 | 720 | 79.8904 | 0.19323 | 7.2324 | 694.284 | 11.6919 | 4.6209 | 43.2399 | 43.2399 | 6.3492 | 173.6508 | 4.8843 | 304.5009 | 304.5009 | 188.2597 | 492.7606 | 0.47984 | 47.98% | 222.8263 | 106.9213 | 74.8449 | 135.7432 | 135.7432 | 55.14% | 11.68% | 11.68% | 85% | 9.926% | 22.1187 | 10.0527 | 6 | 132.712 | 48.9135 | 97.77% | 97.77%
3 | 81 | 22 | 1933 | 13 | 1.1 | 459.53 | 236.47 | 696 | 236.47 | 118.24 | 81 | 1933 | 780 | 79.8904 | 0.19323 | 7.2324 | 754.284 | 12.6919 | -10.3791 | 42.5377 | 42.5377 | 14.1526 | 194.1526 | 10.4975 | 668.3262 | 668.3262 | 201.8398 | 870.166 | 0.62156 | 62.16% | 393.4891 | 244.5786 | 171.205 | 145.3776 | 145.3776 | 117.8% | 11.28% | 11.28% | 95% | 10.72% | 42.1628 | 9.9203 | 6 | 252.9767 | 93.2392 | 174% | 174%
3 | 81 | 22 | 1934 | 14 | 1.5 | 453.89 | 161.67 | 615.56 | 161.67 | 80.84 | 81 | 1934 | 840 | 79.8904 | 0.19323 | 7.2324 | 814.284 | 13.6919 | -25.3791 | 38.4031 | 38.4031 | 33.1563 | 213.1563 | 25.4239 | 659.917 | 659.917 | 137.994 | 797.911 | 0.60627 | 60.63% | 360.8154 | 218.7524 | 153.1267 | 140.745 | 140.745 | 108.8% | 11.35% | 11.35% | 90% | 10.22% | 36.8707 | 9.7891 | 6 | 221.2241 | 81.5362 | 157.2% | 157.2%
3 | 81 | 22 | 1935 | 15 | 0 | 402.31 | 180.36 | 582.67 | 180.36 | 90.18 | 81 | 1935 | 900 | 79.8904 | 0.19323 | 7.2324 | 874.284 | 14.6919 | -40.3791 | 31.6103 | 31.6103 | 49.5261 | 229.5261 | 40.4026 | 584.5066 | 584.5066 | 153.9469 | 738.4534 | 0.58536 | 58.54% | 333.9286 | 195.4676 | 136.8273 | 134.573 | 134.573 | 101.7% | 11.42% | 11.42% | 90% | 10.28% | 34.3203 | 10.287 | 6 | 205.9217 | 75.8963 | 153% | 153%
3 | 81 | 22 | 1936 | 16 | 0.9 | 267.86 | 148.89 | 416.75 | 148.89 | 74.45 | 81 | 1936 | 960 | 79.8904 | 0.19323 | 7.2324 | 934.284 | 15.6919 | -55.3791 | 23.0501 | 23.0501 | 63.4218 | 243.4218 | 55.3911 | 388.5647 | 388.5647 | 127.0856 | 515.6502 | 0.49518 | 49.52% | 233.177 | 115.4656 | 80.8259 | 127.0495 | 127.0495 | 63.62% | 11.65% | 11.65% | 90% | 10.49% | 24.4501 | 9.9864 | 6 | 146.7006 | 54.0692 | 115.5% | 115.5%
3 | 81 | 22 | 1937 | 17 | 2 | 168.89 | 144.72 | 313.61 | 144.72 | 72.36 | 81 | 1937 | 1020 | 79.8904 | 0.19323 | 7.2324 | 994.284 | 16.6919 | -70.3791 | 13.4395 | 13.4395 | 75.5693 | 255.5693 | 70.3827 | 243.9679 | 243.9679 | 123.5262 | 367.4941 | 0.37802 | 37.8% | 166.1808 | 62.8192 | 43.9734 | 120.9976 | 120.9976 | 36.34% | 11.78% | 0% | 85% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1938 | 18 | 0.2 | 83.61 | 114.64 | 198.25 | 114.64 | 57.32 | 81 | 1938 | 1080 | 79.8904 | 0.19323 | 7.2324 | 1054.284 | 17.6919 | -85.3791 | 3.3037 | 3.3037 | 86.7616 | 266.7616 | 85.3753 | 0 | 0 | 97.8514 | 97.8514 | -0.84098 | 0% | 44.2484 | 0 | 0 | 108.2945 | 108.2945 | 0% | 12.12% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1939 | 19 | -0.7 | 0 | 41.75 | 41.75 | 41.75 | 20.88 | 81 | 1939 | 1140 | 79.8904 | 0.19323 | 7.2324 | 1114.284 | 18.6919 | -100.3791 | -6.9452 | 0 | 90.2822 | 270.2822 | 90.1995 | 0 | 0 | 35.6359 | 35.6359 | -3.7754 | 0% | 16.1145 | 0 | 0 | 134.6895 | 134.6895 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1940 | 20 | -1.7 | 0 | 0 | 0 | 0 | 0 | 81 | 1940 | 1200 | 79.8904 | 0.19323 | 7.2324 | 1174.284 | 19.6919 | -115.3791 | -16.9215 | 0 | 90.2822 | 270.2822 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.3005 | 124.3005 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1941 | 21 | -3.3 | 0 | 0 | 0 | 0 | 0 | 81 | 1941 | 1260 | 79.8904 | 0.19323 | 7.2324 | 1234.284 | 20.6919 | -130.3791 | -26.1804 | 0 | 90.2822 | 270.2822 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.8368 | 0 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1942 | 22 | -4.3 | 0 | 0 | 0 | 0 | 0 | 81 | 1942 | 1320 | 79.8904 | 0.19323 | 7.2324 | 1294.284 | 21.6919 | -145.3791 | -34.1321 | 0 | 90.2822 | 270.2822 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.9217 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1943 | 23 | -4.3 | 0 | 0 | 0 | 0 | 0 | 81 | 1943 | 1380 | 79.8904 | 0.19323 | 7.2324 | 1354.284 | 22.6919 | -160.3791 | -39.9861 | 0 | 90.2822 | 270.2822 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.4815 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
3 | 81 | 22 | 1944 | 24 | -4.6 | 0 | 0 | 0 | 0 | 0 | 81 | 1944 | 1440 | 79.8904 | 0.19323 | 7.2324 | 1414.284 | 23.6919 | -175.3791 | -42.8545 | 0 | 90.2822 | 270.2822 | 90.1995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.4986 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1945 | 1 | -3.6 | 0 | 0 | 0 | 0 | 0 | 82 | 1945 | 60 | 80.8767 | 0.59461 | 7.6086 | 34.284 | 0.69821 | 169.5269 | -41.7452 | 0 | 90.8683 | 89.1317 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.4775 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1946 | 2 | -2.6 | 0 | 0 | 0 | 0 | 0 | 82 | 1946 | 120 | 80.8767 | 0.59461 | 7.6086 | 94.284 | 1.6982 | 154.5269 | -37.637 | 0 | 90.8683 | 89.1317 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.7523 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1947 | 3 | -2.5 | 0 | 0 | 0 | 0 | 0 | 82 | 1947 | 180 | 80.8767 | 0.59461 | 7.6086 | 154.284 | 2.6982 | 139.5269 | -30.8882 | 0 | 90.8683 | 89.1317 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.3988 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1948 | 4 | -2.3 | 0 | 0 | 0 | 0 | 0 | 82 | 1948 | 240 | 80.8767 | 0.59461 | 7.6086 | 214.284 | 3.6982 | 124.5269 | -22.3691 | 0 | 90.8683 | 89.1317 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.094 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1949 | 5 | -2.2 | 0 | 0 | 0 | 0 | 0 | 82 | 1949 | 300 | 80.8767 | 0.59461 | 7.6086 | 274.284 | 4.6982 | 109.5269 | -12.787 | 0 | 90.8683 | 89.1317 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4465 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1950 | 6 | -3.2 | 0 | 0 | 0 | 0 | 0 | 82 | 1950 | 360 | 80.8767 | 0.59461 | 7.6086 | 334.284 | 5.6982 | 94.5269 | -2.6644 | 0 | 90.8683 | 89.1317 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.797 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1951 | 7 | -4 | 0 | 0 | 0 | 0 | 0 | 82 | 1951 | 420 | 80.8767 | 0.59461 | 7.6086 | 394.284 | 6.6982 | 79.5269 | 7.5875 | 7.5875 | 82.7353 | 97.2647 | 79.5138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.5338 | 135.5338 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1952 | 8 | -3.9 | 1.19 | 18.06 | 19.25 | 18.06 | 9.03 | 82 | 1952 | 480 | 80.8767 | 0.59461 | 7.6086 | 454.284 | 7.6982 | 64.5269 | 17.5827 | 17.5827 | 71.2588 | 108.7412 | 64.521 | 1.6946 | 1.6946 | 15.4152 | 17.1098 | -9.2013 | 0% | 7.737 | 0 | 0 | 140.0453 | 140.0453 | 0% | 12.38% | 12.38% | 80% | 9.905% | 0.76635 | 11.6553 | 6 | 4.5981 | 1.6947 | 3.283% | 3.283%
3 | 82 | 23 | 1953 | 9 | -3.1 | 5.28 | 67.69 | 72.97 | 67.69 | 33.85 | 82 | 1953 | 540 | 80.8767 | 0.59461 | 7.6086 | 514.284 | 8.6982 | 49.5269 | 26.8755 | 26.8755 | 58.515 | 121.485 | 49.5288 | 7.5811 | 7.5811 | 57.777 | 65.3581 | -1.7844 | 0% | 29.5549 | 0 | 0 | 123.3069 | 123.3069 | 0% | 12.29% | 12.29% | 80% | 9.828% | 2.9047 | 11.366 | 6 | 17.4285 | 6.4236 | 14.13% | 14.13%
3 | 82 | 23 | 1954 | 10 | -3.2 | 36.03 | 138.25 | 174.28 | 138.25 | 69.13 | 82 | 1954 | 600 | 80.8767 | 0.59461 | 7.6086 | 574.284 | 9.6982 | 34.5269 | 34.8712 | 34.8712 | 43.6937 | 136.3063 | 34.5389 | 51.9112 | 51.9112 | 118.0038 | 169.915 | -0.19313 | 0% | 76.8356 | 0 | 0 | 127.3201 | 127.3201 | 0% | 12.16% | 12.16% | 80% | 9.725% | 7.4721 | 11.4019 | 6 | 44.8326 | 16.5239 | 35.21% | 35.21%
3 | 82 | 23 | 1955 | 11 | -1 | 63.53 | 155.92 | 219.45 | 155.92 | 77.96 | 82 | 1955 | 660 | 80.8767 | 0.59461 | 7.6086 | 634.284 | 10.6982 | 19.5269 | 40.7656 | 40.7656 | 26.1865 | 153.8135 | 19.5581 | 91.6807 | 91.6807 | 133.086 | 224.7668 | 0.074652 | 7.465% | 101.6395 | 7.5876 | 5.3113 | 108.884 | 108.884 | 4.878% | 12.02% | 12.02% | 80% | 9.613% | 9.7707 | 10.6277 | 6 | 58.6244 | 21.6071 | 53.84% | 53.84%
3 | 82 | 23 | 1956 | 12 | 0.7 | 34.17 | 158.53 | 192.7 | 158.53 | 79.27 | 82 | 1956 | 720 | 80.8767 | 0.59461 | 7.6086 | 694.284 | 11.6982 | 4.5269 | 43.6472 | 43.6472 | 6.2616 | 173.7384 | 4.678 | 49.3413 | 49.3413 | 135.3138 | 184.6551 | -0.061031 | 0% | 83.5011 | 0 | 0 | 126.9462 | 126.9462 | 0% | 12.01% | 12.01% | 80% | 9.604% | 8.0196 | 10.0527 | 6 | 48.1174 | 17.7346 | 37.9% | 37.9%
3 | 82 | 23 | 1957 | 13 | 0.7 | 32.42 | 190 | 222.42 | 190 | 95 | 82 | 1957 | 780 | 80.8767 | 0.59461 | 7.6086 | 754.284 | 12.6982 | -10.4731 | 42.9175 | 42.9175 | 14.3709 | 194.3709 | 10.5374 | 46.8075 | 46.8075 | 162.1751 | 208.9826 | 0.039666 | 3.967% | 94.5019 | 3.7485 | 2.624 | 106.5909 | 106.5909 | 2.462% | 11.98% | 11.98% | 80% | 9.583% | 9.0566 | 10.0527 | 6 | 54.3395 | 20.0278 | 50.98% | 50.98%
3 | 82 | 23 | 1958 | 14 | 2 | 23.42 | 205.19 | 228.61 | 205.19 | 102.6 | 82 | 1958 | 840 | 80.8767 | 0.59461 | 7.6086 | 814.284 | 13.6982 | -25.4731 | 38.7396 | 38.7396 | 33.4608 | 213.4608 | 25.4946 | 33.7809 | 33.7809 | 175.1406 | 208.9216 | 0.054693 | 5.469% | 94.4743 | 5.1671 | 3.617 | 108.323 | 108.323 | 3.339% | 11.94% | 11.94% | 80% | 9.55% | 9.022 | 9.6266 | 6 | 54.1323 | 19.9515 | 49.97% | 49.97%
3 | 82 | 23 | 1959 | 15 | 0.8 | 17.22 | 151.03 | 168.25 | 151.03 | 75.52 | 82 | 1959 | 900 | 80.8767 | 0.59461 | 7.6086 | 874.284 | 14.6982 | -40.4731 | 31.9034 | 31.9034 | 49.8669 | 229.8669 | 40.4807 | 24.7838 | 24.7838 | 128.9122 | 153.696 | -0.23368 | 0% | 69.5013 | 0 | 0 | 102.3163 | 102.3163 | 0% | 12.03% | 12.03% | 80% | 9.628% | 6.6913 | 10.0195 | 6 | 40.1478 | 14.7972 | 39.24% | 39.24%
3 | 82 | 23 | 1960 | 16 | -2.4 | 53.25 | 140.56 | 193.81 | 140.56 | 70.28 | 82 | 1960 | 960 | 80.8767 | 0.59461 | 7.6086 | 934.284 | 15.6982 | -55.4731 | 23.3094 | 23.3094 | 63.7704 | 243.7704 | 55.4718 | 76.2774 | 76.2774 | 119.9755 | 196.2529 | -0.049092 | 0% | 88.7456 | 0 | 0 | 97.6982 | 97.6982 | 0% | 12.1% | 12.1% | 80% | 9.677% | 8.5876 | 11.1164 | 6 | 51.5256 | 18.9907 | 52.74% | 52.74%
3 | 82 | 23 | 1961 | 17 | -0.6 | 35.08 | 91.58 | 126.66 | 91.58 | 45.79 | 82 | 1961 | 1020 | 80.8767 | 0.59461 | 7.6086 | 994.284 | 16.6982 | -70.4731 | 13.6773 | 13.6773 | 75.9157 | 255.9157 | 70.4644 | 49.6102 | 49.6102 | 78.1684 | 127.7786 | -0.47118 | 0% | 57.7815 | 0 | 0 | 138.1281 | 138.1281 | 0% | 12.11% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1962 | 18 | 1.6 | 2.03 | 43.06 | 45.09 | 43.06 | 21.53 | 82 | 1962 | 1080 | 80.8767 | 0.59461 | 7.6086 | 1054.284 | 17.6982 | -85.4731 | 3.5323 | 3.5323 | 87.1053 | 267.1053 | 85.4571 | 0 | 0 | 36.754 | 36.754 | -3.4819 | 0% | 16.6202 | 0 | 0 | 135.5943 | 135.5943 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1963 | 19 | -0.4 | 0.83 | 15.19 | 16.02 | 15.19 | 7.6 | 82 | 1963 | 1140 | 80.8767 | 0.59461 | 7.6086 | 1114.284 | 18.6982 | -100.4731 | -6.7141 | 0 | 90.8683 | 270.8683 | 90.614 | 0 | 0 | 12.9655 | 12.9655 | -11.7251 | 0% | 5.863 | 0 | 0 | 129.0871 | 129.0871 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1964 | 20 | -1.4 | 0 | 0 | 0 | 0 | 0 | 82 | 1964 | 1200 | 80.8767 | 0.59461 | 7.6086 | 1174.284 | 19.6982 | -115.4731 | -16.6759 | 0 | 90.8683 | 270.8683 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.6793 | 123.6793 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1965 | 21 | -0.9 | 0 | 0 | 0 | 0 | 0 | 82 | 1965 | 1260 | 80.8767 | 0.59461 | 7.6086 | 1234.284 | 20.6982 | -130.4731 | -25.9081 | 0 | 90.8683 | 270.8683 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.294 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1966 | 22 | -1.8 | 0 | 0 | 0 | 0 | 0 | 82 | 1966 | 1320 | 80.8767 | 0.59461 | 7.6086 | 1294.284 | 21.6982 | -145.4731 | -33.8216 | 0 | 90.8683 | 270.8683 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.3377 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1967 | 23 | -3.8 | 0 | 0 | 0 | 0 | 0 | 82 | 1967 | 1380 | 80.8767 | 0.59461 | 7.6086 | 1354.284 | 22.6982 | -160.4731 | -39.6311 | 0 | 90.8683 | 270.8683 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.1845 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
3 | 82 | 23 | 1968 | 24 | -4.5 | 0 | 0 | 0 | 0 | 0 | 82 | 1968 | 1440 | 80.8767 | 0.59461 | 7.6086 | 1414.284 | 23.6982 | -175.4731 | -42.4613 | 0 | 90.8683 | 270.8683 | 90.614 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.0502 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1969 | 1 | -4.9 | 0 | 0 | 0 | 0 | 0 | 83 | 1969 | 60 | 81.863 | 0.996 | 7.9816 | 34.284 | 0.70443 | 169.4336 | -41.3339 | 0 | 91.4545 | 88.5455 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.5017 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1970 | 2 | -5.3 | 0 | 0 | 0 | 0 | 0 | 83 | 1970 | 120 | 81.863 | 0.996 | 7.9816 | 94.284 | 1.7044 | 154.4336 | -37.2297 | 0 | 91.4545 | 88.5455 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.782 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.1725 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1971 | 3 | -6 | 0 | 0 | 0 | 0 | 0 | 83 | 1971 | 180 | 81.863 | 0.996 | 7.9816 | 154.284 | 2.7044 | 139.4336 | -30.4965 | 0 | 91.4545 | 88.5455 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.5196 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1972 | 4 | -6.6 | 0 | 0 | 0 | 0 | 0 | 83 | 1972 | 240 | 81.863 | 0.996 | 7.9816 | 214.284 | 3.7044 | 124.4336 | -21.9941 | 0 | 91.4545 | 88.5455 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.434 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.665 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1973 | 5 | -7.1 | 0 | 0 | 0 | 0 | 0 | 83 | 1973 | 300 | 81.863 | 0.996 | 7.9816 | 274.284 | 4.7044 | 109.4336 | -12.4244 | 0 | 91.4545 | 88.5455 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1297 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1974 | 6 | -7.4 | 0 | 0 | 0 | 0 | 0 | 83 | 1974 | 360 | 81.863 | 0.996 | 7.9816 | 334.284 | 5.7044 | 94.4336 | -2.3076 | 0 | 91.4545 | 88.5455 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5921 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 12.9739 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1975 | 7 | -7.9 | 0 | 0 | 0 | 0 | 0 | 83 | 1975 | 420 | 81.863 | 0.996 | 7.9816 | 394.284 | 6.7044 | 79.4336 | 7.9453 | 7.9453 | 82.9416 | 97.0584 | 79.4089 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.5474 | 137.5474 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1693 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1976 | 8 | -7 | 3.14 | 26.86 | 30 | 26.86 | 13.43 | 83 | 1976 | 480 | 81.863 | 0.996 | 7.9816 | 454.284 | 7.7044 | 64.4336 | 17.9486 | 17.9486 | 71.4578 | 108.5422 | 64.4167 | 4.4 | 4.4 | 22.9264 | 27.3265 | -5.7489 | 0% | 12.357 | 0 | 0 | 145.3779 | 145.3779 | 0% | 12.5% | 12.5% | 80% | 10% | 1.2356 | 12.8189 | 6 | 7.4139 | 2.7325 | 5.1% | 5.1%
3 | 83 | 24 | 1977 | 9 | -5.2 | 17.14 | 73.61 | 90.75 | 73.61 | 36.81 | 83 | 1977 | 540 | 81.863 | 0.996 | 7.9816 | 514.284 | 8.7044 | 49.4336 | 27.2557 | 27.2557 | 58.6936 | 121.3064 | 49.4239 | 24.3444 | 24.3444 | 62.8301 | 87.1745 | -1.1975 | 0% | 39.4203 | 0 | 0 | 130.7422 | 130.7422 | 0% | 12.34% | 12.34% | 80% | 9.872% | 3.8916 | 12.1351 | 6 | 23.3494 | 8.6058 | 17.86% | 17.86%
3 | 83 | 24 | 1978 | 10 | -2 | 71.81 | 104.86 | 176.67 | 104.86 | 52.43 | 83 | 1978 | 600 | 81.863 | 0.996 | 7.9816 | 574.284 | 9.7044 | 34.4336 | 35.2689 | 35.2689 | 43.8257 | 136.1743 | 34.4318 | 102.576 | 102.576 | 89.5036 | 192.0796 | -0.062424 | 0% | 86.8584 | 0 | 0 | 138.6041 | 138.6041 | 0% | 12.09% | 12.09% | 80% | 9.67% | 8.3993 | 10.9754 | 6 | 50.3956 | 18.5742 | 36.36% | 36.36%
3 | 83 | 24 | 1979 | 11 | 0.4 | 74.17 | 149.44 | 223.61 | 149.44 | 74.72 | 83 | 1979 | 660 | 81.863 | 0.996 | 7.9816 | 634.284 | 10.7044 | 19.4336 | 41.1764 | 41.1764 | 26.2296 | 153.7704 | 19.4434 | 106.2306 | 106.2306 | 127.555 | 233.7857 | 0.1176 | 11.76% | 105.7179 | 12.4322 | 8.7025 | 118.9358 | 118.9358 | 7.317% | 11.96% | 11.96% | 80% | 9.57% | 10.1171 | 10.1527 | 6 | 60.7026 | 22.3731 | 51.04% | 51.04%
3 | 83 | 24 | 1980 | 12 | 2.2 | 132.31 | 185.64 | 317.95 | 185.64 | 92.82 | 83 | 1980 | 720 | 81.863 | 0.996 | 7.9816 | 694.284 | 11.7044 | 4.4336 | 44.0544 | 44.0544 | 6.1739 | 173.8261 | 4.5007 | 189.6939 | 189.6939 | 158.4537 | 348.1475 | 0.35575 | 35.57% | 157.4323 | 56.0061 | 39.2043 | 119.344 | 119.344 | 32.85% | 11.79% | 11.79% | 85% | 10.03% | 15.7829 | 9.5621 | 6 | 94.6975 | 34.9025 | 79.35% | 79.35%
3 | 83 | 24 | 1981 | 13 | 3.3 | 127.22 | 214.44 | 341.66 | 214.44 | 107.22 | 83 | 1981 | 780 | 81.863 | 0.996 | 7.9816 | 754.284 | 12.7044 | -10.5664 | 43.2969 | 43.2969 | 14.591 | 194.591 | 10.5921 | 182.3505 | 182.3505 | 183.036 | 365.3865 | 0.38422 | 38.42% | 165.2278 | 63.4835 | 44.4384 | 120.2778 | 120.2778 | 36.95% | 11.75% | 11.75% | 85% | 9.989% | 16.5038 | 9.2124 | 6 | 99.0228 | 36.4967 | 82.33% | 82.33%
3 | 83 | 24 | 1982 | 14 | 3.9 | 32.03 | 223.61 | 255.64 | 223.61 | 111.81 | 83 | 1982 | 840 | 81.863 | 0.996 | 7.9816 | 814.284 | 13.7044 | -25.5664 | 39.0757 | 39.0757 | 33.7673 | 213.7673 | 25.5705 | 45.8364 | 45.8364 | 190.8631 | 236.6995 | 0.16213 | 16.21% | 107.0355 | 17.3537 | 12.1476 | 116.3923 | 116.3923 | 10.44% | 11.85% | 11.85% | 80% | 9.481% | 10.1477 | 9.0252 | 6 | 60.8859 | 22.4406 | 52.31% | 52.31%
3 | 83 | 24 | 1983 | 15 | 4.1 | 21.67 | 251.94 | 273.61 | 251.94 | 125.97 | 83 | 1983 | 900 | 81.863 | 0.996 | 7.9816 | 874.284 | 14.7044 | -40.5664 | 32.1961 | 32.1961 | 50.2092 | 230.2092 | 40.5612 | 30.8978 | 30.8978 | 215.0442 | 245.9421 | 0.18822 | 18.82% | 111.215 | 20.9324 | 14.6527 | 115.1792 | 115.1792 | 12.72% | 11.84% | 11.84% | 80% | 9.469% | 10.5312 | 8.9633 | 6 | 63.1872 | 23.2888 | 54.86% | 54.86%
3 | 83 | 24 | 1984 | 16 | 4.5 | 14.36 | 174.72 | 189.08 | 174.72 | 87.36 | 83 | 1984 | 960 | 81.863 | 0.996 | 7.9816 | 934.284 | 15.7044 | -55.5664 | 23.5684 | 23.5684 | 64.1198 | 244.1198 | 55.5538 | 20.3141 | 20.3141 | 149.1328 | 169.447 | -0.084081 | 0% | 76.6239 | 0 | 0 | 110.078 | 110.078 | 0% | 11.89% | 11.89% | 80% | 9.512% | 7.2882 | 8.8405 | 6 | 43.7291 | 16.1172 | 39.73% | 39.73%
3 | 83 | 24 | 1985 | 17 | 5 | 4.92 | 79.17 | 84.09 | 79.17 | 39.59 | 83 | 1985 | 1020 | 81.863 | 0.996 | 7.9816 | 994.284 | 16.7044 | -70.5664 | 13.9151 | 13.9151 | 76.2622 | 256.2622 | 70.5464 | 6.8136 | 6.8136 | 67.5758 | 74.3895 | -1.2027 | 0% | 33.6389 | 0 | 0 | 145.9114 | 145.9114 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1986 | 18 | 4.5 | 3.42 | 55.36 | 58.78 | 55.36 | 27.68 | 83 | 1986 | 1080 | 81.863 | 0.996 | 7.9816 | 1054.284 | 17.7044 | -85.5664 | 3.7612 | 3.7612 | 87.4486 | 267.4486 | 85.5382 | 0 | 0 | 47.2527 | 47.2527 | -2.3806 | 0% | 21.3677 | 0 | 0 | 141.6369 | 141.6369 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1987 | 19 | 3.5 | 2.14 | 26.19 | 28.33 | 26.19 | 13.1 | 83 | 1987 | 1140 | 81.863 | 0.996 | 7.9816 | 1114.284 | 18.7044 | -100.5664 | -6.4822 | 0 | 91.4545 | 271.4545 | 91.0284 | 0 | 0 | 22.3546 | 22.3546 | -6.0357 | 0% | 10.1087 | 0 | 0 | 136.3391 | 136.3391 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1988 | 20 | 2.3 | 0 | 0 | 0 | 0 | 0 | 83 | 1988 | 1200 | 81.863 | 0.996 | 7.9816 | 1174.284 | 19.7044 | -115.5664 | -16.4292 | 0 | 91.4545 | 271.4545 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.2134 | 129.2134 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1989 | 21 | 1.3 | 0 | 0 | 0 | 0 | 0 | 83 | 1989 | 1260 | 81.863 | 0.996 | 7.9816 | 1234.284 | 20.7044 | -130.5664 | -25.6345 | 0 | 91.4545 | 271.4545 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2063 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1990 | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 83 | 1990 | 1320 | 81.863 | 0.996 | 7.9816 | 1294.284 | 21.7044 | -145.5664 | -33.5099 | 0 | 91.4545 | 271.4545 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4979 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1991 | 23 | -0.3 | 0 | 0 | 0 | 0 | 0 | 83 | 1991 | 1380 | 81.863 | 0.996 | 7.9816 | 1354.284 | 22.7044 | -160.5664 | -39.2752 | 0 | 91.4545 | 271.4545 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1498 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
3 | 83 | 24 | 1992 | 24 | -0.9 | 0 | 0 | 0 | 0 | 0 | 83 | 1992 | 1440 | 81.863 | 0.996 | 7.9816 | 1414.284 | 23.7044 | -175.5664 | -42.0677 | 0 | 91.4545 | 271.4545 | 91.0284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.735 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 1993 | 1 | -1.8 | 0 | 0 | 0 | 0 | 0 | 84 | 1993 | 60 | 82.8493 | 1.3973 | 8.3511 | 34.284 | 0.71059 | 169.3412 | -40.9228 | 0 | 92.0406 | 87.9594 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5694 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 1994 | 2 | -1.8 | 0 | 0 | 0 | 0 | 0 | 84 | 1994 | 120 | 82.8493 | 1.3973 | 8.3511 | 94.284 | 1.7106 | 154.3412 | -36.8228 | 0 | 92.0406 | 87.9594 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2094 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 1995 | 3 | -1.8 | 0 | 0 | 0 | 0 | 0 | 84 | 1995 | 180 | 82.8493 | 1.3973 | 8.3511 | 154.284 | 2.7106 | 139.3412 | -30.1051 | 0 | 92.0406 | 87.9594 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8494 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 1996 | 4 | -2 | 0 | 0 | 0 | 0 | 0 | 84 | 1996 | 240 | 82.8493 | 1.3973 | 8.3511 | 214.284 | 3.7106 | 124.3412 | -21.6195 | 0 | 92.0406 | 87.9594 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.1542 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 1997 | 5 | -2.8 | 0 | 0 | 0 | 0 | 0 | 84 | 1997 | 300 | 82.8493 | 1.3973 | 8.3511 | 274.284 | 4.7106 | 109.3412 | -12.0622 | 0 | 92.0406 | 87.9594 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6375 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 1998 | 6 | -2.8 | 0 | 0 | 0 | 0 | 0 | 84 | 1998 | 360 | 82.8493 | 1.3973 | 8.3511 | 334.284 | 5.7106 | 94.3412 | -1.9515 | 0 | 92.0406 | 87.9594 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7469 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 1999 | 7 | -3.6 | 0 | 0 | 0 | 0 | 0 | 84 | 1999 | 420 | 82.8493 | 1.3973 | 8.3511 | 394.284 | 6.7106 | 79.3412 | 8.3024 | 8.3024 | 83.1488 | 96.8512 | 79.3055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 150.5578 | 150.5578 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 2000 | 8 | -3.6 | 8.81 | 35.19 | 44 | 35.19 | 17.6 | 84 | 2000 | 480 | 82.8493 | 1.3973 | 8.3511 | 454.284 | 7.7106 | 64.3412 | 18.3136 | 18.3136 | 71.6583 | 108.3417 | 64.3146 | 12.1524 | 12.1524 | 30.0365 | 42.189 | -3.2357 | 0% | 19.0779 | 0 | 0 | 159.6824 | 159.6824 | 0% | 12.34% | 12.34% | 80% | 9.869% | 1.8827 | 11.5463 | 6 | 11.2962 | 4.1634 | 7.074% | 7.074%
3 | 84 | 25 | 2001 | 9 | -0.6 | 11.67 | 98.69 | 110.36 | 98.69 | 49.35 | 84 | 2001 | 540 | 82.8493 | 1.3973 | 8.3511 | 514.284 | 8.7106 | 49.3412 | 27.635 | 27.635 | 58.8741 | 121.1259 | 49.3224 | 16.3991 | 16.3991 | 84.2372 | 100.6363 | -0.81511 | 0% | 45.5077 | 0 | 0 | 147.1413 | 147.1413 | 0% | 12.14% | 12.14% | 80% | 9.716% | 4.4213 | 10.4906 | 6 | 26.5278 | 9.7773 | 18.03% | 18.03%
3 | 84 | 25 | 2002 | 10 | 1.4 | 39.17 | 153.14 | 192.31 | 153.14 | 76.57 | 84 | 2002 | 600 | 82.8493 | 1.3973 | 8.3511 | 574.284 | 9.7106 | 34.3412 | 35.6659 | 35.6659 | 43.9599 | 136.0401 | 34.3297 | 55.4779 | 55.4779 | 130.7132 | 186.1911 | -0.044666 | 0% | 84.1956 | 0 | 0 | 153.0994 | 153.0994 | 0% | 11.98% | 11.98% | 80% | 9.584% | 8.0693 | 9.8218 | 6 | 48.4155 | 17.8444 | 31.62% | 31.62%
3 | 84 | 25 | 2003 | 11 | 3.1 | 196.94 | 214.64 | 411.58 | 214.64 | 107.32 | 84 | 2003 | 660 | 82.8493 | 1.3973 | 8.3511 | 634.284 | 10.7106 | 19.3412 | 41.5868 | 41.5868 | 26.2743 | 153.7257 | 19.3374 | 279.9674 | 279.9674 | 183.2067 | 463.1741 | 0.4718 | 47.18% | 209.4473 | 98.8165 | 69.1716 | 139.6191 | 139.6191 | 49.54% | 11.67% | 11.67% | 85% | 9.915% | 20.7674 | 9.2753 | 6 | 124.6042 | 45.9252 | 89.25% | 89.25%
3 | 84 | 25 | 2004 | 12 | 4.1 | 194.53 | 245.28 | 439.81 | 245.28 | 122.64 | 84 | 2004 | 720 | 82.8493 | 1.3973 | 8.3511 | 694.284 | 11.7106 | 4.3412 | 44.4614 | 44.4614 | 6.0863 | 173.9137 | 4.3562 | 276.9277 | 276.9277 | 209.3596 | 486.2873 | 0.49256 | 49.26% | 219.8991 | 108.3144 | 75.8201 | 133.7895 | 133.7895 | 56.67% | 11.63% | 11.63% | 85% | 9.882% | 21.7313 | 8.9633 | 6 | 130.3877 | 48.0568 | 97.46% | 97.46%
3 | 84 | 25 | 2005 | 13 | 4.3 | 267.22 | 251.11 | 518.33 | 251.11 | 125.56 | 84 | 2005 | 780 | 82.8493 | 1.3973 | 8.3511 | 754.284 | 12.7106 | -10.6588 | 43.6761 | 43.6761 | 14.8125 | 194.8125 | 10.6615 | 380.2702 | 380.2702 | 214.3358 | 594.606 | 0.55011 | 55.01% | 268.8808 | 147.914 | 103.5398 | 136.055 | 136.055 | 76.1% | 11.53% | 11.53% | 90% | 10.38% | 27.9002 | 8.9018 | 6 | 167.4013 | 61.6988 | 123% | 123%
3 | 84 | 25 | 2006 | 14 | 5.9 | 183.42 | 229.81 | 413.23 | 229.81 | 114.91 | 84 | 2006 | 840 | 82.8493 | 1.3973 | 8.3511 | 814.284 | 13.7106 | -25.6588 | 39.4112 | 39.4112 | 34.0755 | 214.0755 | 25.6515 | 260.4311 | 260.4311 | 196.1551 | 456.5862 | 0.48177 | 48.18% | 206.4683 | 99.4712 | 69.6298 | 133.3797 | 133.3797 | 52.2% | 11.62% | 11.62% | 85% | 9.876% | 20.3899 | 8.4194 | 6 | 122.3395 | 45.0905 | 91.72% | 91.72%
3 | 84 | 25 | 2007 | 15 | 5.3 | 211.75 | 214.92 | 426.67 | 214.92 | 107.46 | 84 | 2007 | 900 | 82.8493 | 1.3973 | 8.3511 | 874.284 | 14.7106 | -40.6588 | 32.4883 | 32.4883 | 50.5526 | 230.5526 | 40.6442 | 299.1274 | 299.1274 | 183.4457 | 482.5731 | 0.49615 | 49.62% | 218.2196 | 108.2697 | 75.7888 | 130.9987 | 130.9987 | 57.85% | 11.61% | 11.61% | 85% | 9.867% | 21.5325 | 8.5982 | 6 | 129.1949 | 47.6172 | 98.62% | 98.62%
3 | 84 | 25 | 2008 | 16 | 6.1 | 177.5 | 191.47 | 368.97 | 191.47 | 95.74 | 84 | 2008 | 960 | 82.8493 | 1.3973 | 8.3511 | 934.284 | 15.7106 | -55.6588 | 23.8272 | 23.8272 | 64.4696 | 244.4696 | 55.6368 | 248.0021 | 248.0021 | 163.4299 | 411.4319 | 0.44757 | 44.76% | 186.0495 | 83.2705 | 58.2894 | 128.4412 | 128.4412 | 45.38% | 11.65% | 11.65% | 85% | 9.902% | 18.4221 | 8.3603 | 6 | 110.5324 | 40.7388 | 86.06% | 86.06%
3 | 84 | 25 | 2009 | 17 | 5.3 | 89.72 | 150.56 | 240.28 | 150.56 | 75.28 | 84 | 2009 | 1020 | 82.8493 | 1.3973 | 8.3511 | 994.284 | 16.7106 | -70.6588 | 14.153 | 14.153 | 76.6086 | 256.6086 | 70.6285 | 121.7094 | 121.7094 | 128.511 | 250.2204 | 0.21028 | 21.03% | 113.1497 | 23.7935 | 16.6554 | 118.6568 | 118.6568 | 14.04% | 11.8% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 2010 | 18 | 5.3 | 101.39 | 79.25 | 180.64 | 79.25 | 39.63 | 84 | 2010 | 1080 | 82.8493 | 1.3973 | 8.3511 | 1054.284 | 17.7106 | -85.6588 | 3.9906 | 3.9906 | 87.7914 | 267.7914 | 85.6187 | 0 | 0 | 67.6441 | 67.6441 | -1.3922 | 0% | 30.5887 | 0 | 0 | 112.9365 | 112.9365 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 2011 | 19 | 4.5 | 9.64 | 32.42 | 42.06 | 32.42 | 16.21 | 84 | 2011 | 1140 | 82.8493 | 1.3973 | 8.3511 | 1114.284 | 18.7106 | -100.6588 | -6.2495 | 0 | 92.0406 | 272.0406 | 91.4428 | 0 | 0 | 27.6722 | 27.6722 | -4.634 | 0% | 12.5134 | 0 | 0 | 141.0039 | 141.0039 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 2012 | 20 | 3.2 | 0 | 0 | 0 | 0 | 0 | 84 | 2012 | 1200 | 82.8493 | 1.3973 | 8.3511 | 1174.284 | 19.7106 | -115.6588 | -16.1814 | 0 | 92.0406 | 272.0406 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.9767 | 129.9767 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 2013 | 21 | 2.1 | 0 | 0 | 0 | 0 | 0 | 84 | 2013 | 1260 | 82.8493 | 1.3973 | 8.3511 | 1234.284 | 20.7106 | -130.6588 | -25.3597 | 0 | 92.0406 | 272.0406 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2754 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 2014 | 22 | 1.9 | 0 | 0 | 0 | 0 | 0 | 84 | 2014 | 1320 | 82.8493 | 1.3973 | 8.3511 | 1294.284 | 21.7106 | -145.6588 | -33.197 | 0 | 92.0406 | 272.0406 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0106 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 2015 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 84 | 2015 | 1380 | 82.8493 | 1.3973 | 8.3511 | 1354.284 | 22.7106 | -160.6588 | -38.9186 | 0 | 92.0406 | 272.0406 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4982 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
3 | 84 | 25 | 2016 | 24 | 1.4 | 0 | 0 | 0 | 0 | 0 | 84 | 2016 | 1440 | 82.8493 | 1.3973 | 8.3511 | 1414.284 | 23.7106 | -175.6588 | -41.6739 | 0 | 92.0406 | 272.0406 | 91.4428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0526 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2017 | 1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 85 | 2017 | 60 | 83.8356 | 1.7983 | 8.7166 | 34.284 | 0.71668 | 169.2498 | -40.5121 | 0 | 92.6265 | 87.3735 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5665 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2018 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 85 | 2018 | 120 | 83.8356 | 1.7983 | 8.7166 | 94.284 | 1.7167 | 154.2498 | -36.4164 | 0 | 92.6265 | 87.3735 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0412 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2019 | 3 | -0.3 | 0 | 0 | 0 | 0 | 0 | 85 | 2019 | 180 | 83.8356 | 1.7983 | 8.7166 | 154.284 | 2.7167 | 139.2498 | -29.7143 | 0 | 92.6265 | 87.3735 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8207 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2020 | 4 | -1.1 | 0 | 0 | 0 | 0 | 0 | 85 | 2020 | 240 | 83.8356 | 1.7983 | 8.7166 | 214.284 | 3.7167 | 124.2498 | -21.2455 | 0 | 92.6265 | 87.3735 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0398 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2021 | 5 | -1.2 | 0 | 0 | 0 | 0 | 0 | 85 | 2021 | 300 | 83.8356 | 1.7983 | 8.7166 | 274.284 | 4.7167 | 109.2498 | -11.7007 | 0 | 92.6265 | 87.3735 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.3123 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2022 | 6 | -1.9 | 0 | 0 | 0 | 0 | 0 | 85 | 2022 | 360 | 83.8356 | 1.7983 | 8.7166 | 334.284 | 5.7167 | 94.2498 | -1.5963 | 0 | 92.6265 | 87.3735 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.9294 | 3.9294 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2023 | 7 | -2.1 | 0.08 | 0.92 | 1 | 0.92 | 0.46 | 85 | 2023 | 420 | 83.8356 | 1.7983 | 8.7166 | 394.284 | 6.7167 | 79.2498 | 8.6584 | 8.6584 | 83.357 | 96.643 | 79.2036 | 0 | 0 | 0.78527 | 0.78527 | -211.4442 | 0% | 0.3551 | 0 | 0 | 170.4483 | 170.4483 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2024 | 8 | -1.8 | 19.44 | 36.11 | 55.55 | 36.11 | 18.06 | 85 | 2024 | 480 | 83.8356 | 1.7983 | 8.7166 | 454.284 | 7.7167 | 64.2498 | 18.6776 | 18.6776 | 71.8604 | 108.1396 | 64.2148 | 26.4061 | 26.4061 | 30.8218 | 57.2279 | -2.0953 | 0% | 25.8785 | 0 | 0 | 183.8743 | 183.8743 | 0% | 12.24% | 12.24% | 80% | 9.794% | 2.5346 | 10.9053 | 6 | 15.2073 | 5.6049 | 8.27% | 8.27%
3 | 85 | 26 | 2025 | 9 | -1.9 | 88.81 | 92.03 | 180.84 | 92.03 | 46.02 | 85 | 2025 | 540 | 83.8356 | 1.7983 | 8.7166 | 514.284 | 8.7167 | 49.2498 | 28.0133 | 28.0133 | 59.0567 | 120.9433 | 49.2243 | 123.493 | 123.493 | 78.5525 | 202.0455 | -0.018452 | 0% | 91.365 | 0 | 0 | 170.313 | 170.313 | 0% | 12.07% | 12.07% | 80% | 9.658% | 8.8238 | 10.9403 | 6 | 52.943 | 19.5131 | 31.09% | 31.09%
3 | 85 | 26 | 2026 | 10 | -1.2 | 221.03 | 140.64 | 361.67 | 140.64 | 70.32 | 85 | 2026 | 600 | 83.8356 | 1.7983 | 8.7166 | 574.284 | 9.7167 | 34.2498 | 36.0621 | 36.0621 | 44.0964 | 135.9036 | 34.2327 | 310.4311 | 310.4311 | 120.0437 | 430.4749 | 0.42203 | 42.2% | 194.6607 | 82.152 | 57.5064 | 156.7991 | 156.7991 | 36.68% | 11.78% | 11.78% | 85% | 10.02% | 19.4961 | 10.6967 | 6 | 116.9767 | 43.1139 | 74.6% | 74.6%
3 | 85 | 26 | 2027 | 11 | -0.6 | 368.33 | 152.58 | 520.91 | 152.58 | 76.29 | 85 | 2027 | 660 | 83.8356 | 1.7983 | 8.7166 | 634.284 | 10.7167 | 19.2498 | 41.9967 | 41.9967 | 26.3209 | 153.6791 | 19.2404 | 519.7474 | 519.7474 | 130.2352 | 649.9826 | 0.55331 | 55.33% | 293.9221 | 162.6313 | 113.8419 | 155.978 | 155.978 | 72.99% | 11.52% | 11.52% | 90% | 10.37% | 30.4791 | 10.4906 | 6 | 182.8743 | 67.4017 | 117.2% | 117.2%
3 | 85 | 26 | 2028 | 12 | -1.6 | 355.56 | 197.86 | 553.42 | 197.86 | 98.93 | 85 | 2028 | 720 | 83.8356 | 1.7983 | 8.7166 | 694.284 | 11.7167 | 4.2498 | 44.868 | 44.868 | 5.9989 | 174.0011 | 4.2478 | 502.6159 | 502.6159 | 168.8841 | 671.5 | 0.55765 | 55.76% | 303.6523 | 169.3312 | 118.5319 | 142.408 | 142.408 | 83.23% | 11.5% | 11.5% | 90% | 10.35% | 31.4407 | 10.8355 | 6 | 188.6444 | 69.5284 | 132.5% | 132.5%
3 | 85 | 26 | 2029 | 13 | 3 | 439.25 | 202.03 | 641.28 | 202.03 | 101.02 | 85 | 2029 | 780 | 83.8356 | 1.7983 | 8.7166 | 754.284 | 12.7167 | -10.7502 | 44.0547 | 44.0547 | 15.0353 | 195.0353 | 10.7449 | 620.6253 | 620.6253 | 172.4434 | 793.0687 | 0.60968 | 60.97% | 358.6256 | 218.6461 | 153.0523 | 150.0607 | 150.0607 | 102% | 11.36% | 11.36% | 90% | 10.22% | 36.661 | 9.3069 | 6 | 219.9659 | 81.0725 | 146.6% | 146.6%
3 | 85 | 26 | 2030 | 14 | 2.5 | 469.44 | 212.14 | 681.58 | 212.14 | 106.07 | 85 | 2030 | 840 | 83.8356 | 1.7983 | 8.7166 | 814.284 | 13.7167 | -25.7502 | 39.746 | 39.746 | 34.3854 | 214.3854 | 25.7374 | 661.3668 | 661.3668 | 181.0728 | 842.4396 | 0.61962 | 61.96% | 380.9512 | 236.0459 | 165.2322 | 149.2575 | 149.2575 | 110.7% | 11.31% | 11.31% | 95% | 10.75% | 40.9355 | 9.4659 | 6 | 245.6128 | 90.5251 | 164.6% | 164.6%
3 | 85 | 26 | 2031 | 15 | 1.8 | 241.58 | 230.83 | 472.41 | 230.83 | 115.42 | 85 | 2031 | 900 | 83.8356 | 1.7983 | 8.7166 | 874.284 | 14.7167 | -40.7502 | 32.7798 | 32.7798 | 50.8972 | 230.8972 | 40.7294 | 338.1326 | 338.1326 | 197.0257 | 535.1583 | 0.51056 | 51.06% | 241.9986 | 123.5556 | 86.4889 | 136.1866 | 136.1866 | 63.51% | 11.62% | 11.62% | 90% | 10.46% | 25.3019 | 9.6914 | 6 | 151.8115 | 55.9529 | 111.5% | 111.5%
3 | 85 | 26 | 2032 | 16 | 2.1 | 293.42 | 206.03 | 499.45 | 206.03 | 103.02 | 85 | 2032 | 960 | 83.8356 | 1.7983 | 8.7166 | 934.284 | 15.7167 | -55.7502 | 24.0856 | 24.0856 | 64.8198 | 244.8198 | 55.7206 | 404.9551 | 404.9551 | 175.8576 | 580.8127 | 0.53489 | 53.49% | 262.6435 | 140.4855 | 98.3399 | 135.8898 | 135.8898 | 72.37% | 11.57% | 11.57% | 90% | 10.41% | 27.3438 | 9.5943 | 6 | 164.0631 | 60.4685 | 120.7% | 120.7%
3 | 85 | 26 | 2033 | 17 | 2.9 | 188.81 | 172.58 | 361.39 | 172.58 | 86.29 | 85 | 2033 | 1020 | 83.8356 | 1.7983 | 8.7166 | 994.284 | 16.7167 | -70.7502 | 14.3909 | 14.3909 | 76.9549 | 256.9549 | 70.7105 | 250.956 | 250.956 | 147.3062 | 398.2622 | 0.41643 | 41.64% | 180.0942 | 74.997 | 52.4979 | 127.3232 | 127.3232 | 41.23% | 11.73% | 0% | 85% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2034 | 18 | 4.2 | 123.81 | 113.97 | 237.78 | 113.97 | 56.99 | 85 | 2034 | 1080 | 83.8356 | 1.7983 | 8.7166 | 1054.284 | 17.7167 | -85.7502 | 4.2204 | 4.2204 | 88.1334 | 268.1334 | 85.6984 | 0 | 0 | 97.2795 | 97.2795 | -0.75035 | 0% | 43.9898 | 0 | 0 | 118.607 | 118.607 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2035 | 19 | 3.5 | 17.78 | 37.58 | 55.36 | 37.58 | 18.79 | 85 | 2035 | 1140 | 83.8356 | 1.7983 | 8.7166 | 1114.284 | 18.7167 | -100.7502 | -6.0161 | 0 | 92.6265 | 272.6265 | 91.8569 | 0 | 0 | 32.0765 | 32.0765 | -3.9627 | 0% | 14.505 | 0 | 0 | 143.7795 | 143.7795 | 0% | 12.05% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2036 | 20 | 2.3 | 0 | 1.11 | 1.11 | 1.11 | 0.56 | 85 | 2036 | 1200 | 83.8356 | 1.7983 | 8.7166 | 1174.284 | 19.7167 | -115.7502 | -15.9326 | 0 | 92.6265 | 272.6265 | 91.8569 | 0 | 0 | 0.94744 | 0.94744 | -163.6534 | 0% | 0.42843 | 0 | 0 | 130.0416 | 130.0416 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2037 | 21 | -0.9 | 0 | 0 | 0 | 0 | 0 | 85 | 2037 | 1260 | 83.8356 | 1.7983 | 8.7166 | 1234.284 | 20.7167 | -130.7502 | -25.0836 | 0 | 92.6265 | 272.6265 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8656 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2038 | 22 | -1.9 | 0 | 0 | 0 | 0 | 0 | 85 | 2038 | 1320 | 83.8356 | 1.7983 | 8.7166 | 1294.284 | 21.7167 | -145.7502 | -32.883 | 0 | 92.6265 | 272.6265 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.2195 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2039 | 23 | -3.5 | 0 | 0 | 0 | 0 | 0 | 85 | 2039 | 1380 | 83.8356 | 1.7983 | 8.7166 | 1354.284 | 22.7167 | -160.7502 | -38.5613 | 0 | 92.6265 | 272.6265 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.0658 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
3 | 85 | 26 | 2040 | 24 | -4.2 | 0 | 0 | 0 | 0 | 0 | 85 | 2040 | 1440 | 83.8356 | 1.7983 | 8.7166 | 1414.284 | 23.7167 | -175.7502 | -41.28 | 0 | 92.6265 | 272.6265 | 91.8569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.5405 | 0 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2041 | 1 | -4 | 0 | 0 | 0 | 0 | 0 | 86 | 2041 | 60 | 84.8219 | 2.1991 | 9.0777 | 34.284 | 0.7227 | 169.1596 | -40.1019 | 0 | 93.212 | 86.788 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.0332 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2042 | 2 | -4.5 | 0 | 0 | 0 | 0 | 0 | 86 | 2042 | 120 | 84.8219 | 2.1991 | 9.0777 | 94.284 | 1.7227 | 154.1596 | -36.0107 | 0 | 93.212 | 86.788 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.8848 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2043 | 3 | -5.1 | 0 | 0 | 0 | 0 | 0 | 86 | 2043 | 180 | 84.8219 | 2.1991 | 9.0777 | 154.284 | 2.7227 | 139.1596 | -29.3243 | 0 | 93.212 | 86.788 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.8887 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2044 | 4 | -4.8 | 0 | 0 | 0 | 0 | 0 | 86 | 2044 | 240 | 84.8219 | 2.1991 | 9.0777 | 214.284 | 3.7227 | 124.1596 | -20.8722 | 0 | 93.212 | 86.788 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4315 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2045 | 5 | -5.1 | 0 | 0 | 0 | 0 | 0 | 86 | 2045 | 300 | 84.8219 | 2.1991 | 9.0777 | 274.284 | 4.7227 | 109.1596 | -11.3402 | 0 | 93.212 | 86.788 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.8411 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2046 | 6 | -6 | 0 | 0 | 0 | 0 | 0 | 86 | 2046 | 360 | 84.8219 | 2.1991 | 9.0777 | 334.284 | 5.7227 | 94.1596 | -1.242 | 0 | 93.212 | 86.788 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.4808 | 8.4808 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2047 | 7 | -6 | 0.08 | 1.58 | 1.66 | 1.58 | 0.79 | 86 | 2047 | 420 | 84.8219 | 2.1991 | 9.0777 | 394.284 | 6.7227 | 79.1596 | 9.0134 | 9.0134 | 83.5661 | 96.4339 | 79.1035 | 0 | 0 | 1.3486 | 1.3486 | -130.0805 | 0% | 0.60984 | 0 | 0 | 182.4388 | 182.4388 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2048 | 8 | -4.9 | 29.92 | 29.25 | 59.17 | 29.25 | 14.63 | 86 | 2048 | 480 | 84.8219 | 2.1991 | 9.0777 | 454.284 | 7.7227 | 64.1596 | 19.0404 | 19.0404 | 72.0639 | 107.9361 | 64.1175 | 40.0352 | 40.0352 | 24.9664 | 65.0016 | -1.8685 | 0% | 29.3937 | 0 | 0 | 200.0121 | 200.0121 | 0% | 12.36% | 12.36% | 80% | 9.887% | 2.9061 | 12.0233 | 6 | 17.4367 | 6.4266 | 8.718% | 8.718%
3 | 86 | 27 | 2049 | 9 | -2.2 | 145.83 | 65 | 210.83 | 65 | 32.5 | 86 | 2049 | 540 | 84.8219 | 2.1991 | 9.0777 | 514.284 | 8.7227 | 49.1596 | 28.3904 | 28.3904 | 59.2414 | 120.7586 | 49.1297 | 200.6904 | 200.6904 | 55.481 | 256.1713 | 0.1524 | 15.24% | 115.8407 | 17.6539 | 12.3577 | 171.1489 | 171.1489 | 7.22% | 12.02% | 12.02% | 80% | 9.613% | 11.1355 | 11.0458 | 6 | 66.8133 | 24.6253 | 39.04% | 39.04%
3 | 86 | 27 | 2050 | 10 | 1.2 | 318.25 | 86.58 | 404.83 | 86.58 | 43.29 | 86 | 2050 | 600 | 84.8219 | 2.1991 | 9.0777 | 574.284 | 9.7227 | 34.1596 | 36.4572 | 36.4572 | 44.2354 | 135.7646 | 34.1409 | 443.273 | 443.273 | 73.9007 | 517.1736 | 0.49752 | 49.75% | 233.8659 | 116.3525 | 81.4468 | 180.6887 | 180.6887 | 45.08% | 11.64% | 11.64% | 90% | 10.48% | 24.5091 | 9.8874 | 6 | 147.0549 | 54.1998 | 81.39% | 81.39%
3 | 86 | 27 | 2051 | 11 | 1.3 | 412.03 | 130.19 | 542.22 | 130.19 | 65.1 | 86 | 2051 | 660 | 84.8219 | 2.1991 | 9.0777 | 634.284 | 10.7227 | 19.1596 | 42.4059 | 42.4059 | 26.3693 | 153.6307 | 19.1525 | 577.1593 | 577.1593 | 111.1241 | 688.2834 | 0.57407 | 57.41% | 311.2418 | 178.6736 | 125.0715 | 173.8028 | 173.8028 | 71.96% | 11.47% | 11.47% | 90% | 10.32% | 32.1208 | 9.8546 | 6 | 192.7248 | 71.0323 | 110.9% | 110.9%
3 | 86 | 27 | 2052 | 12 | 5 | 443.53 | 189.17 | 632.7 | 189.17 | 94.59 | 86 | 2052 | 720 | 84.8219 | 2.1991 | 9.0777 | 694.284 | 11.7227 | 4.1596 | 45.2741 | 45.2741 | 5.9118 | 174.0882 | 4.1783 | 622.6076 | 622.6076 | 161.4667 | 784.0743 | 0.61361 | 61.36% | 354.5584 | 217.5605 | 152.2924 | 164.6718 | 164.6718 | 92.48% | 11.37% | 11.37% | 90% | 10.23% | 36.2664 | 8.6885 | 6 | 217.5987 | 80.2 | 132.1% | 132.1%
3 | 86 | 27 | 2053 | 13 | 5.5 | 458.61 | 181.31 | 639.92 | 181.31 | 90.66 | 86 | 2053 | 780 | 84.8219 | 2.1991 | 9.0777 | 754.284 | 12.7227 | -10.8404 | 44.4328 | 44.4328 | 15.2594 | 195.2594 | 10.842 | 643.396 | 643.396 | 154.7578 | 798.1538 | 0.61847 | 61.85% | 360.9251 | 223.2217 | 156.2552 | 159.9394 | 159.9394 | 97.7% | 11.35% | 11.35% | 90% | 10.22% | 36.8798 | 8.5383 | 6 | 221.2787 | 81.5564 | 138.4% | 138.4%
3 | 86 | 27 | 2054 | 14 | 5.2 | 397.31 | 224.25 | 621.56 | 224.25 | 112.13 | 86 | 2054 | 840 | 84.8219 | 2.1991 | 9.0777 | 814.284 | 13.7227 | -25.8404 | 40.0802 | 40.0802 | 34.6968 | 214.6968 | 25.828 | 555.4335 | 555.4335 | 191.4093 | 746.8429 | 0.60476 | 60.48% | 337.7224 | 204.2415 | 142.969 | 155.3471 | 155.3471 | 92.03% | 11.4% | 11.4% | 90% | 10.26% | 34.6359 | 8.6282 | 6 | 207.8156 | 76.5943 | 133.8% | 133.8%
3 | 86 | 27 | 2055 | 15 | 5 | 309.81 | 267.5 | 577.31 | 267.5 | 133.75 | 86 | 2055 | 900 | 84.8219 | 2.1991 | 9.0777 | 874.284 | 14.7227 | -40.8404 | 33.0708 | 33.0708 | 51.2426 | 231.2426 | 40.8168 | 429.6796 | 429.6796 | 228.3255 | 658.0051 | 0.57713 | 57.71% | 297.5499 | 171.7257 | 120.208 | 148.4135 | 148.4135 | 81% | 11.47% | 11.47% | 90% | 10.32% | 30.7138 | 8.6885 | 6 | 184.2827 | 67.9208 | 124.2% | 124.2%
3 | 86 | 27 | 2056 | 16 | 4.7 | 157.14 | 203.14 | 360.28 | 203.14 | 101.57 | 86 | 2056 | 960 | 84.8219 | 2.1991 | 9.0777 | 934.284 | 15.7227 | -55.8404 | 24.3436 | 24.3436 | 65.1702 | 245.1702 | 55.8053 | 214.2454 | 214.2454 | 173.3908 | 387.6362 | 0.41704 | 41.7% | 175.2891 | 73.1019 | 51.1713 | 134.2435 | 134.2435 | 38.12% | 11.7% | 11.7% | 85% | 9.944% | 17.431 | 8.7795 | 6 | 104.5861 | 38.5471 | 77.91% | 77.91%
3 | 86 | 27 | 2057 | 17 | 4.1 | 54.53 | 143.69 | 198.22 | 143.69 | 71.85 | 86 | 2057 | 1020 | 84.8219 | 2.1991 | 9.0777 | 994.284 | 16.7227 | -70.8404 | 14.6288 | 14.6288 | 77.3007 | 257.3007 | 70.7925 | 71.0333 | 71.0333 | 122.6471 | 193.6803 | 0.022056 | 2.206% | 87.5823 | 1.9317 | 1.3522 | 120.8885 | 120.8885 | 1.119% | 11.88% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2058 | 18 | 4.1 | 40.19 | 93.69 | 133.88 | 93.69 | 46.85 | 86 | 2058 | 1080 | 84.8219 | 2.1991 | 9.0777 | 1054.284 | 17.7227 | -85.8404 | 4.4505 | 4.4505 | 88.4746 | 268.4746 | 85.7771 | 0 | 0 | 79.9694 | 79.9694 | -1.0898 | 0% | 36.1622 | 0 | 0 | 154.0818 | 154.0818 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2059 | 19 | 3.4 | 2.58 | 34.25 | 36.83 | 34.25 | 17.13 | 86 | 2059 | 1140 | 84.8219 | 2.1991 | 9.0777 | 1114.284 | 18.7227 | -100.8404 | -5.7819 | 0 | 93.212 | 273.212 | 92.2706 | 0 | 0 | 29.2342 | 29.2342 | -4.4344 | 0% | 13.2197 | 0 | 0 | 142.6356 | 142.6356 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2060 | 20 | 2.6 | 0 | 1.25 | 1.25 | 1.25 | 0.63 | 86 | 2060 | 1200 | 84.8219 | 2.1991 | 9.0777 | 1174.284 | 19.7227 | -115.8404 | -15.6828 | 0 | 93.212 | 273.212 | 92.2706 | 0 | 0 | 1.0669 | 1.0669 | -144.5492 | 0% | 0.48247 | 0 | 0 | 131.1375 | 131.1375 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2061 | 21 | 0.6 | 0 | 0 | 0 | 0 | 0 | 86 | 2061 | 1260 | 84.8219 | 2.1991 | 9.0777 | 1234.284 | 20.7227 | -130.8404 | -24.8065 | 0 | 93.212 | 273.212 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.9097 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2062 | 22 | -0.1 | 0 | 0 | 0 | 0 | 0 | 86 | 2062 | 1320 | 84.8219 | 2.1991 | 9.0777 | 1294.284 | 21.7227 | -145.8404 | -32.568 | 0 | 93.212 | 273.212 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.821 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2063 | 23 | -0.1 | 0 | 0 | 0 | 0 | 0 | 86 | 2063 | 1380 | 84.8219 | 2.1991 | 9.0777 | 1354.284 | 22.7227 | -160.8404 | -38.2034 | 0 | 93.212 | 273.212 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9106 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
3 | 86 | 27 | 2064 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 2064 | 1440 | 84.8219 | 2.1991 | 9.0777 | 1414.284 | 23.7227 | -175.8404 | -40.8862 | 0 | 93.212 | 273.212 | 92.2706 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8477 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2065 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 87 | 2065 | 60 | 85.8082 | 2.5993 | 9.4341 | 34.284 | 0.72863 | 169.0705 | -39.6924 | 0 | 93.797 | 86.203 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5168 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2066 | 2 | 0.3 | 0 | 0 | 0 | 0 | 0 | 87 | 2066 | 120 | 85.8082 | 2.5993 | 9.4341 | 94.284 | 1.7286 | 154.0705 | -35.6059 | 0 | 93.797 | 86.203 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4662 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2067 | 3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 87 | 2067 | 180 | 85.8082 | 2.5993 | 9.4341 | 154.284 | 2.7286 | 139.0705 | -28.9351 | 0 | 93.797 | 86.203 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7204 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2068 | 4 | 0.3 | 0 | 0 | 0 | 0 | 0 | 87 | 2068 | 240 | 85.8082 | 2.5993 | 9.4341 | 214.284 | 3.7286 | 124.0705 | -20.4999 | 0 | 93.797 | 86.203 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7204 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2069 | 5 | 0.4 | 0 | 0 | 0 | 0 | 0 | 87 | 2069 | 300 | 85.8082 | 2.5993 | 9.4341 | 274.284 | 4.7286 | 109.0705 | -10.9806 | 0 | 93.797 | 86.203 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.0095 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2070 | 6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 87 | 2070 | 360 | 85.8082 | 2.5993 | 9.4341 | 334.284 | 5.7286 | 94.0705 | -0.88893 | 0 | 93.797 | 86.203 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.1512 | 10.1512 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2071 | 7 | 0.6 | 0 | 1.47 | 1.47 | 1.47 | 0.74 | 87 | 2071 | 420 | 85.8082 | 2.5993 | 9.4341 | 394.284 | 6.7286 | 79.0705 | 9.367 | 9.367 | 83.7764 | 96.2236 | 79.0051 | 0 | 0 | 1.2547 | 1.2547 | -126.697 | 0% | 0.56739 | 0 | 0 | 180.988 | 180.988 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2072 | 8 | 0.6 | 27.97 | 35.19 | 63.16 | 35.19 | 17.6 | 87 | 2072 | 480 | 85.8082 | 2.5993 | 9.4341 | 454.284 | 7.7286 | 64.0705 | 19.4018 | 19.4018 | 72.2691 | 107.7309 | 64.0229 | 36.8801 | 36.8801 | 30.0365 | 66.9166 | -1.5867 | 0% | 30.2597 | 0 | 0 | 195.7757 | 195.7757 | 0% | 12.13% | 12.13% | 80% | 9.707% | 2.9374 | 10.0859 | 6 | 17.6245 | 6.4958 | 9.002% | 9.002%
3 | 87 | 28 | 2073 | 9 | 1 | 124.53 | 81.58 | 206.11 | 81.58 | 40.79 | 87 | 2073 | 540 | 85.8082 | 2.5993 | 9.4341 | 514.284 | 8.7286 | 49.0705 | 28.7662 | 28.7662 | 59.4283 | 120.5717 | 49.0388 | 169.6368 | 169.6368 | 69.6329 | 239.2696 | 0.1395 | 13.95% | 108.1977 | 15.0933 | 10.5653 | 162.9009 | 162.9009 | 6.486% | 11.94% | 11.94% | 80% | 9.55% | 10.3333 | 9.9533 | 6 | 61.9997 | 22.8511 | 38.06% | 38.06%
3 | 87 | 28 | 2074 | 10 | 1.8 | 286.19 | 125.28 | 411.47 | 125.28 | 62.64 | 87 | 2074 | 600 | 85.8082 | 2.5993 | 9.4341 | 574.284 | 9.7286 | 34.0705 | 36.8512 | 36.8512 | 44.3768 | 135.6232 | 34.0545 | 395.355 | 395.355 | 106.9332 | 502.2881 | 0.49136 | 49.14% | 227.1347 | 111.6051 | 78.1235 | 170.4061 | 170.4061 | 45.85% | 11.65% | 11.65% | 90% | 10.49% | 23.8151 | 9.6914 | 6 | 142.8906 | 52.665 | 83.85% | 83.85%
3 | 87 | 28 | 2075 | 11 | 2.4 | 379.25 | 185.92 | 565.17 | 185.92 | 92.96 | 87 | 2075 | 660 | 85.8082 | 2.5993 | 9.4341 | 634.284 | 10.7286 | 19.0705 | 42.8142 | 42.8142 | 26.4199 | 153.5801 | 19.074 | 527.3925 | 527.3925 | 158.6926 | 686.0851 | 0.57725 | 57.72% | 310.2477 | 179.0902 | 125.3631 | 167.1304 | 167.1304 | 75.01% | 11.46% | 11.46% | 90% | 10.32% | 32.0053 | 9.4979 | 6 | 192.0317 | 70.7768 | 114.9% | 114.9%
3 | 87 | 28 | 2076 | 12 | 5.6 | 377.78 | 185.92 | 563.7 | 185.92 | 92.96 | 87 | 2076 | 720 | 85.8082 | 2.5993 | 9.4341 | 694.284 | 11.7286 | 4.0705 | 45.6796 | 45.6796 | 5.8252 | 174.1748 | 4.1496 | 526.6515 | 526.6515 | 158.6926 | 685.3442 | 0.58828 | 58.83% | 309.9126 | 182.316 | 127.6212 | 155.6811 | 155.6811 | 81.98% | 11.44% | 11.44% | 90% | 10.3% | 31.9164 | 8.5084 | 6 | 191.4986 | 70.5804 | 123% | 123%
3 | 87 | 28 | 2077 | 13 | 6.1 | 507.14 | 163.33 | 670.47 | 163.33 | 81.67 | 87 | 2077 | 780 | 85.8082 | 2.5993 | 9.4341 | 754.284 | 12.7286 | -10.9295 | 44.8102 | 44.8102 | 15.4845 | 195.4845 | 10.9523 | 706.4852 | 706.4852 | 139.4109 | 845.896 | 0.63064 | 63.06% | 382.5142 | 241.2281 | 168.8597 | 156.4911 | 156.4911 | 107.9% | 11.32% | 11.32% | 95% | 10.75% | 41.1244 | 8.3603 | 6 | 246.7461 | 90.9428 | 157.7% | 157.7%
3 | 87 | 28 | 2078 | 14 | 9.2 | 422.58 | 175.75 | 598.33 | 175.75 | 87.88 | 87 | 2078 | 840 | 85.8082 | 2.5993 | 9.4341 | 814.284 | 13.7286 | -25.9295 | 40.4136 | 40.4136 | 35.0095 | 215.0095 | 25.9231 | 586.2413 | 586.2413 | 150.012 | 736.2533 | 0.61479 | 61.48% | 332.9338 | 204.6829 | 143.278 | 155.804 | 155.804 | 91.96% | 11.39% | 11.39% | 90% | 10.25% | 34.1286 | 7.481 | 6 | 204.7718 | 75.4724 | 131.4% | 131.4%
3 | 87 | 28 | 2079 | 15 | 9.5 | 355.19 | 216.39 | 571.58 | 216.39 | 108.2 | 87 | 2079 | 900 | 85.8082 | 2.5993 | 9.4341 | 874.284 | 14.7286 | -40.9295 | 33.361 | 33.361 | 51.5887 | 231.5887 | 40.9062 | 488.1617 | 488.1617 | 184.7004 | 672.8621 | 0.598 | 59.8% | 304.2683 | 181.9537 | 127.3676 | 151.38 | 151.38 | 84.14% | 11.43% | 11.43% | 90% | 10.28% | 31.2875 | 7.3995 | 6 | 187.7252 | 69.1896 | 124% | 124%
3 | 87 | 28 | 2080 | 16 | 10.1 | 230.83 | 177.58 | 408.41 | 177.58 | 88.79 | 87 | 2080 | 960 | 85.8082 | 2.5993 | 9.4341 | 934.284 | 15.7286 | -55.9295 | 24.6013 | 24.6013 | 65.5206 | 245.5206 | 55.8907 | 310.9369 | 310.9369 | 151.574 | 462.5109 | 0.50735 | 50.73% | 209.1474 | 106.1108 | 74.2776 | 142.1171 | 142.1171 | 52.27% | 11.54% | 11.54% | 85% | 9.805% | 20.5077 | 7.2383 | 6 | 123.0464 | 45.351 | 86.58% | 86.58%
3 | 87 | 28 | 2081 | 17 | 11.9 | 178.42 | 123.69 | 302.11 | 123.69 | 61.85 | 87 | 2081 | 1020 | 85.8082 | 2.5993 | 9.4341 | 994.284 | 16.7286 | -70.9295 | 14.8667 | 14.8667 | 77.646 | 257.646 | 70.8741 | 227.8446 | 227.8446 | 105.576 | 333.4206 | 0.40503 | 40.5% | 150.7728 | 61.0673 | 42.7471 | 136.128 | 136.128 | 31.4% | 11.56% | 0% | 85% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2082 | 18 | 13.6 | 109.36 | 84.44 | 193.8 | 84.44 | 42.22 | 87 | 2082 | 1080 | 85.8082 | 2.5993 | 9.4341 | 1054.284 | 17.7286 | -85.9295 | 4.681 | 4.681 | 88.8148 | 268.8148 | 85.8548 | 0 | 0 | 72.074 | 72.074 | -0.98747 | 0% | 32.5919 | 0 | 0 | 128.1476 | 128.1476 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2083 | 19 | 10.5 | 13.81 | 32.22 | 46.03 | 32.22 | 16.11 | 87 | 2083 | 1140 | 85.8082 | 2.5993 | 9.4341 | 1114.284 | 18.7286 | -100.9295 | -5.547 | 0 | 93.797 | 273.797 | 92.6839 | 0 | 0 | 27.5015 | 27.5015 | -4.1511 | 0% | 12.4362 | 0 | 0 | 151.4741 | 151.4741 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2084 | 20 | 6.4 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 87 | 2084 | 1200 | 85.8082 | 2.5993 | 9.4341 | 1174.284 | 19.7286 | -115.9295 | -15.4321 | 0 | 93.797 | 273.797 | 92.6839 | 0 | 0 | 1.6559 | 1.6559 | -87.3238 | 0% | 0.7488 | 0 | 0 | 133.8212 | 133.8212 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2085 | 21 | 6.5 | 0 | 0 | 0 | 0 | 0 | 87 | 2085 | 1260 | 85.8082 | 2.5993 | 9.4341 | 1234.284 | 20.7286 | -130.9295 | -24.5282 | 0 | 93.797 | 273.797 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1202 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2086 | 22 | 5.6 | 0 | 0 | 0 | 0 | 0 | 87 | 2086 | 1320 | 85.8082 | 2.5993 | 9.4341 | 1294.284 | 21.7286 | -145.9295 | -32.252 | 0 | 93.797 | 273.797 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3723 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2087 | 23 | 3.4 | 0 | 0 | 0 | 0 | 0 | 87 | 2087 | 1380 | 85.8082 | 2.5993 | 9.4341 | 1354.284 | 22.7286 | -160.9295 | -37.8451 | 0 | 93.797 | 273.797 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.9793 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
3 | 87 | 28 | 2088 | 24 | 3.1 | 0 | 0 | 0 | 0 | 0 | 87 | 2088 | 1440 | 85.8082 | 2.5993 | 9.4341 | 1414.284 | 23.7286 | -175.9295 | -40.4926 | 0 | 93.797 | 273.797 | 92.6839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.6907 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2089 | 1 | 2.9 | 0 | 0 | 0 | 0 | 0 | 88 | 2089 | 60 | 86.7945 | 2.999 | 9.7852 | 34.284 | 0.73449 | 168.9827 | -39.2837 | 0 | 94.3814 | 85.6186 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.138 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2090 | 2 | 3.1 | 0 | 0 | 0 | 0 | 0 | 88 | 2090 | 120 | 86.7945 | 2.999 | 9.7852 | 94.284 | 1.7345 | 153.9827 | -35.202 | 0 | 94.3814 | 85.6186 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.299 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2091 | 3 | 3.1 | 0 | 0 | 0 | 0 | 0 | 88 | 2091 | 180 | 86.7945 | 2.999 | 9.7852 | 154.284 | 2.7345 | 138.9827 | -28.5469 | 0 | 94.3814 | 85.6186 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7649 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2092 | 4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 88 | 2092 | 240 | 86.7945 | 2.999 | 9.7852 | 214.284 | 3.7345 | 123.9827 | -20.1287 | 0 | 94.3814 | 85.6186 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7461 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2093 | 5 | 1.9 | 0 | 0 | 0 | 0 | 0 | 88 | 2093 | 300 | 86.7945 | 2.999 | 9.7852 | 274.284 | 4.7345 | 108.9827 | -10.6222 | 0 | 94.3814 | 85.6186 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.3973 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2094 | 6 | 1.9 | 0 | 0 | 0 | 0 | 0 | 88 | 2094 | 360 | 86.7945 | 2.999 | 9.7852 | 334.284 | 5.7345 | 93.9827 | -0.53718 | 0 | 94.3814 | 85.6186 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.4993 | 3.4993 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2095 | 7 | 1.8 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 88 | 2095 | 420 | 86.7945 | 2.999 | 9.7852 | 394.284 | 6.7345 | 78.9827 | 9.7192 | 9.7192 | 83.9876 | 96.0124 | 78.9086 | 0 | 0 | 1.6559 | 1.6559 | -94.03 | 0% | 0.7488 | 0 | 0 | 168.4415 | 168.4415 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2096 | 8 | 1.9 | 35.36 | 29.25 | 64.61 | 29.25 | 14.63 | 88 | 2096 | 480 | 86.7945 | 2.999 | 9.7852 | 454.284 | 7.7345 | 63.9827 | 19.7616 | 19.7616 | 72.4759 | 107.5241 | 63.9309 | 45.9591 | 45.9591 | 24.9664 | 70.9255 | -1.4066 | 0% | 32.0725 | 0 | 0 | 181.2304 | 181.2304 | 0% | 12.08% | 12.08% | 80% | 9.662% | 3.0989 | 9.659 | 6 | 18.5935 | 6.853 | 10.26% | 10.26%
3 | 88 | 29 | 2097 | 9 | 2.7 | 121.19 | 71.11 | 192.3 | 71.11 | 35.56 | 88 | 2097 | 540 | 86.7945 | 2.999 | 9.7852 | 514.284 | 8.7345 | 48.9827 | 29.1404 | 29.1404 | 59.6174 | 120.3826 | 48.9516 | 163.435 | 163.435 | 60.6962 | 224.1312 | 0.11315 | 11.32% | 101.3521 | 11.4684 | 8.0279 | 168.6108 | 168.6108 | 4.761% | 11.9% | 11.9% | 80% | 9.52% | 9.6487 | 9.4021 | 6 | 57.892 | 21.3372 | 34.33% | 34.33%
3 | 88 | 29 | 2098 | 10 | 4.1 | 233.25 | 85.56 | 318.81 | 85.56 | 42.78 | 88 | 2098 | 600 | 86.7945 | 2.999 | 9.7852 | 574.284 | 9.7345 | 33.9827 | 37.2439 | 37.2439 | 44.5209 | 135.4791 | 33.9736 | 319.6135 | 319.6135 | 73.03 | 392.6435 | 0.41829 | 41.83% | 177.5534 | 74.2685 | 51.9879 | 153.045 | 153.045 | 33.97% | 11.71% | 11.71% | 85% | 9.952% | 17.6701 | 8.9633 | 6 | 106.0207 | 39.0759 | 69.27% | 69.27%
3 | 88 | 29 | 2099 | 11 | 4.8 | 319.36 | 117.69 | 437.05 | 117.69 | 58.85 | 88 | 2099 | 660 | 86.7945 | 2.999 | 9.7852 | 634.284 | 10.7345 | 18.9827 | 43.2216 | 43.2216 | 26.4726 | 153.5274 | 19.005 | 440.9205 | 440.9205 | 100.4547 | 541.3752 | 0.52737 | 52.74% | 244.8099 | 129.1054 | 90.3738 | 151.0206 | 151.0206 | 59.84% | 11.57% | 11.57% | 90% | 10.41% | 25.4881 | 8.7491 | 6 | 152.9287 | 56.3647 | 101.3% | 101.3%
3 | 88 | 29 | 2100 | 12 | 4.4 | 395.19 | 122.42 | 517.61 | 122.42 | 61.21 | 88 | 2100 | 720 | 86.7945 | 2.999 | 9.7852 | 694.284 | 11.7345 | 3.9827 | 46.0844 | 46.0844 | 5.7392 | 174.2608 | 4.1623 | 547.1523 | 547.1523 | 104.492 | 651.6443 | 0.5727 | 57.27% | 294.6736 | 168.7603 | 118.1322 | 141.5279 | 141.5279 | 83.47% | 11.48% | 11.48% | 90% | 10.33% | 30.4438 | 8.8711 | 6 | 182.6627 | 67.3237 | 129.1% | 129.1%
3 | 88 | 29 | 2101 | 13 | 6.7 | 430.28 | 103.69 | 533.97 | 103.69 | 51.85 | 88 | 2101 | 780 | 86.7945 | 2.999 | 9.7852 | 754.284 | 12.7345 | -11.0173 | 45.1869 | 45.1869 | 15.7106 | 195.7106 | 11.075 | 595.2373 | 595.2373 | 88.505 | 683.7422 | 0.59162 | 59.16% | 309.1882 | 182.9207 | 128.0445 | 142.753 | 142.753 | 89.7% | 11.44% | 11.44% | 90% | 10.29% | 31.8258 | 8.1849 | 6 | 190.9548 | 70.3799 | 133.8% | 133.8%
3 | 88 | 29 | 2102 | 14 | 8.3 | 427.22 | 101.58 | 528.8 | 101.58 | 50.79 | 88 | 2102 | 840 | 86.7945 | 2.999 | 9.7852 | 814.284 | 13.7345 | -26.0173 | 40.7462 | 40.7462 | 35.3233 | 215.3233 | 26.0225 | 588.1782 | 588.1782 | 86.704 | 674.8821 | 0.59444 | 59.44% | 305.1817 | 181.4131 | 126.9892 | 143.5615 | 143.5615 | 88.46% | 11.43% | 11.43% | 90% | 10.29% | 31.4009 | 7.7294 | 6 | 188.4057 | 69.4404 | 131.2% | 131.2%
3 | 88 | 29 | 2103 | 15 | 9 | 390.47 | 104.53 | 495 | 104.53 | 52.27 | 88 | 2103 | 900 | 86.7945 | 2.999 | 9.7852 | 874.284 | 14.7345 | -41.0173 | 33.6506 | 33.6506 | 51.9355 | 231.9355 | 40.9975 | 531.8331 | 531.8331 | 89.2219 | 621.055 | 0.57893 | 57.89% | 280.8411 | 162.5881 | 113.8116 | 140.9354 | 140.9354 | 80.75% | 11.46% | 11.46% | 90% | 10.31% | 28.9666 | 7.5357 | 6 | 173.7997 | 64.0571 | 123.3% | 123.3%
3 | 88 | 29 | 2104 | 16 | 9.5 | 322.42 | 117.03 | 439.45 | 117.03 | 58.52 | 88 | 2104 | 960 | 86.7945 | 2.999 | 9.7852 | 934.284 | 15.7345 | -56.0173 | 24.8585 | 24.8585 | 65.8709 | 245.8709 | 55.9766 | 429.1464 | 429.1464 | 99.8914 | 529.0378 | 0.542 | 54.2% | 239.2309 | 129.6637 | 90.7646 | 137.9472 | 137.9472 | 65.8% | 11.51% | 11.51% | 90% | 10.36% | 24.7787 | 7.3995 | 6 | 148.6719 | 54.7958 | 107.8% | 107.8%
3 | 88 | 29 | 2105 | 17 | 9.3 | 231.75 | 101.75 | 333.5 | 101.75 | 50.88 | 88 | 2105 | 1020 | 86.7945 | 2.999 | 9.7852 | 994.284 | 16.7345 | -71.0173 | 15.1046 | 15.1046 | 77.9907 | 257.9907 | 70.9554 | 290.2007 | 290.2007 | 86.8491 | 377.0498 | 0.43515 | 43.51% | 170.5019 | 74.1937 | 51.9356 | 130.2043 | 130.2043 | 39.89% | 11.6% | 11.6% | 85% | 9.861% | 16.8128 | 7.4538 | 6 | 100.8768 | 37.18 | 77.48% | 77.48%
3 | 88 | 29 | 2106 | 18 | 7.9 | 123.69 | 64.08 | 187.77 | 64.08 | 32.04 | 88 | 2106 | 1080 | 86.7945 | 2.999 | 9.7852 | 1054.284 | 17.7345 | -86.0173 | 4.9119 | 4.9119 | 89.1538 | 269.1538 | 85.9314 | 0 | 0 | 54.6957 | 54.6957 | -1.799 | 0% | 24.7334 | 0 | 0 | 116.543 | 116.543 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2107 | 19 | 7.1 | 26.03 | 29.17 | 55.2 | 29.17 | 14.59 | 88 | 2107 | 1140 | 86.7945 | 2.999 | 9.7852 | 1114.284 | 18.7345 | -101.0173 | -5.3115 | 0 | 94.3814 | 274.3814 | 93.0966 | 0 | 0 | 24.8982 | 24.8982 | -4.9902 | 0% | 11.2589 | 0 | 0 | 145.1704 | 145.1704 | 0% | 11.9% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2108 | 20 | 5.4 | 0 | 2.5 | 2.5 | 2.5 | 1.25 | 88 | 2108 | 1200 | 86.7945 | 2.999 | 9.7852 | 1174.284 | 19.7345 | -116.0173 | -15.1804 | 0 | 94.3814 | 274.3814 | 93.0966 | 0 | 0 | 2.1339 | 2.1339 | -68.7032 | 0% | 0.96494 | 0 | 0 | 131.4694 | 131.4694 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2109 | 21 | 4.5 | 0 | 0 | 0 | 0 | 0 | 88 | 2109 | 1260 | 86.7945 | 2.999 | 9.7852 | 1234.284 | 20.7345 | -131.0173 | -24.249 | 0 | 94.3814 | 274.3814 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7176 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2110 | 22 | 2.9 | 0 | 0 | 0 | 0 | 0 | 88 | 2110 | 1320 | 86.7945 | 2.999 | 9.7852 | 1294.284 | 21.7345 | -146.0173 | -31.9353 | 0 | 94.3814 | 274.3814 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7404 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2111 | 23 | 2.8 | 0 | 0 | 0 | 0 | 0 | 88 | 2111 | 1380 | 86.7945 | 2.999 | 9.7852 | 1354.284 | 22.7345 | -161.0173 | -37.4864 | 0 | 94.3814 | 274.3814 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3586 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
3 | 88 | 29 | 2112 | 24 | 2.2 | 0 | 0 | 0 | 0 | 0 | 88 | 2112 | 1440 | 86.7945 | 2.999 | 9.7852 | 1414.284 | 23.7345 | -176.0173 | -40.0992 | 0 | 94.3814 | 274.3814 | 93.0966 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7389 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2113 | 1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 89 | 2113 | 60 | 87.7808 | 3.3979 | 10.1307 | 34.284 | 0.74024 | 168.8963 | -38.8759 | 0 | 94.965 | 85.035 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9572 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2114 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 89 | 2114 | 120 | 87.7808 | 3.3979 | 10.1307 | 94.284 | 1.7402 | 153.8963 | -34.7992 | 0 | 94.965 | 85.035 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5271 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2115 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 89 | 2115 | 180 | 87.7808 | 3.3979 | 10.1307 | 154.284 | 2.7402 | 138.8963 | -28.1599 | 0 | 94.965 | 85.035 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3349 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2116 | 4 | 0.3 | 0 | 0 | 0 | 0 | 0 | 89 | 2116 | 240 | 87.7808 | 3.3979 | 10.1307 | 214.284 | 3.7402 | 123.8963 | -19.7588 | 0 | 94.965 | 85.035 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.7065 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2117 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 2117 | 300 | 87.7808 | 3.3979 | 10.1307 | 274.284 | 4.7402 | 108.8963 | -10.2652 | 0 | 94.965 | 85.035 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7415 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2118 | 6 | -0.6 | 0 | 0 | 0 | 0 | 0 | 89 | 2118 | 360 | 87.7808 | 3.3979 | 10.1307 | 334.284 | 5.7402 | 93.8963 | -0.18693 | 0 | 94.965 | 85.035 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.6579 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2119 | 7 | -0.6 | 0 | 2.5 | 2.5 | 2.5 | 1.25 | 89 | 2119 | 420 | 87.7808 | 3.3979 | 10.1307 | 394.284 | 6.7402 | 78.8963 | 10.0697 | 10.0697 | 84.1999 | 95.8001 | 78.8141 | 0 | 0 | 2.1339 | 2.1339 | -75.555 | 0% | 0.96494 | 0 | 0 | 159.3074 | 159.3074 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2120 | 8 | 0.5 | 31.94 | 43.89 | 75.83 | 43.89 | 21.95 | 89 | 2120 | 480 | 87.7808 | 3.3979 | 10.1307 | 454.284 | 7.7402 | 63.8963 | 20.1197 | 20.1197 | 72.6842 | 107.3158 | 63.8418 | 40.9346 | 40.9346 | 37.4625 | 78.397 | -1.2398 | 0% | 35.4511 | 0 | 0 | 173.2394 | 173.2394 | 0% | 12.13% | 12.13% | 80% | 9.701% | 3.439 | 10.1193 | 6 | 20.6341 | 7.6051 | 11.91% | 11.91%
3 | 89 | 30 | 2121 | 9 | 2.5 | 83.97 | 107.58 | 191.55 | 107.58 | 53.79 | 89 | 2121 | 540 | 87.7808 | 3.3979 | 10.1307 | 514.284 | 8.7402 | 48.8963 | 29.513 | 29.513 | 59.8087 | 120.1913 | 48.8684 | 112.1242 | 112.1242 | 91.8253 | 203.9495 | 0.042405 | 4.241% | 92.226 | 3.9109 | 2.7376 | 161.5444 | 161.5444 | 1.695% | 11.93% | 11.93% | 80% | 9.541% | 8.7989 | 9.4659 | 6 | 52.7932 | 19.4579 | 32.68% | 32.68%
3 | 89 | 30 | 2122 | 10 | 3.6 | 155.36 | 142.86 | 298.22 | 142.86 | 71.43 | 89 | 2122 | 600 | 87.7808 | 3.3979 | 10.1307 | 574.284 | 9.7402 | 33.8963 | 37.6351 | 37.6351 | 44.6677 | 135.3323 | 33.8983 | 211.1805 | 211.1805 | 121.9386 | 333.1192 | 0.34574 | 34.57% | 150.6365 | 52.0807 | 36.4565 | 145.2866 | 145.2866 | 25.09% | 11.77% | 11.77% | 85% | 10.01% | 15.0744 | 9.1184 | 6 | 90.4466 | 33.3358 | 62.25% | 62.25%
3 | 89 | 30 | 2123 | 11 | 4.9 | 262.69 | 172.58 | 435.27 | 172.58 | 86.29 | 89 | 2123 | 660 | 87.7808 | 3.3979 | 10.1307 | 634.284 | 10.7402 | 18.8963 | 43.6278 | 43.6278 | 26.5277 | 153.4723 | 18.9456 | 360.1014 | 360.1014 | 147.3062 | 507.4076 | 0.50933 | 50.93% | 229.4497 | 116.8645 | 81.8052 | 146.5658 | 146.5658 | 55.81% | 11.59% | 11.59% | 90% | 10.44% | 23.9442 | 8.7188 | 6 | 143.6653 | 52.9505 | 98.02% | 98.02%
3 | 89 | 30 | 2124 | 12 | 5.5 | 351.19 | 171.47 | 522.66 | 171.47 | 85.74 | 89 | 2124 | 720 | 87.7808 | 3.3979 | 10.1307 | 694.284 | 11.7402 | 3.8963 | 46.4883 | 46.4883 | 5.654 | 174.346 | 4.2159 | 482.9338 | 482.9338 | 146.3588 | 629.2926 | 0.56869 | 56.87% | 284.5661 | 161.8291 | 113.2803 | 140.6662 | 140.6662 | 80.53% | 11.49% | 11.49% | 90% | 10.34% | 29.4222 | 8.5383 | 6 | 176.5333 | 65.0646 | 125.5% | 125.5%
3 | 89 | 30 | 2125 | 13 | 6.1 | 263.53 | 258.25 | 521.78 | 258.25 | 129.13 | 89 | 2125 | 780 | 87.7808 | 3.3979 | 10.1307 | 754.284 | 12.7402 | -11.1037 | 45.5626 | 45.5626 | 15.9374 | 195.9374 | 11.2096 | 362.04 | 362.04 | 220.4302 | 582.4702 | 0.55223 | 55.22% | 263.393 | 145.4547 | 101.8183 | 139.0547 | 139.0547 | 73.22% | 11.52% | 11.52% | 90% | 10.37% | 27.3046 | 8.3603 | 6 | 163.8274 | 60.3816 | 117.8% | 117.8%
3 | 89 | 30 | 2126 | 14 | 7.2 | 249.53 | 263.25 | 512.78 | 263.25 | 131.63 | 89 | 2126 | 840 | 87.7808 | 3.3979 | 10.1307 | 814.284 | 13.7402 | -26.1037 | 41.0778 | 41.0778 | 35.6382 | 215.6382 | 26.126 | 340.9536 | 340.9536 | 224.6979 | 565.6515 | 0.54938 | 54.94% | 255.7876 | 140.5238 | 98.3666 | 138.4832 | 138.4832 | 71.03% | 11.52% | 11.52% | 90% | 10.37% | 26.5131 | 8.0406 | 6 | 159.0787 | 58.6314 | 114.9% | 114.9%
3 | 89 | 30 | 2127 | 15 | 7.3 | 174.81 | 190.92 | 365.73 | 190.92 | 95.46 | 89 | 2127 | 900 | 87.7808 | 3.3979 | 10.1307 | 874.284 | 14.7402 | -41.1037 | 33.9394 | 33.9394 | 52.2826 | 232.2826 | 41.0904 | 235.9772 | 235.9772 | 162.9604 | 398.9377 | 0.44357 | 44.36% | 180.3996 | 80.0191 | 56.0133 | 128.8289 | 128.8289 | 43.48% | 11.63% | 11.63% | 85% | 9.887% | 17.8367 | 8.012 | 6 | 107.0201 | 39.4442 | 83.07% | 83.07%
3 | 89 | 30 | 2128 | 16 | 7.5 | 113.69 | 177.03 | 290.72 | 177.03 | 88.52 | 89 | 2128 | 960 | 87.7808 | 3.3979 | 10.1307 | 934.284 | 15.7402 | -56.1037 | 25.1153 | 25.1153 | 66.221 | 246.221 | 56.0629 | 149.5403 | 149.5403 | 151.1046 | 300.6449 | 0.3273 | 32.73% | 135.9516 | 44.4972 | 31.148 | 123.5112 | 123.5112 | 25.22% | 11.7% | 11.7% | 85% | 9.941% | 13.515 | 7.9549 | 6 | 81.0898 | 29.8871 | 65.65% | 65.65%
3 | 89 | 30 | 2129 | 17 | 7.5 | 65.83 | 130.47 | 196.3 | 130.47 | 65.24 | 89 | 2129 | 1020 | 87.7808 | 3.3979 | 10.1307 | 994.284 | 16.7402 | -71.1037 | 15.3424 | 15.3424 | 78.3345 | 258.3345 | 71.0362 | 80.8538 | 80.8538 | 111.3631 | 192.2169 | 0.0584 | 5.84% | 86.9205 | 5.0762 | 3.5533 | 116.0906 | 116.0906 | 3.061% | 11.77% | 11.77% | 80% | 9.416% | 8.1843 | 7.9549 | 6 | 49.106 | 18.0989 | 42.3% | 42.3%
3 | 89 | 30 | 2130 | 18 | 5.3 | 46.86 | 80.56 | 127.42 | 80.56 | 40.28 | 89 | 2130 | 1080 | 87.7808 | 3.3979 | 10.1307 | 1054.284 | 17.7402 | -86.1037 | 5.1431 | 5.1431 | 89.4915 | 269.4915 | 86.0068 | 0 | 0 | 68.7623 | 68.7623 | -1.3565 | 0% | 31.0943 | 0 | 0 | 147.8292 | 147.8292 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2131 | 19 | 5.7 | 5.28 | 43.81 | 49.09 | 43.81 | 21.91 | 89 | 2131 | 1140 | 87.7808 | 3.3979 | 10.1307 | 1114.284 | 18.7402 | -101.1037 | -5.0753 | 0 | 94.965 | 274.965 | 93.5086 | 0 | 0 | 37.3942 | 37.3942 | -3.1432 | 0% | 16.9096 | 0 | 0 | 140.2637 | 140.2637 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2132 | 20 | 6.1 | 0 | 2.22 | 2.22 | 2.22 | 1.11 | 89 | 2132 | 1200 | 87.7808 | 3.3979 | 10.1307 | 1174.284 | 19.7402 | -116.1037 | -14.9278 | 0 | 94.965 | 274.965 | 93.5086 | 0 | 0 | 1.8949 | 1.8949 | -76.5863 | 0% | 0.85687 | 0 | 0 | 132.4481 | 132.4481 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2133 | 21 | 5.2 | 0 | 0 | 0 | 0 | 0 | 89 | 2133 | 1260 | 87.7808 | 3.3979 | 10.1307 | 1234.284 | 20.7402 | -131.1037 | -23.9688 | 0 | 94.965 | 274.965 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4138 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2134 | 22 | 4.6 | 0 | 0 | 0 | 0 | 0 | 89 | 2134 | 1320 | 87.7808 | 3.3979 | 10.1307 | 1294.284 | 21.7402 | -146.1037 | -31.6177 | 0 | 94.965 | 274.965 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6381 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2135 | 23 | 4.1 | 0 | 0 | 0 | 0 | 0 | 89 | 2135 | 1380 | 87.7808 | 3.3979 | 10.1307 | 1354.284 | 22.7402 | -161.1037 | -37.1274 | 0 | 94.965 | 274.965 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9032 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
3 | 89 | 30 | 2136 | 24 | 3.7 | 0 | 0 | 0 | 0 | 0 | 89 | 2136 | 1440 | 87.7808 | 3.3979 | 10.1307 | 1414.284 | 23.7402 | -176.1037 | -39.7063 | 0 | 94.965 | 274.965 | 93.5086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0158 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2137 | 1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 90 | 2137 | 60 | 88.7671 | 3.7961 | 10.4702 | 34.284 | 0.7459 | 168.8115 | -38.4691 | 0 | 95.5477 | 84.4523 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.8798 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2138 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 90 | 2138 | 120 | 88.7671 | 3.7961 | 10.4702 | 94.284 | 1.7459 | 153.8115 | -34.3978 | 0 | 95.5477 | 84.4523 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4167 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2139 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 90 | 2139 | 180 | 88.7671 | 3.7961 | 10.4702 | 154.284 | 2.7459 | 138.8115 | -27.7743 | 0 | 95.5477 | 84.4523 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7825 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2140 | 4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 90 | 2140 | 240 | 88.7671 | 3.7961 | 10.4702 | 214.284 | 3.7459 | 123.8115 | -19.3902 | 0 | 95.5477 | 84.4523 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6301 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2141 | 5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 90 | 2141 | 300 | 88.7671 | 3.7961 | 10.4702 | 274.284 | 4.7459 | 108.8115 | -9.9098 | 0 | 95.5477 | 84.4523 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.9865 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2142 | 6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 90 | 2142 | 360 | 88.7671 | 3.7961 | 10.4702 | 334.284 | 5.7459 | 93.8115 | 0.16165 | 0.16165 | 95.3749 | 84.6251 | 93.6833 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.2005 | 6.2005 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2143 | 7 | 0.5 | 0.28 | 3.06 | 3.34 | 3.06 | 1.53 | 90 | 2143 | 420 | 88.7671 | 3.7961 | 10.4702 | 394.284 | 6.7459 | 78.8115 | 10.4184 | 10.4184 | 84.4133 | 95.5867 | 78.7218 | 0.30282 | 0.30282 | 2.6119 | 2.9147 | -54.1674 | 0% | 1.318 | 0 | 0 | 171.7129 | 171.7129 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2144 | 8 | 1.7 | 33.06 | 33.89 | 66.95 | 33.89 | 16.95 | 90 | 2144 | 480 | 88.7671 | 3.7961 | 10.4702 | 454.284 | 7.7459 | 63.8115 | 20.4759 | 20.4759 | 72.8943 | 107.1057 | 63.7556 | 41.7913 | 41.7913 | 28.9269 | 70.7182 | -1.42 | 0% | 31.9788 | 0 | 0 | 187.2793 | 187.2793 | 0% | 12.09% | 12.09% | 80% | 9.669% | 3.092 | 9.7239 | 6 | 18.5518 | 6.8376 | 9.906% | 9.906%
3 | 90 | 31 | 2145 | 9 | 3.7 | 118.61 | 68.06 | 186.67 | 68.06 | 34.03 | 90 | 2145 | 540 | 88.7671 | 3.7961 | 10.4702 | 514.284 | 8.7459 | 48.8115 | 29.8836 | 29.8836 | 60.0023 | 119.9977 | 48.7891 | 156.8402 | 156.8402 | 58.0928 | 214.933 | 0.094877 | 9.488% | 97.1927 | 9.2214 | 6.455 | 176.5163 | 176.5163 | 3.657% | 11.88% | 11.88% | 80% | 9.501% | 9.2345 | 9.0873 | 6 | 55.4069 | 20.4212 | 31.39% | 31.39%
3 | 90 | 31 | 2146 | 10 | 4.6 | 222.78 | 123.53 | 346.31 | 123.53 | 61.77 | 90 | 2146 | 600 | 88.7671 | 3.7961 | 10.4702 | 574.284 | 9.7459 | 33.8115 | 38.0246 | 38.0246 | 44.8172 | 135.1828 | 33.8287 | 300.4293 | 300.4293 | 105.4395 | 405.8688 | 0.43383 | 43.38% | 183.5339 | 79.6218 | 55.7353 | 161.9338 | 161.9338 | 34.42% | 11.69% | 11.69% | 85% | 9.933% | 18.2303 | 8.8099 | 6 | 109.382 | 40.3148 | 67.55% | 67.55%
3 | 90 | 31 | 2147 | 11 | 6 | 396.67 | 144.25 | 540.92 | 144.25 | 72.13 | 90 | 2147 | 660 | 88.7671 | 3.7961 | 10.4702 | 634.284 | 10.7459 | 18.8115 | 44.0327 | 44.0327 | 26.5852 | 153.4148 | 18.8961 | 539.9357 | 539.9357 | 123.1251 | 663.0608 | 0.58247 | 58.25% | 299.8361 | 174.6469 | 122.2529 | 163.8995 | 163.8995 | 74.59% | 11.46% | 11.46% | 90% | 10.31% | 30.9182 | 8.3898 | 6 | 185.5092 | 68.3728 | 113.2% | 113.2%
3 | 90 | 31 | 2148 | 12 | 8.5 | 457.42 | 159.64 | 617.06 | 159.64 | 79.82 | 90 | 2148 | 720 | 88.7671 | 3.7961 | 10.4702 | 694.284 | 11.7459 | 3.8115 | 46.8912 | 46.8912 | 5.5697 | 174.4303 | 4.3086 | 624.7828 | 624.7828 | 136.2613 | 761.0441 | 0.61879 | 61.88% | 344.1441 | 212.952 | 149.0664 | 157.2726 | 157.2726 | 94.78% | 11.38% | 11.38% | 90% | 10.24% | 35.2368 | 7.6737 | 6 | 211.421 | 77.9231 | 134.4% | 134.4%
3 | 90 | 31 | 2149 | 13 | 7.6 | 522.69 | 208.53 | 731.22 | 208.53 | 104.27 | 90 | 2149 | 780 | 88.7671 | 3.7961 | 10.4702 | 754.284 | 12.7459 | -11.1885 | 45.9375 | 45.9375 | 16.1648 | 196.1648 | 11.3554 | 713.1525 | 713.1525 | 177.9915 | 891.144 | 0.64344 | 64.34% | 402.9753 | 259.2913 | 181.5039 | 157.3097 | 157.3097 | 115.4% | 11.29% | 11.29% | 95% | 10.73% | 43.2205 | 7.9264 | 6 | 259.323 | 95.5783 | 164.8% | 164.8%
3 | 90 | 31 | 2150 | 14 | 7.5 | 392.14 | 227.5 | 619.64 | 227.5 | 113.75 | 90 | 2150 | 840 | 88.7671 | 3.7961 | 10.4702 | 814.284 | 13.7459 | -26.1885 | 41.4085 | 41.4085 | 35.9539 | 215.9539 | 26.2334 | 531.8077 | 531.8077 | 194.1834 | 725.9911 | 0.60659 | 60.66% | 328.2932 | 199.1398 | 139.3979 | 150.7437 | 150.7437 | 92.47% | 11.4% | 11.4% | 90% | 10.26% | 33.6914 | 7.9549 | 6 | 202.1484 | 74.5055 | 134.1% | 134.1%
3 | 90 | 31 | 2151 | 15 | 8.5 | 318.14 | 228.89 | 547.03 | 228.89 | 114.45 | 90 | 2151 | 900 | 88.7671 | 3.7961 | 10.4702 | 874.284 | 14.7459 | -41.1885 | 34.2273 | 34.2273 | 52.6299 | 232.6299 | 41.1849 | 425.6673 | 425.6673 | 195.3698 | 621.0372 | 0.57703 | 57.7% | 280.833 | 162.0499 | 113.4349 | 145.6218 | 145.6218 | 77.9% | 11.47% | 11.47% | 90% | 10.32% | 28.9782 | 7.6737 | 6 | 173.8695 | 64.0828 | 119.4% | 119.4%
3 | 90 | 31 | 2152 | 16 | 9.2 | 258.69 | 193.89 | 452.58 | 193.89 | 96.95 | 90 | 2152 | 960 | 88.7671 | 3.7961 | 10.4702 | 934.284 | 15.7459 | -56.1885 | 25.3717 | 25.3717 | 66.5706 | 246.5706 | 56.1495 | 336.2928 | 336.2928 | 165.4955 | 501.7883 | 0.52637 | 52.64% | 226.9087 | 119.4387 | 83.6071 | 140.1635 | 140.1635 | 59.65% | 11.53% | 11.53% | 90% | 10.38% | 23.5446 | 7.481 | 6 | 141.2673 | 52.0667 | 100.8% | 100.8%
3 | 90 | 31 | 2153 | 17 | 9.24 | 192.31 | 132.78 | 325.09 | 132.78 | 66.39 | 90 | 2153 | 1020 | 88.7671 | 3.7961 | 10.4702 | 994.284 | 16.7459 | -71.1885 | 15.5801 | 15.5801 | 78.6773 | 258.6773 | 71.1164 | 231.7343 | 231.7343 | 113.3348 | 345.0692 | 0.40056 | 40.06% | 156.0403 | 62.5029 | 43.752 | 130.9258 | 130.9258 | 33.42% | 11.62% | 11.62% | 85% | 9.878% | 15.4137 | 7.4701 | 6 | 92.4824 | 34.0861 | 70.64% | 70.64%
3 | 90 | 31 | 2154 | 18 | 8.12 | 86.67 | 96.39 | 183.06 | 96.39 | 48.2 | 90 | 2154 | 1080 | 88.7671 | 3.7961 | 10.4702 | 1054.284 | 17.7459 | -86.1885 | 5.3746 | 5.3746 | 89.8277 | 269.8277 | 86.0808 | 0 | 0 | 82.274 | 82.274 | -0.92013 | 0% | 37.2043 | 0 | 0 | 117.0583 | 117.0583 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.7797 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2155 | 19 | 6.25 | 15.83 | 43.14 | 58.97 | 43.14 | 21.57 | 90 | 2155 | 1140 | 88.7671 | 3.7961 | 10.4702 | 1114.284 | 18.7459 | -101.1885 | -4.8385 | 0 | 95.5477 | 275.5477 | 93.9198 | 0 | 0 | 36.8223 | 36.8223 | -3.1688 | 0% | 16.651 | 0 | 0 | 144.1945 | 144.1945 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.3162 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2156 | 20 | 4.39 | 0 | 3.75 | 3.75 | 3.75 | 1.88 | 90 | 2156 | 1200 | 88.7671 | 3.7961 | 10.4702 | 1174.284 | 19.7459 | -116.1885 | -14.6744 | 0 | 95.5477 | 275.5477 | 93.9198 | 0 | 0 | 3.2008 | 3.2008 | -46.2925 | 0% | 1.4474 | 0 | 0 | 130.0269 | 130.0269 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8741 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2157 | 21 | 3.7 | 0 | 0 | 0 | 0 | 0 | 90 | 2157 | 1260 | 88.7671 | 3.7961 | 10.4702 | 1234.284 | 20.7459 | -131.1885 | -23.6877 | 0 | 95.5477 | 275.5477 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0588 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2158 | 22 | 3.5 | 0 | 0 | 0 | 0 | 0 | 90 | 2158 | 1320 | 88.7671 | 3.7961 | 10.4702 | 1294.284 | 21.7459 | -146.1885 | -31.2995 | 0 | 95.5477 | 275.5477 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1164 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2159 | 23 | 3.66 | 0 | 0 | 0 | 0 | 0 | 90 | 2159 | 1380 | 88.7671 | 3.7961 | 10.4702 | 1354.284 | 22.7459 | -161.1885 | -36.7683 | 0 | 95.5477 | 275.5477 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2571 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0997 | 6 | 0 | 0 | 0% | 0%
3 | 90 | 31 | 2160 | 24 | 3.96 | 0 | 0 | 0 | 0 | 0 | 90 | 2160 | 1440 | 88.7671 | 3.7961 | 10.4702 | 1414.284 | 23.7459 | -176.1885 | -39.3139 | 0 | 95.5477 | 275.5477 | 93.9198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1845 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0066 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2161 | 1 | 4.07 | 0 | 0 | 0 | 0 | 0 | 91 | 2161 | 60 | 89.7534 | 4.1933 | 10.8033 | 34.284 | 0.75146 | 168.7282 | -38.0636 | 0 | 96.1293 | 83.8707 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0829 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9726 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2162 | 2 | 3.86 | 0 | 0 | 0 | 0 | 0 | 91 | 2162 | 120 | 89.7534 | 4.1933 | 10.8033 | 94.284 | 1.7515 | 153.7282 | -33.9977 | 0 | 96.1293 | 83.8707 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1244 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0376 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2163 | 3 | 3.31 | 0 | 0 | 0 | 0 | 0 | 91 | 2163 | 180 | 89.7534 | 4.1933 | 10.8033 | 154.284 | 2.7515 | 138.7282 | -27.3901 | 0 | 96.1293 | 83.8707 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.684 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2092 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2164 | 4 | 2.76 | 0 | 0 | 0 | 0 | 0 | 91 | 2164 | 240 | 89.7534 | 4.1933 | 10.8033 | 214.284 | 3.7515 | 123.7282 | -19.0232 | 0 | 96.1293 | 83.8707 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5222 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.383 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2165 | 5 | 2.29 | 0 | 0 | 0 | 0 | 0 | 91 | 2165 | 300 | 89.7534 | 4.1933 | 10.8033 | 274.284 | 4.7515 | 108.7282 | -9.556 | 0 | 96.1293 | 83.8707 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8163 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.5332 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2166 | 6 | 1.97 | 0 | 0 | 0 | 0 | 0 | 91 | 2166 | 360 | 89.7534 | 4.1933 | 10.8033 | 334.284 | 5.7515 | 93.7282 | 0.50841 | 0.50841 | 95.5857 | 84.4143 | 93.5861 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9039 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6363 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2167 | 7 | 2.15 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 91 | 2167 | 420 | 89.7534 | 4.1933 | 10.8033 | 394.284 | 6.7515 | 78.7282 | 10.7652 | 10.7652 | 84.6277 | 95.3723 | 78.6317 | 0 | 0 | 1.6559 | 1.6559 | -93.5137 | 0% | 0.7488 | 0 | 0 | 143.8684 | 143.8684 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5782 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2168 | 8 | 2.9 | 1.86 | 25.75 | 27.61 | 25.75 | 12.88 | 91 | 2168 | 480 | 89.7534 | 4.1933 | 10.8033 | 454.284 | 7.7515 | 63.7282 | 20.8301 | 20.8301 | 73.106 | 106.894 | 63.6725 | 2.3198 | 2.3198 | 21.979 | 24.2988 | -5.5483 | 0% | 10.9879 | 0 | 0 | 150.7225 | 150.7225 | 0% | 12.08% | 12.08% | 80% | 9.665% | 1.062 | 9.3386 | 6 | 6.372 | 2.3485 | 4.228% | 4.228%
4 | 91 | 1 | 2169 | 9 | 6 | 5.28 | 69.17 | 74.45 | 69.17 | 34.59 | 91 | 2169 | 540 | 89.7534 | 4.1933 | 10.8033 | 514.284 | 8.7515 | 48.7282 | 30.2523 | 30.2523 | 60.1983 | 119.8017 | 48.714 | 6.915 | 6.915 | 59.0403 | 65.9553 | -1.423 | 0% | 29.825 | 0 | 0 | 137.3198 | 137.3198 | 0% | 11.92% | 11.92% | 80% | 9.534% | 2.8434 | 8.3898 | 6 | 17.0607 | 6.288 | 12.42% | 12.42%
4 | 91 | 1 | 2170 | 10 | 11 | 38.69 | 157.86 | 196.55 | 157.86 | 78.93 | 91 | 2170 | 600 | 89.7534 | 4.1933 | 10.8033 | 574.284 | 9.7515 | 33.7282 | 38.4123 | 38.4123 | 44.9697 | 135.0303 | 33.765 | 51.7674 | 51.7674 | 134.7419 | 186.5093 | 0.07959 | 7.959% | 84.3395 | 6.7126 | 4.6988 | 149.8477 | 149.8477 | 3.136% | 11.66% | 11.66% | 80% | 9.325% | 7.8643 | 7.0013 | 6 | 47.1856 | 17.3911 | 31.49% | 31.49%
4 | 91 | 1 | 2171 | 11 | 13.2 | 155.08 | 163.33 | 318.41 | 163.33 | 81.67 | 91 | 2171 | 660 | 89.7534 | 4.1933 | 10.8033 | 634.284 | 10.7515 | 18.7282 | 44.4362 | 44.4362 | 26.6454 | 153.3546 | 18.8564 | 209.6187 | 209.6187 | 139.4109 | 349.0295 | 0.43144 | 43.14% | 157.8312 | 68.0948 | 47.6664 | 133.8773 | 133.8773 | 35.6% | 11.52% | 11.52% | 85% | 9.793% | 15.4557 | 6.4458 | 6 | 92.7343 | 34.1789 | 69.27% | 69.27%
4 | 91 | 1 | 2172 | 12 | 15.4 | 189.92 | 142.14 | 332.06 | 142.14 | 71.07 | 91 | 2172 | 720 | 89.7534 | 4.1933 | 10.8033 | 694.284 | 11.7515 | 3.7282 | 47.293 | 47.293 | 5.4866 | 174.5134 | 4.4377 | 257.6788 | 257.6788 | 121.3241 | 379.0029 | 0.47412 | 47.41% | 171.3851 | 81.2578 | 56.8805 | 131.4894 | 131.4894 | 43.26% | 11.46% | 11.46% | 85% | 9.74% | 16.6925 | 5.9242 | 5.9242 | 98.8891 | 36.9139 | 75.21% | 75.21%
4 | 91 | 1 | 2173 | 13 | 16.7 | 159.36 | 131.39 | 290.75 | 131.39 | 65.7 | 91 | 2173 | 780 | 89.7534 | 4.1933 | 10.8033 | 754.284 | 12.7515 | -11.2718 | 46.3113 | 46.3113 | 16.3927 | 196.3927 | 11.5119 | 215.9502 | 215.9502 | 112.1484 | 328.0986 | 0.43187 | 43.19% | 148.3662 | 64.0756 | 44.8529 | 130.2656 | 130.2656 | 34.43% | 11.44% | 11.44% | 85% | 9.722% | 14.4242 | 5.6319 | 5.6319 | 81.2351 | 31.8978 | 62.36% | 62.36%
4 | 91 | 1 | 2174 | 14 | 17.4 | 116.11 | 133.53 | 249.64 | 133.53 | 66.77 | 91 | 2174 | 840 | 89.7534 | 4.1933 | 10.8033 | 814.284 | 13.7515 | -26.2718 | 41.7381 | 41.7381 | 36.2703 | 216.2703 | 26.3445 | 156.2969 | 156.2969 | 113.975 | 270.2719 | 0.35806 | 35.81% | 122.2169 | 43.7608 | 30.6326 | 128.8455 | 128.8455 | 23.77% | 11.43% | 11.43% | 80% | 9.142% | 11.1733 | 5.4794 | 5.4794 | 61.2229 | 24.7088 | 47.52% | 47.52%
4 | 91 | 1 | 2175 | 15 | 18 | 159.44 | 165.19 | 324.63 | 165.19 | 82.6 | 91 | 2175 | 900 | 89.7534 | 4.1933 | 10.8033 | 874.284 | 14.7515 | -41.2718 | 34.5144 | 34.5144 | 52.9774 | 232.9774 | 41.2809 | 211.4609 | 211.4609 | 140.9985 | 352.4594 | 0.46584 | 46.58% | 159.3821 | 74.2472 | 51.973 | 131.4905 | 131.4905 | 39.53% | 11.4% | 11.4% | 85% | 9.691% | 15.4458 | 5.3514 | 5.3514 | 82.6566 | 34.157 | 62.86% | 62.86%
4 | 91 | 1 | 2176 | 16 | 18.5 | 136.47 | 140.36 | 276.83 | 140.36 | 70.18 | 91 | 2176 | 960 | 89.7534 | 4.1933 | 10.8033 | 934.284 | 15.7515 | -56.2718 | 25.6275 | 25.6275 | 66.9195 | 246.9195 | 56.2363 | 175.3587 | 175.3587 | 119.8048 | 295.1634 | 0.40397 | 40.4% | 133.4729 | 53.9191 | 37.7434 | 129.1413 | 129.1413 | 29.23% | 11.39% | 11.39% | 80% | 9.115% | 12.1659 | 5.2467 | 5.2467 | 63.8308 | 26.9039 | 49.43% | 49.43%
4 | 91 | 1 | 2177 | 17 | 17.9 | 49.25 | 85.19 | 134.44 | 85.19 | 42.6 | 91 | 2177 | 1020 | 89.7534 | 4.1933 | 10.8033 | 994.284 | 16.7515 | -71.2718 | 15.8177 | 15.8177 | 79.019 | 259.019 | 71.1959 | 58.2399 | 58.2399 | 72.7142 | 130.9541 | -0.10784 | 0% | 59.2175 | 0 | 0 | 161.7804 | 161.7804 | 0% | 11.43% | 11.43% | 80% | 9.143% | 5.4145 | 5.3726 | 5.3726 | 29.0897 | 11.9737 | 17.98% | 17.98%
4 | 91 | 1 | 2178 | 18 | 17.3 | 3.53 | 39.25 | 42.78 | 39.25 | 19.63 | 91 | 2178 | 1080 | 89.7534 | 4.1933 | 10.8033 | 1054.284 | 17.7515 | -86.2718 | 5.6064 | 5.6064 | 90.1623 | 270.1623 | 86.1533 | 0 | 0 | 33.502 | 33.502 | -2.8002 | 0% | 15.1496 | 0 | 0 | 153.6806 | 153.6806 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2179 | 19 | 15.8 | 2.78 | 19.17 | 21.95 | 19.17 | 9.59 | 91 | 2179 | 1140 | 89.7534 | 4.1933 | 10.8033 | 1114.284 | 18.7515 | -101.2718 | -4.601 | 0 | 96.1293 | 276.1293 | 94.3299 | 0 | 0 | 16.3626 | 16.3626 | -6.7816 | 0% | 7.3992 | 0 | 0 | 147.7967 | 147.7967 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2180 | 20 | 12.8 | 0 | 1.81 | 1.81 | 1.81 | 0.91 | 91 | 2180 | 1200 | 89.7534 | 4.1933 | 10.8033 | 1174.284 | 19.7515 | -116.2718 | -14.4201 | 0 | 96.1293 | 276.1293 | 94.3299 | 0 | 0 | 1.5449 | 1.5449 | -83.9583 | 0% | 0.69862 | 0 | 0 | 138.2439 | 138.2439 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2181 | 21 | 10.8 | 0 | 0 | 0 | 0 | 0 | 91 | 2181 | 1260 | 89.7534 | 4.1933 | 10.8033 | 1234.284 | 20.7515 | -131.2718 | -23.4058 | 0 | 96.1293 | 276.1293 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8046 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2182 | 22 | 9.1 | 0 | 0 | 0 | 0 | 0 | 91 | 2182 | 1320 | 89.7534 | 4.1933 | 10.8033 | 1294.284 | 21.7515 | -146.2718 | -30.9807 | 0 | 96.1293 | 276.1293 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.253 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2183 | 23 | 7.5 | 0 | 0 | 0 | 0 | 0 | 91 | 2183 | 1380 | 89.7534 | 4.1933 | 10.8033 | 1354.284 | 22.7515 | -161.2718 | -36.4091 | 0 | 96.1293 | 276.1293 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4128 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
4 | 91 | 1 | 2184 | 24 | 6.1 | 0 | 0 | 0 | 0 | 0 | 91 | 2184 | 1440 | 89.7534 | 4.1933 | 10.8033 | 1414.284 | 23.7515 | -176.2718 | -38.9222 | 0 | 96.1293 | 276.1293 | 94.3299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2678 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2185 | 1 | 5.8 | 0 | 0 | 0 | 0 | 0 | 92 | 2185 | 60 | 90.7397 | 4.5894 | 11.1297 | 34.284 | 0.75689 | 168.6466 | -37.6594 | 0 | 96.7097 | 83.2903 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.9226 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2186 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 92 | 2186 | 120 | 90.7397 | 4.5894 | 11.1297 | 94.284 | 1.7569 | 153.6466 | -33.5992 | 0 | 96.7097 | 83.2903 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6653 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2187 | 3 | 4.6 | 0 | 0 | 0 | 0 | 0 | 92 | 2187 | 180 | 90.7397 | 4.5894 | 11.1297 | 154.284 | 2.7569 | 138.6466 | -27.0076 | 0 | 96.7097 | 83.2903 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7984 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2188 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 92 | 2188 | 240 | 90.7397 | 4.5894 | 11.1297 | 214.284 | 3.7569 | 123.6466 | -18.6579 | 0 | 96.7097 | 83.2903 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7127 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2189 | 5 | 3.8 | 0 | 0 | 0 | 0 | 0 | 92 | 2189 | 300 | 90.7397 | 4.5894 | 11.1297 | 274.284 | 4.7569 | 108.6466 | -9.204 | 0 | 96.7097 | 83.2903 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9181 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2190 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 92 | 2190 | 360 | 90.7397 | 4.5894 | 11.1297 | 334.284 | 5.7569 | 93.6466 | 0.85317 | 0.85317 | 95.7971 | 84.2029 | 93.4906 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.4903 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2191 | 7 | 2.5 | 0.28 | 3.61 | 3.89 | 3.61 | 1.81 | 92 | 2191 | 420 | 90.7397 | 4.5894 | 11.1297 | 394.284 | 6.7569 | 78.6466 | 11.1098 | 11.1098 | 84.8432 | 95.1568 | 78.5439 | 0.28861 | 0.28861 | 3.0813 | 3.3699 | -45.2879 | 0% | 1.5239 | 0 | 0 | 158.6116 | 158.6116 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2192 | 8 | 3.9 | 30.36 | 35.92 | 66.28 | 35.92 | 17.96 | 92 | 2192 | 480 | 90.7397 | 4.5894 | 11.1297 | 454.284 | 7.7569 | 63.6466 | 21.182 | 21.182 | 73.3193 | 106.6807 | 63.5925 | 37.3693 | 37.3693 | 30.6596 | 68.0289 | -1.4293 | 0% | 30.7627 | 0 | 0 | 171.9056 | 171.9056 | 0% | 12% | 12% | 80% | 9.6% | 2.9533 | 9.0252 | 6 | 17.7195 | 6.5309 | 10.31% | 10.31%
4 | 92 | 2 | 2193 | 9 | 7.6 | 97.03 | 69.72 | 166.75 | 69.72 | 34.86 | 92 | 2193 | 540 | 90.7397 | 4.5894 | 11.1297 | 514.284 | 8.7569 | 48.6466 | 30.6187 | 30.6187 | 60.3967 | 119.6033 | 48.643 | 125.8779 | 125.8779 | 59.5097 | 185.3877 | 0.032211 | 3.221% | 83.8323 | 2.7004 | 1.8903 | 162.3089 | 162.3089 | 1.165% | 11.77% | 11.77% | 80% | 9.417% | 7.8944 | 7.9264 | 6 | 47.3666 | 17.4578 | 29.18% | 29.18%
4 | 92 | 2 | 2194 | 10 | 11.8 | 177.31 | 98.81 | 276.12 | 98.81 | 49.41 | 92 | 2194 | 600 | 90.7397 | 4.5894 | 11.1297 | 574.284 | 9.7569 | 33.6466 | 38.7981 | 38.7981 | 45.1251 | 134.8749 | 33.7071 | 235.4083 | 235.4083 | 84.3396 | 319.7479 | 0.38725 | 38.72% | 144.59 | 55.9919 | 39.1943 | 150.7522 | 150.7522 | 26% | 11.57% | 11.57% | 85% | 9.833% | 14.218 | 6.7954 | 6 | 85.3078 | 31.4418 | 56.59% | 56.59%
4 | 92 | 2 | 2195 | 11 | 13.8 | 278.33 | 104.72 | 383.05 | 104.72 | 52.36 | 92 | 2195 | 660 | 90.7397 | 4.5894 | 11.1297 | 634.284 | 10.7569 | 18.6466 | 44.8381 | 44.8381 | 26.7083 | 153.2917 | 18.8268 | 373.6162 | 373.6162 | 89.3841 | 463.0003 | 0.52611 | 52.61% | 209.3687 | 110.1519 | 77.1063 | 151.6579 | 151.6579 | 50.84% | 11.47% | 11.47% | 85% | 9.747% | 20.4069 | 6.3002 | 6 | 122.4415 | 45.1281 | 80.74% | 80.74%
4 | 92 | 2 | 2196 | 12 | 15.1 | 348.69 | 120.56 | 469.25 | 120.56 | 60.28 | 92 | 2196 | 720 | 90.7397 | 4.5894 | 11.1297 | 694.284 | 11.7569 | 3.6466 | 47.6936 | 47.6936 | 5.4046 | 174.5954 | 4.5998 | 469.9671 | 469.9671 | 102.9044 | 572.8715 | 0.58457 | 58.46% | 259.0525 | 151.4352 | 106.0046 | 146.9752 | 146.9752 | 72.12% | 11.41% | 11.41% | 90% | 10.27% | 26.6096 | 5.9933 | 5.9933 | 159.4796 | 58.8447 | 108.5% | 108.5%
4 | 92 | 2 | 2197 | 13 | 17.5 | 357.78 | 141.19 | 498.97 | 141.19 | 70.6 | 92 | 2197 | 780 | 90.7397 | 4.5894 | 11.1297 | 754.284 | 12.7569 | -11.3534 | 46.6839 | 46.6839 | 16.6209 | 196.6209 | 11.6781 | 481.5608 | 481.5608 | 120.5132 | 602.074 | 0.60419 | 60.42% | 272.2579 | 164.4948 | 115.1464 | 149.1493 | 149.1493 | 77.2% | 11.38% | 11.38% | 90% | 10.24% | 27.8827 | 5.4579 | 5.4579 | 152.1804 | 61.6602 | 102% | 102%
4 | 92 | 2 | 2198 | 14 | 18.3 | 308.25 | 204.72 | 512.97 | 204.72 | 102.36 | 92 | 2198 | 840 | 90.7397 | 4.5894 | 11.1297 | 814.284 | 13.7569 | -26.3534 | 42.0666 | 42.0666 | 36.5871 | 216.5871 | 26.4591 | 411.8865 | 411.8865 | 174.7395 | 586.626 | 0.60197 | 60.2% | 265.2723 | 159.6848 | 111.7794 | 149.744 | 149.744 | 74.65% | 11.37% | 11.37% | 90% | 10.23% | 27.15 | 5.2884 | 5.2884 | 143.5787 | 60.0397 | 95.88% | 95.88%
4 | 92 | 2 | 2199 | 15 | 18 | 223.33 | 169.44 | 392.77 | 169.44 | 84.72 | 92 | 2199 | 900 | 90.7397 | 4.5894 | 11.1297 | 874.284 | 14.7569 | -41.3534 | 34.8007 | 34.8007 | 53.3247 | 233.3247 | 41.3781 | 293.6255 | 293.6255 | 144.6261 | 438.2516 | 0.53204 | 53.2% | 198.1774 | 105.4386 | 73.807 | 141.3226 | 141.3226 | 52.23% | 11.39% | 11.39% | 85% | 9.683% | 19.1896 | 5.3514 | 5.3514 | 102.691 | 42.436 | 72.66% | 72.66%
4 | 92 | 2 | 2200 | 16 | 18.6 | 187.14 | 176.11 | 363.25 | 176.11 | 88.06 | 92 | 2200 | 960 | 90.7397 | 4.5894 | 11.1297 | 934.284 | 15.7569 | -56.3534 | 25.8828 | 25.8828 | 67.2678 | 247.2678 | 56.3231 | 237.7167 | 237.7167 | 150.3193 | 388.036 | 0.50029 | 50.03% | 175.4699 | 87.7851 | 61.4496 | 139.17 | 139.17 | 44.15% | 11.38% | 11.38% | 85% | 9.676% | 16.9788 | 5.2259 | 5.2259 | 88.7299 | 37.547 | 63.76% | 63.76%
4 | 92 | 2 | 2201 | 17 | 18.6 | 119.53 | 117.58 | 237.11 | 117.58 | 58.79 | 92 | 2201 | 1020 | 90.7397 | 4.5894 | 11.1297 | 994.284 | 16.7569 | -71.3534 | 16.0553 | 16.0553 | 79.3594 | 259.3594 | 71.2745 | 138.7495 | 138.7495 | 100.3608 | 239.1103 | 0.31112 | 31.11% | 108.1257 | 33.6404 | 23.5483 | 130.6628 | 130.6628 | 18.02% | 11.4% | 11.4% | 80% | 9.116% | 9.8569 | 5.2259 | 5.2259 | 51.5116 | 21.7977 | 39.42% | 39.42%
4 | 92 | 2 | 2202 | 18 | 17.7 | 64.64 | 80.92 | 145.56 | 80.92 | 40.46 | 92 | 2202 | 1080 | 90.7397 | 4.5894 | 11.1297 | 1054.284 | 17.7569 | -86.3534 | 5.8384 | 5.8384 | 90.4952 | 270.4952 | 86.2243 | 0 | 0 | 69.0695 | 69.0695 | -0.93128 | 0% | 31.2332 | 0 | 0 | 163.191 | 163.191 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2203 | 19 | 16.7 | 12.97 | 33.61 | 46.58 | 33.61 | 16.81 | 92 | 2203 | 1140 | 90.7397 | 4.5894 | 11.1297 | 1114.284 | 18.7569 | -101.3534 | -4.3631 | 0 | 96.7097 | 276.7097 | 94.739 | 0 | 0 | 28.6879 | 28.6879 | -3.4519 | 0% | 12.9727 | 0 | 0 | 152.593 | 152.593 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2204 | 20 | 13.8 | 0 | 2.58 | 2.58 | 2.58 | 1.29 | 92 | 2204 | 1200 | 90.7397 | 4.5894 | 11.1297 | 1174.284 | 19.7569 | -116.3534 | -14.1652 | 0 | 96.7097 | 276.7097 | 94.739 | 0 | 0 | 2.2022 | 2.2022 | -57.6208 | 0% | 0.99582 | 0 | 0 | 139.6174 | 139.6174 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2205 | 21 | 12.8 | 0 | 0 | 0 | 0 | 0 | 92 | 2205 | 1260 | 90.7397 | 4.5894 | 11.1297 | 1234.284 | 20.7569 | -131.3534 | -23.1232 | 0 | 96.7097 | 276.7097 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3941 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2206 | 22 | 11.3 | 0 | 0 | 0 | 0 | 0 | 92 | 2206 | 1320 | 90.7397 | 4.5894 | 11.1297 | 1294.284 | 21.7569 | -146.3534 | -30.6614 | 0 | 96.7097 | 276.7097 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9703 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2207 | 23 | 9.8 | 0 | 0 | 0 | 0 | 0 | 92 | 2207 | 1380 | 90.7397 | 4.5894 | 11.1297 | 1354.284 | 22.7569 | -161.3534 | -36.0501 | 0 | 96.7097 | 276.7097 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7797 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
4 | 92 | 2 | 2208 | 24 | 9.3 | 0 | 0 | 0 | 0 | 0 | 92 | 2208 | 1440 | 90.7397 | 4.5894 | 11.1297 | 1414.284 | 23.7569 | -176.3534 | -38.5313 | 0 | 96.7097 | 276.7097 | 94.739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0652 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2209 | 1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 93 | 2209 | 60 | 91.726 | 4.9843 | 11.4489 | 34.284 | 0.76221 | 168.5668 | -37.2567 | 0 | 97.2887 | 82.7113 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4691 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2210 | 2 | 7.7 | 0 | 0 | 0 | 0 | 0 | 93 | 2210 | 120 | 91.726 | 4.9843 | 11.4489 | 94.284 | 1.7622 | 153.5668 | -33.2025 | 0 | 97.2887 | 82.7113 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3652 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2211 | 3 | 7.2 | 0 | 0 | 0 | 0 | 0 | 93 | 2211 | 180 | 91.726 | 4.9843 | 11.4489 | 154.284 | 2.7622 | 138.5668 | -26.627 | 0 | 97.2887 | 82.7113 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.633 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2212 | 4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 93 | 2212 | 240 | 91.726 | 4.9843 | 11.4489 | 214.284 | 3.7622 | 123.5668 | -18.2946 | 0 | 97.2887 | 82.7113 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1946 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2213 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 93 | 2213 | 300 | 91.726 | 4.9843 | 11.4489 | 274.284 | 4.7622 | 108.5668 | -8.8541 | 0 | 97.2887 | 82.7113 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.5435 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2214 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 93 | 2214 | 360 | 91.726 | 4.9843 | 11.4489 | 334.284 | 5.7622 | 93.5668 | 1.1958 | 1.1958 | 96.009 | 83.991 | 93.3968 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.7045 | 7.7045 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2215 | 7 | 7.8 | 0.56 | 3.33 | 3.89 | 3.33 | 1.67 | 93 | 2215 | 420 | 91.726 | 4.9843 | 11.4489 | 394.284 | 6.7622 | 78.5668 | 11.4521 | 11.4521 | 85.0598 | 94.9402 | 78.4586 | 0.56431 | 0.56431 | 2.8423 | 3.4066 | -41.0574 | 0% | 1.5405 | 0 | 0 | 170.1465 | 170.1465 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2216 | 8 | 8.2 | 35.19 | 48.53 | 83.72 | 48.53 | 24.27 | 93 | 2216 | 480 | 91.726 | 4.9843 | 11.4489 | 454.284 | 7.7622 | 63.5668 | 21.5315 | 21.5315 | 73.5344 | 106.4656 | 63.5157 | 42.759 | 42.759 | 41.4229 | 84.1819 | -0.87881 | 0% | 38.0671 | 0 | 0 | 183.3253 | 183.3253 | 0% | 11.82% | 11.82% | 80% | 9.453% | 3.5986 | 7.7573 | 6 | 21.5914 | 7.9579 | 11.78% | 11.78%
4 | 93 | 3 | 2217 | 9 | 8.2 | 87.14 | 97.42 | 184.56 | 97.42 | 48.71 | 93 | 2217 | 540 | 91.726 | 4.9843 | 11.4489 | 514.284 | 8.7622 | 48.5668 | 30.9828 | 30.9828 | 60.5975 | 119.4025 | 48.5763 | 111.9969 | 111.9969 | 83.1532 | 195.15 | 0.078086 | 7.809% | 88.2468 | 6.8908 | 4.8236 | 167.9224 | 167.9224 | 2.872% | 11.74% | 11.74% | 80% | 9.396% | 8.2914 | 7.7573 | 6 | 49.7481 | 18.3356 | 29.63% | 29.63%
4 | 93 | 3 | 2218 | 10 | 10 | 147.14 | 161.03 | 308.17 | 161.03 | 80.52 | 93 | 2218 | 600 | 91.726 | 4.9843 | 11.4489 | 574.284 | 9.7622 | 33.5668 | 39.1816 | 39.1816 | 45.2836 | 134.7164 | 33.6553 | 193.8606 | 193.8606 | 137.4477 | 331.3083 | 0.38917 | 38.92% | 149.8176 | 58.3041 | 40.8129 | 153.2995 | 153.2995 | 26.62% | 11.61% | 11.61% | 85% | 9.868% | 14.7845 | 7.265 | 6 | 88.7068 | 32.6945 | 57.87% | 57.87%
4 | 93 | 3 | 2219 | 11 | 12.5 | 302.14 | 213.06 | 515.2 | 213.06 | 106.53 | 93 | 2219 | 660 | 91.726 | 4.9843 | 11.4489 | 634.284 | 10.7622 | 18.5668 | 45.2383 | 45.2383 | 26.7741 | 153.2259 | 18.8071 | 402.8057 | 402.8057 | 181.8581 | 584.6637 | 0.57884 | 57.88% | 264.3849 | 153.037 | 107.1259 | 159.3874 | 159.3874 | 67.21% | 11.44% | 11.44% | 90% | 10.3% | 27.223 | 6.6189 | 6 | 163.3382 | 60.2013 | 102.5% | 102.5%
4 | 93 | 3 | 2220 | 12 | 13.1 | 364.08 | 238.53 | 602.61 | 238.53 | 119.27 | 93 | 2220 | 720 | 91.726 | 4.9843 | 11.4489 | 694.284 | 11.7622 | 3.5668 | 48.0928 | 48.0928 | 5.3241 | 174.6759 | 4.7911 | 487.4956 | 487.4956 | 203.5981 | 691.0937 | 0.61551 | 61.55% | 312.5126 | 192.355 | 134.6485 | 153.1224 | 153.1224 | 87.94% | 11.39% | 11.39% | 90% | 10.25% | 32.045 | 6.4703 | 6 | 192.2702 | 70.8647 | 125.6% | 125.6%
4 | 93 | 3 | 2221 | 13 | 14.3 | 321.31 | 225.36 | 546.67 | 225.36 | 112.68 | 93 | 2221 | 780 | 91.726 | 4.9843 | 11.4489 | 754.284 | 12.7622 | -11.4332 | 47.0553 | 47.0553 | 16.8493 | 196.8493 | 11.8536 | 429.5811 | 429.5811 | 192.3568 | 621.9378 | 0.59896 | 59.9% | 281.2403 | 168.4523 | 117.9166 | 149.8375 | 149.8375 | 78.7% | 11.41% | 11.41% | 90% | 10.27% | 28.8751 | 6.1808 | 6 | 173.2503 | 63.8546 | 115.6% | 115.6%
4 | 93 | 3 | 2222 | 14 | 14 | 300.28 | 217.58 | 517.86 | 217.58 | 108.79 | 93 | 2222 | 840 | 91.726 | 4.9843 | 11.4489 | 814.284 | 13.7622 | -26.4332 | 42.3939 | 42.3939 | 36.9043 | 216.9043 | 26.577 | 398.3105 | 398.3105 | 185.7161 | 584.0267 | 0.58448 | 58.45% | 264.0969 | 154.3597 | 108.0518 | 146.6319 | 146.6319 | 73.69% | 11.42% | 11.42% | 90% | 10.28% | 27.1517 | 6.2522 | 6 | 162.9099 | 60.0435 | 111.1% | 111.1%
4 | 93 | 3 | 2223 | 15 | 11.5 | 231.75 | 223.81 | 455.56 | 223.81 | 111.91 | 93 | 2223 | 900 | 91.726 | 4.9843 | 11.4489 | 874.284 | 14.7622 | -41.4332 | 35.0859 | 35.0859 | 53.6717 | 233.6717 | 41.4764 | 302.0745 | 302.0745 | 191.0338 | 493.1083 | 0.53236 | 53.24% | 222.9836 | 118.7066 | 83.0946 | 137.467 | 137.467 | 60.45% | 11.5% | 11.5% | 85% | 9.771% | 21.7881 | 6.8721 | 6 | 130.7284 | 48.1824 | 95.1% | 95.1%
4 | 93 | 3 | 2224 | 16 | 9.6 | 209.25 | 214.44 | 423.69 | 214.44 | 107.22 | 93 | 2224 | 960 | 91.726 | 4.9843 | 11.4489 | 934.284 | 15.7622 | -56.4332 | 26.1375 | 26.1375 | 67.615 | 247.615 | 56.4099 | 262.7925 | 262.7925 | 183.036 | 445.8285 | 0.49363 | 49.36% | 201.6036 | 99.5173 | 69.6621 | 131.3649 | 131.3649 | 53.03% | 11.55% | 11.55% | 85% | 9.821% | 19.8003 | 7.3724 | 6 | 118.8018 | 43.7866 | 90.44% | 90.44%
4 | 93 | 3 | 2225 | 17 | 7.7 | 144.53 | 140.19 | 284.72 | 140.19 | 70.1 | 93 | 2225 | 1020 | 91.726 | 4.9843 | 11.4489 | 994.284 | 16.7622 | -71.4332 | 16.2926 | 16.2926 | 79.6983 | 259.6983 | 71.3523 | 164.7279 | 164.7279 | 119.6596 | 284.3875 | 0.30172 | 30.17% | 128.6 | 38.8006 | 27.1604 | 119.3261 | 119.3261 | 22.76% | 11.7% | 11.7% | 80% | 9.361% | 12.0378 | 7.8981 | 6 | 72.2268 | 26.6205 | 60.53% | 60.53%
4 | 93 | 3 | 2226 | 18 | 7.5 | 68.81 | 86.03 | 154.84 | 86.03 | 43.02 | 93 | 2226 | 1080 | 91.726 | 4.9843 | 11.4489 | 1054.284 | 17.7622 | -86.4332 | 6.0707 | 6.0707 | 90.8261 | 270.8261 | 86.2937 | 0 | 0 | 73.4312 | 73.4312 | -1.1477 | 0% | 33.2056 | 0 | 0 | 108.6664 | 108.6664 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2227 | 19 | 6.7 | 10.83 | 32.86 | 43.69 | 32.86 | 16.43 | 93 | 2227 | 1140 | 91.726 | 4.9843 | 11.4489 | 1114.284 | 18.7622 | -101.4332 | -4.1245 | 0 | 97.2887 | 277.2887 | 95.1469 | 0 | 0 | 28.0478 | 28.0478 | -4.3735 | 0% | 12.6832 | 0 | 0 | 139.1283 | 139.1283 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2228 | 20 | 6.6 | 0 | 2.78 | 2.78 | 2.78 | 1.39 | 93 | 2228 | 1200 | 91.726 | 4.9843 | 11.4489 | 1174.284 | 19.7622 | -116.4332 | -13.9095 | 0 | 97.2887 | 277.2887 | 95.1469 | 0 | 0 | 2.3729 | 2.3729 | -60.4945 | 0% | 1.073 | 0 | 0 | 130.0601 | 130.0601 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2229 | 21 | 6.3 | 0 | 0 | 0 | 0 | 0 | 93 | 2229 | 1260 | 91.726 | 4.9843 | 11.4489 | 1234.284 | 20.7622 | -131.4332 | -22.8398 | 0 | 97.2887 | 277.2887 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0481 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2230 | 22 | 6.1 | 0 | 0 | 0 | 0 | 0 | 93 | 2230 | 1320 | 91.726 | 4.9843 | 11.4489 | 1294.284 | 21.7622 | -146.4332 | -30.3417 | 0 | 97.2887 | 277.2887 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.7807 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2231 | 23 | 5.7 | 0 | 0 | 0 | 0 | 0 | 93 | 2231 | 1380 | 91.726 | 4.9843 | 11.4489 | 1354.284 | 22.7622 | -161.4332 | -35.6912 | 0 | 97.2887 | 277.2887 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.896 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
4 | 93 | 3 | 2232 | 24 | 5.4 | 0 | 0 | 0 | 0 | 0 | 93 | 2232 | 1440 | 91.726 | 4.9843 | 11.4489 | 1414.284 | 23.7622 | -176.4332 | -38.1413 | 0 | 97.2887 | 277.2887 | 95.1469 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.8589 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2233 | 1 | 5.1 | 0 | 0 | 0 | 0 | 0 | 94 | 2233 | 60 | 92.7123 | 5.3779 | 11.7606 | 34.284 | 0.76741 | 168.4889 | -36.8556 | 0 | 97.8662 | 82.1338 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0701 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2234 | 2 | 4.9 | 0 | 0 | 0 | 0 | 0 | 94 | 2234 | 120 | 92.7123 | 5.3779 | 11.7606 | 94.284 | 1.7674 | 153.4889 | -32.8076 | 0 | 97.8662 | 82.1338 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7866 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2235 | 3 | 4.9 | 0 | 0 | 0 | 0 | 0 | 94 | 2235 | 180 | 92.7123 | 5.3779 | 11.7606 | 154.284 | 2.7674 | 138.4889 | -26.2483 | 0 | 97.8662 | 82.1338 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1983 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2236 | 4 | 4.8 | 0 | 0 | 0 | 0 | 0 | 94 | 2236 | 240 | 92.7123 | 5.3779 | 11.7606 | 214.284 | 3.7674 | 123.4889 | -17.9333 | 0 | 97.8662 | 82.1338 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3507 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2237 | 5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 94 | 2237 | 300 | 92.7123 | 5.3779 | 11.7606 | 274.284 | 4.7674 | 108.4889 | -8.5063 | 0 | 97.8662 | 82.1338 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.488 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2238 | 6 | 3.9 | 0 | 0 | 0 | 0 | 0 | 94 | 2238 | 360 | 92.7123 | 5.3779 | 11.7606 | 334.284 | 5.7674 | 93.4889 | 1.5361 | 1.5361 | 96.2216 | 83.7784 | 93.3049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.6878 | 5.6878 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2239 | 7 | 3.2 | 1.03 | 5.28 | 6.31 | 5.28 | 2.64 | 94 | 2239 | 420 | 92.7123 | 5.3779 | 11.7606 | 394.284 | 6.7674 | 78.4889 | 11.792 | 11.792 | 85.2774 | 94.7226 | 78.3757 | 1.0156 | 1.0156 | 4.5068 | 5.5223 | -27.015 | 0% | 2.4972 | 0 | 0 | 169.6523 | 169.6523 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2240 | 8 | 2.8 | 32.22 | 46.47 | 78.69 | 46.47 | 23.24 | 94 | 2240 | 480 | 92.7123 | 5.3779 | 11.7606 | 454.284 | 7.7674 | 63.4889 | 21.8785 | 21.8785 | 73.7512 | 106.2488 | 63.4422 | 38.6582 | 38.6582 | 39.6646 | 78.3229 | -1.1698 | 0% | 35.4176 | 0 | 0 | 181.5936 | 181.5936 | 0% | 12.03% | 12.03% | 80% | 9.628% | 3.4099 | 9.3703 | 6 | 20.4595 | 7.5407 | 11.27% | 11.27%
4 | 94 | 4 | 2241 | 9 | 3.4 | 133.89 | 111.39 | 245.28 | 111.39 | 55.7 | 94 | 2241 | 540 | 92.7123 | 5.3779 | 11.7606 | 514.284 | 8.7674 | 48.4889 | 31.3443 | 31.3443 | 60.8008 | 119.1992 | 48.5139 | 170.5062 | 170.5062 | 95.0773 | 265.5836 | 0.22738 | 22.74% | 120.0969 | 27.3078 | 19.1155 | 149.694 | 149.694 | 12.77% | 11.84% | 11.84% | 80% | 9.472% | 11.3755 | 9.181 | 6 | 68.253 | 25.1559 | 45.6% | 45.6%
4 | 94 | 4 | 2242 | 10 | 4.6 | 220.36 | 154.81 | 375.17 | 154.81 | 77.41 | 94 | 2242 | 600 | 92.7123 | 5.3779 | 11.7606 | 574.284 | 9.7674 | 33.4889 | 39.5629 | 39.5629 | 45.4452 | 134.5548 | 33.6094 | 288.1384 | 288.1384 | 132.1386 | 420.277 | 0.44652 | 44.65% | 190.0492 | 84.8602 | 59.4022 | 154.2299 | 154.2299 | 38.52% | 11.67% | 11.67% | 85% | 9.923% | 18.8578 | 8.8099 | 6 | 113.1467 | 41.7023 | 73.36% | 73.36%
4 | 94 | 4 | 2243 | 11 | 6 | 327.69 | 200.08 | 527.77 | 200.08 | 100.04 | 94 | 2243 | 660 | 92.7123 | 5.3779 | 11.7606 | 634.284 | 10.7674 | 18.4889 | 45.6366 | 45.6366 | 26.8429 | 153.1571 | 18.7974 | 433.9127 | 433.9127 | 170.779 | 604.6916 | 0.56109 | 56.11% | 273.4416 | 153.4258 | 107.398 | 154.5505 | 154.5505 | 69.49% | 11.5% | 11.5% | 90% | 10.35% | 28.3071 | 8.3898 | 6 | 169.8425 | 62.5986 | 109.9% | 109.9%
4 | 94 | 4 | 2244 | 12 | 7.4 | 330.75 | 211.58 | 542.33 | 211.58 | 105.79 | 94 | 2244 | 720 | 92.7123 | 5.3779 | 11.7606 | 694.284 | 11.7674 | 3.4889 | 48.4906 | 48.4906 | 5.2452 | 174.7548 | 5.008 | 439.9931 | 439.9931 | 180.5948 | 620.5879 | 0.57268 | 57.27% | 280.6298 | 160.7114 | 112.498 | 144.6392 | 144.6392 | 77.78% | 11.48% | 11.48% | 90% | 10.33% | 28.9854 | 7.9834 | 6 | 173.9125 | 64.0987 | 120.2% | 120.2%
4 | 94 | 4 | 2245 | 13 | 8.7 | 331.67 | 168.89 | 500.56 | 168.89 | 84.45 | 94 | 2245 | 780 | 92.7123 | 5.3779 | 11.7606 | 754.284 | 12.7674 | -11.5111 | 47.4253 | 47.4253 | 17.0776 | 197.0776 | 12.0376 | 440.4922 | 440.4922 | 144.1566 | 584.6489 | 0.56371 | 56.37% | 264.3782 | 149.0331 | 104.3232 | 141.2194 | 141.2194 | 73.87% | 11.49% | 11.49% | 90% | 10.34% | 27.3295 | 7.6183 | 6 | 163.9767 | 60.4367 | 116.1% | 116.1%
4 | 94 | 4 | 2246 | 14 | 10 | 244.92 | 172.5 | 417.42 | 172.5 | 86.25 | 94 | 2246 | 840 | 92.7123 | 5.3779 | 11.7606 | 814.284 | 13.7674 | -26.5111 | 42.72 | 42.72 | 37.2217 | 217.2217 | 26.6979 | 322.5284 | 322.5284 | 147.238 | 469.7664 | 0.51143 | 51.14% | 212.4284 | 108.6432 | 76.0502 | 137.8546 | 137.8546 | 55.17% | 11.53% | 11.53% | 85% | 9.804% | 20.8256 | 7.265 | 6 | 124.9536 | 46.0539 | 90.64% | 90.64%
4 | 94 | 4 | 2247 | 15 | 10.4 | 244.64 | 178.06 | 422.7 | 178.06 | 89.03 | 94 | 2247 | 900 | 92.7123 | 5.3779 | 11.7606 | 874.284 | 14.7674 | -41.5111 | 35.3702 | 35.3702 | 54.0182 | 234.0182 | 41.5757 | 316.1577 | 316.1577 | 151.9837 | 468.1414 | 0.51241 | 51.24% | 211.6935 | 108.4742 | 75.932 | 135.6212 | 135.6212 | 55.99% | 11.53% | 11.53% | 85% | 9.798% | 20.742 | 7.1587 | 6 | 124.4522 | 45.8691 | 91.76% | 91.76%
4 | 94 | 4 | 2248 | 16 | 11.4 | 196.31 | 169.08 | 365.39 | 169.08 | 84.54 | 94 | 2248 | 960 | 92.7123 | 5.3779 | 11.7606 | 934.284 | 15.7674 | -56.5111 | 26.3917 | 26.3917 | 67.9612 | 247.9612 | 56.4964 | 243.7792 | 243.7792 | 144.3188 | 388.098 | 0.45826 | 45.83% | 175.4979 | 80.4234 | 56.2964 | 132.4351 | 132.4351 | 42.51% | 11.55% | 11.55% | 85% | 9.815% | 17.2248 | 6.8978 | 6 | 103.3487 | 38.0911 | 78.04% | 78.04%
4 | 94 | 4 | 2249 | 17 | 11.6 | 105.19 | 107.42 | 212.61 | 107.42 | 53.71 | 94 | 2249 | 1020 | 92.7123 | 5.3779 | 11.7606 | 994.284 | 16.7674 | -71.5111 | 16.5298 | 16.5298 | 80.0356 | 260.0356 | 71.429 | 117.7478 | 117.7478 | 91.6887 | 209.4365 | 0.16553 | 16.55% | 94.7072 | 15.677 | 10.9739 | 122.6293 | 122.6293 | 8.949% | 11.62% | 11.62% | 80% | 9.3% | 8.8076 | 6.8464 | 6 | 52.8459 | 19.4773 | 43.09% | 43.09%
4 | 94 | 4 | 2250 | 18 | 10.7 | 55.36 | 70.08 | 125.44 | 70.08 | 35.04 | 94 | 2250 | 1080 | 92.7123 | 5.3779 | 11.7606 | 1054.284 | 17.7674 | -86.5111 | 6.3032 | 6.3032 | 91.155 | 271.155 | 86.3613 | 0 | 0 | 59.817 | 59.817 | -1.4664 | 0% | 27.0493 | 0 | 0 | 154.9077 | 154.9077 | 0% | 11.73% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2251 | 19 | 9.1 | 10.92 | 25.64 | 36.56 | 25.64 | 12.82 | 94 | 2251 | 1140 | 92.7123 | 5.3779 | 11.7606 | 1114.284 | 18.7674 | -101.5111 | -3.8855 | 0 | 97.8662 | 277.8662 | 95.5534 | 0 | 0 | 21.8851 | 21.8851 | -5.5722 | 0% | 9.8964 | 0 | 0 | 143.7346 | 143.7346 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2252 | 20 | 8.7 | 0 | 2.64 | 2.64 | 2.64 | 1.32 | 94 | 2252 | 1200 | 92.7123 | 5.3779 | 11.7606 | 1174.284 | 19.7674 | -116.5111 | -13.6532 | 0 | 97.8662 | 277.8662 | 95.5534 | 0 | 0 | 2.2534 | 2.2534 | -61.5398 | 0% | 1.019 | 0 | 0 | 134.6385 | 134.6385 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2253 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 94 | 2253 | 1260 | 92.7123 | 5.3779 | 11.7606 | 1234.284 | 20.7674 | -131.5111 | -22.5559 | 0 | 97.8662 | 277.8662 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0219 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2254 | 22 | 7.8 | 0 | 0 | 0 | 0 | 0 | 94 | 2254 | 1320 | 92.7123 | 5.3779 | 11.7606 | 1294.284 | 21.7674 | -146.5111 | -30.0218 | 0 | 97.8662 | 277.8662 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7202 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2255 | 23 | 6.7 | 0 | 0 | 0 | 0 | 0 | 94 | 2255 | 1380 | 92.7123 | 5.3779 | 11.7606 | 1354.284 | 22.7674 | -161.5111 | -35.3327 | 0 | 97.8662 | 277.8662 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8083 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
4 | 94 | 4 | 2256 | 24 | 6.9 | 0 | 0 | 0 | 0 | 0 | 94 | 2256 | 1440 | 92.7123 | 5.3779 | 11.7606 | 1414.284 | 23.7674 | -176.5111 | -37.7524 | 0 | 97.8662 | 277.8662 | 95.5534 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9152 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2257 | 1 | 5.6 | 0 | 0 | 0 | 0 | 0 | 95 | 2257 | 60 | 93.6986 | 5.7701 | 12.0645 | 34.284 | 0.77247 | 168.4129 | -36.4563 | 0 | 98.4419 | 81.5581 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4266 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2258 | 2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 95 | 2258 | 120 | 93.6986 | 5.7701 | 12.0645 | 94.284 | 1.7725 | 153.4129 | -32.4148 | 0 | 98.4419 | 81.5581 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.3657 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2259 | 3 | 4.1 | 0 | 0 | 0 | 0 | 0 | 95 | 2259 | 180 | 93.6986 | 5.7701 | 12.0645 | 154.284 | 2.7725 | 138.4129 | -25.8717 | 0 | 98.4419 | 81.5581 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.8476 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2260 | 4 | 3.5 | 0 | 0 | 0 | 0 | 0 | 95 | 2260 | 240 | 93.6986 | 5.7701 | 12.0645 | 214.284 | 3.7725 | 123.4129 | -17.5741 | 0 | 98.4419 | 81.5581 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.762 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2261 | 5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 95 | 2261 | 300 | 93.6986 | 5.7701 | 12.0645 | 274.284 | 4.7725 | 108.4129 | -8.1609 | 0 | 98.4419 | 81.5581 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8001 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2262 | 6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 95 | 2262 | 360 | 93.6986 | 5.7701 | 12.0645 | 334.284 | 5.7725 | 93.4129 | 1.8739 | 1.8739 | 96.4347 | 83.5653 | 93.2149 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.0395 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2263 | 7 | 2.2 | 0.75 | 4.17 | 4.92 | 4.17 | 2.09 | 95 | 2263 | 420 | 93.6986 | 5.7701 | 12.0645 | 394.284 | 6.7725 | 78.4129 | 12.1293 | 12.1293 | 85.4961 | 94.5039 | 78.2956 | 0.7241 | 0.7241 | 3.5593 | 4.2834 | -35.6291 | 0% | 1.937 | 0 | 0 | 160.4729 | 160.4729 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2264 | 8 | 2.6 | 19.92 | 41.19 | 61.11 | 41.19 | 20.6 | 95 | 2264 | 480 | 93.6986 | 5.7701 | 12.0645 | 454.284 | 7.7725 | 63.4129 | 22.2228 | 22.2228 | 73.9696 | 106.0304 | 63.372 | 23.6061 | 23.6061 | 35.1579 | 58.764 | -1.8351 | 0% | 26.5731 | 0 | 0 | 171.24 | 171.24 | 0% | 12.06% | 12.06% | 80% | 9.649% | 2.5641 | 9.4339 | 6 | 15.3844 | 5.6702 | 8.984% | 8.984%
4 | 95 | 5 | 2265 | 9 | 3.4 | 65.47 | 83.89 | 149.36 | 83.89 | 41.95 | 95 | 2265 | 540 | 93.6986 | 5.7701 | 12.0645 | 514.284 | 8.7725 | 48.4129 | 31.7032 | 31.7032 | 61.0065 | 118.9935 | 48.4559 | 82.6221 | 82.6221 | 71.6046 | 154.2267 | -0.18896 | 0% | 69.7413 | 0 | 0 | 156.7214 | 156.7214 | 0% | 11.94% | 11.94% | 80% | 9.553% | 6.6626 | 9.181 | 6 | 39.9755 | 14.7337 | 25.51% | 25.51%
4 | 95 | 5 | 2266 | 10 | 6.1 | 202.22 | 111.86 | 314.08 | 111.86 | 55.93 | 95 | 2266 | 600 | 93.6986 | 5.7701 | 12.0645 | 574.284 | 9.7725 | 33.4129 | 39.9417 | 39.9417 | 45.61 | 134.39 | 33.5697 | 262.4464 | 262.4464 | 95.4785 | 357.9249 | 0.39429 | 39.43% | 161.8537 | 63.8171 | 44.6719 | 146.0433 | 146.0433 | 30.59% | 11.69% | 11.69% | 85% | 9.936% | 16.0825 | 8.3603 | 6 | 96.4953 | 35.5651 | 66.07% | 66.07%
4 | 95 | 5 | 2267 | 11 | 7.6 | 286.94 | 121.11 | 408.05 | 121.11 | 60.56 | 95 | 2267 | 660 | 93.6986 | 5.7701 | 12.0645 | 634.284 | 10.7725 | 18.4129 | 46.0328 | 46.0328 | 26.9149 | 153.0851 | 18.7976 | 377.409 | 377.409 | 103.3739 | 480.7828 | 0.5064 | 50.64% | 217.41 | 110.0968 | 77.0678 | 145.7017 | 145.7017 | 52.89% | 11.57% | 11.57% | 85% | 9.834% | 21.3806 | 7.9264 | 6 | 128.2839 | 47.2814 | 88.05% | 88.05%
4 | 95 | 5 | 2268 | 12 | 9.4 | 367.14 | 116.03 | 483.17 | 116.03 | 58.02 | 95 | 2268 | 720 | 93.6986 | 5.7701 | 12.0645 | 694.284 | 11.7725 | 3.4129 | 48.8867 | 48.8867 | 5.168 | 174.832 | 5.2469 | 485.2619 | 485.2619 | 99.0378 | 584.2997 | 0.56638 | 56.64% | 264.2203 | 149.6493 | 104.7545 | 141.461 | 141.461 | 74.05% | 11.48% | 11.48% | 90% | 10.33% | 27.2939 | 7.4266 | 6 | 163.7634 | 60.358 | 115.8% | 115.8%
4 | 95 | 5 | 2269 | 13 | 10.5 | 404.72 | 122.42 | 527.14 | 122.42 | 61.21 | 95 | 2269 | 780 | 93.6986 | 5.7701 | 12.0645 | 754.284 | 12.7725 | -11.5871 | 47.794 | 47.794 | 17.3057 | 197.3057 | 12.2295 | 533.9783 | 533.9783 | 104.492 | 638.4703 | 0.59057 | 59.06% | 288.7163 | 170.5058 | 119.3541 | 142.7527 | 142.7527 | 83.61% | 11.44% | 11.44% | 90% | 10.29% | 29.7169 | 7.1323 | 6 | 178.3012 | 65.7162 | 124.9% | 124.9%
4 | 95 | 5 | 2270 | 14 | 9.8 | 408.81 | 128.33 | 537.14 | 128.33 | 64.17 | 95 | 2270 | 840 | 93.6986 | 5.7701 | 12.0645 | 814.284 | 13.7725 | -26.5871 | 43.0447 | 43.0447 | 37.539 | 217.539 | 26.8217 | 534.4925 | 534.4925 | 109.5365 | 644.029 | 0.58987 | 58.99% | 291.2299 | 171.7883 | 120.2518 | 141.1587 | 141.1587 | 85.19% | 11.44% | 11.44% | 90% | 10.3% | 29.9837 | 7.3186 | 6 | 179.9023 | 66.3063 | 127.4% | 127.4%
4 | 95 | 5 | 2271 | 15 | 9.5 | 380.47 | 131.94 | 512.41 | 131.94 | 65.97 | 95 | 2271 | 900 | 93.6986 | 5.7701 | 12.0645 | 874.284 | 14.7725 | -41.5871 | 35.6535 | 35.6535 | 54.3642 | 234.3642 | 41.6758 | 487.5436 | 487.5436 | 112.6178 | 600.1615 | 0.57305 | 57.31% | 271.393 | 155.522 | 108.8654 | 137.8714 | 137.8714 | 78.96% | 11.47% | 11.47% | 90% | 10.32% | 28.0096 | 7.3995 | 6 | 168.0574 | 61.9407 | 121.9% | 121.9%
4 | 95 | 5 | 2272 | 16 | 8.9 | 323.42 | 119.36 | 442.78 | 119.36 | 59.68 | 95 | 2272 | 960 | 93.6986 | 5.7701 | 12.0645 | 934.284 | 15.7725 | -56.5871 | 26.6452 | 26.6452 | 68.3061 | 248.3061 | 56.5826 | 397.1741 | 397.1741 | 101.8801 | 499.0543 | 0.52344 | 52.34% | 225.6723 | 118.1262 | 82.6883 | 132.91 | 132.91 | 62.21% | 11.54% | 11.54% | 85% | 9.805% | 22.128 | 7.5632 | 6 | 132.768 | 48.9341 | 99.89% | 99.89%
4 | 95 | 5 | 2273 | 17 | 7.7 | 212.69 | 87.58 | 300.27 | 87.58 | 43.79 | 95 | 2273 | 1020 | 93.6986 | 5.7701 | 12.0645 | 994.284 | 16.7725 | -71.5871 | 16.7668 | 16.7668 | 80.3712 | 260.3712 | 71.5045 | 233.8889 | 233.8889 | 74.7542 | 308.6431 | 0.34119 | 34.12% | 139.5684 | 47.6192 | 33.3334 | 122.2571 | 122.2571 | 27.27% | 11.68% | 11.68% | 85% | 9.932% | 13.8616 | 7.8981 | 6 | 83.1695 | 30.6536 | 68.03% | 68.03%
4 | 95 | 5 | 2274 | 18 | 7.5 | 127.86 | 55.75 | 183.61 | 55.75 | 27.88 | 95 | 2274 | 1080 | 93.6986 | 5.7701 | 12.0645 | 1054.284 | 17.7725 | -86.5871 | 6.5358 | 6.5358 | 91.4817 | 271.4817 | 86.427 | 0 | 0 | 47.5856 | 47.5856 | -2.2078 | 0% | 21.5182 | 0 | 0 | 112.6282 | 112.6282 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2275 | 19 | 7.3 | 27.78 | 33.33 | 61.11 | 33.33 | 16.67 | 95 | 2275 | 1140 | 93.6986 | 5.7701 | 12.0645 | 1114.284 | 18.7725 | -101.5871 | -3.6461 | 0 | 98.4419 | 278.4419 | 95.9585 | 0 | 0 | 28.4489 | 28.4489 | -4.2503 | 0% | 12.8646 | 0 | 0 | 143.19 | 143.19 | 0% | 11.89% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2276 | 20 | 6.4 | 0 | 3.06 | 3.06 | 3.06 | 1.53 | 95 | 2276 | 1200 | 93.6986 | 5.7701 | 12.0645 | 1174.284 | 19.7725 | -116.5871 | -13.3963 | 0 | 98.4419 | 278.4419 | 95.9585 | 0 | 0 | 2.6119 | 2.6119 | -55.0679 | 0% | 1.1811 | 0 | 0 | 131.5645 | 131.5645 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2277 | 21 | 5.9 | 0 | 0 | 0 | 0 | 0 | 95 | 2277 | 1260 | 93.6986 | 5.7701 | 12.0645 | 1234.284 | 20.7725 | -131.5871 | -22.2714 | 0 | 98.4419 | 278.4419 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.868 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2278 | 22 | 5.1 | 0 | 0 | 0 | 0 | 0 | 95 | 2278 | 1320 | 93.6986 | 5.7701 | 12.0645 | 1294.284 | 21.7725 | -146.5871 | -29.7016 | 0 | 98.4419 | 278.4419 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4861 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2279 | 23 | 4.2 | 0 | 0 | 0 | 0 | 0 | 95 | 2279 | 1380 | 93.6986 | 5.7701 | 12.0645 | 1354.284 | 22.7725 | -161.5871 | -34.9746 | 0 | 98.4419 | 278.4419 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4252 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
4 | 95 | 5 | 2280 | 24 | 3.6 | 0 | 0 | 0 | 0 | 0 | 95 | 2280 | 1440 | 93.6986 | 5.7701 | 12.0645 | 1414.284 | 23.7725 | -176.5871 | -37.3647 | 0 | 98.4419 | 278.4419 | 95.9585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9071 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2281 | 1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 96 | 2281 | 60 | 94.6849 | 6.1608 | 12.3601 | 34.284 | 0.7774 | 168.339 | -36.0588 | 0 | 99.0159 | 80.9841 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0412 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2282 | 2 | 2.2 | 0 | 0 | 0 | 0 | 0 | 96 | 2282 | 120 | 94.6849 | 6.1608 | 12.3601 | 94.284 | 1.7774 | 153.339 | -32.0241 | 0 | 99.0159 | 80.9841 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0254 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2283 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 96 | 2283 | 180 | 94.6849 | 6.1608 | 12.3601 | 154.284 | 2.7774 | 138.339 | -25.4973 | 0 | 99.0159 | 80.9841 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7047 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2284 | 4 | 0.3 | 0 | 0 | 0 | 0 | 0 | 96 | 2284 | 240 | 94.6849 | 6.1608 | 12.3601 | 214.284 | 3.7774 | 123.339 | -17.2174 | 0 | 99.0159 | 80.9841 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5335 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2285 | 5 | -1.1 | 0 | 0 | 0 | 0 | 0 | 96 | 2285 | 300 | 94.6849 | 6.1608 | 12.3601 | 274.284 | 4.7774 | 108.339 | -7.8179 | 0 | 99.0159 | 80.9841 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5505 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2286 | 6 | -1 | 0 | 0 | 0 | 0 | 0 | 96 | 2286 | 360 | 94.6849 | 6.1608 | 12.3601 | 334.284 | 5.7774 | 93.339 | 2.2092 | 2.2092 | 96.6485 | 83.3515 | 93.127 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.483 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2287 | 7 | -0.3 | 0.28 | 4.25 | 4.53 | 4.25 | 2.13 | 96 | 2287 | 420 | 94.6849 | 6.1608 | 12.3601 | 394.284 | 6.7774 | 78.339 | 12.4638 | 12.4638 | 85.7159 | 94.2841 | 78.2181 | 0.2649 | 0.2649 | 3.6276 | 3.8925 | -40.8655 | 0% | 1.7602 | 0 | 0 | 156.3866 | 156.3866 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2288 | 8 | 0.6 | 15 | 36.47 | 51.47 | 36.47 | 18.24 | 96 | 2288 | 480 | 94.6849 | 6.1608 | 12.3601 | 454.284 | 7.7774 | 63.339 | 22.5642 | 22.5642 | 74.1898 | 105.8102 | 63.3054 | 17.5611 | 17.5611 | 31.1291 | 48.6902 | -2.4816 | 0% | 22.0177 | 0 | 0 | 166.9798 | 166.9798 | 0% | 12.15% | 12.15% | 80% | 9.723% | 2.1408 | 10.0859 | 6 | 12.8446 | 4.7341 | 7.692% | 7.692%
4 | 96 | 6 | 2289 | 9 | 1.6 | 90.36 | 79.72 | 170.08 | 79.72 | 39.86 | 96 | 2289 | 540 | 94.6849 | 6.1608 | 12.3601 | 514.284 | 8.7774 | 48.339 | 32.0591 | 32.0591 | 61.2148 | 118.7852 | 48.4024 | 113.0184 | 113.0184 | 68.0453 | 181.0637 | -0.065993 | 0% | 81.877 | 0 | 0 | 154.6008 | 154.6008 | 0% | 11.98% | 11.98% | 80% | 9.583% | 7.846 | 9.7564 | 6 | 47.0761 | 17.3508 | 30.45% | 30.45%
4 | 96 | 6 | 2290 | 10 | 4 | 169.08 | 131.31 | 300.39 | 131.31 | 65.66 | 96 | 2290 | 600 | 94.6849 | 6.1608 | 12.3601 | 574.284 | 9.7774 | 33.339 | 40.3178 | 40.3178 | 45.7781 | 134.2219 | 33.536 | 217.819 | 217.819 | 112.0801 | 329.8991 | 0.3442 | 34.42% | 149.1804 | 51.3474 | 35.9432 | 141.8239 | 141.8239 | 25.34% | 11.77% | 11.77% | 85% | 10% | 14.9193 | 8.9942 | 6 | 89.5157 | 32.9927 | 63.12% | 63.12%
4 | 96 | 6 | 2291 | 11 | 6.1 | 297.31 | 134.64 | 431.95 | 134.64 | 67.32 | 96 | 2291 | 660 | 94.6849 | 6.1608 | 12.3601 | 634.284 | 10.7774 | 18.339 | 46.4269 | 46.4269 | 26.9902 | 153.0098 | 18.8078 | 388.457 | 388.457 | 114.9224 | 503.3794 | 0.51268 | 51.27% | 227.6282 | 116.6998 | 81.6898 | 144.8033 | 144.8033 | 56.41% | 11.58% | 11.58% | 90% | 10.42% | 23.7209 | 8.3603 | 6 | 142.3253 | 52.4566 | 98.29% | 98.29%
4 | 96 | 6 | 2292 | 12 | 4 | 363.25 | 148.06 | 511.31 | 148.06 | 74.03 | 96 | 2292 | 720 | 94.6849 | 6.1608 | 12.3601 | 694.284 | 11.7774 | 3.339 | 49.2811 | 49.2811 | 5.0927 | 174.9073 | 5.5044 | 477.0625 | 477.0625 | 126.3771 | 603.4396 | 0.55263 | 55.26% | 272.8754 | 150.7982 | 105.5587 | 135.6275 | 135.6275 | 77.83% | 11.52% | 11.52% | 90% | 10.37% | 28.3039 | 8.9942 | 6 | 169.8236 | 62.5916 | 125.2% | 125.2%
4 | 96 | 6 | 2293 | 13 | 4.6 | 397.86 | 126.31 | 524.17 | 126.31 | 63.16 | 96 | 2293 | 780 | 94.6849 | 6.1608 | 12.3601 | 754.284 | 12.7774 | -11.661 | 48.161 | 48.161 | 17.5334 | 197.5334 | 12.4285 | 521.5094 | 521.5094 | 107.8123 | 629.3217 | 0.56526 | 56.53% | 284.5793 | 160.8624 | 112.6037 | 135.0661 | 135.0661 | 83.37% | 11.5% | 11.5% | 90% | 10.35% | 29.4452 | 8.8099 | 6 | 176.6709 | 65.1153 | 130.8% | 130.8%
4 | 96 | 6 | 2294 | 14 | 7.1 | 393.25 | 140.47 | 533.72 | 140.47 | 70.24 | 96 | 2294 | 840 | 94.6849 | 6.1608 | 12.3601 | 814.284 | 13.7774 | -26.661 | 43.3681 | 43.3681 | 37.8561 | 217.8561 | 26.9481 | 510.4975 | 510.4975 | 119.8986 | 630.3962 | 0.57515 | 57.52% | 285.0651 | 163.9556 | 114.7689 | 138.6461 | 138.6461 | 82.78% | 11.47% | 11.47% | 90% | 10.33% | 29.4333 | 8.0693 | 6 | 176.5996 | 65.089 | 127.4% | 127.4%
4 | 96 | 6 | 2295 | 15 | 5.2 | 366.19 | 108.81 | 475 | 108.81 | 54.41 | 96 | 2295 | 900 | 94.6849 | 6.1608 | 12.3601 | 874.284 | 14.7774 | -41.661 | 35.9357 | 35.9357 | 54.7093 | 234.7093 | 41.7766 | 465.3201 | 465.3201 | 92.8751 | 558.1953 | 0.53743 | 53.74% | 252.4159 | 135.6551 | 94.9586 | 131.5023 | 131.5023 | 72.21% | 11.55% | 11.55% | 90% | 10.39% | 26.236 | 8.6282 | 6 | 157.4158 | 58.0185 | 119.7% | 119.7%
4 | 96 | 6 | 2296 | 16 | 4.6 | 315 | 107.03 | 422.03 | 107.03 | 53.52 | 96 | 2296 | 960 | 94.6849 | 6.1608 | 12.3601 | 934.284 | 15.7774 | -56.661 | 26.8981 | 26.8981 | 68.6496 | 248.6496 | 56.6684 | 382.5941 | 382.5941 | 91.3558 | 473.95 | 0.487 | 48.7% | 214.3202 | 104.374 | 73.0618 | 127.4645 | 127.4645 | 57.32% | 11.63% | 11.63% | 85% | 9.884% | 21.1833 | 8.8099 | 6 | 127.0997 | 46.8449 | 99.71% | 99.71%
4 | 96 | 6 | 2297 | 17 | 4.7 | 226.67 | 84.53 | 311.2 | 84.53 | 42.27 | 96 | 2297 | 1020 | 94.6849 | 6.1608 | 12.3601 | 994.284 | 16.7774 | -71.661 | 17.0036 | 17.0036 | 80.7048 | 260.7048 | 71.5788 | 244.9383 | 244.9383 | 72.1509 | 317.0892 | 0.33094 | 33.09% | 143.3877 | 47.4532 | 33.2172 | 120.4981 | 120.4981 | 27.57% | 11.76% | 11.76% | 85% | 9.995% | 14.3311 | 8.7795 | 6 | 85.9863 | 31.6918 | 71.36% | 71.36%
4 | 96 | 6 | 2298 | 18 | 3.9 | 124.92 | 62.22 | 187.14 | 62.22 | 31.11 | 96 | 2298 | 1080 | 94.6849 | 6.1608 | 12.3601 | 1054.284 | 17.7774 | -86.661 | 6.7686 | 6.7686 | 91.8061 | 271.8061 | 86.4908 | 0 | 0 | 53.1081 | 53.1081 | -2.0568 | 0% | 24.0155 | 0 | 0 | 109.5716 | 109.5716 | 0% | 12.01% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2299 | 19 | 2.5 | 23.69 | 37.14 | 60.83 | 37.14 | 18.57 | 96 | 2299 | 1140 | 94.6849 | 6.1608 | 12.3601 | 1114.284 | 18.7774 | -101.661 | -3.4062 | 0 | 99.0159 | 279.0159 | 96.362 | 0 | 0 | 31.701 | 31.701 | -4.0958 | 0% | 14.3352 | 0 | 0 | 137.9308 | 137.9308 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2300 | 20 | 1.1 | 0 | 3.53 | 3.53 | 3.53 | 1.77 | 96 | 2300 | 1200 | 94.6849 | 6.1608 | 12.3601 | 1174.284 | 19.7774 | -116.661 | -13.1388 | 0 | 99.0159 | 279.0159 | 96.362 | 0 | 0 | 3.013 | 3.013 | -51.8835 | 0% | 1.3625 | 0 | 0 | 125.8358 | 125.8358 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2301 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 2301 | 1260 | 94.6849 | 6.1608 | 12.3601 | 1234.284 | 20.7774 | -131.661 | -21.9864 | 0 | 99.0159 | 279.0159 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5346 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2302 | 22 | -0.8 | 0 | 0 | 0 | 0 | 0 | 96 | 2302 | 1320 | 94.6849 | 6.1608 | 12.3601 | 1294.284 | 21.7774 | -146.661 | -29.3813 | 0 | 99.0159 | 279.0159 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.1471 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2303 | 23 | -1.7 | 0 | 0 | 0 | 0 | 0 | 96 | 2303 | 1380 | 94.6849 | 6.1608 | 12.3601 | 1354.284 | 22.7774 | -161.661 | -34.617 | 0 | 99.0159 | 279.0159 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.1313 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
4 | 96 | 6 | 2304 | 24 | -2 | 0 | 0 | 0 | 0 | 0 | 96 | 2304 | 1440 | 94.6849 | 6.1608 | 12.3601 | 1414.284 | 23.7774 | -176.661 | -36.9783 | 0 | 99.0159 | 279.0159 | 96.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.201 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2305 | 1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 97 | 2305 | 60 | 95.6712 | 6.5497 | 12.6472 | 34.284 | 0.78219 | 168.2672 | -35.6634 | 0 | 99.5879 | 80.4121 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.585 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2306 | 2 | -2 | 0 | 0 | 0 | 0 | 0 | 97 | 2306 | 120 | 95.6712 | 6.5497 | 12.6472 | 94.284 | 1.7822 | 153.2672 | -31.6357 | 0 | 99.5879 | 80.4121 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1498 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2307 | 3 | -2.6 | 0 | 0 | 0 | 0 | 0 | 97 | 2307 | 180 | 95.6712 | 6.5497 | 12.6472 | 154.284 | 2.7822 | 138.2672 | -25.1254 | 0 | 99.5879 | 80.4121 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.391 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2308 | 4 | -2.4 | 0 | 0 | 0 | 0 | 0 | 97 | 2308 | 240 | 95.6712 | 6.5497 | 12.6472 | 214.284 | 3.7822 | 123.2672 | -16.8631 | 0 | 99.5879 | 80.4121 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0862 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2309 | 5 | -2.3 | 0 | 0 | 0 | 0 | 0 | 97 | 2309 | 300 | 95.6712 | 6.5497 | 12.6472 | 274.284 | 4.7822 | 108.2672 | -7.4775 | 0 | 99.5879 | 80.4121 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.4239 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2310 | 6 | -2.7 | 0 | 0 | 0 | 0 | 0 | 97 | 2310 | 360 | 95.6712 | 6.5497 | 12.6472 | 334.284 | 5.7822 | 93.2672 | 2.5416 | 2.5416 | 96.8628 | 83.1372 | 93.0412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.3301 | 6.3301 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2311 | 7 | -2.9 | 1.47 | 8.06 | 9.53 | 8.06 | 4.03 | 97 | 2311 | 420 | 95.6712 | 6.5497 | 12.6472 | 394.284 | 6.7822 | 78.2672 | 12.7953 | 12.7953 | 85.9367 | 94.0633 | 78.1434 | 1.3638 | 1.3638 | 6.8796 | 8.2434 | -19.6577 | 0% | 3.7277 | 0 | 0 | 175.476 | 175.476 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2312 | 8 | -2.6 | 54.53 | 59.44 | 113.97 | 59.44 | 29.72 | 97 | 2312 | 480 | 95.6712 | 6.5497 | 12.6472 | 454.284 | 7.7822 | 63.2672 | 22.9026 | 22.9026 | 74.4117 | 105.5883 | 63.2423 | 63.0848 | 63.0848 | 50.7352 | 113.82 | -0.67133 | 0% | 51.4694 | 0 | 0 | 192.3718 | 192.3718 | 0% | 12.2% | 12.2% | 80% | 9.764% | 5.0254 | 11.1874 | 6 | 30.1526 | 11.1133 | 15.67% | 15.67%
4 | 97 | 7 | 2313 | 9 | -3 | 173.81 | 101.39 | 275.2 | 101.39 | 50.7 | 97 | 2313 | 540 | 95.6712 | 6.5497 | 12.6472 | 514.284 | 8.7822 | 48.2672 | 32.4121 | 32.4121 | 61.4256 | 118.5744 | 48.3534 | 215.488 | 215.488 | 86.5418 | 302.0297 | 0.2447 | 24.47% | 136.5778 | 33.4208 | 23.3946 | 158.7879 | 158.7879 | 14.73% | 11.98% | 11.98% | 85% | 10.18% | 13.91 | 11.3301 | 6 | 83.4598 | 30.7606 | 52.56% | 52.56%
4 | 97 | 7 | 2314 | 10 | -2.1 | 246.39 | 145.75 | 392.14 | 145.75 | 72.88 | 97 | 2314 | 600 | 95.6712 | 6.5497 | 12.6472 | 574.284 | 9.7822 | 33.2672 | 40.6912 | 40.6912 | 45.9495 | 134.0505 | 33.5085 | 315.1024 | 315.1024 | 124.4054 | 439.5078 | 0.42478 | 42.48% | 198.7454 | 84.4223 | 59.0956 | 161.8193 | 161.8193 | 36.52% | 11.79% | 11.79% | 85% | 10.02% | 19.9176 | 11.0106 | 6 | 119.5054 | 44.0459 | 73.85% | 73.85%
4 | 97 | 7 | 2315 | 11 | -1.2 | 386.47 | 161.67 | 548.14 | 161.67 | 80.84 | 97 | 2315 | 660 | 95.6712 | 6.5497 | 12.6472 | 634.284 | 10.7822 | 18.2672 | 46.8186 | 46.8186 | 27.0689 | 152.9311 | 18.8279 | 501.6395 | 501.6395 | 137.994 | 639.6334 | 0.54693 | 54.69% | 289.2422 | 158.1955 | 110.7369 | 159.9378 | 159.9378 | 69.24% | 11.54% | 11.54% | 90% | 10.39% | 30.0381 | 10.6967 | 6 | 180.2284 | 66.4265 | 112.7% | 112.7%
4 | 97 | 7 | 2316 | 12 | -0.4 | 486.58 | 179.92 | 666.5 | 179.92 | 89.96 | 97 | 2316 | 720 | 95.6712 | 6.5497 | 12.6472 | 694.284 | 11.7822 | 3.2672 | 49.6737 | 49.6737 | 5.0194 | 174.9806 | 5.7777 | 635.0031 | 635.0031 | 153.5713 | 788.5744 | 0.598 | 59.8% | 356.5934 | 213.2429 | 149.27 | 151.1017 | 151.1017 | 98.79% | 11.36% | 11.36% | 90% | 10.23% | 36.4736 | 10.4224 | 6 | 218.8414 | 80.6581 | 144.8% | 144.8%
4 | 97 | 7 | 2317 | 13 | 0.1 | 391.19 | 242.03 | 633.22 | 242.03 | 121.02 | 97 | 2317 | 780 | 95.6712 | 6.5497 | 12.6472 | 754.284 | 12.7822 | -11.7328 | 48.5265 | 48.5265 | 17.7606 | 197.7606 | 12.634 | 509.4586 | 509.4586 | 206.5855 | 716.0441 | 0.57886 | 57.89% | 323.7952 | 187.4318 | 131.2023 | 147.3464 | 147.3464 | 89.04% | 11.44% | 11.44% | 90% | 10.3% | 33.3493 | 10.2533 | 6 | 200.0957 | 73.749 | 135.8% | 135.8%
4 | 97 | 7 | 2318 | 14 | 0.9 | 380 | 219.36 | 599.36 | 219.36 | 109.68 | 97 | 2318 | 840 | 95.6712 | 6.5497 | 12.6472 | 814.284 | 13.7822 | -26.7328 | 43.69 | 43.69 | 38.1729 | 218.1729 | 27.0769 | 489.8264 | 489.8264 | 187.2355 | 677.0618 | 0.56881 | 56.88% | 306.1674 | 174.1499 | 121.9049 | 145.2135 | 145.2135 | 83.95% | 11.48% | 11.48% | 90% | 10.33% | 31.6364 | 9.9864 | 6 | 189.8182 | 69.961 | 130.7% | 130.7%
4 | 97 | 7 | 2319 | 15 | 1.3 | 334.72 | 208.97 | 543.69 | 208.97 | 104.49 | 97 | 2319 | 900 | 95.6712 | 6.5497 | 12.6472 | 874.284 | 14.7822 | -41.7328 | 36.2167 | 36.2167 | 55.0534 | 235.0534 | 41.8779 | 421.8086 | 421.8086 | 178.3671 | 600.1757 | 0.54031 | 54.03% | 271.3995 | 146.6404 | 102.6483 | 140.1122 | 140.1122 | 73.26% | 11.56% | 11.56% | 90% | 10.4% | 28.2303 | 9.8546 | 6 | 169.382 | 62.4289 | 120.9% | 120.9%
4 | 97 | 7 | 2320 | 16 | 1.6 | 268.53 | 178.14 | 446.67 | 178.14 | 89.07 | 97 | 2320 | 960 | 95.6712 | 6.5497 | 12.6472 | 934.284 | 15.7822 | -56.7328 | 27.1503 | 27.1503 | 68.9915 | 248.9915 | 56.7536 | 322.6182 | 322.6182 | 152.052 | 474.6702 | 0.47214 | 47.21% | 214.6459 | 101.3428 | 70.94 | 133.8958 | 133.8958 | 52.98% | 11.68% | 11.68% | 85% | 9.929% | 21.3123 | 9.7564 | 6 | 127.8738 | 47.1302 | 95.5% | 95.5%
4 | 97 | 7 | 2321 | 17 | 1.1 | 217.78 | 139.36 | 357.14 | 139.36 | 69.68 | 97 | 2321 | 1020 | 95.6712 | 6.5497 | 12.6472 | 994.284 | 16.7822 | -71.7328 | 17.2401 | 17.2401 | 81.0364 | 261.0364 | 71.6517 | 231.3115 | 231.3115 | 118.9512 | 350.2627 | 0.35077 | 35.08% | 158.3888 | 55.558 | 38.8906 | 125.6794 | 125.6794 | 30.94% | 11.82% | 11.82% | 85% | 10.05% | 15.9127 | 9.9203 | 6 | 95.4759 | 35.1894 | 75.97% | 75.97%
4 | 97 | 7 | 2322 | 18 | 0 | 144.44 | 96.47 | 240.91 | 96.47 | 48.24 | 97 | 2322 | 1080 | 95.6712 | 6.5497 | 12.6472 | 1054.284 | 17.7822 | -86.7328 | 7.0015 | 7.0015 | 92.128 | 272.128 | 86.5526 | 0 | 0 | 82.3423 | 82.3423 | -1.1568 | 0% | 37.2352 | 0 | 0 | 113.3649 | 113.3649 | 0% | 12.14% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2323 | 19 | 0.3 | 40 | 52.03 | 92.03 | 52.03 | 26.02 | 97 | 2323 | 1140 | 95.6712 | 6.5497 | 12.6472 | 1114.284 | 18.7822 | -101.7328 | -3.166 | 0 | 99.5879 | 279.5879 | 96.7638 | 0 | 0 | 44.4104 | 44.4104 | -2.8149 | 0% | 20.0824 | 0 | 0 | 142.2826 | 142.2826 | 0% | 12.17% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2324 | 20 | -0.2 | 0 | 5.19 | 5.19 | 5.19 | 2.6 | 97 | 2324 | 1200 | 95.6712 | 6.5497 | 12.6472 | 1174.284 | 19.7822 | -116.7328 | -12.8809 | 0 | 99.5879 | 279.5879 | 96.7638 | 0 | 0 | 4.4299 | 4.4299 | -35.7544 | 0% | 2.0032 | 0 | 0 | 127.1143 | 127.1143 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2325 | 21 | -0.3 | 0 | 0 | 0 | 0 | 0 | 97 | 2325 | 1260 | 95.6712 | 6.5497 | 12.6472 | 1234.284 | 20.7822 | -131.7328 | -21.7011 | 0 | 99.5879 | 279.5879 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3483 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2326 | 22 | -0.3 | 0 | 0 | 0 | 0 | 0 | 97 | 2326 | 1320 | 95.6712 | 6.5497 | 12.6472 | 1294.284 | 21.7822 | -146.7328 | -29.0611 | 0 | 99.5879 | 279.5879 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2517 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2327 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 2327 | 1380 | 95.6712 | 6.5497 | 12.6472 | 1354.284 | 22.7822 | -161.7328 | -34.2601 | 0 | 99.5879 | 279.5879 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1213 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
4 | 97 | 7 | 2328 | 24 | -0.6 | 0 | 0 | 0 | 0 | 0 | 97 | 2328 | 1440 | 95.6712 | 6.5497 | 12.6472 | 1414.284 | 23.7822 | -176.7328 | -36.5933 | 0 | 99.5879 | 279.5879 | 96.7638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3625 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2329 | 1 | -0.8 | 0 | 0 | 0 | 0 | 0 | 98 | 2329 | 60 | 96.6575 | 6.9369 | 12.9255 | 34.284 | 0.78682 | 168.1976 | -35.2701 | 0 | 100.1578 | 79.8422 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.6087 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2330 | 2 | -1.1 | 0 | 0 | 0 | 0 | 0 | 98 | 2330 | 120 | 96.6575 | 6.9369 | 12.9255 | 94.284 | 1.7868 | 153.1976 | -31.2498 | 0 | 100.1578 | 79.8422 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.6293 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2331 | 3 | -0.6 | 0 | 0 | 0 | 0 | 0 | 98 | 2331 | 180 | 96.6575 | 6.9369 | 12.9255 | 154.284 | 2.7868 | 138.1976 | -24.7561 | 0 | 100.1578 | 79.8422 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.4307 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2332 | 4 | -0.9 | 0 | 0 | 0 | 0 | 0 | 98 | 2332 | 240 | 96.6575 | 6.9369 | 12.9255 | 214.284 | 3.7868 | 123.1976 | -16.5115 | 0 | 100.1578 | 79.8422 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8878 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2333 | 5 | -0.9 | 0 | 0 | 0 | 0 | 0 | 98 | 2333 | 300 | 96.6575 | 6.9369 | 12.9255 | 274.284 | 4.7868 | 108.1976 | -7.1399 | 0 | 100.1578 | 79.8422 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4606 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2334 | 6 | 0.2 | 0 | 0 | 0 | 0 | 0 | 98 | 2334 | 360 | 96.6575 | 6.9369 | 12.9255 | 334.284 | 5.7868 | 93.1976 | 2.8711 | 2.8711 | 97.0777 | 82.9223 | 92.9577 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.7867 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2335 | 7 | 0.5 | 0.75 | 5.92 | 6.67 | 5.92 | 2.96 | 98 | 2335 | 420 | 96.6575 | 6.9369 | 12.9255 | 394.284 | 6.7868 | 78.1976 | 13.1238 | 13.1238 | 86.1586 | 93.8414 | 78.0716 | 0.68272 | 0.68272 | 5.053 | 5.7358 | -27.1303 | 0% | 2.5937 | 0 | 0 | 161.0705 | 161.0705 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2336 | 8 | 1.4 | 6.19 | 40.28 | 46.47 | 40.28 | 20.14 | 98 | 2336 | 480 | 96.6575 | 6.9369 | 12.9255 | 454.284 | 7.7868 | 63.1976 | 23.2378 | 23.2378 | 74.6352 | 105.3648 | 63.1828 | 7.078 | 7.078 | 34.3811 | 41.4591 | -3.0073 | 0% | 18.7478 | 0 | 0 | 171.9136 | 171.9136 | 0% | 12.13% | 12.13% | 80% | 9.702% | 1.819 | 9.8218 | 6 | 10.9139 | 4.0225 | 6.348% | 6.348%
4 | 98 | 8 | 2337 | 9 | 1.7 | 66.39 | 97.42 | 163.81 | 97.42 | 48.71 | 98 | 2337 | 540 | 96.6575 | 6.9369 | 12.9255 | 514.284 | 8.7868 | 48.1976 | 32.7619 | 32.7619 | 61.6389 | 118.3611 | 48.309 | 81.5983 | 81.5983 | 83.1532 | 164.7515 | -0.15065 | 0% | 74.5006 | 0 | 0 | 158.6173 | 158.6173 | 0% | 11.99% | 11.99% | 80% | 9.593% | 7.1469 | 9.7239 | 6 | 42.8815 | 15.8048 | 27.03% | 27.03%
4 | 98 | 8 | 2338 | 10 | 2 | 192.86 | 137.22 | 330.08 | 137.22 | 68.61 | 98 | 2338 | 600 | 96.6575 | 6.9369 | 12.9255 | 574.284 | 9.7868 | 33.1976 | 41.0615 | 41.0615 | 46.1243 | 133.8757 | 33.4872 | 244.8691 | 244.8691 | 117.1246 | 361.9937 | 0.37154 | 37.15% | 163.6935 | 60.8194 | 42.5736 | 144.7064 | 144.7064 | 29.42% | 11.79% | 11.79% | 85% | 10.02% | 16.3985 | 9.6266 | 6 | 98.3908 | 36.2637 | 67.99% | 67.99%
4 | 98 | 8 | 2339 | 11 | 4.5 | 308.14 | 202.78 | 510.92 | 202.78 | 101.39 | 98 | 2339 | 660 | 96.6575 | 6.9369 | 12.9255 | 634.284 | 10.7868 | 18.1976 | 47.2078 | 47.2078 | 27.1511 | 152.8489 | 18.8577 | 397.3716 | 397.3716 | 173.0836 | 570.4552 | 0.54021 | 54.02% | 257.9598 | 139.3514 | 97.546 | 150.0651 | 150.0651 | 65% | 11.55% | 11.55% | 90% | 10.39% | 26.8096 | 8.8405 | 6 | 160.8573 | 59.2869 | 107.2% | 107.2%
4 | 98 | 8 | 2340 | 12 | 6.5 | 471.19 | 191.75 | 662.94 | 191.75 | 95.88 | 98 | 2340 | 720 | 96.6575 | 6.9369 | 12.9255 | 694.284 | 11.7868 | 3.1976 | 50.0643 | 50.0643 | 4.9484 | 175.0516 | 6.064 | 611.0781 | 611.0781 | 163.6689 | 774.7469 | 0.61595 | 61.59% | 350.3406 | 215.7919 | 151.0543 | 149.2327 | 149.2327 | 101.2% | 11.37% | 11.37% | 90% | 10.23% | 35.8527 | 8.2431 | 6 | 215.1163 | 79.2851 | 144.1% | 144.1%
4 | 98 | 8 | 2341 | 13 | 6.6 | 472.69 | 186.67 | 659.36 | 186.67 | 93.34 | 98 | 2341 | 780 | 96.6575 | 6.9369 | 12.9255 | 754.284 | 12.7868 | -11.8024 | 48.8903 | 48.8903 | 17.9871 | 197.9871 | 12.8455 | 611.665 | 611.665 | 159.3328 | 770.9978 | 0.61534 | 61.53% | 348.6452 | 214.5365 | 150.1755 | 146.8927 | 146.8927 | 102.2% | 11.37% | 11.37% | 90% | 10.24% | 35.6875 | 8.2139 | 6 | 214.1247 | 78.9196 | 145.8% | 145.8%
4 | 98 | 8 | 2342 | 14 | 6.1 | 373.25 | 205.08 | 578.33 | 205.08 | 102.54 | 98 | 2342 | 840 | 96.6575 | 6.9369 | 12.9255 | 814.284 | 13.7868 | -26.8024 | 44.0104 | 44.0104 | 38.4891 | 218.4891 | 27.2078 | 477.7728 | 477.7728 | 175.0467 | 652.8195 | 0.57937 | 57.94% | 295.205 | 171.0315 | 119.7221 | 142.0295 | 142.0295 | 84.29% | 11.46% | 11.46% | 90% | 10.32% | 30.4594 | 8.3603 | 6 | 182.7567 | 67.3584 | 128.7% | 128.7%
4 | 98 | 8 | 2343 | 15 | 6.1 | 329.17 | 165.47 | 494.64 | 165.47 | 82.74 | 98 | 2343 | 900 | 96.6575 | 6.9369 | 12.9255 | 874.284 | 14.7868 | -41.8024 | 36.4967 | 36.4967 | 55.3964 | 235.3964 | 41.9796 | 411.4142 | 411.4142 | 141.2375 | 552.6517 | 0.53865 | 53.87% | 249.9091 | 134.6136 | 94.2295 | 135.9637 | 135.9637 | 69.3% | 11.54% | 11.54% | 90% | 10.39% | 25.958 | 8.3603 | 6 | 155.7482 | 57.4039 | 114.6% | 114.6%
4 | 98 | 8 | 2344 | 16 | 5.8 | 297.58 | 113.97 | 411.55 | 113.97 | 56.99 | 98 | 2344 | 960 | 96.6575 | 6.9369 | 12.9255 | 934.284 | 15.7868 | -56.8024 | 27.4018 | 27.4018 | 69.3317 | 249.3317 | 56.8381 | 353.6907 | 353.6907 | 97.2795 | 450.9702 | 0.47723 | 47.72% | 203.9287 | 97.3213 | 68.1249 | 130.4422 | 130.4422 | 52.23% | 11.62% | 11.62% | 85% | 9.881% | 20.15 | 8.449 | 6 | 120.9 | 44.5599 | 92.68% | 92.68%
4 | 98 | 8 | 2345 | 17 | 5.5 | 227.03 | 103.69 | 330.72 | 103.69 | 51.85 | 98 | 2345 | 1020 | 96.6575 | 6.9369 | 12.9255 | 994.284 | 16.7868 | -71.8024 | 17.4764 | 17.4764 | 81.3658 | 261.3658 | 71.7232 | 237.0807 | 237.0807 | 88.505 | 325.5857 | 0.34919 | 34.92% | 147.2298 | 51.4107 | 35.9875 | 123.8393 | 123.8393 | 29.06% | 11.73% | 11.73% | 85% | 9.971% | 14.68 | 8.5383 | 6 | 88.0799 | 32.4635 | 71.12% | 71.12%
4 | 98 | 8 | 2346 | 18 | 5.5 | 124.17 | 102.86 | 227.03 | 102.86 | 51.43 | 98 | 2346 | 1080 | 96.6575 | 6.9369 | 12.9255 | 1054.284 | 17.7868 | -86.8024 | 7.2345 | 7.2345 | 92.4473 | 272.4473 | 86.6123 | 0 | 0 | 87.7965 | 87.7965 | -0.88264 | 0% | 39.7016 | 0 | 0 | 114.65 | 114.65 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2347 | 19 | 5.3 | 32.42 | 58.33 | 90.75 | 58.33 | 29.17 | 98 | 2347 | 1140 | 96.6575 | 6.9369 | 12.9255 | 1114.284 | 18.7868 | -101.8024 | -2.9255 | 0 | 100.1578 | 280.1578 | 97.1637 | 0 | 0 | 49.7878 | 49.7878 | -2.1799 | 0% | 22.514 | 0 | 0 | 144.2578 | 144.2578 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2348 | 20 | 5 | 0 | 4.64 | 4.64 | 4.64 | 2.32 | 98 | 2348 | 1200 | 96.6575 | 6.9369 | 12.9255 | 1174.284 | 19.7868 | -116.8024 | -12.6226 | 0 | 100.1578 | 280.1578 | 97.1637 | 0 | 0 | 3.9605 | 3.9605 | -36.8883 | 0% | 1.7909 | 0 | 0 | 131.4169 | 131.4169 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2349 | 21 | 4.7 | 0 | 0 | 0 | 0 | 0 | 98 | 2349 | 1260 | 96.6575 | 6.9369 | 12.9255 | 1234.284 | 20.7868 | -131.8024 | -21.4155 | 0 | 100.1578 | 280.1578 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9716 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2350 | 22 | 4.3 | 0 | 0 | 0 | 0 | 0 | 98 | 2350 | 1320 | 96.6575 | 6.9369 | 12.9255 | 1294.284 | 21.7868 | -146.8024 | -28.7409 | 0 | 100.1578 | 280.1578 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1463 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2351 | 23 | 2.5 | 0 | 0 | 0 | 0 | 0 | 98 | 2351 | 1380 | 96.6575 | 6.9369 | 12.9255 | 1354.284 | 22.7868 | -161.8024 | -33.904 | 0 | 100.1578 | 280.1578 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4528 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
4 | 98 | 8 | 2352 | 24 | 1.9 | 0 | 0 | 0 | 0 | 0 | 98 | 2352 | 1440 | 96.6575 | 6.9369 | 12.9255 | 1414.284 | 23.7868 | -176.8024 | -36.2099 | 0 | 100.1578 | 280.1578 | 97.1637 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9306 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2353 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 99 | 2353 | 60 | 97.6438 | 7.3221 | 13.1945 | 34.284 | 0.79131 | 168.1304 | -34.8792 | 0 | 100.7253 | 79.2747 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2888 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2354 | 2 | -0.2 | 0 | 0 | 0 | 0 | 0 | 99 | 2354 | 120 | 97.6438 | 7.3221 | 13.1945 | 94.284 | 1.7913 | 153.1304 | -30.8664 | 0 | 100.7253 | 79.2747 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.7281 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2355 | 3 | -1.2 | 0 | 0 | 0 | 0 | 0 | 99 | 2355 | 180 | 97.6438 | 7.3221 | 13.1945 | 154.284 | 2.7913 | 138.1304 | -24.3895 | 0 | 100.7253 | 79.2747 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6245 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2356 | 4 | -1.2 | 0 | 0 | 0 | 0 | 0 | 99 | 2356 | 240 | 97.6438 | 7.3221 | 13.1945 | 214.284 | 3.7913 | 123.1304 | -16.1627 | 0 | 100.7253 | 79.2747 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6245 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2357 | 5 | -1.3 | 0 | 0 | 0 | 0 | 0 | 99 | 2357 | 300 | 97.6438 | 7.3221 | 13.1945 | 274.284 | 4.7913 | 108.1304 | -6.8053 | 0 | 100.7253 | 79.2747 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3462 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2358 | 6 | -1.4 | 0 | 0 | 0 | 0 | 0 | 99 | 2358 | 360 | 97.6438 | 7.3221 | 13.1945 | 334.284 | 5.7913 | 93.1304 | 3.1976 | 3.1976 | 97.2931 | 82.7069 | 92.8765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.6442 | 1.6442 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2359 | 7 | -1.5 | 2.78 | 8.33 | 11.11 | 8.33 | 4.17 | 99 | 2359 | 420 | 97.6438 | 7.3221 | 13.1945 | 394.284 | 6.7913 | 78.1304 | 13.4491 | 13.4491 | 86.3815 | 93.6185 | 78.0028 | 2.4846 | 2.4846 | 7.1101 | 9.5947 | -16.4114 | 0% | 4.3387 | 0 | 0 | 168.006 | 168.006 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2360 | 8 | -0.9 | 43.61 | 55.92 | 99.53 | 55.92 | 27.96 | 99 | 2360 | 480 | 97.6438 | 7.3221 | 13.1945 | 454.284 | 7.7913 | 63.1304 | 23.5696 | 23.5696 | 74.8605 | 105.1395 | 63.127 | 49.2978 | 49.2978 | 47.7307 | 97.0285 | -0.88298 | 0% | 43.8763 | 0 | 0 | 182.8126 | 182.8126 | 0% | 12.16% | 12.16% | 80% | 9.728% | 4.2683 | 10.5933 | 6 | 25.6099 | 9.439 | 14.01% | 14.01%
4 | 99 | 9 | 2361 | 9 | 0.2 | 147.97 | 104.72 | 252.69 | 104.72 | 52.36 | 99 | 2361 | 540 | 97.6438 | 7.3221 | 13.1945 | 514.284 | 8.7913 | 48.1304 | 33.1083 | 33.1083 | 61.8548 | 118.1452 | 48.2693 | 180.317 | 180.317 | 89.3841 | 269.7011 | 0.20718 | 20.72% | 121.9589 | 25.267 | 17.6869 | 151.0275 | 151.0275 | 11.71% | 11.93% | 11.93% | 80% | 9.544% | 11.6393 | 10.2197 | 6 | 69.8356 | 25.7392 | 46.24% | 46.24%
4 | 99 | 9 | 2362 | 10 | 2 | 226.11 | 136.11 | 362.22 | 136.11 | 68.06 | 99 | 2362 | 600 | 97.6438 | 7.3221 | 13.1945 | 574.284 | 9.7913 | 33.1304 | 41.4288 | 41.4288 | 46.3026 | 133.6974 | 33.4721 | 285.0445 | 285.0445 | 116.1772 | 401.2216 | 0.41383 | 41.38% | 181.4324 | 75.0814 | 52.557 | 155.5197 | 155.5197 | 33.79% | 11.75% | 11.75% | 85% | 9.985% | 18.1156 | 9.6266 | 6 | 108.6937 | 40.0611 | 69.89% | 69.89%
4 | 99 | 9 | 2363 | 11 | 3.4 | 300 | 175.75 | 475.75 | 175.75 | 87.88 | 99 | 2363 | 660 | 97.6438 | 7.3221 | 13.1945 | 634.284 | 10.7913 | 18.1304 | 47.5944 | 47.5944 | 27.2371 | 152.7629 | 18.8971 | 384.3911 | 384.3911 | 150.012 | 534.4031 | 0.51744 | 51.74% | 241.6571 | 125.0422 | 87.5296 | 153.7012 | 153.7012 | 56.95% | 11.59% | 11.59% | 90% | 10.44% | 25.217 | 9.181 | 6 | 151.3021 | 55.7652 | 98.44% | 98.44%
4 | 99 | 9 | 2364 | 12 | 4.8 | 372.69 | 186.47 | 559.16 | 186.47 | 93.24 | 99 | 2364 | 720 | 97.6438 | 7.3221 | 13.1945 | 694.284 | 11.7913 | 3.1304 | 50.4528 | 50.4528 | 4.8798 | 175.1202 | 6.3613 | 480.3466 | 480.3466 | 159.1621 | 639.5087 | 0.56982 | 56.98% | 289.1858 | 164.7836 | 115.3485 | 146.19 | 146.19 | 78.9% | 11.49% | 11.49% | 90% | 10.34% | 29.8947 | 8.7491 | 6 | 179.3684 | 66.1096 | 122.7% | 122.7%
4 | 99 | 9 | 2365 | 13 | 7.7 | 374.44 | 205.75 | 580.19 | 205.75 | 102.88 | 99 | 2365 | 780 | 97.6438 | 7.3221 | 13.1945 | 754.284 | 12.7913 | -11.8696 | 49.2522 | 49.2522 | 18.2127 | 198.2127 | 13.0623 | 481.4625 | 481.4625 | 175.6186 | 657.0812 | 0.58661 | 58.66% | 297.1321 | 174.3004 | 122.0103 | 147.9173 | 147.9173 | 82.49% | 11.45% | 11.45% | 90% | 10.3% | 30.6159 | 7.8981 | 6 | 183.6957 | 67.7044 | 124.2% | 124.2%
4 | 99 | 9 | 2366 | 14 | 9.2 | 392.5 | 233.06 | 625.56 | 233.06 | 116.53 | 99 | 2366 | 840 | 97.6438 | 7.3221 | 13.1945 | 814.284 | 13.7913 | -26.8696 | 44.3293 | 44.3293 | 38.8045 | 218.8045 | 27.3407 | 498.9467 | 498.9467 | 198.9292 | 697.8758 | 0.60438 | 60.44% | 315.5794 | 190.73 | 133.511 | 150.0582 | 150.0582 | 88.97% | 11.41% | 11.41% | 90% | 10.27% | 32.4144 | 7.481 | 6 | 194.4865 | 71.6816 | 129.6% | 129.6%
4 | 99 | 9 | 2367 | 15 | 9 | 298.42 | 229.81 | 528.23 | 229.81 | 114.91 | 99 | 2367 | 900 | 97.6438 | 7.3221 | 13.1945 | 874.284 | 14.7913 | -41.8696 | 36.7754 | 36.7754 | 55.7381 | 235.7381 | 42.0815 | 369.9555 | 369.9555 | 196.1551 | 566.1106 | 0.55709 | 55.71% | 255.9952 | 142.612 | 99.8284 | 142.362 | 142.362 | 70.12% | 11.49% | 11.49% | 90% | 10.34% | 26.4805 | 7.5357 | 6 | 158.8832 | 58.5594 | 111.6% | 111.6%
4 | 99 | 9 | 2368 | 16 | 9.8 | 160 | 259.72 | 419.72 | 259.72 | 129.86 | 99 | 2368 | 960 | 97.6438 | 7.3221 | 13.1945 | 934.284 | 15.7913 | -56.8696 | 27.6525 | 27.6525 | 69.6699 | 249.6699 | 56.9219 | 188.1568 | 188.1568 | 221.6849 | 409.8417 | 0.46752 | 46.75% | 185.3304 | 86.6451 | 60.6516 | 136.2956 | 136.2956 | 44.5% | 11.57% | 11.57% | 85% | 9.835% | 18.2277 | 7.3186 | 6 | 109.3662 | 40.3089 | 80.24% | 80.24%
4 | 99 | 9 | 2369 | 17 | 9.5 | 97.22 | 202.31 | 299.53 | 202.31 | 101.16 | 99 | 2369 | 1020 | 97.6438 | 7.3221 | 13.1945 | 994.284 | 16.7913 | -71.8696 | 17.7123 | 17.7123 | 81.6929 | 261.6929 | 71.7932 | 99.8436 | 99.8436 | 172.6824 | 272.526 | 0.2954 | 29.54% | 123.2363 | 36.404 | 25.4828 | 126.9287 | 126.9287 | 20.08% | 11.66% | 11.66% | 80% | 9.325% | 11.4921 | 7.3995 | 6 | 68.9529 | 25.4138 | 54.32% | 54.32%
4 | 99 | 9 | 2370 | 18 | 9.4 | 71.39 | 120.19 | 191.58 | 120.19 | 60.1 | 99 | 2370 | 1080 | 97.6438 | 7.3221 | 13.1945 | 1054.284 | 17.7913 | -86.8696 | 7.4675 | 7.4675 | 92.7638 | 272.7638 | 86.6698 | 0 | 0 | 102.5886 | 102.5886 | -0.54938 | 0% | 46.3906 | 0 | 0 | 117.4763 | 117.4763 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2371 | 19 | 8.1 | 16.47 | 50.28 | 66.75 | 50.28 | 25.14 | 99 | 2371 | 1140 | 97.6438 | 7.3221 | 13.1945 | 1114.284 | 18.7913 | -101.8696 | -2.6847 | 0 | 100.7253 | 280.7253 | 97.5617 | 0 | 0 | 42.9167 | 42.9167 | -2.5024 | 0% | 19.4069 | 0 | 0 | 146.5877 | 146.5877 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2372 | 20 | 6.6 | 0 | 4.44 | 4.44 | 4.44 | 2.22 | 99 | 2372 | 1200 | 97.6438 | 7.3221 | 13.1945 | 1174.284 | 19.7913 | -116.8696 | -12.3639 | 0 | 100.7253 | 280.7253 | 97.5617 | 0 | 0 | 3.7898 | 3.7898 | -37.5766 | 0% | 1.7137 | 0 | 0 | 133.5749 | 133.5749 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2373 | 21 | 5.6 | 0 | 0 | 0 | 0 | 0 | 99 | 2373 | 1260 | 97.6438 | 7.3221 | 13.1945 | 1234.284 | 20.7913 | -131.8696 | -21.1297 | 0 | 100.7253 | 280.7253 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8373 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2374 | 22 | 4.5 | 0 | 0 | 0 | 0 | 0 | 99 | 2374 | 1320 | 97.6438 | 7.3221 | 13.1945 | 1294.284 | 21.7913 | -146.8696 | -28.421 | 0 | 100.7253 | 280.7253 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0755 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2375 | 23 | 4.2 | 0 | 0 | 0 | 0 | 0 | 99 | 2375 | 1380 | 97.6438 | 7.3221 | 13.1945 | 1354.284 | 22.7913 | -161.8696 | -33.5488 | 0 | 100.7253 | 280.7253 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9052 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
4 | 99 | 9 | 2376 | 24 | 3.2 | 0 | 0 | 0 | 0 | 0 | 99 | 2376 | 1440 | 97.6438 | 7.3221 | 13.1945 | 1414.284 | 23.7913 | -176.8696 | -35.8283 | 0 | 100.7253 | 280.7253 | 97.5617 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.8016 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2377 | 1 | 2.5 | 0 | 0 | 0 | 0 | 0 | 100 | 2377 | 60 | 98.6301 | 7.7053 | 13.454 | 34.284 | 0.79563 | 168.0655 | -34.4907 | 0 | 101.2904 | 78.7096 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0523 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2378 | 2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 100 | 2378 | 120 | 98.6301 | 7.7053 | 13.454 | 94.284 | 1.7956 | 153.0655 | -30.4858 | 0 | 101.2904 | 78.7096 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0619 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2379 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 100 | 2379 | 180 | 98.6301 | 7.7053 | 13.454 | 154.284 | 2.7956 | 138.0655 | -24.0257 | 0 | 101.2904 | 78.7096 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0716 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2380 | 4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 100 | 2380 | 240 | 98.6301 | 7.7053 | 13.454 | 214.284 | 3.7956 | 123.0655 | -15.8169 | 0 | 101.2904 | 78.7096 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3764 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2381 | 5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 100 | 2381 | 300 | 98.6301 | 7.7053 | 13.454 | 274.284 | 4.7956 | 108.0655 | -6.4737 | 0 | 101.2904 | 78.7096 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7882 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2382 | 6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 100 | 2382 | 360 | 98.6301 | 7.7053 | 13.454 | 334.284 | 5.7956 | 93.0655 | 3.5208 | 3.5208 | 97.5091 | 82.4909 | 92.7977 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.7005 | 1.7005 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2383 | 7 | 1 | 0.36 | 6.94 | 7.3 | 6.94 | 3.47 | 100 | 2383 | 420 | 98.6301 | 7.7053 | 13.454 | 394.284 | 6.7956 | 78.0655 | 13.771 | 13.771 | 86.6053 | 93.3947 | 77.937 | 0.31606 | 0.31606 | 5.9237 | 6.2397 | -24.6771 | 0% | 2.8216 | 0 | 0 | 166.8885 | 166.8885 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2384 | 8 | 2.8 | 34.72 | 54.72 | 89.44 | 54.72 | 27.36 | 100 | 2384 | 480 | 98.6301 | 7.7053 | 13.454 | 454.284 | 7.7956 | 63.0655 | 23.898 | 23.898 | 75.0874 | 104.9126 | 63.0749 | 38.8096 | 38.8096 | 46.7064 | 85.516 | -1.0038 | 0% | 38.6703 | 0 | 0 | 182.2496 | 182.2496 | 0% | 12.03% | 12.03% | 80% | 9.622% | 3.721 | 9.3703 | 6 | 22.3259 | 8.2286 | 12.25% | 12.25%
4 | 100 | 10 | 2385 | 9 | 4.5 | 136.47 | 97.69 | 234.16 | 97.69 | 48.85 | 100 | 2385 | 540 | 98.6301 | 7.7053 | 13.454 | 514.284 | 8.7956 | 48.0655 | 33.4512 | 33.4512 | 62.0733 | 117.9267 | 48.2342 | 164.9067 | 164.9067 | 83.3836 | 248.2903 | 0.19792 | 19.79% | 112.2769 | 22.2223 | 15.5556 | 150.8391 | 150.8391 | 10.31% | 11.82% | 11.82% | 80% | 9.458% | 10.619 | 8.8405 | 6 | 63.714 | 23.483 | 42.24% | 42.24%
4 | 100 | 10 | 2386 | 10 | 5.5 | 175.47 | 125.83 | 301.3 | 125.83 | 62.92 | 100 | 2386 | 600 | 98.6301 | 7.7053 | 13.454 | 574.284 | 9.7956 | 33.0655 | 41.7928 | 41.7928 | 46.4845 | 133.5155 | 33.4631 | 219.6516 | 219.6516 | 107.4026 | 327.0542 | 0.35123 | 35.12% | 147.8939 | 51.9446 | 36.3612 | 151.7893 | 151.7893 | 23.96% | 11.73% | 11.73% | 85% | 9.97% | 14.7447 | 8.5383 | 6 | 88.4684 | 32.6066 | 58.28% | 58.28%
4 | 100 | 10 | 2387 | 11 | 7.8 | 173.53 | 226.86 | 400.39 | 226.86 | 113.43 | 100 | 2387 | 660 | 98.6301 | 7.7053 | 13.454 | 634.284 | 10.7956 | 18.0655 | 47.9783 | 47.9783 | 27.3268 | 152.6732 | 18.946 | 220.9329 | 220.9329 | 193.6371 | 414.57 | 0.46001 | 46% | 187.4686 | 86.2379 | 60.3665 | 151.2987 | 151.2987 | 39.9% | 11.61% | 11.61% | 85% | 9.869% | 18.5013 | 7.8698 | 6 | 111.008 | 40.914 | 73.37% | 73.37%
4 | 100 | 10 | 2388 | 12 | 9.2 | 272.22 | 261.11 | 533.33 | 261.11 | 130.56 | 100 | 2388 | 720 | 98.6301 | 7.7053 | 13.454 | 694.284 | 11.7956 | 3.0655 | 50.8391 | 50.8391 | 4.8138 | 175.1862 | 6.6676 | 348.7071 | 348.7071 | 222.8713 | 571.5784 | 0.56027 | 56.03% | 258.4678 | 144.8122 | 101.3685 | 147.008 | 147.008 | 68.95% | 11.49% | 11.49% | 90% | 10.34% | 26.7228 | 7.481 | 6 | 160.3366 | 59.095 | 109.1% | 109.1%
4 | 100 | 10 | 2389 | 13 | 9.9 | 171.47 | 232.5 | 403.97 | 232.5 | 116.25 | 100 | 2389 | 780 | 98.6301 | 7.7053 | 13.454 | 754.284 | 12.7956 | -11.9345 | 49.6123 | 49.6123 | 18.4372 | 198.4372 | 13.2838 | 219.0983 | 219.0983 | 198.4512 | 417.5494 | 0.47429 | 47.43% | 188.8158 | 89.5531 | 62.6872 | 139.2005 | 139.2005 | 45.03% | 11.56% | 11.56% | 85% | 9.83% | 18.5602 | 7.2918 | 6 | 111.3611 | 41.0442 | 80% | 80%
4 | 100 | 10 | 2390 | 14 | 10.6 | 101.75 | 235.08 | 336.83 | 235.08 | 117.54 | 100 | 2390 | 840 | 98.6301 | 7.7053 | 13.454 | 814.284 | 13.7956 | -26.9345 | 44.6465 | 44.6465 | 39.1191 | 219.1191 | 27.4753 | 128.4612 | 128.4612 | 200.6533 | 329.1146 | 0.39065 | 39.07% | 148.8256 | 58.139 | 40.6973 | 135.3677 | 135.3677 | 30.06% | 11.6% | 11.6% | 85% | 9.856% | 14.6684 | 7.1059 | 6 | 88.0107 | 32.438 | 65.02% | 65.02%
4 | 100 | 10 | 2391 | 15 | 11.5 | 136.19 | 213.69 | 349.88 | 213.69 | 106.85 | 100 | 2391 | 900 | 98.6301 | 7.7053 | 13.454 | 874.284 | 14.7956 | -41.9345 | 37.0529 | 37.0529 | 56.0782 | 236.0782 | 42.1835 | 167.4817 | 167.4817 | 182.3958 | 349.8776 | 0.42115 | 42.12% | 158.2146 | 66.6323 | 46.6426 | 133.7104 | 133.7104 | 34.88% | 11.56% | 11.56% | 85% | 9.828% | 15.5494 | 6.8721 | 6 | 93.2966 | 34.3862 | 69.78% | 69.78%
4 | 100 | 10 | 2392 | 16 | 11.1 | 114.64 | 173.25 | 287.89 | 173.25 | 86.63 | 100 | 2392 | 960 | 98.6301 | 7.7053 | 13.454 | 934.284 | 15.7956 | -56.9345 | 27.9025 | 27.9025 | 70.0061 | 250.0061 | 57.0047 | 133.4055 | 133.4055 | 147.8781 | 281.2836 | 0.32449 | 32.45% | 127.1964 | 41.2745 | 28.8922 | 127.7052 | 127.7052 | 22.62% | 11.61% | 11.61% | 80% | 9.285% | 11.8098 | 6.9753 | 6 | 70.8591 | 26.1164 | 55.49% | 55.49%
4 | 100 | 10 | 2393 | 17 | 11 | 8.47 | 109.58 | 118.05 | 109.58 | 54.79 | 100 | 2393 | 1020 | 98.6301 | 7.7053 | 13.454 | 994.284 | 16.7956 | -71.9345 | 17.9479 | 17.9479 | 82.0174 | 262.0174 | 71.8614 | 8.5569 | 8.5569 | 93.5324 | 102.0893 | -0.51944 | 0% | 46.1648 | 0 | 0 | 158.3452 | 158.3452 | 0% | 11.7% | 11.7% | 80% | 9.358% | 4.3201 | 7.0013 | 6 | 25.9205 | 9.5535 | 16.37% | 16.37%
4 | 100 | 10 | 2394 | 18 | 10.6 | 25.92 | 70.92 | 96.84 | 70.92 | 35.46 | 100 | 2394 | 1080 | 98.6301 | 7.7053 | 13.454 | 1054.284 | 17.7956 | -86.9345 | 7.7005 | 7.7005 | 93.0775 | 273.0775 | 86.725 | 0 | 0 | 60.534 | 60.534 | -1.4433 | 0% | 27.3735 | 0 | 0 | 152.9899 | 152.9899 | 0% | 11.73% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2395 | 19 | 9.5 | 8.06 | 47.14 | 55.2 | 47.14 | 23.57 | 100 | 2395 | 1140 | 98.6301 | 7.7053 | 13.454 | 1114.284 | 18.7956 | -101.9345 | -2.4436 | 0 | 101.2904 | 281.2904 | 97.9575 | 0 | 0 | 40.2365 | 40.2365 | -2.6408 | 0% | 18.1949 | 0 | 0 | 145.5136 | 145.5136 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2396 | 20 | 8.1 | 0 | 5.92 | 5.92 | 5.92 | 2.96 | 100 | 2396 | 1200 | 98.6301 | 7.7053 | 13.454 | 1174.284 | 19.7956 | -116.9345 | -12.105 | 0 | 101.2904 | 281.2904 | 97.9575 | 0 | 0 | 5.053 | 5.053 | -27.2778 | 0% | 2.285 | 0 | 0 | 134.6827 | 134.6827 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2397 | 21 | 7.3 | 0 | 0 | 0 | 0 | 0 | 100 | 2397 | 1260 | 98.6301 | 7.7053 | 13.454 | 1234.284 | 20.7956 | -131.9345 | -20.8438 | 0 | 101.2904 | 281.2904 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2211 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2398 | 22 | 6.7 | 0 | 0 | 0 | 0 | 0 | 100 | 2398 | 1320 | 98.6301 | 7.7053 | 13.454 | 1294.284 | 21.7956 | -146.9345 | -28.1014 | 0 | 101.2904 | 281.2904 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4514 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2399 | 23 | 6.8 | 0 | 0 | 0 | 0 | 0 | 100 | 2399 | 1380 | 98.6301 | 7.7053 | 13.454 | 1354.284 | 22.7956 | -161.9345 | -33.1947 | 0 | 101.2904 | 281.2904 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.699 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
4 | 100 | 10 | 2400 | 24 | 6.7 | 0 | 0 | 0 | 0 | 0 | 100 | 2400 | 1440 | 98.6301 | 7.7053 | 13.454 | 1414.284 | 23.7956 | -176.9345 | -35.4484 | 0 | 101.2904 | 281.2904 | 97.9575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2515 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2401 | 1 | 6.8 | 0 | 0 | 0 | 0 | 0 | 101 | 2401 | 60 | 99.6164 | 8.0863 | 13.7038 | 34.284 | 0.7998 | 168.0031 | -34.1047 | 0 | 101.8529 | 78.1471 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.2816 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2402 | 2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 101 | 2402 | 120 | 99.6164 | 8.0863 | 13.7038 | 94.284 | 1.7998 | 153.0031 | -30.1081 | 0 | 101.8529 | 78.1471 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0471 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2403 | 3 | 6.4 | 0 | 0 | 0 | 0 | 0 | 101 | 2403 | 180 | 99.6164 | 8.0863 | 13.7038 | 154.284 | 2.7998 | 138.0031 | -23.6649 | 0 | 101.8529 | 78.1471 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8126 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2404 | 4 | 5.9 | 0 | 0 | 0 | 0 | 0 | 101 | 2404 | 240 | 99.6164 | 8.0863 | 13.7038 | 214.284 | 3.7998 | 123.0031 | -15.4741 | 0 | 101.8529 | 78.1471 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5746 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2405 | 5 | 5.9 | 0 | 0 | 0 | 0 | 0 | 101 | 2405 | 300 | 99.6164 | 8.0863 | 13.7038 | 274.284 | 4.7998 | 108.0031 | -6.1454 | 0 | 101.8529 | 78.1471 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.0563 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2406 | 6 | 5.5 | 0 | 0 | 0 | 0 | 0 | 101 | 2406 | 360 | 99.6164 | 8.0863 | 13.7038 | 334.284 | 5.7998 | 93.0031 | 3.8406 | 3.8406 | 97.7256 | 82.2744 | 92.7214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.7866 | 6.7866 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2407 | 7 | 5.6 | 2.31 | 11.19 | 13.5 | 11.19 | 5.6 | 101 | 2407 | 420 | 99.6164 | 8.0863 | 13.7038 | 394.284 | 6.7998 | 78.0031 | 14.0894 | 14.0894 | 86.8302 | 93.1698 | 77.8742 | 1.9933 | 1.9933 | 9.5513 | 11.5445 | -12.0022 | 0% | 5.2204 | 0 | 0 | 172.577 | 172.577 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2408 | 8 | 7.9 | 11.19 | 55.47 | 66.66 | 55.47 | 27.74 | 101 | 2408 | 480 | 99.6164 | 8.0863 | 13.7038 | 454.284 | 7.7998 | 63.0031 | 24.2227 | 24.2227 | 75.3159 | 104.6841 | 63.0265 | 12.3708 | 12.3708 | 47.3466 | 59.7174 | -1.5801 | 0% | 27.0042 | 0 | 0 | 187.2279 | 187.2279 | 0% | 11.84% | 11.84% | 80% | 9.476% | 2.5588 | 7.8416 | 6 | 15.3531 | 5.6587 | 8.2% | 8.2%
4 | 101 | 11 | 2409 | 9 | 7.6 | 45.47 | 114.44 | 159.91 | 114.44 | 57.22 | 101 | 2409 | 540 | 99.6164 | 8.0863 | 13.7038 | 514.284 | 8.7998 | 48.0031 | 33.7905 | 33.7905 | 62.2943 | 117.7057 | 48.2037 | 54.4899 | 54.4899 | 97.6807 | 152.1706 | -0.13626 | 0% | 68.8115 | 0 | 0 | 171.6388 | 171.6388 | 0% | 11.79% | 11.79% | 80% | 9.435% | 6.4924 | 7.9264 | 6 | 38.9544 | 14.3574 | 22.7% | 22.7%
4 | 101 | 11 | 2410 | 10 | 8.9 | 243.69 | 165.92 | 409.61 | 165.92 | 82.96 | 101 | 2410 | 600 | 99.6164 | 8.0863 | 13.7038 | 574.284 | 9.7998 | 33.0031 | 42.1533 | 42.1533 | 46.6699 | 133.3301 | 33.4603 | 302.9321 | 302.9321 | 141.6216 | 444.5537 | 0.48905 | 48.9% | 201.0272 | 98.3115 | 68.818 | 162.8617 | 162.8617 | 42.26% | 11.57% | 11.57% | 85% | 9.834% | 19.7683 | 7.5632 | 6 | 118.6099 | 43.7159 | 72.83% | 72.83%
4 | 101 | 11 | 2411 | 11 | 10.9 | 352.03 | 193.89 | 545.92 | 193.89 | 96.95 | 101 | 2411 | 660 | 99.6164 | 8.0863 | 13.7038 | 634.284 | 10.7998 | 18.0031 | 48.3592 | 48.3592 | 27.4205 | 152.5795 | 19.0041 | 445.379 | 445.379 | 165.4955 | 610.8745 | 0.58245 | 58.24% | 276.2374 | 160.8935 | 112.6254 | 163.9057 | 163.9057 | 68.71% | 11.45% | 11.45% | 90% | 10.3% | 28.458 | 7.0274 | 6 | 170.7477 | 62.9322 | 104.2% | 104.2%
4 | 101 | 11 | 2412 | 12 | 12 | 547.5 | 166.31 | 713.81 | 166.31 | 83.16 | 101 | 2412 | 720 | 99.6164 | 8.0863 | 13.7038 | 694.284 | 11.7998 | 3.0031 | 51.223 | 51.223 | 4.7506 | 175.2494 | 6.9811 | 697.0862 | 697.0862 | 141.9545 | 839.0406 | 0.64573 | 64.57% | 379.4142 | 244.9994 | 171.4996 | 160.3389 | 160.3389 | 107% | 11.33% | 11.33% | 95% | 10.77% | 40.8556 | 6.7446 | 6 | 245.1338 | 90.3486 | 152.9% | 152.9%
4 | 101 | 11 | 2413 | 13 | 12.5 | 431.58 | 177.69 | 609.27 | 177.69 | 88.85 | 101 | 2413 | 780 | 99.6164 | 8.0863 | 13.7038 | 754.284 | 12.7998 | -11.9969 | 49.9703 | 49.9703 | 18.6605 | 198.6605 | 13.5095 | 548.0376 | 548.0376 | 151.6679 | 699.7055 | 0.61586 | 61.59% | 316.4068 | 194.8626 | 136.4039 | 153.8973 | 153.8973 | 88.63% | 11.39% | 11.39% | 90% | 10.25% | 32.4445 | 6.6189 | 6 | 194.6668 | 71.748 | 126.5% | 126.5%
4 | 101 | 11 | 2414 | 14 | 13.4 | 372.14 | 216.47 | 588.61 | 216.47 | 108.24 | 101 | 2414 | 840 | 99.6164 | 8.0863 | 13.7038 | 814.284 | 13.7998 | -26.9969 | 44.962 | 44.962 | 39.4324 | 219.4324 | 27.6114 | 466.6573 | 466.6573 | 184.7687 | 651.426 | 0.60509 | 60.51% | 294.5748 | 178.2439 | 124.7707 | 153.2434 | 153.2434 | 81.42% | 11.41% | 11.41% | 90% | 10.27% | 30.2391 | 6.397 | 6 | 181.4346 | 66.8711 | 118.4% | 118.4%
4 | 101 | 11 | 2415 | 15 | 14.2 | 100.47 | 180 | 280.47 | 180 | 90 | 101 | 2415 | 900 | 99.6164 | 8.0863 | 13.7038 | 874.284 | 14.7998 | -41.9969 | 37.3291 | 37.3291 | 56.4167 | 236.4167 | 42.2855 | 122.5739 | 122.5739 | 153.6396 | 276.2135 | 0.3415 | 34.15% | 124.9038 | 42.6547 | 29.8583 | 137.9363 | 137.9363 | 21.65% | 11.52% | 11.52% | 80% | 9.215% | 11.5102 | 6.2045 | 6 | 69.0613 | 25.4538 | 50.07% | 50.07%
4 | 101 | 11 | 2416 | 16 | 14.3 | 99.64 | 176.11 | 275.75 | 176.11 | 88.06 | 101 | 2416 | 960 | 99.6164 | 8.0863 | 13.7038 | 934.284 | 15.7998 | -56.9969 | 28.1517 | 28.1517 | 70.34 | 250.34 | 57.0865 | 114.7537 | 114.7537 | 150.3193 | 265.073 | 0.32292 | 32.29% | 119.866 | 38.7073 | 27.0951 | 135.3361 | 135.3361 | 20.02% | 11.52% | 11.52% | 80% | 9.216% | 11.0466 | 6.1808 | 6 | 66.2794 | 24.4285 | 48.97% | 48.97%
4 | 101 | 11 | 2417 | 17 | 14.3 | 224.03 | 176.81 | 400.84 | 176.81 | 88.41 | 101 | 2417 | 1020 | 99.6164 | 8.0863 | 13.7038 | 994.284 | 16.7998 | -71.9969 | 18.1832 | 18.1832 | 82.3393 | 262.3393 | 71.928 | 222.7061 | 222.7061 | 150.9168 | 373.6229 | 0.46269 | 46.27% | 168.9523 | 78.1727 | 54.7209 | 138.4651 | 138.4651 | 39.52% | 11.49% | 11.49% | 85% | 9.763% | 16.4945 | 6.1808 | 6 | 98.967 | 36.4761 | 71.47% | 71.47%
4 | 101 | 11 | 2418 | 18 | 13.3 | 108.75 | 114.03 | 222.78 | 114.03 | 57.02 | 101 | 2418 | 1080 | 99.6164 | 8.0863 | 13.7038 | 1054.284 | 17.7998 | -86.9969 | 7.9335 | 7.9335 | 93.3881 | 273.3881 | 86.7778 | 0 | 0 | 97.3307 | 97.3307 | -0.52965 | 0% | 44.0129 | 0 | 0 | 123.5875 | 123.5875 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2419 | 19 | 12.5 | 23.81 | 43.53 | 67.34 | 43.53 | 21.77 | 101 | 2419 | 1140 | 99.6164 | 8.0863 | 13.7038 | 1114.284 | 18.7998 | -101.9969 | -2.2024 | 0 | 101.8529 | 281.8529 | 98.3512 | 0 | 0 | 37.1552 | 37.1552 | -2.739 | 0% | 16.8016 | 0 | 0 | 151.0056 | 151.0056 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2420 | 20 | 10.9 | 0 | 6.39 | 6.39 | 6.39 | 3.2 | 101 | 2420 | 1200 | 99.6164 | 8.0863 | 13.7038 | 1174.284 | 19.7998 | -116.9969 | -11.8458 | 0 | 101.8529 | 281.8529 | 98.3512 | 0 | 0 | 5.4542 | 5.4542 | -24.0101 | 0% | 2.4664 | 0 | 0 | 137.188 | 137.188 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2421 | 21 | 9.4 | 0 | 0 | 0 | 0 | 0 | 101 | 2421 | 1260 | 99.6164 | 8.0863 | 13.7038 | 1234.284 | 20.7998 | -131.9969 | -20.5579 | 0 | 101.8529 | 281.8529 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2425 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2422 | 22 | 8.1 | 0 | 0 | 0 | 0 | 0 | 101 | 2422 | 1320 | 99.6164 | 8.0863 | 13.7038 | 1294.284 | 21.7998 | -146.9969 | -27.7822 | 0 | 101.8529 | 281.8529 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9184 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2423 | 23 | 7.3 | 0 | 0 | 0 | 0 | 0 | 101 | 2423 | 1380 | 99.6164 | 8.0863 | 13.7038 | 1354.284 | 22.7998 | -161.9969 | -32.8417 | 0 | 101.8529 | 281.8529 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5983 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
4 | 101 | 11 | 2424 | 24 | 6.8 | 0 | 0 | 0 | 0 | 0 | 101 | 2424 | 1440 | 99.6164 | 8.0863 | 13.7038 | 1414.284 | 23.7998 | -176.9969 | -35.0705 | 0 | 101.8529 | 281.8529 | 98.3512 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8209 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2425 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 102 | 2425 | 60 | 100.6027 | 8.465 | 13.9434 | 34.284 | 0.80379 | 167.9431 | -33.7214 | 0 | 102.4127 | 77.5873 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7201 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2426 | 2 | 5.5 | 0 | 0 | 0 | 0 | 0 | 102 | 2426 | 120 | 100.6027 | 8.465 | 13.9434 | 94.284 | 1.8038 | 152.9431 | -29.7333 | 0 | 102.4127 | 77.5873 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1079 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2427 | 3 | 5.3 | 0 | 0 | 0 | 0 | 0 | 102 | 2427 | 180 | 100.6027 | 8.465 | 13.9434 | 154.284 | 2.8038 | 137.9431 | -23.3073 | 0 | 102.4127 | 77.5873 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0386 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2428 | 4 | 3.8 | 0 | 0 | 0 | 0 | 0 | 102 | 2428 | 240 | 100.6027 | 8.465 | 13.9434 | 214.284 | 3.8038 | 122.9431 | -15.1346 | 0 | 102.4127 | 77.5873 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3245 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2429 | 5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 102 | 2429 | 300 | 100.6027 | 8.465 | 13.9434 | 274.284 | 4.8038 | 107.9431 | -5.8204 | 0 | 102.4127 | 77.5873 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3207 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2430 | 6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 102 | 2430 | 360 | 100.6027 | 8.465 | 13.9434 | 334.284 | 5.8038 | 92.9431 | 4.157 | 4.157 | 97.9426 | 82.0574 | 92.6477 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.8764 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2431 | 7 | 3.4 | 1.19 | 9.72 | 10.91 | 9.72 | 4.86 | 102 | 2431 | 420 | 100.6027 | 8.465 | 13.9434 | 394.284 | 6.8038 | 77.9431 | 14.4041 | 14.4041 | 87.056 | 92.944 | 77.8147 | 1.0097 | 1.0097 | 8.2965 | 9.3063 | -15.6516 | 0% | 4.2083 | 0 | 0 | 156.9024 | 156.9024 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2432 | 8 | 5 | 17.69 | 58.06 | 75.75 | 58.06 | 29.03 | 102 | 2432 | 480 | 100.6027 | 8.465 | 13.9434 | 454.284 | 7.8038 | 62.9431 | 24.5436 | 24.5436 | 75.5461 | 104.4539 | 62.982 | 19.346 | 19.346 | 49.5573 | 68.9033 | -1.3625 | 0% | 31.1581 | 0 | 0 | 169.4154 | 169.4154 | 0% | 11.96% | 11.96% | 80% | 9.564% | 2.98 | 8.6885 | 6 | 17.88 | 6.59 | 10.55% | 10.55%
4 | 102 | 12 | 2433 | 9 | 6.9 | 37.69 | 118.61 | 156.3 | 118.61 | 59.31 | 102 | 2433 | 540 | 100.6027 | 8.465 | 13.9434 | 514.284 | 8.8038 | 47.9431 | 34.126 | 34.126 | 62.5179 | 117.4821 | 48.178 | 44.7981 | 44.7981 | 101.24 | 146.0381 | -0.18711 | 0% | 66.0384 | 0 | 0 | 156.1933 | 156.1933 | 0% | 11.82% | 11.82% | 80% | 9.459% | 6.2463 | 8.127 | 6 | 37.4776 | 13.8131 | 23.99% | 23.99%
4 | 102 | 12 | 2434 | 10 | 8 | 99.81 | 216.11 | 315.92 | 216.11 | 108.06 | 102 | 2434 | 600 | 100.6027 | 8.465 | 13.9434 | 574.284 | 9.8038 | 32.9431 | 42.5102 | 42.5102 | 46.8589 | 133.1411 | 33.4636 | 123.2239 | 123.2239 | 184.4614 | 307.6853 | 0.34205 | 34.21% | 139.1353 | 47.5917 | 33.3142 | 143.6225 | 143.6225 | 23.2% | 11.68% | 11.68% | 85% | 9.925% | 13.8097 | 7.8134 | 6 | 82.8583 | 30.539 | 57.69% | 57.69%
4 | 102 | 12 | 2435 | 11 | 9.7 | 195.92 | 258.61 | 454.53 | 258.61 | 129.31 | 102 | 2435 | 660 | 100.6027 | 8.465 | 13.9434 | 634.284 | 10.8038 | 17.9431 | 48.737 | 48.737 | 27.5182 | 152.4818 | 19.0713 | 246.3336 | 246.3336 | 220.7374 | 467.0711 | 0.50825 | 50.82% | 211.2095 | 107.3462 | 75.1423 | 147.1792 | 147.1792 | 51.06% | 11.54% | 11.54% | 85% | 9.81% | 20.7186 | 7.3455 | 6 | 124.3118 | 45.8174 | 84.46% | 84.46%
4 | 102 | 12 | 2436 | 12 | 11.7 | 425.75 | 233.53 | 659.28 | 233.53 | 116.77 | 102 | 2436 | 720 | 100.6027 | 8.465 | 13.9434 | 694.284 | 11.8038 | 2.9431 | 51.6045 | 51.6045 | 4.6903 | 175.3097 | 7.3006 | 538.8235 | 538.8235 | 199.3303 | 738.1539 | 0.62316 | 62.32% | 333.7932 | 208.0067 | 145.6047 | 150.2788 | 150.2788 | 96.89% | 11.38% | 11.38% | 90% | 10.24% | 34.1878 | 6.8209 | 6 | 205.1268 | 75.6033 | 136.5% | 136.5%
4 | 102 | 12 | 2437 | 13 | 12.3 | 394.36 | 194.81 | 589.17 | 194.81 | 97.41 | 102 | 2437 | 780 | 100.6027 | 8.465 | 13.9434 | 754.284 | 12.8038 | -12.0569 | 50.3263 | 50.3263 | 18.8823 | 198.8823 | 13.7387 | 497.7008 | 497.7008 | 166.2807 | 663.9816 | 0.60505 | 60.5% | 300.2525 | 181.6663 | 127.1664 | 146.1031 | 146.1031 | 87.04% | 11.41% | 11.41% | 90% | 10.27% | 30.8319 | 6.669 | 6 | 184.9911 | 68.1819 | 126.6% | 126.6%
4 | 102 | 12 | 2438 | 14 | 12.4 | 338.61 | 144.31 | 482.92 | 144.31 | 72.16 | 102 | 2438 | 840 | 100.6027 | 8.465 | 13.9434 | 814.284 | 13.8038 | -27.0569 | 45.2757 | 45.2757 | 39.7445 | 219.7445 | 27.7488 | 421.7711 | 421.7711 | 123.1763 | 544.9474 | 0.56201 | 56.2% | 246.4252 | 138.4933 | 96.9453 | 140.7553 | 140.7553 | 68.88% | 11.46% | 11.46% | 90% | 10.31% | 25.4132 | 6.6439 | 6 | 152.4793 | 56.1991 | 108.3% | 108.3%
4 | 102 | 12 | 2439 | 15 | 12.8 | 330.47 | 200.64 | 531.11 | 200.64 | 100.32 | 102 | 2439 | 900 | 100.6027 | 8.465 | 13.9434 | 874.284 | 14.8038 | -42.0569 | 37.604 | 37.604 | 56.7533 | 236.7533 | 42.3872 | 400.0114 | 400.0114 | 171.257 | 571.2684 | 0.57477 | 57.48% | 258.3276 | 148.4788 | 103.9352 | 141.5265 | 141.5265 | 73.44% | 11.44% | 11.44% | 90% | 10.3% | 26.6034 | 6.5443 | 6 | 159.6204 | 58.831 | 112.8% | 112.8%
4 | 102 | 12 | 2440 | 16 | 12.5 | 227.97 | 131.67 | 359.64 | 131.67 | 65.84 | 102 | 2440 | 960 | 100.6027 | 8.465 | 13.9434 | 934.284 | 15.8038 | -57.0569 | 28.4001 | 28.4001 | 70.6716 | 250.6716 | 57.1671 | 259.8753 | 259.8753 | 112.3874 | 372.2627 | 0.45037 | 45.04% | 168.3372 | 75.8146 | 53.0703 | 132.0378 | 132.0378 | 40.19% | 11.53% | 11.53% | 85% | 9.799% | 16.4957 | 6.6189 | 6 | 98.9739 | 36.4787 | 74.96% | 74.96%
4 | 102 | 12 | 2441 | 17 | 11.7 | 81.39 | 94.08 | 175.47 | 94.08 | 47.04 | 102 | 2441 | 1020 | 100.6027 | 8.465 | 13.9434 | 994.284 | 16.8038 | -72.0569 | 18.418 | 18.418 | 82.6584 | 262.6584 | 71.9927 | 79.6358 | 79.6358 | 80.3023 | 159.9381 | -0.030619 | 0% | 72.324 | 0 | 0 | 119.4228 | 119.4228 | 0% | 11.64% | 11.64% | 80% | 9.315% | 6.7372 | 6.8209 | 6 | 40.4234 | 14.8988 | 33.85% | 33.85%
4 | 102 | 12 | 2442 | 18 | 11.6 | 103.53 | 96.86 | 200.39 | 96.86 | 48.43 | 102 | 2442 | 1080 | 100.6027 | 8.465 | 13.9434 | 1054.284 | 17.8038 | -87.0569 | 8.1664 | 8.1664 | 93.6956 | 273.6956 | 86.8283 | 0 | 0 | 82.6752 | 82.6752 | -0.8134 | 0% | 37.3857 | 0 | 0 | 117.3061 | 117.3061 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2443 | 19 | 10.8 | 15.08 | 42.31 | 57.39 | 42.31 | 21.16 | 102 | 2443 | 1140 | 100.6027 | 8.465 | 13.9434 | 1114.284 | 18.8038 | -102.0569 | -1.9611 | 0 | 102.4127 | 282.4127 | 98.7425 | 0 | 0 | 36.1138 | 36.1138 | -2.9501 | 0% | 16.3307 | 0 | 0 | 145.9131 | 145.9131 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2444 | 20 | 10.1 | 0 | 4.44 | 4.44 | 4.44 | 2.22 | 102 | 2444 | 1200 | 100.6027 | 8.465 | 13.9434 | 1174.284 | 19.8038 | -117.0569 | -11.5866 | 0 | 102.4127 | 282.4127 | 98.7425 | 0 | 0 | 3.7898 | 3.7898 | -35.3997 | 0% | 1.7137 | 0 | 0 | 135.5454 | 135.5454 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2445 | 21 | 9.4 | 0 | 0 | 0 | 0 | 0 | 102 | 2445 | 1260 | 100.6027 | 8.465 | 13.9434 | 1234.284 | 20.8038 | -132.0569 | -20.272 | 0 | 102.4127 | 282.4127 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2621 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2446 | 22 | 8.8 | 0 | 0 | 0 | 0 | 0 | 102 | 2446 | 1320 | 100.6027 | 8.465 | 13.9434 | 1294.284 | 21.8038 | -147.0569 | -27.4636 | 0 | 102.4127 | 282.4127 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5753 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2447 | 23 | 8.3 | 0 | 0 | 0 | 0 | 0 | 102 | 2447 | 1380 | 100.6027 | 8.465 | 13.9434 | 1354.284 | 22.8038 | -162.0569 | -32.49 | 0 | 102.4127 | 282.4127 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9632 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
4 | 102 | 12 | 2448 | 24 | 8.1 | 0 | 0 | 0 | 0 | 0 | 102 | 2448 | 1440 | 100.6027 | 8.465 | 13.9434 | 1414.284 | 23.8038 | -177.0569 | -34.6948 | 0 | 102.4127 | 282.4127 | 98.7425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8938 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2449 | 1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 103 | 2449 | 60 | 101.589 | 8.8412 | 14.1727 | 34.284 | 0.80761 | 167.8858 | -33.341 | 0 | 102.9695 | 77.0305 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.775 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2450 | 2 | 7.7 | 0 | 0 | 0 | 0 | 0 | 103 | 2450 | 120 | 101.589 | 8.8412 | 14.1727 | 94.284 | 1.8076 | 152.8858 | -29.3617 | 0 | 102.9695 | 77.0305 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5812 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2451 | 3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 103 | 2451 | 180 | 101.589 | 8.8412 | 14.1727 | 154.284 | 2.8076 | 137.8858 | -22.953 | 0 | 102.9695 | 77.0305 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9971 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2452 | 4 | 6.7 | 0 | 0 | 0 | 0 | 0 | 103 | 2452 | 240 | 101.589 | 8.8412 | 14.1727 | 214.284 | 3.8076 | 122.8858 | -14.7985 | 0 | 102.9695 | 77.0305 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.6067 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2453 | 5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 103 | 2453 | 300 | 101.589 | 8.8412 | 14.1727 | 274.284 | 4.8076 | 107.8858 | -5.4988 | 0 | 102.9695 | 77.0305 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.1631 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2454 | 6 | 6.4 | 0 | 0 | 0 | 0 | 0 | 103 | 2454 | 360 | 101.589 | 8.8412 | 14.1727 | 334.284 | 5.8076 | 92.8858 | 4.4697 | 4.4697 | 98.1601 | 81.8399 | 92.5766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.8433 | 5.8433 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2455 | 7 | 6.6 | 5.36 | 11.67 | 17.03 | 11.67 | 5.84 | 103 | 2455 | 420 | 101.589 | 8.8412 | 14.1727 | 394.284 | 6.8076 | 77.8858 | 14.715 | 14.715 | 87.2827 | 92.7173 | 77.7583 | 4.4743 | 4.4743 | 9.961 | 14.4352 | -9.2723 | 0% | 6.5276 | 0 | 0 | 173.0296 | 173.0296 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2456 | 8 | 7.7 | 62.42 | 52.14 | 114.56 | 52.14 | 26.07 | 103 | 2456 | 480 | 101.589 | 8.8412 | 14.1727 | 454.284 | 7.8076 | 62.8858 | 24.8606 | 24.8606 | 75.7778 | 104.2222 | 62.9414 | 67.5409 | 67.5409 | 44.5043 | 112.0451 | -0.47087 | 0% | 50.6668 | 0 | 0 | 189.2479 | 189.2479 | 0% | 11.82% | 11.82% | 80% | 9.454% | 4.79 | 7.8981 | 6 | 28.74 | 10.5927 | 15.19% | 15.19%
4 | 103 | 13 | 2457 | 9 | 9.3 | 165.75 | 78.61 | 244.36 | 78.61 | 39.31 | 103 | 2457 | 540 | 101.589 | 8.8412 | 14.1727 | 514.284 | 8.8076 | 47.8858 | 34.4575 | 34.4575 | 62.744 | 117.256 | 48.157 | 195.4249 | 195.4249 | 67.0978 | 262.5227 | 0.27424 | 27.42% | 118.7128 | 32.5552 | 22.7887 | 157.2574 | 157.2574 | 14.49% | 11.67% | 11.67% | 80% | 9.335% | 11.0814 | 7.4538 | 6 | 66.4885 | 24.5056 | 42.28% | 42.28%
4 | 103 | 13 | 2458 | 10 | 11.1 | 257.58 | 108.14 | 365.72 | 108.14 | 54.07 | 103 | 2458 | 600 | 101.589 | 8.8412 | 14.1727 | 574.284 | 9.8076 | 32.8858 | 42.8634 | 42.8634 | 47.0515 | 132.9485 | 33.473 | 315.8518 | 315.8518 | 92.3033 | 408.1551 | 0.47354 | 47.35% | 184.5677 | 87.401 | 61.1807 | 163.7481 | 163.7481 | 37.36% | 11.54% | 11.54% | 85% | 9.812% | 18.1102 | 6.9753 | 6 | 108.6613 | 40.0491 | 66.36% | 66.36%
4 | 103 | 13 | 2459 | 11 | 13.3 | 379.81 | 146.86 | 526.67 | 146.86 | 73.43 | 103 | 2459 | 660 | 101.589 | 8.8412 | 14.1727 | 634.284 | 10.8076 | 17.8858 | 49.1116 | 49.1116 | 27.6201 | 152.3799 | 19.1473 | 474.6101 | 474.6101 | 125.3529 | 599.9629 | 0.58765 | 58.76% | 271.3032 | 159.43 | 111.601 | 166.3075 | 166.3075 | 67.11% | 11.43% | 11.43% | 90% | 10.28% | 27.8985 | 6.4214 | 6 | 167.391 | 61.695 | 100.7% | 100.7%
4 | 103 | 13 | 2460 | 12 | 15.4 | 539.64 | 165.64 | 705.28 | 165.64 | 82.82 | 103 | 2460 | 720 | 101.589 | 8.8412 | 14.1727 | 694.284 | 11.8076 | 2.8858 | 51.9833 | 51.9833 | 4.633 | 175.367 | 7.6247 | 678.9125 | 678.9125 | 141.3826 | 820.2951 | 0.65159 | 65.16% | 370.9375 | 241.6979 | 169.1885 | 164.8314 | 164.8314 | 102.6% | 11.35% | 11.35% | 95% | 10.78% | 39.9853 | 5.9242 | 5.9242 | 236.88 | 88.4239 | 143.7% | 143.7%
4 | 103 | 13 | 2461 | 13 | 15.7 | 667.22 | 135.83 | 803.05 | 135.83 | 67.92 | 103 | 2461 | 780 | 101.589 | 8.8412 | 14.1727 | 754.284 | 12.8076 | -12.1142 | 50.6802 | 50.6802 | 19.1025 | 199.1025 | 13.9711 | 836.95 | 836.95 | 115.9382 | 952.8882 | 0.67351 | 67.35% | 430.896 | 290.2113 | 203.1479 | 166.8045 | 166.8045 | 121.8% | 11.32% | 11.32% | 95% | 10.75% | 46.3215 | 5.8557 | 5.8557 | 271.2439 | 102.436 | 162.6% | 162.6%
4 | 103 | 13 | 2462 | 14 | 17.4 | 600.83 | 173.14 | 773.97 | 173.14 | 86.57 | 103 | 2462 | 840 | 101.589 | 8.8412 | 14.1727 | 814.284 | 13.8076 | -27.1142 | 45.5876 | 45.5876 | 40.0551 | 220.0551 | 27.8873 | 743.4398 | 743.4398 | 147.7842 | 891.224 | 0.66876 | 66.88% | 403.0115 | 269.5197 | 188.6638 | 167.8968 | 167.8968 | 112.4% | 11.34% | 11.34% | 95% | 10.77% | 43.4124 | 5.4794 | 5.4794 | 237.8732 | 96.0027 | 141.7% | 141.7%
4 | 103 | 13 | 2463 | 15 | 18 | 617.22 | 128.33 | 745.55 | 128.33 | 64.17 | 103 | 2463 | 900 | 101.589 | 8.8412 | 14.1727 | 874.284 | 14.8076 | -42.1142 | 37.8775 | 37.8775 | 57.0878 | 237.0878 | 42.4886 | 741.3087 | 741.3087 | 109.5365 | 850.8452 | 0.66392 | 66.39% | 384.7522 | 255.4447 | 178.8113 | 165.4087 | 165.4087 | 108.1% | 11.35% | 11.35% | 95% | 10.78% | 41.4728 | 5.3514 | 5.3514 | 221.9374 | 91.7133 | 134.2% | 134.2%
4 | 103 | 13 | 2464 | 16 | 18.7 | 467.5 | 130.75 | 598.25 | 130.75 | 65.38 | 103 | 2464 | 960 | 101.589 | 8.8412 | 14.1727 | 934.284 | 15.8076 | -57.1142 | 28.6475 | 28.6475 | 71.0006 | 251.0006 | 57.2465 | 527.5739 | 527.5739 | 111.6021 | 639.176 | 0.61997 | 62% | 289.0354 | 179.1921 | 125.4345 | 159.1023 | 159.1023 | 78.84% | 11.36% | 11.36% | 90% | 10.23% | 29.5601 | 5.2053 | 5.2053 | 153.8683 | 65.3695 | 96.71% | 96.71%
4 | 103 | 13 | 2465 | 17 | 18.8 | 375.92 | 118.97 | 494.89 | 118.97 | 59.49 | 103 | 2465 | 1020 | 101.589 | 8.8412 | 14.1727 | 994.284 | 16.8076 | -72.1142 | 18.6524 | 18.6524 | 82.9746 | 262.9746 | 72.0556 | 362.1313 | 362.1313 | 101.5472 | 463.6786 | 0.55079 | 55.08% | 209.6754 | 115.487 | 80.8409 | 151.936 | 151.936 | 53.21% | 11.37% | 11.37% | 85% | 9.668% | 20.2716 | 5.1847 | 5.1847 | 105.1016 | 44.8288 | 69.17% | 69.17%
4 | 103 | 13 | 2466 | 18 | 18.4 | 194.92 | 80.92 | 275.84 | 80.92 | 40.46 | 103 | 2466 | 1080 | 101.589 | 8.8412 | 14.1727 | 1054.284 | 17.8076 | -87.1142 | 8.3992 | 8.3992 | 93.9998 | 273.9998 | 86.8763 | 0 | 0 | 69.0695 | 69.0695 | -0.90871 | 0% | 31.2332 | 0 | 0 | 135.4167 | 135.4167 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2467 | 19 | 17.5 | 58.25 | 53.97 | 112.22 | 53.97 | 26.99 | 103 | 2467 | 1140 | 101.589 | 8.8412 | 14.1727 | 1114.284 | 18.8076 | -102.1142 | -1.7197 | 0 | 102.9695 | 282.9695 | 99.1313 | 0 | 0 | 46.0663 | 46.0663 | -1.8075 | 0% | 20.8312 | 0 | 0 | 160.9715 | 160.9715 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2468 | 20 | 16.4 | 0 | 9.72 | 9.72 | 9.72 | 4.86 | 103 | 2468 | 1200 | 101.589 | 8.8412 | 14.1727 | 1174.284 | 19.8076 | -117.1142 | -11.3272 | 0 | 102.9695 | 282.9695 | 99.1313 | 0 | 0 | 8.2965 | 8.2965 | -13.9935 | 0% | 3.7517 | 0 | 0 | 143.3787 | 143.3787 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2469 | 21 | 15.6 | 0 | 0 | 0 | 0 | 0 | 103 | 2469 | 1260 | 101.589 | 8.8412 | 14.1727 | 1234.284 | 20.8076 | -132.1142 | -19.9863 | 0 | 102.9695 | 282.9695 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.5192 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2470 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 103 | 2470 | 1320 | 101.589 | 8.8412 | 14.1727 | 1294.284 | 21.8076 | -147.1142 | -27.1456 | 0 | 102.9695 | 282.9695 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4503 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2471 | 23 | 13.6 | 0 | 0 | 0 | 0 | 0 | 103 | 2471 | 1380 | 101.589 | 8.8412 | 14.1727 | 1354.284 | 22.8076 | -162.1142 | -32.1397 | 0 | 102.9695 | 282.9695 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0853 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
4 | 103 | 13 | 2472 | 24 | 14.5 | 0 | 0 | 0 | 0 | 0 | 103 | 2472 | 1440 | 101.589 | 8.8412 | 14.1727 | 1414.284 | 23.8076 | -177.1142 | -34.3212 | 0 | 102.9695 | 282.9695 | 99.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2152 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2473 | 1 | 13.7 | 0 | 0 | 0 | 0 | 0 | 104 | 2473 | 60 | 102.5753 | 9.215 | 14.3914 | 34.284 | 0.81126 | 167.8312 | -32.9635 | 0 | 103.5232 | 76.4768 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5438 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2474 | 2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 104 | 2474 | 120 | 102.5753 | 9.215 | 14.3914 | 94.284 | 1.8113 | 152.8312 | -28.9934 | 0 | 103.5232 | 76.4768 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7156 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2475 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 104 | 2475 | 180 | 102.5753 | 9.215 | 14.3914 | 154.284 | 2.8113 | 137.8312 | -22.602 | 0 | 103.5232 | 76.4768 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3446 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2476 | 4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 104 | 2476 | 240 | 102.5753 | 9.215 | 14.3914 | 214.284 | 3.8113 | 122.8312 | -14.4659 | 0 | 103.5232 | 76.4768 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4782 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2477 | 5 | 8.6 | 0 | 0 | 0 | 0 | 0 | 104 | 2477 | 300 | 102.5753 | 9.215 | 14.3914 | 274.284 | 4.8113 | 107.8312 | -5.181 | 0 | 103.5232 | 76.4768 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.5566 | 0.5566 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2478 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 104 | 2478 | 360 | 102.5753 | 9.215 | 14.3914 | 334.284 | 5.8113 | 92.8312 | 4.7786 | 4.7786 | 98.378 | 81.622 | 92.5083 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 11.3872 | 11.3872 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2479 | 7 | 8 | 5.28 | 10.47 | 15.75 | 10.47 | 5.24 | 104 | 2479 | 420 | 102.5753 | 9.215 | 14.3914 | 394.284 | 6.8113 | 77.8312 | 15.0219 | 15.0219 | 87.5103 | 92.4897 | 77.7052 | 4.3379 | 4.3379 | 8.9367 | 13.2746 | -9.9032 | 0% | 6.0028 | 0 | 0 | 180.2884 | 180.2884 | 0% | 11.87% | 11.87% | 80% | 9.497% | 0.57008 | 7.8134 | 6 | 3.4205 | 1.2607 | 1.897% | 1.897%
4 | 104 | 14 | 2480 | 8 | 8.8 | 80.83 | 39.64 | 120.47 | 39.64 | 19.82 | 104 | 2480 | 480 | 102.5753 | 9.215 | 14.3914 | 454.284 | 7.8113 | 62.8312 | 25.1735 | 25.1735 | 76.0111 | 103.9889 | 62.9046 | 86.5522 | 86.5522 | 33.8349 | 120.387 | -0.36099 | 0% | 54.439 | 0 | 0 | 197.0682 | 197.0682 | 0% | 11.77% | 11.77% | 80% | 9.417% | 5.1263 | 7.5907 | 6 | 30.7575 | 11.3363 | 15.61% | 15.61%
4 | 104 | 14 | 2481 | 9 | 10.7 | 188.53 | 71.58 | 260.11 | 71.58 | 35.79 | 104 | 2481 | 540 | 102.5753 | 9.215 | 14.3914 | 514.284 | 8.8113 | 47.8312 | 34.7849 | 34.7849 | 62.9726 | 117.0274 | 48.1407 | 220.521 | 220.521 | 61.0974 | 281.6183 | 0.32176 | 32.18% | 127.3478 | 40.976 | 28.6832 | 165.4351 | 165.4351 | 17.34% | 11.62% | 11.62% | 80% | 9.294% | 11.8354 | 7.0797 | 6 | 71.0121 | 26.1728 | 42.92% | 42.92%
4 | 104 | 14 | 2482 | 10 | 12.4 | 297.22 | 129.64 | 426.86 | 129.64 | 64.82 | 104 | 2482 | 600 | 102.5753 | 9.215 | 14.3914 | 574.284 | 9.8113 | 32.8312 | 43.2127 | 43.2127 | 47.2479 | 132.7521 | 33.4885 | 362.0233 | 362.0233 | 110.6547 | 472.6779 | 0.52501 | 52.5% | 213.745 | 112.2184 | 78.5529 | 172.1808 | 172.1808 | 45.62% | 11.49% | 11.49% | 85% | 9.765% | 20.8733 | 6.6439 | 6 | 125.2396 | 46.1594 | 72.74% | 72.74%
4 | 104 | 14 | 2483 | 11 | 14.7 | 414.64 | 148.89 | 563.53 | 148.89 | 74.45 | 104 | 2483 | 660 | 102.5753 | 9.215 | 14.3914 | 634.284 | 10.8113 | 17.8312 | 49.4828 | 49.4828 | 27.7263 | 152.2737 | 19.2318 | 514.9892 | 514.9892 | 127.0856 | 642.0748 | 0.60681 | 60.68% | 290.3462 | 176.1849 | 123.3294 | 171.8621 | 171.8621 | 71.76% | 11.4% | 11.4% | 90% | 10.26% | 29.7844 | 6.0865 | 6 | 178.7063 | 65.8655 | 104% | 104%
4 | 104 | 14 | 2484 | 12 | 15.7 | 471.39 | 166.03 | 637.42 | 166.03 | 83.02 | 104 | 2484 | 720 | 102.5753 | 9.215 | 14.3914 | 694.284 | 11.8113 | 2.8312 | 52.3595 | 52.3595 | 4.5791 | 175.4209 | 7.9523 | 589.5713 | 589.5713 | 141.7155 | 731.2868 | 0.63396 | 63.4% | 330.6879 | 209.6439 | 146.7508 | 162.1223 | 162.1223 | 90.52% | 11.37% | 11.37% | 90% | 10.23% | 33.8341 | 5.8557 | 5.8557 | 198.1214 | 74.8211 | 122.2% | 122.2%
4 | 104 | 14 | 2485 | 13 | 16.7 | 509.25 | 173.97 | 683.22 | 173.97 | 86.99 | 104 | 2485 | 780 | 102.5753 | 9.215 | 14.3914 | 754.284 | 12.8113 | -12.1688 | 51.0317 | 51.0317 | 19.3208 | 199.3208 | 14.2061 | 634.9586 | 634.9586 | 148.4927 | 783.4512 | 0.64816 | 64.82% | 354.2766 | 229.6276 | 160.7393 | 161.7819 | 161.7819 | 99.36% | 11.36% | 11.36% | 90% | 10.22% | 36.2053 | 5.6319 | 5.6319 | 203.9038 | 80.0648 | 126% | 126%
4 | 104 | 14 | 2486 | 14 | 18.1 | 504.72 | 196.31 | 701.03 | 196.31 | 98.16 | 104 | 2486 | 840 | 102.5753 | 9.215 | 14.3914 | 814.284 | 13.8113 | -27.1688 | 45.8977 | 45.8977 | 40.3641 | 220.3641 | 28.0267 | 620.432 | 620.432 | 167.5611 | 787.9931 | 0.65303 | 65.3% | 356.3305 | 232.6944 | 162.886 | 162.8738 | 162.8738 | 100% | 11.35% | 11.35% | 90% | 10.22% | 36.4096 | 5.3303 | 5.3303 | 194.0746 | 80.5166 | 119.2% | 119.2%
4 | 104 | 14 | 2487 | 15 | 18.9 | 405.75 | 204.36 | 610.11 | 204.36 | 102.18 | 104 | 2487 | 900 | 102.5753 | 9.215 | 14.3914 | 874.284 | 14.8113 | -42.1688 | 38.1496 | 38.1496 | 57.4201 | 237.4201 | 42.5895 | 483.5898 | 483.5898 | 174.4322 | 658.022 | 0.62591 | 62.59% | 297.5575 | 186.2444 | 130.3711 | 157.2573 | 157.2573 | 82.9% | 11.36% | 11.36% | 90% | 10.22% | 30.4239 | 5.1642 | 5.1642 | 157.1135 | 67.2797 | 99.91% | 99.91%
4 | 104 | 14 | 2488 | 16 | 17.6 | 329.08 | 194.17 | 523.25 | 194.17 | 97.09 | 104 | 2488 | 960 | 102.5753 | 9.215 | 14.3914 | 934.284 | 15.8113 | -57.1688 | 28.8941 | 28.8941 | 71.3269 | 251.3269 | 57.3246 | 367.687 | 367.687 | 165.7345 | 533.4214 | 0.57889 | 57.89% | 241.2132 | 139.6359 | 97.7451 | 149.3287 | 149.3287 | 65.46% | 11.39% | 11.39% | 90% | 10.25% | 24.7207 | 5.4364 | 5.4364 | 134.3924 | 54.6675 | 90% | 90%
4 | 104 | 14 | 2489 | 17 | 18.1 | 187.58 | 131.11 | 318.69 | 131.11 | 65.56 | 104 | 2489 | 1020 | 102.5753 | 9.215 | 14.3914 | 994.284 | 16.8113 | -72.1688 | 18.8863 | 18.8863 | 83.2877 | 263.2877 | 72.1164 | 177.9563 | 177.9563 | 111.9094 | 289.8657 | 0.39359 | 39.36% | 131.0773 | 51.5908 | 36.1135 | 137.2818 | 137.2818 | 26.31% | 11.41% | 11.41% | 80% | 9.124% | 11.9598 | 5.3303 | 5.3303 | 63.7496 | 26.4481 | 46.44% | 46.44%
4 | 104 | 14 | 2490 | 18 | 17.7 | 111.75 | 109.81 | 221.56 | 109.81 | 54.91 | 104 | 2490 | 1080 | 102.5753 | 9.215 | 14.3914 | 1054.284 | 17.8113 | -87.1688 | 8.6318 | 8.6318 | 94.3006 | 274.3006 | 86.9217 | 0 | 0 | 93.7287 | 93.7287 | -0.47475 | 0% | 42.3841 | 0 | 0 | 127.1856 | 127.1856 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2491 | 19 | 16.4 | 19.72 | 73.06 | 92.78 | 73.06 | 36.53 | 104 | 2491 | 1140 | 102.5753 | 9.215 | 14.3914 | 1114.284 | 18.8113 | -102.1688 | -1.4784 | 0 | 103.5232 | 283.5232 | 99.5175 | 0 | 0 | 62.3606 | 62.3606 | -1.1647 | 0% | 28.1995 | 0 | 0 | 155.0601 | 155.0601 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2492 | 20 | 14.2 | 0 | 8.61 | 8.61 | 8.61 | 4.31 | 104 | 2492 | 1200 | 102.5753 | 9.215 | 14.3914 | 1174.284 | 19.8113 | -117.1688 | -11.0679 | 0 | 103.5232 | 283.5232 | 99.5175 | 0 | 0 | 7.3491 | 7.3491 | -16.5789 | 0% | 3.3233 | 0 | 0 | 139.2328 | 139.2328 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2493 | 21 | 13.3 | 0 | 0 | 0 | 0 | 0 | 104 | 2493 | 1260 | 102.5753 | 9.215 | 14.3914 | 1234.284 | 20.8113 | -132.1688 | -19.7008 | 0 | 103.5232 | 283.5232 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4029 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2494 | 22 | 12.5 | 0 | 0 | 0 | 0 | 0 | 104 | 2494 | 1320 | 102.5753 | 9.215 | 14.3914 | 1294.284 | 21.8113 | -147.1688 | -26.8284 | 0 | 103.5232 | 283.5232 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3436 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2495 | 23 | 11.7 | 0 | 0 | 0 | 0 | 0 | 104 | 2495 | 1380 | 102.5753 | 9.215 | 14.3914 | 1354.284 | 22.8113 | -162.1688 | -31.791 | 0 | 103.5232 | 283.5232 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9058 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
4 | 104 | 14 | 2496 | 24 | 11.3 | 0 | 0 | 0 | 0 | 0 | 104 | 2496 | 1440 | 102.5753 | 9.215 | 14.3914 | 1414.284 | 23.8113 | -177.1688 | -33.95 | 0 | 103.5232 | 283.5232 | 99.5175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8584 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2497 | 1 | 11.1 | 0 | 0 | 0 | 0 | 0 | 105 | 2497 | 60 | 103.5616 | 9.5861 | 14.5991 | 34.284 | 0.81472 | 167.7792 | -32.5892 | 0 | 104.0737 | 75.9263 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8992 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2498 | 2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 105 | 2498 | 120 | 103.5616 | 9.5861 | 14.5991 | 94.284 | 1.8147 | 152.7792 | -28.6285 | 0 | 104.0737 | 75.9263 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9977 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2499 | 3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 105 | 2499 | 180 | 103.5616 | 9.5861 | 14.5991 | 154.284 | 2.8147 | 137.7792 | -22.2546 | 0 | 104.0737 | 75.9263 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4011 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2500 | 4 | 8.6 | 0 | 0 | 0 | 0 | 0 | 105 | 2500 | 240 | 103.5616 | 9.5861 | 14.5991 | 214.284 | 3.8147 | 122.7792 | -14.1369 | 0 | 104.0737 | 75.9263 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.687 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2501 | 5 | 7.2 | 0 | 0 | 0 | 0 | 0 | 105 | 2501 | 300 | 103.5616 | 9.5861 | 14.5991 | 274.284 | 4.8147 | 107.7792 | -4.8669 | 0 | 104.0737 | 75.9263 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.0567 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2502 | 6 | 6.3 | 0 | 0 | 0 | 0 | 0 | 105 | 2502 | 360 | 103.5616 | 9.5861 | 14.5991 | 334.284 | 5.8147 | 92.7792 | 5.0836 | 5.0836 | 98.5963 | 81.4037 | 92.4427 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.7284 | 2.7284 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2503 | 7 | 6 | 7.42 | 14.81 | 22.23 | 14.81 | 7.41 | 105 | 2503 | 420 | 103.5616 | 9.5861 | 14.5991 | 394.284 | 6.8147 | 77.7792 | 15.3248 | 15.3248 | 87.7387 | 92.2613 | 77.6555 | 6.0022 | 6.0022 | 12.6411 | 18.6433 | -7.0747 | 0% | 8.4305 | 0 | 0 | 166.5016 | 166.5016 | 0% | 11.95% | 11.95% | 80% | 9.563% | 0.8062 | 8.3898 | 6 | 4.8372 | 1.7828 | 2.905% | 2.905%
4 | 105 | 15 | 2504 | 8 | 8.5 | 59.17 | 48.89 | 108.06 | 48.89 | 24.45 | 105 | 2504 | 480 | 103.5616 | 9.5861 | 14.5991 | 454.284 | 7.8147 | 62.7792 | 25.4822 | 25.4822 | 76.2459 | 103.7541 | 62.8718 | 62.7118 | 62.7118 | 41.7302 | 104.442 | -0.5456 | 0% | 47.2287 | 0 | 0 | 182.2072 | 182.2072 | 0% | 11.79% | 11.79% | 80% | 9.434% | 4.4553 | 7.6737 | 6 | 26.732 | 9.8526 | 14.67% | 14.67%
4 | 105 | 15 | 2505 | 9 | 11.5 | 141.11 | 82.78 | 223.89 | 82.78 | 41.39 | 105 | 2505 | 540 | 103.5616 | 9.5861 | 14.5991 | 514.284 | 8.8147 | 47.7792 | 35.1081 | 35.1081 | 63.2037 | 116.7963 | 48.1291 | 163.7645 | 163.7645 | 70.6571 | 234.4216 | 0.23259 | 23.26% | 106.0055 | 24.6562 | 17.2593 | 151.0019 | 151.0019 | 11.43% | 11.62% | 11.62% | 80% | 9.293% | 9.8512 | 6.8721 | 6 | 59.1073 | 21.7851 | 39.14% | 39.14%
4 | 105 | 15 | 2506 | 10 | 14.5 | 231.86 | 92.78 | 324.64 | 92.78 | 46.39 | 105 | 2506 | 600 | 103.5616 | 9.5861 | 14.5991 | 574.284 | 9.8147 | 32.7792 | 43.558 | 43.558 | 47.448 | 132.552 | 33.5099 | 280.5487 | 280.5487 | 79.1927 | 359.7414 | 0.45079 | 45.08% | 162.675 | 73.3316 | 51.3321 | 157.5954 | 157.5954 | 32.57% | 11.49% | 11.49% | 85% | 9.762% | 15.881 | 6.1335 | 6 | 95.2859 | 35.1194 | 60.46% | 60.46%
4 | 105 | 15 | 2507 | 11 | 15.3 | 352.5 | 100.83 | 453.33 | 100.83 | 50.42 | 105 | 2507 | 660 | 103.5616 | 9.5861 | 14.5991 | 634.284 | 10.8147 | 17.7792 | 49.8505 | 49.8505 | 27.8369 | 152.1631 | 19.3247 | 435.1845 | 435.1845 | 86.0638 | 521.2482 | 0.56371 | 56.37% | 235.7085 | 132.8715 | 93.01 | 156.9677 | 156.9677 | 59.25% | 11.42% | 11.42% | 90% | 10.28% | 24.2347 | 5.9472 | 5.9472 | 144.1277 | 53.5929 | 91.82% | 91.82%
4 | 105 | 15 | 2508 | 12 | 15.2 | 304.17 | 149.25 | 453.42 | 149.25 | 74.63 | 105 | 2508 | 720 | 103.5616 | 9.5861 | 14.5991 | 694.284 | 11.8147 | 2.7792 | 52.7329 | 52.7329 | 4.5286 | 175.4714 | 8.2826 | 378.2225 | 378.2225 | 127.3928 | 505.6153 | 0.55583 | 55.58% | 228.6393 | 127.0854 | 88.9598 | 145.9118 | 145.9118 | 60.97% | 11.43% | 11.43% | 90% | 10.29% | 23.5195 | 5.9702 | 5.9702 | 140.4163 | 52.0114 | 96.23% | 96.23%
4 | 105 | 15 | 2509 | 13 | 16.1 | 401.47 | 156.11 | 557.58 | 156.11 | 78.06 | 105 | 2509 | 780 | 103.5616 | 9.5861 | 14.5991 | 754.284 | 12.8147 | -12.2208 | 51.381 | 51.381 | 19.5372 | 199.5372 | 14.4433 | 497.6002 | 497.6002 | 133.2482 | 630.8484 | 0.60832 | 60.83% | 285.2697 | 173.5357 | 121.475 | 148.6216 | 148.6216 | 81.73% | 11.39% | 11.39% | 90% | 10.25% | 29.2386 | 5.7653 | 5.7653 | 168.5697 | 64.6585 | 113.4% | 113.4%
4 | 105 | 15 | 2510 | 14 | 16.1 | 397.97 | 143.53 | 541.5 | 143.53 | 71.77 | 105 | 2510 | 840 | 103.5616 | 9.5861 | 14.5991 | 814.284 | 13.8147 | -27.2208 | 46.2058 | 46.2058 | 40.6711 | 220.6711 | 28.1667 | 486.0448 | 486.0448 | 122.5105 | 608.5553 | 0.60115 | 60.12% | 275.1887 | 165.4307 | 115.8015 | 146.2906 | 146.2906 | 79.16% | 11.39% | 11.39% | 90% | 10.25% | 28.2172 | 5.7653 | 5.7653 | 162.681 | 62.3998 | 111.2% | 111.2%
4 | 105 | 15 | 2511 | 15 | 16.6 | 226.03 | 176.47 | 402.5 | 176.47 | 88.24 | 105 | 2511 | 900 | 103.5616 | 9.5861 | 14.5991 | 874.284 | 14.8147 | -42.2208 | 38.4203 | 38.4203 | 57.7501 | 237.7501 | 42.6898 | 267.3533 | 267.3533 | 150.6266 | 417.9799 | 0.51136 | 51.14% | 189.0105 | 96.6521 | 67.6565 | 138.745 | 138.745 | 48.76% | 11.42% | 11.42% | 85% | 9.71% | 18.3528 | 5.6539 | 5.6539 | 103.7655 | 40.5855 | 74.79% | 74.79%
4 | 105 | 15 | 2512 | 16 | 17.1 | 155.28 | 162.5 | 317.78 | 162.5 | 81.25 | 105 | 2512 | 960 | 103.5616 | 9.5861 | 14.5991 | 934.284 | 15.8147 | -57.2208 | 29.1397 | 29.1397 | 71.6503 | 251.6503 | 57.4012 | 171.8023 | 171.8023 | 138.7024 | 310.5048 | 0.41368 | 41.37% | 140.4102 | 58.0847 | 40.6593 | 133.6801 | 133.6801 | 30.42% | 11.43% | 11.43% | 85% | 9.716% | 13.6416 | 5.5443 | 5.5443 | 75.6336 | 30.1673 | 56.58% | 56.58%
4 | 105 | 15 | 2513 | 17 | 17.2 | 135.56 | 123.42 | 258.98 | 123.42 | 61.71 | 105 | 2513 | 1020 | 103.5616 | 9.5861 | 14.5991 | 994.284 | 16.8147 | -72.2208 | 19.1197 | 19.1197 | 83.5976 | 263.5976 | 72.1752 | 126.6889 | 126.6889 | 105.3456 | 232.0345 | 0.28264 | 28.26% | 104.926 | 29.6566 | 20.7596 | 128.557 | 128.557 | 16.15% | 11.44% | 11.44% | 80% | 9.152% | 9.6024 | 5.5226 | 5.5226 | 53.0301 | 21.2348 | 41.25% | 41.25%
4 | 105 | 15 | 2514 | 18 | 16.1 | 79.17 | 83.89 | 163.06 | 83.89 | 41.95 | 105 | 2514 | 1080 | 103.5616 | 9.5861 | 14.5991 | 1054.284 | 17.8147 | -87.2208 | 8.8642 | 8.8642 | 94.5978 | 274.5978 | 86.9645 | 0 | 0 | 71.6046 | 71.6046 | -0.91996 | 0% | 32.3796 | 0 | 0 | 118.6475 | 118.6475 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2515 | 19 | 14.7 | 29.72 | 42.42 | 72.14 | 42.42 | 21.21 | 105 | 2515 | 1140 | 103.5616 | 9.5861 | 14.5991 | 1114.284 | 18.8147 | -102.2208 | -1.237 | 0 | 104.0737 | 284.0737 | 99.901 | 0 | 0 | 36.2077 | 36.2077 | -2.6928 | 0% | 16.3731 | 0 | 0 | 150.2272 | 150.2272 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2516 | 20 | 13 | 0 | 6.75 | 6.75 | 6.75 | 3.38 | 105 | 2516 | 1200 | 103.5616 | 9.5861 | 14.5991 | 1174.284 | 19.8147 | -117.2208 | -10.8086 | 0 | 104.0737 | 284.0737 | 99.901 | 0 | 0 | 5.7615 | 5.7615 | -21.8452 | 0% | 2.6053 | 0 | 0 | 137.5264 | 137.5264 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2517 | 21 | 12.4 | 0 | 0 | 0 | 0 | 0 | 105 | 2517 | 1260 | 103.5616 | 9.5861 | 14.5991 | 1234.284 | 20.8147 | -132.2208 | -19.4157 | 0 | 104.0737 | 284.0737 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1299 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2518 | 22 | 11.6 | 0 | 0 | 0 | 0 | 0 | 105 | 2518 | 1320 | 103.5616 | 9.5861 | 14.5991 | 1294.284 | 21.8147 | -147.2208 | -26.5121 | 0 | 104.0737 | 284.0737 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6704 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2519 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 105 | 2519 | 1380 | 103.5616 | 9.5861 | 14.5991 | 1354.284 | 22.8147 | -162.2208 | -31.4439 | 0 | 104.0737 | 284.0737 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0737 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
4 | 105 | 15 | 2520 | 24 | 10.8 | 0 | 0 | 0 | 0 | 0 | 105 | 2520 | 1440 | 103.5616 | 9.5861 | 14.5991 | 1414.284 | 23.8147 | -177.2208 | -33.5813 | 0 | 104.0737 | 284.0737 | 99.901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8675 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2521 | 1 | 10.7 | 0 | 0 | 0 | 0 | 0 | 106 | 2521 | 60 | 104.5479 | 9.9544 | 14.7958 | 34.284 | 0.818 | 167.7301 | -32.218 | 0 | 104.6208 | 75.3792 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0124 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2522 | 2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 106 | 2522 | 120 | 104.5479 | 9.9544 | 14.7958 | 94.284 | 1.818 | 152.7301 | -28.2671 | 0 | 104.6208 | 75.3792 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8251 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2523 | 3 | 10.2 | 0 | 0 | 0 | 0 | 0 | 106 | 2523 | 180 | 104.5479 | 9.9544 | 14.7958 | 154.284 | 2.818 | 137.7301 | -21.911 | 0 | 104.6208 | 75.3792 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4854 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2524 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 106 | 2524 | 240 | 104.5479 | 9.9544 | 14.7958 | 214.284 | 3.818 | 122.7301 | -13.8117 | 0 | 104.6208 | 75.3792 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7902 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2525 | 5 | 9.7 | 0 | 0 | 0 | 0 | 0 | 106 | 2525 | 300 | 104.5479 | 9.9544 | 14.7958 | 274.284 | 4.818 | 107.7301 | -4.5567 | 0 | 104.6208 | 75.3792 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.9359 | 2.9359 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2526 | 6 | 9.4 | 0 | 0 | 0 | 0 | 0 | 106 | 2526 | 360 | 104.5479 | 9.9544 | 14.7958 | 334.284 | 5.818 | 92.7301 | 5.3845 | 5.3845 | 98.815 | 81.185 | 92.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 14.7798 | 14.7798 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2527 | 7 | 9.6 | 11.86 | 17.5 | 29.36 | 17.5 | 8.75 | 106 | 2527 | 420 | 104.5479 | 9.9544 | 14.7958 | 394.284 | 6.818 | 77.7301 | 15.6234 | 15.6234 | 87.9679 | 92.0321 | 77.609 | 9.4497 | 9.4497 | 14.9372 | 24.3869 | -4.8701 | 0% | 11.0277 | 0 | 0 | 185.8469 | 185.8469 | 0% | 11.8% | 11.8% | 80% | 9.437% | 1.0406 | 7.3724 | 6 | 6.2438 | 2.3013 | 3.36% | 3.36%
4 | 106 | 16 | 2528 | 8 | 9.8 | 89.25 | 52.69 | 141.94 | 52.69 | 26.35 | 106 | 2528 | 480 | 104.5479 | 9.9544 | 14.7958 | 454.284 | 7.818 | 62.7301 | 25.7865 | 25.7865 | 76.4821 | 103.5179 | 62.8429 | 93.643 | 93.643 | 44.9737 | 138.6167 | -0.19086 | 0% | 62.6825 | 0 | 0 | 201.9169 | 201.9169 | 0% | 11.72% | 11.72% | 80% | 9.378% | 5.8786 | 7.3186 | 6 | 35.2718 | 13.0001 | 17.47% | 17.47%
4 | 106 | 16 | 2529 | 9 | 11.9 | 199.64 | 89.92 | 289.56 | 89.92 | 44.96 | 106 | 2529 | 540 | 104.5479 | 9.9544 | 14.7958 | 514.284 | 8.818 | 47.7301 | 35.4269 | 35.4269 | 63.4373 | 116.5627 | 48.1223 | 229.9062 | 229.9062 | 76.7515 | 306.6577 | 0.37021 | 37.02% | 138.6706 | 51.3372 | 35.936 | 170.9854 | 170.9854 | 21.02% | 11.57% | 11.57% | 85% | 9.836% | 13.6397 | 6.77 | 6 | 81.838 | 30.1629 | 47.86% | 47.86%
4 | 106 | 16 | 2530 | 10 | 15.7 | 303.42 | 127.42 | 430.84 | 127.42 | 63.71 | 106 | 2530 | 600 | 104.5479 | 9.9544 | 14.7958 | 574.284 | 9.818 | 32.7301 | 43.899 | 43.899 | 47.6517 | 132.3483 | 33.5372 | 364.7431 | 364.7431 | 108.7598 | 473.5029 | 0.54139 | 54.14% | 214.118 | 115.9217 | 81.1452 | 179.6613 | 179.6613 | 45.17% | 11.43% | 11.43% | 85% | 9.715% | 20.8012 | 5.8557 | 5.8557 | 121.8051 | 46 | 67.8% | 67.8%
4 | 106 | 16 | 2531 | 11 | 17 | 417.86 | 141.39 | 559.25 | 141.39 | 70.7 | 106 | 2531 | 660 | 104.5479 | 9.9544 | 14.7958 | 634.284 | 10.818 | 17.7301 | 50.2145 | 50.2145 | 27.952 | 152.048 | 19.4256 | 512.8181 | 512.8181 | 120.6839 | 633.5021 | 0.61233 | 61.23% | 286.4696 | 175.4151 | 122.7906 | 177.2433 | 177.2433 | 69.28% | 11.38% | 11.38% | 90% | 10.24% | 29.3389 | 5.5661 | 5.5661 | 163.303 | 64.8803 | 92.13% | 92.13%
4 | 106 | 16 | 2532 | 12 | 16.8 | 530.19 | 183.89 | 714.08 | 183.89 | 91.95 | 106 | 2532 | 720 | 104.5479 | 9.9544 | 14.7958 | 694.284 | 11.818 | 2.7301 | 53.1033 | 53.1033 | 4.4817 | 175.5183 | 8.6148 | 655.4906 | 655.4906 | 156.9599 | 812.4506 | 0.654 | 65.4% | 367.3902 | 240.2724 | 168.1907 | 168.9183 | 168.9183 | 99.57% | 11.35% | 11.35% | 95% | 10.78% | 39.6132 | 5.6099 | 5.6099 | 222.2252 | 87.601 | 131.6% | 131.6%
4 | 106 | 16 | 2533 | 13 | 16.4 | 509.25 | 183.33 | 692.58 | 183.33 | 91.67 | 106 | 2533 | 780 | 104.5479 | 9.9544 | 14.7958 | 754.284 | 12.818 | -12.2699 | 51.7278 | 51.7278 | 19.7513 | 199.7513 | 14.6821 | 627.482 | 627.482 | 156.4819 | 783.964 | 0.6474 | 64.74% | 354.5085 | 229.5092 | 160.6564 | 164.0882 | 164.0882 | 97.91% | 11.36% | 11.36% | 90% | 10.22% | 36.2296 | 5.6983 | 5.6983 | 206.4462 | 80.1184 | 125.8% | 125.8%
4 | 106 | 16 | 2534 | 14 | 17.8 | 384.81 | 209.44 | 594.25 | 209.44 | 104.72 | 106 | 2534 | 840 | 104.5479 | 9.9544 | 14.7958 | 814.284 | 13.818 | -27.2699 | 46.5119 | 46.5119 | 40.9761 | 220.9761 | 28.3071 | 466.9689 | 466.9689 | 178.7682 | 645.7371 | 0.61874 | 61.87% | 292.0023 | 180.6722 | 126.4706 | 160.9993 | 160.9993 | 78.55% | 11.37% | 11.37% | 90% | 10.23% | 29.8823 | 5.3938 | 5.3938 | 161.1788 | 66.0822 | 100.1% | 100.1%
4 | 106 | 16 | 2535 | 15 | 18.5 | 407.69 | 197.97 | 605.66 | 197.97 | 98.99 | 106 | 2535 | 900 | 104.5479 | 9.9544 | 14.7958 | 874.284 | 14.818 | -42.2699 | 38.6895 | 38.6895 | 58.0774 | 238.0774 | 42.7893 | 478.6218 | 478.6218 | 168.978 | 647.5997 | 0.62167 | 62.17% | 292.8446 | 182.054 | 127.4378 | 159.5367 | 159.5367 | 79.88% | 11.36% | 11.36% | 90% | 10.23% | 29.9525 | 5.2467 | 5.2467 | 157.151 | 66.2372 | 98.5% | 98.5%
4 | 106 | 16 | 2536 | 16 | 16.3 | 329.25 | 191.86 | 521.11 | 191.86 | 95.93 | 106 | 2536 | 960 | 104.5479 | 9.9544 | 14.7958 | 934.284 | 15.818 | -57.2699 | 29.3844 | 29.3844 | 71.9707 | 251.9707 | 57.4762 | 360.7768 | 360.7768 | 163.7628 | 524.5396 | 0.56952 | 56.95% | 237.1968 | 135.0888 | 94.5622 | 150.4705 | 150.4705 | 62.84% | 11.41% | 11.41% | 90% | 10.27% | 24.3536 | 5.7206 | 5.7206 | 139.3161 | 53.8558 | 92.59% | 92.59%
4 | 106 | 16 | 2537 | 17 | 16.7 | 268.69 | 144.25 | 412.94 | 144.25 | 72.13 | 106 | 2537 | 1020 | 104.5479 | 9.9544 | 14.7958 | 994.284 | 16.818 | -72.2699 | 19.3525 | 19.3525 | 83.9041 | 263.9041 | 72.2318 | 247.4365 | 247.4365 | 123.1251 | 370.5615 | 0.47452 | 47.45% | 167.5679 | 79.5138 | 55.6597 | 143.0705 | 143.0705 | 38.9% | 11.43% | 11.43% | 85% | 9.715% | 16.28 | 5.6319 | 5.6319 | 91.6868 | 36.0017 | 64.09% | 64.09%
4 | 106 | 16 | 2538 | 18 | 16.9 | 177.69 | 95.75 | 273.44 | 95.75 | 47.88 | 106 | 2538 | 1080 | 104.5479 | 9.9544 | 14.7958 | 1054.284 | 17.818 | -87.2699 | 9.0963 | 9.0963 | 94.8914 | 274.8914 | 87.0047 | 0 | 0 | 81.7277 | 81.7277 | -0.68442 | 0% | 36.9573 | 0 | 0 | 131.8082 | 131.8082 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2539 | 19 | 15.9 | 40.75 | 60.56 | 101.31 | 60.56 | 30.28 | 106 | 2539 | 1140 | 104.5479 | 9.9544 | 14.7958 | 1114.284 | 18.818 | -102.2699 | -0.99585 | 0 | 104.6208 | 284.6208 | 100.2817 | 0 | 0 | 51.6912 | 51.6912 | -1.5928 | 0% | 23.3748 | 0 | 0 | 157.0457 | 157.0457 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2540 | 20 | 14 | 0 | 14.92 | 14.92 | 14.92 | 7.46 | 106 | 2540 | 1200 | 104.5479 | 9.9544 | 14.7958 | 1174.284 | 19.818 | -117.2699 | -10.5495 | 0 | 104.6208 | 284.6208 | 100.2817 | 0 | 0 | 12.735 | 12.735 | -9.2631 | 0% | 5.7588 | 0 | 0 | 139.8608 | 139.8608 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2541 | 21 | 13.4 | 0 | 0 | 0 | 0 | 0 | 106 | 2541 | 1260 | 104.5479 | 9.9544 | 14.7958 | 1234.284 | 20.818 | -132.2699 | -19.131 | 0 | 104.6208 | 284.6208 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8822 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2542 | 22 | 11.8 | 0 | 0 | 0 | 0 | 0 | 106 | 2542 | 1320 | 104.5479 | 9.9544 | 14.7958 | 1294.284 | 21.818 | -147.2699 | -26.1968 | 0 | 104.6208 | 284.6208 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2696 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2543 | 23 | 11.1 | 0 | 0 | 0 | 0 | 0 | 106 | 2543 | 1380 | 104.5479 | 9.9544 | 14.7958 | 1354.284 | 22.818 | -162.2699 | -31.0986 | 0 | 104.6208 | 284.6208 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6919 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
4 | 106 | 16 | 2544 | 24 | 10.4 | 0 | 0 | 0 | 0 | 0 | 106 | 2544 | 1440 | 104.5479 | 9.9544 | 14.7958 | 1414.284 | 23.818 | -177.2699 | -33.2152 | 0 | 104.6208 | 284.6208 | 100.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1141 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2545 | 1 | 10.3 | 0 | 0 | 0 | 0 | 0 | 107 | 2545 | 60 | 105.5342 | 10.3198 | 14.981 | 34.284 | 0.82108 | 167.6837 | -31.8502 | 0 | 105.1643 | 74.8357 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6694 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2546 | 2 | 9.5 | 0 | 0 | 0 | 0 | 0 | 107 | 2546 | 120 | 105.5342 | 10.3198 | 14.981 | 94.284 | 1.8211 | 152.6837 | -27.9094 | 0 | 105.1643 | 74.8357 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9542 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2547 | 3 | 9.4 | 0 | 0 | 0 | 0 | 0 | 107 | 2547 | 180 | 105.5342 | 10.3198 | 14.981 | 154.284 | 2.8211 | 137.6837 | -21.5711 | 0 | 105.1643 | 74.8357 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1723 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2548 | 4 | 9.1 | 0 | 0 | 0 | 0 | 0 | 107 | 2548 | 240 | 105.5342 | 10.3198 | 14.981 | 214.284 | 3.8211 | 122.6837 | -13.4905 | 0 | 105.1643 | 74.8357 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6295 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2549 | 5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 107 | 2549 | 300 | 105.5342 | 10.3198 | 14.981 | 274.284 | 4.8211 | 107.6837 | -4.2505 | 0 | 105.1643 | 74.8357 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.7802 | 9.7802 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2550 | 6 | 8.8 | 0 | 0 | 0 | 0 | 0 | 107 | 2550 | 360 | 105.5342 | 10.3198 | 14.981 | 334.284 | 5.8211 | 92.6837 | 5.6813 | 5.6813 | 99.034 | 80.966 | 92.3203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 25.5734 | 25.5734 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2551 | 7 | 8.7 | 15.47 | 18.69 | 34.16 | 18.69 | 9.35 | 107 | 2551 | 420 | 105.5342 | 10.3198 | 14.981 | 394.284 | 6.8211 | 77.6837 | 15.9178 | 15.9178 | 88.1978 | 91.8022 | 77.566 | 12.1452 | 12.1452 | 15.9529 | 28.0981 | -4.1958 | 0% | 12.706 | 0 | 0 | 204.5077 | 204.5077 | 0% | 11.83% | 11.83% | 80% | 9.465% | 1.2027 | 7.6183 | 6 | 7.216 | 2.6596 | 3.528% | 3.528%
4 | 107 | 17 | 2552 | 8 | 10 | 128.06 | 49.92 | 177.98 | 49.92 | 24.96 | 107 | 2552 | 480 | 105.5342 | 10.3198 | 14.981 | 454.284 | 7.8211 | 62.6837 | 26.0864 | 26.0864 | 76.7198 | 103.2802 | 62.818 | 133.0379 | 133.0379 | 42.6094 | 175.6473 | 0.021537 | 2.154% | 79.4277 | 1.7106 | 1.1974 | 184.8459 | 184.8459 | 0.6478% | 11.7% | 11.7% | 80% | 9.356% | 7.4315 | 7.265 | 6 | 44.589 | 16.4341 | 24.12% | 24.12%
4 | 107 | 17 | 2553 | 9 | 11.7 | 292.78 | 68.61 | 361.39 | 68.61 | 34.31 | 107 | 2553 | 540 | 105.5342 | 10.3198 | 14.981 | 514.284 | 8.8211 | 47.6837 | 35.7412 | 35.7412 | 63.6733 | 116.3267 | 48.1201 | 334.6059 | 334.6059 | 58.5623 | 393.1682 | 0.46448 | 46.45% | 177.7907 | 82.5807 | 57.8065 | 197.039 | 197.039 | 29.34% | 11.54% | 11.54% | 85% | 9.807% | 17.436 | 6.8209 | 6 | 104.6162 | 38.5582 | 53.09% | 53.09%
4 | 107 | 17 | 2554 | 10 | 13.1 | 418.42 | 91.19 | 509.61 | 91.19 | 45.6 | 107 | 2554 | 600 | 105.5342 | 10.3198 | 14.981 | 574.284 | 9.8211 | 32.6837 | 44.2357 | 44.2357 | 47.8592 | 132.1408 | 33.5703 | 499.7493 | 499.7493 | 77.8355 | 577.5848 | 0.57847 | 57.85% | 261.1839 | 151.0867 | 105.7607 | 200.3295 | 200.3295 | 52.79% | 11.44% | 11.44% | 90% | 10.29% | 26.883 | 6.4703 | 6 | 161.2983 | 59.4495 | 80.52% | 80.52%
4 | 107 | 17 | 2555 | 11 | 14.8 | 446.75 | 149.08 | 595.83 | 149.08 | 74.54 | 107 | 2555 | 660 | 105.5342 | 10.3198 | 14.981 | 634.284 | 10.8211 | 17.6837 | 50.5748 | 50.5748 | 28.0717 | 151.9283 | 19.5342 | 545.0628 | 545.0628 | 127.2477 | 672.3106 | 0.61602 | 61.6% | 304.0188 | 187.2804 | 131.0963 | 192.8099 | 192.8099 | 67.99% | 11.39% | 11.39% | 90% | 10.25% | 31.1609 | 6.0631 | 6 | 186.9655 | 68.9096 | 96.97% | 96.97%
4 | 107 | 17 | 2556 | 12 | 16.3 | 555.75 | 142.97 | 698.72 | 142.97 | 71.49 | 107 | 2556 | 720 | 105.5342 | 10.3198 | 14.981 | 694.284 | 11.8211 | 2.6837 | 53.4706 | 53.4706 | 4.4386 | 175.5614 | 8.9482 | 683.1997 | 683.1997 | 122.0325 | 805.2323 | 0.65126 | 65.13% | 364.126 | 237.1399 | 165.998 | 179.5205 | 179.5205 | 92.47% | 11.35% | 11.35% | 95% | 10.78% | 39.2651 | 5.7206 | 5.7206 | 224.6183 | 86.8313 | 125.1% | 125.1%
4 | 107 | 17 | 2557 | 13 | 17 | 698.81 | 116.19 | 815 | 116.19 | 58.1 | 107 | 2557 | 780 | 105.5342 | 10.3198 | 14.981 | 754.284 | 12.8211 | -12.3163 | 52.072 | 52.072 | 19.963 | 199.963 | 14.9223 | 856.056 | 856.056 | 99.1744 | 955.2304 | 0.67689 | 67.69% | 431.9552 | 292.3855 | 204.6698 | 179.6344 | 179.6344 | 113.9% | 11.33% | 11.33% | 95% | 10.76% | 46.4787 | 5.5661 | 5.5661 | 258.7049 | 102.7834 | 144% | 144%
4 | 107 | 17 | 2558 | 14 | 17.3 | 628.69 | 150.83 | 779.52 | 150.83 | 75.42 | 107 | 2558 | 840 | 105.5342 | 10.3198 | 14.981 | 814.284 | 13.8211 | -27.3163 | 46.8159 | 46.8159 | 41.2788 | 221.2788 | 28.4478 | 758.102 | 758.102 | 128.7415 | 886.8435 | 0.66784 | 66.78% | 401.0306 | 267.8259 | 187.4781 | 176.0208 | 176.0208 | 106.5% | 11.34% | 11.34% | 95% | 10.77% | 43.1996 | 5.501 | 5.501 | 237.6391 | 95.5321 | 135% | 135%
4 | 107 | 17 | 2559 | 15 | 17.4 | 542.31 | 168.14 | 710.45 | 168.14 | 84.07 | 107 | 2559 | 900 | 105.5342 | 10.3198 | 14.981 | 874.284 | 14.8211 | -42.3163 | 38.9571 | 38.9571 | 58.4021 | 238.4021 | 42.8879 | 631.9688 | 631.9688 | 143.5165 | 775.4853 | 0.64858 | 64.86% | 350.6744 | 227.4407 | 159.2085 | 169.0668 | 169.0668 | 94.17% | 11.36% | 11.36% | 90% | 10.22% | 35.8388 | 5.4794 | 5.4794 | 196.3742 | 79.2542 | 116.2% | 116.2%
4 | 107 | 17 | 2560 | 16 | 18.1 | 415.47 | 189.81 | 605.28 | 189.81 | 94.91 | 107 | 2560 | 960 | 105.5342 | 10.3198 | 14.981 | 934.284 | 15.8211 | -57.3163 | 29.628 | 29.628 | 72.288 | 252.288 | 57.5497 | 450.9365 | 450.9365 | 162.013 | 612.9494 | 0.60992 | 60.99% | 277.1757 | 169.054 | 118.3378 | 162.5019 | 162.5019 | 72.82% | 11.37% | 11.37% | 90% | 10.23% | 28.3673 | 5.3303 | 5.3303 | 151.2064 | 62.7316 | 93.05% | 93.05%
4 | 107 | 17 | 2561 | 17 | 17.9 | 138.81 | 167.86 | 306.67 | 167.86 | 83.93 | 107 | 2561 | 1020 | 105.5342 | 10.3198 | 14.981 | 994.284 | 16.8211 | -72.3163 | 19.5848 | 19.5848 | 84.2072 | 264.2072 | 72.2862 | 125.9982 | 125.9982 | 143.2775 | 269.2756 | 0.36055 | 36.06% | 121.7664 | 43.9034 | 30.7324 | 143.4418 | 143.4418 | 21.42% | 11.41% | 11.41% | 80% | 9.131% | 11.1181 | 5.3726 | 5.3726 | 59.7324 | 24.5866 | 41.64% | 41.64%
4 | 107 | 17 | 2562 | 18 | 13.5 | 48.53 | 103.97 | 152.5 | 103.97 | 51.99 | 107 | 2562 | 1080 | 105.5342 | 10.3198 | 14.981 | 1054.284 | 17.8211 | -87.3163 | 9.3281 | 9.3281 | 95.1813 | 275.1813 | 87.0421 | 0 | 0 | 88.7439 | 88.7439 | -0.65353 | 0% | 40.13 | 0 | 0 | 122.317 | 122.317 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2563 | 19 | 10.6 | 12.22 | 58.42 | 70.64 | 58.42 | 29.21 | 107 | 2563 | 1140 | 105.5342 | 10.3198 | 14.981 | 1114.284 | 18.8211 | -102.3163 | -0.75484 | 0 | 105.1643 | 285.1643 | 100.6594 | 0 | 0 | 49.8646 | 49.8646 | -1.9242 | 0% | 22.5488 | 0 | 0 | 149.286 | 149.286 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2564 | 20 | 10.6 | 0 | 6.47 | 6.47 | 6.47 | 3.24 | 107 | 2564 | 1200 | 105.5342 | 10.3198 | 14.981 | 1174.284 | 19.8211 | -117.3163 | -10.2907 | 0 | 105.1643 | 285.1643 | 100.6594 | 0 | 0 | 5.5225 | 5.5225 | -23.8296 | 0% | 2.4973 | 0 | 0 | 135.8418 | 135.8418 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2565 | 21 | 10.6 | 0 | 0 | 0 | 0 | 0 | 107 | 2565 | 1260 | 105.5342 | 10.3198 | 14.981 | 1234.284 | 20.8211 | -132.3163 | -18.8469 | 0 | 105.1643 | 285.1643 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8192 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2566 | 22 | 10.2 | 0 | 0 | 0 | 0 | 0 | 107 | 2566 | 1320 | 105.5342 | 10.3198 | 14.981 | 1294.284 | 21.8211 | -147.3163 | -25.8826 | 0 | 105.1643 | 285.1643 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6248 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2567 | 23 | 10 | 0 | 0 | 0 | 0 | 0 | 107 | 2567 | 1380 | 105.5342 | 10.3198 | 14.981 | 1354.284 | 22.8211 | -162.3163 | -30.7552 | 0 | 105.1643 | 285.1643 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9953 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
4 | 107 | 17 | 2568 | 24 | 9.9 | 0 | 0 | 0 | 0 | 0 | 107 | 2568 | 1440 | 105.5342 | 10.3198 | 14.981 | 1414.284 | 23.8211 | -177.3163 | -32.8518 | 0 | 105.1643 | 285.1643 | 100.6594 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2133 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2569 | 1 | 9.6 | 0 | 0 | 0 | 0 | 0 | 108 | 2569 | 60 | 106.5205 | 10.6822 | 15.1547 | 34.284 | 0.82398 | 167.6403 | -31.4859 | 0 | 105.704 | 74.296 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6767 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2570 | 2 | 9.4 | 0 | 0 | 0 | 0 | 0 | 108 | 2570 | 120 | 106.5205 | 10.6822 | 15.1547 | 94.284 | 1.824 | 152.6403 | -27.5555 | 0 | 105.704 | 74.296 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3144 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2571 | 3 | 9 | 0 | 0 | 0 | 0 | 0 | 108 | 2571 | 180 | 106.5205 | 10.6822 | 15.1547 | 154.284 | 2.824 | 137.6403 | -21.2351 | 0 | 105.704 | 74.296 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2568 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2572 | 4 | 8.9 | 0 | 0 | 0 | 0 | 0 | 108 | 2572 | 240 | 106.5205 | 10.6822 | 15.1547 | 214.284 | 3.824 | 122.6403 | -13.1733 | 0 | 105.704 | 74.296 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4091 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2573 | 5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 108 | 2573 | 300 | 106.5205 | 10.6822 | 15.1547 | 274.284 | 4.824 | 107.6403 | -3.9485 | 0 | 105.704 | 74.296 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.7305 | 1.7305 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2574 | 6 | 8.7 | 0 | 0 | 0 | 0 | 0 | 108 | 2574 | 360 | 106.5205 | 10.6822 | 15.1547 | 334.284 | 5.824 | 92.6403 | 5.9738 | 5.9738 | 99.2533 | 80.7467 | 92.2635 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 12.9908 | 12.9908 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2575 | 7 | 8.8 | 6.86 | 20.47 | 27.33 | 20.47 | 10.24 | 108 | 2575 | 420 | 106.5205 | 10.6822 | 15.1547 | 394.284 | 6.824 | 77.6403 | 16.2076 | 16.2076 | 88.4285 | 91.5715 | 77.5265 | 5.3084 | 5.3084 | 17.4722 | 22.7807 | -5.3525 | 0% | 10.3014 | 0 | 0 | 181.7866 | 181.7866 | 0% | 11.83% | 11.83% | 80% | 9.465% | 0.97499 | 7.5907 | 6 | 5.8499 | 2.1561 | 3.218% | 3.218%
4 | 108 | 18 | 2576 | 8 | 10.3 | 69.81 | 60.75 | 130.56 | 60.75 | 30.38 | 108 | 2576 | 480 | 106.5205 | 10.6822 | 15.1547 | 454.284 | 7.824 | 62.6403 | 26.3817 | 26.3817 | 76.9588 | 103.0412 | 62.797 | 71.8203 | 71.8203 | 51.8534 | 123.6737 | -0.30163 | 0% | 55.9252 | 0 | 0 | 198.6598 | 198.6598 | 0% | 11.71% | 11.71% | 80% | 9.37% | 5.2403 | 7.1852 | 6 | 31.442 | 11.5885 | 15.83% | 15.83%
4 | 108 | 18 | 2577 | 9 | 12.1 | 125.36 | 135.83 | 261.19 | 135.83 | 67.92 | 108 | 2577 | 540 | 106.5205 | 10.6822 | 15.1547 | 514.284 | 8.824 | 47.6403 | 36.0507 | 36.0507 | 63.9117 | 116.0883 | 48.1226 | 142.1961 | 142.1961 | 115.9382 | 258.1343 | 0.29046 | 29.05% | 116.7283 | 33.9043 | 23.733 | 166.1088 | 166.1088 | 14.29% | 11.59% | 11.59% | 80% | 9.27% | 10.8207 | 6.7193 | 6 | 64.924 | 23.9289 | 39.09% | 39.09%
4 | 108 | 18 | 2578 | 10 | 13.7 | 281.11 | 161.86 | 442.97 | 161.86 | 80.93 | 108 | 2578 | 600 | 106.5205 | 10.6822 | 15.1547 | 574.284 | 9.824 | 32.6403 | 44.5679 | 44.5679 | 48.0705 | 131.9295 | 33.6091 | 333.6179 | 333.6179 | 138.1562 | 471.774 | 0.5308 | 53.08% | 213.3362 | 113.2384 | 79.2669 | 173.3587 | 173.3587 | 45.72% | 11.47% | 11.47% | 85% | 9.746% | 20.7915 | 6.3243 | 6 | 124.7488 | 45.9785 | 71.96% | 71.96%
4 | 108 | 18 | 2579 | 11 | 15.8 | 372.31 | 194.72 | 567.03 | 194.72 | 97.36 | 108 | 2579 | 660 | 106.5205 | 10.6822 | 15.1547 | 634.284 | 10.824 | 17.6403 | 50.9311 | 50.9311 | 28.1961 | 151.8039 | 19.6502 | 451.614 | 451.614 | 166.2039 | 617.8179 | 0.6031 | 60.31% | 279.3773 | 168.4923 | 117.9446 | 172.2366 | 172.2366 | 68.48% | 11.39% | 11.39% | 90% | 10.25% | 28.6492 | 5.833 | 5.833 | 167.1104 | 63.3552 | 97.02% | 97.02%
4 | 108 | 18 | 2580 | 12 | 17.3 | 357.5 | 271.11 | 628.61 | 271.11 | 135.56 | 108 | 2580 | 720 | 106.5205 | 10.6822 | 15.1547 | 694.284 | 11.824 | 2.6403 | 53.8347 | 53.8347 | 4.3995 | 175.6005 | 9.2822 | 437.0258 | 437.0258 | 231.4069 | 668.4326 | 0.62335 | 62.34% | 302.2652 | 188.4185 | 131.893 | 163.337 | 163.337 | 80.75% | 11.37% | 11.37% | 90% | 10.23% | 30.935 | 5.501 | 5.501 | 170.172 | 68.41 | 104.2% | 104.2%
4 | 108 | 18 | 2581 | 13 | 18.2 | 224.53 | 289.25 | 513.78 | 289.25 | 144.63 | 108 | 2581 | 780 | 106.5205 | 10.6822 | 15.1547 | 754.284 | 12.824 | -12.3597 | 52.4137 | 52.4137 | 20.1722 | 200.1722 | 15.1633 | 273.4769 | 273.4769 | 246.8903 | 520.3673 | 0.57581 | 57.58% | 235.3101 | 135.4946 | 94.8462 | 156.4638 | 156.4638 | 60.62% | 11.38% | 11.38% | 90% | 10.24% | 24.0998 | 5.3093 | 5.3093 | 127.953 | 53.2945 | 81.78% | 81.78%
4 | 108 | 18 | 2582 | 14 | 18.7 | 265.75 | 274.25 | 540 | 274.25 | 137.13 | 108 | 2582 | 840 | 106.5205 | 10.6822 | 15.1547 | 814.284 | 13.824 | -27.3597 | 47.1178 | 47.1178 | 41.579 | 221.579 | 28.5885 | 318.4551 | 318.4551 | 234.087 | 552.5422 | 0.59111 | 59.11% | 249.8596 | 147.6947 | 103.3863 | 155.9056 | 155.9056 | 66.31% | 11.37% | 11.37% | 90% | 10.23% | 25.5674 | 5.2053 | 5.2053 | 133.0856 | 56.5401 | 85.36% | 85.36%
4 | 108 | 18 | 2583 | 15 | 18.9 | 33.33 | 202.5 | 235.83 | 202.5 | 101.25 | 108 | 2583 | 900 | 106.5205 | 10.6822 | 15.1547 | 874.284 | 14.824 | -42.3597 | 39.2232 | 39.2232 | 58.7238 | 238.7238 | 42.9855 | 38.5578 | 38.5578 | 172.8446 | 211.4024 | 0.24967 | 24.97% | 95.5962 | 23.8675 | 16.7072 | 139.2842 | 139.2842 | 12% | 11.39% | 11.39% | 80% | 9.11% | 8.7089 | 5.1642 | 5.1642 | 44.9741 | 19.2589 | 32.29% | 32.29%
4 | 108 | 18 | 2584 | 16 | 17.8 | 48.53 | 162.78 | 211.31 | 162.78 | 81.39 | 108 | 2584 | 960 | 106.5205 | 10.6822 | 15.1547 | 934.284 | 15.824 | -57.3597 | 29.8706 | 29.8706 | 72.6019 | 252.6019 | 57.6213 | 52.1811 | 52.1811 | 138.9414 | 191.1225 | 0.17806 | 17.81% | 86.4256 | 15.3885 | 10.772 | 133.2446 | 133.2446 | 8.084% | 11.43% | 11.43% | 80% | 9.141% | 7.8998 | 5.3938 | 5.3938 | 42.6096 | 17.4696 | 31.98% | 31.98%
4 | 108 | 18 | 2585 | 17 | 16.9 | 114.25 | 104.53 | 218.78 | 104.53 | 52.27 | 108 | 2585 | 1020 | 106.5205 | 10.6822 | 15.1547 | 994.284 | 16.824 | -72.3597 | 19.8164 | 19.8164 | 84.5067 | 264.5067 | 72.3383 | 102.2488 | 102.2488 | 89.2219 | 191.4707 | 0.16868 | 16.87% | 86.5831 | 14.6049 | 10.2234 | 129.0762 | 129.0762 | 7.92% | 11.46% | 11.46% | 80% | 9.165% | 7.935 | 5.588 | 5.588 | 44.3404 | 17.5475 | 34.35% | 34.35%
4 | 108 | 18 | 2586 | 18 | 16.8 | 8.69 | 78.81 | 87.5 | 78.81 | 39.41 | 108 | 2586 | 1080 | 106.5205 | 10.6822 | 15.1547 | 1054.284 | 17.824 | -87.3597 | 9.5596 | 9.5596 | 95.4672 | 275.4672 | 87.0768 | 0 | 0 | 67.2685 | 67.2685 | -1.0077 | 0% | 30.4188 | 0 | 0 | 159.5753 | 159.5753 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2587 | 19 | 15.8 | 14.08 | 54.44 | 68.52 | 54.44 | 27.22 | 108 | 2587 | 1140 | 106.5205 | 10.6822 | 15.1547 | 1114.284 | 18.824 | -102.3597 | -0.51408 | 0 | 105.704 | 285.704 | 101.034 | 0 | 0 | 46.4674 | 46.4674 | -1.8671 | 0% | 21.0126 | 0 | 0 | 152.9112 | 152.9112 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2588 | 20 | 14.6 | 0 | 7.86 | 7.86 | 7.86 | 3.93 | 108 | 2588 | 1200 | 106.5205 | 10.6822 | 15.1547 | 1174.284 | 19.824 | -117.3597 | -10.0322 | 0 | 105.704 | 285.704 | 101.034 | 0 | 0 | 6.7089 | 6.7089 | -18.1019 | 0% | 3.0338 | 0 | 0 | 140.5618 | 140.5618 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2589 | 21 | 13.9 | 0 | 0 | 0 | 0 | 0 | 108 | 2589 | 1260 | 106.5205 | 10.6822 | 15.1547 | 1234.284 | 20.824 | -132.3597 | -18.5635 | 0 | 105.704 | 285.704 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5581 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2590 | 22 | 12.4 | 0 | 0 | 0 | 0 | 0 | 108 | 2590 | 1320 | 106.5205 | 10.6822 | 15.1547 | 1294.284 | 21.824 | -147.3597 | -25.5696 | 0 | 105.704 | 285.704 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4112 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2591 | 23 | 10.9 | 0 | 0 | 0 | 0 | 0 | 108 | 2591 | 1380 | 106.5205 | 10.6822 | 15.1547 | 1354.284 | 22.824 | -162.3597 | -30.4138 | 0 | 105.704 | 285.704 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.03 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
4 | 108 | 18 | 2592 | 24 | 10.6 | 0 | 0 | 0 | 0 | 0 | 108 | 2592 | 1440 | 106.5205 | 10.6822 | 15.1547 | 1414.284 | 23.824 | -177.3597 | -32.4913 | 0 | 105.704 | 285.704 | 101.034 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.82 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2593 | 1 | 10.3 | 0 | 0 | 0 | 0 | 0 | 109 | 2593 | 60 | 107.5068 | 11.0414 | 15.3166 | 34.284 | 0.82668 | 167.5998 | -31.1252 | 0 | 106.2399 | 73.7601 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3382 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2594 | 2 | 9.4 | 0 | 0 | 0 | 0 | 0 | 109 | 2594 | 120 | 107.5068 | 11.0414 | 15.3166 | 94.284 | 1.8267 | 152.5998 | -27.2055 | 0 | 106.2399 | 73.7601 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9408 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2595 | 3 | 8.6 | 0 | 0 | 0 | 0 | 0 | 109 | 2595 | 180 | 107.5068 | 11.0414 | 15.3166 | 154.284 | 2.8267 | 137.5998 | -20.9033 | 0 | 106.2399 | 73.7601 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3909 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2596 | 4 | 8.6 | 0 | 0 | 0 | 0 | 0 | 109 | 2596 | 240 | 107.5068 | 11.0414 | 15.3166 | 214.284 | 3.8267 | 122.5998 | -12.8602 | 0 | 106.2399 | 73.7601 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3909 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2597 | 5 | 7.8 | 0 | 0 | 0 | 0 | 0 | 109 | 2597 | 300 | 107.5068 | 11.0414 | 15.3166 | 274.284 | 4.8267 | 107.5998 | -3.6508 | 0 | 106.2399 | 73.7601 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.3468 | 5.3468 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2598 | 6 | 6.9 | 0 | 0 | 0 | 0 | 0 | 109 | 2598 | 360 | 107.5068 | 11.0414 | 15.3166 | 334.284 | 5.8267 | 92.5998 | 6.2618 | 6.2618 | 99.4729 | 80.5271 | 92.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 18.2807 | 18.2807 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2599 | 7 | 7.4 | 13.42 | 25.28 | 38.7 | 25.28 | 12.64 | 109 | 2599 | 420 | 107.5068 | 11.0414 | 15.3166 | 394.284 | 6.8267 | 77.5998 | 16.4929 | 16.4929 | 88.6597 | 91.3403 | 77.4904 | 10.239 | 10.239 | 21.5778 | 31.8169 | -3.7079 | 0% | 14.3876 | 0 | 0 | 193.8393 | 193.8393 | 0% | 11.88% | 11.88% | 80% | 9.507% | 1.3679 | 7.9834 | 6 | 8.2074 | 3.025 | 4.234% | 4.234%
4 | 109 | 19 | 2600 | 8 | 8.2 | 105 | 63.81 | 168.81 | 63.81 | 31.91 | 109 | 2600 | 480 | 107.5068 | 11.0414 | 15.3166 | 454.284 | 7.8267 | 62.5998 | 26.6722 | 26.6722 | 77.1991 | 102.8009 | 62.78 | 106.9936 | 106.9936 | 54.4652 | 161.4589 | -0.073389 | 0% | 73.0117 | 0 | 0 | 171.1243 | 171.1243 | 0% | 11.77% | 11.77% | 80% | 9.413% | 6.8727 | 7.7573 | 6 | 41.2361 | 15.1983 | 24.1% | 24.1%
4 | 109 | 19 | 2601 | 9 | 9 | 229.44 | 112.69 | 342.13 | 112.69 | 56.35 | 109 | 2601 | 540 | 107.5068 | 11.0414 | 15.3166 | 514.284 | 8.8267 | 47.5998 | 36.3555 | 36.3555 | 64.1524 | 115.8476 | 48.1297 | 258.3339 | 258.3339 | 96.1869 | 354.5208 | 0.40972 | 40.97% | 160.3143 | 65.6846 | 45.9792 | 181.4564 | 181.4564 | 25.34% | 11.62% | 11.62% | 85% | 9.878% | 15.8363 | 7.5357 | 6 | 95.0179 | 35.0206 | 52.36% | 52.36%
4 | 109 | 19 | 2602 | 10 | 12.8 | 254.44 | 162.42 | 416.86 | 162.42 | 81.21 | 109 | 2602 | 600 | 107.5068 | 11.0414 | 15.3166 | 574.284 | 9.8267 | 32.5998 | 44.8955 | 44.8955 | 48.2855 | 131.7145 | 33.6536 | 300.0736 | 300.0736 | 138.6341 | 438.7078 | 0.50551 | 50.55% | 198.3837 | 100.284 | 70.1988 | 186.0098 | 186.0098 | 37.74% | 11.5% | 11.5% | 85% | 9.771% | 19.3837 | 6.5443 | 6 | 116.3022 | 42.8653 | 62.52% | 62.52%
4 | 109 | 19 | 2603 | 11 | 15.4 | 231.67 | 186.31 | 417.98 | 186.31 | 93.16 | 109 | 2603 | 660 | 107.5068 | 11.0414 | 15.3166 | 634.284 | 10.8267 | 17.5998 | 51.2833 | 51.2833 | 28.3252 | 151.6748 | 19.7732 | 279.4117 | 279.4117 | 159.0255 | 438.4372 | 0.51884 | 51.88% | 198.2613 | 102.8663 | 72.0064 | 178.4425 | 178.4425 | 40.35% | 11.44% | 11.44% | 85% | 9.727% | 19.2848 | 5.9242 | 5.9242 | 114.2466 | 42.6466 | 64.02% | 64.02%
4 | 109 | 19 | 2604 | 12 | 18.1 | 341.31 | 218.61 | 559.92 | 218.61 | 109.31 | 109 | 2604 | 720 | 107.5068 | 11.0414 | 15.3166 | 694.284 | 11.8267 | 2.5998 | 54.1956 | 54.1956 | 4.3645 | 175.6355 | 9.6161 | 414.9279 | 414.9279 | 186.5953 | 601.5232 | 0.60623 | 60.62% | 272.0088 | 164.8997 | 115.4298 | 172.0647 | 172.0647 | 67.09% | 11.37% | 11.37% | 90% | 10.24% | 27.8414 | 5.3303 | 5.3303 | 148.4033 | 61.5687 | 86.25% | 86.25%
4 | 109 | 19 | 2605 | 13 | 18.8 | 517.86 | 220.56 | 738.42 | 220.56 | 110.28 | 109 | 2605 | 780 | 107.5068 | 11.0414 | 15.3166 | 754.284 | 12.8267 | -12.4002 | 52.7527 | 52.7527 | 20.3785 | 200.3785 | 15.4048 | 627.1808 | 627.1808 | 188.2597 | 815.4406 | 0.66002 | 66% | 368.7422 | 243.3767 | 170.3637 | 176.6458 | 176.6458 | 96.44% | 11.35% | 11.35% | 95% | 10.78% | 39.7631 | 5.1847 | 5.1847 | 206.1588 | 87.9325 | 116.7% | 116.7%
4 | 109 | 19 | 2606 | 14 | 18.6 | 243.06 | 300 | 543.06 | 300 | 150 | 109 | 2606 | 840 | 107.5068 | 11.0414 | 15.3166 | 814.284 | 13.8267 | -27.4002 | 47.4176 | 47.4176 | 41.8766 | 221.8766 | 28.7291 | 289.4724 | 289.4724 | 256.066 | 545.5385 | 0.58797 | 58.8% | 246.6925 | 145.0481 | 101.5337 | 167.1151 | 167.1151 | 60.76% | 11.37% | 11.37% | 90% | 10.23% | 25.2476 | 5.2259 | 5.2259 | 131.9423 | 55.8328 | 78.95% | 78.95%
4 | 109 | 19 | 2607 | 15 | 19.3 | 70.56 | 222.78 | 293.34 | 222.78 | 111.39 | 109 | 2607 | 900 | 107.5068 | 11.0414 | 15.3166 | 874.284 | 14.8267 | -42.4002 | 39.4877 | 39.4877 | 59.0424 | 239.0424 | 43.082 | 81.0418 | 81.0418 | 190.1546 | 271.1964 | 0.37515 | 37.52% | 122.635 | 46.007 | 32.2049 | 152.9916 | 152.9916 | 21.05% | 11.37% | 11.37% | 80% | 9.098% | 11.1572 | 5.0828 | 5.0828 | 56.7093 | 24.6731 | 37.07% | 37.07%
4 | 109 | 19 | 2608 | 16 | 19.3 | 61.39 | 143.06 | 204.45 | 143.06 | 71.53 | 109 | 2608 | 960 | 107.5068 | 11.0414 | 15.3166 | 934.284 | 15.8267 | -57.4002 | 30.1121 | 30.1121 | 72.9124 | 252.9124 | 57.6911 | 65.4023 | 65.4023 | 122.1093 | 187.5116 | 0.18376 | 18.38% | 84.7928 | 15.5818 | 10.9073 | 145.2746 | 145.2746 | 7.508% | 11.38% | 11.38% | 80% | 9.1% | 7.7165 | 5.0828 | 5.0828 | 39.2213 | 17.0644 | 27% | 27%
4 | 109 | 19 | 2609 | 17 | 18.7 | 107.69 | 119.25 | 226.94 | 119.25 | 59.63 | 109 | 2609 | 1020 | 107.5068 | 11.0414 | 15.3166 | 994.284 | 16.8267 | -72.4002 | 20.0473 | 20.0473 | 84.8024 | 264.8024 | 72.388 | 95.0526 | 95.0526 | 101.7862 | 196.8389 | 0.2064 | 20.64% | 89.0105 | 18.3721 | 12.8605 | 141.1898 | 141.1898 | 9.109% | 11.4% | 11.4% | 80% | 9.116% | 8.1143 | 5.2053 | 5.2053 | 42.2371 | 17.944 | 29.92% | 29.92%
4 | 109 | 19 | 2610 | 18 | 18.1 | 174.25 | 81.67 | 255.92 | 81.67 | 40.84 | 109 | 2610 | 1080 | 107.5068 | 11.0414 | 15.3166 | 1054.284 | 17.8267 | -87.4002 | 9.7907 | 9.7907 | 95.7492 | 275.7492 | 87.1087 | 0 | 0 | 69.7097 | 69.7097 | -0.90256 | 0% | 31.5227 | 0 | 0 | 136.6681 | 136.6681 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2611 | 19 | 17.1 | 66.39 | 33.81 | 100.2 | 33.81 | 16.91 | 109 | 2611 | 1140 | 107.5068 | 11.0414 | 15.3166 | 1114.284 | 18.8267 | -102.4002 | -0.27364 | 0 | 106.2399 | 286.2399 | 101.4053 | 0 | 0 | 28.8586 | 28.8586 | -3.3957 | 0% | 13.0499 | 0 | 0 | 162.9856 | 162.9856 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2612 | 20 | 13.7 | 0 | 8.97 | 8.97 | 8.97 | 4.49 | 109 | 2612 | 1200 | 107.5068 | 11.0414 | 15.3166 | 1174.284 | 19.8267 | -117.4002 | -9.7741 | 0 | 106.2399 | 286.2399 | 101.4053 | 0 | 0 | 7.6564 | 7.6564 | -16.0303 | 0% | 3.4622 | 0 | 0 | 141.4955 | 141.4955 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2613 | 21 | 12 | 0 | 0 | 0 | 0 | 0 | 109 | 2613 | 1260 | 107.5068 | 11.0414 | 15.3166 | 1234.284 | 20.8267 | -132.4002 | -18.2808 | 0 | 106.2399 | 286.2399 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8812 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2614 | 22 | 11.1 | 0 | 0 | 0 | 0 | 0 | 109 | 2614 | 1320 | 107.5068 | 11.0414 | 15.3166 | 1294.284 | 21.8267 | -147.4002 | -25.258 | 0 | 106.2399 | 286.2399 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4262 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2615 | 23 | 10.6 | 0 | 0 | 0 | 0 | 0 | 109 | 2615 | 1380 | 107.5068 | 11.0414 | 15.3166 | 1354.284 | 22.8267 | -162.4002 | -30.0746 | 0 | 106.2399 | 286.2399 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4191 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
4 | 109 | 19 | 2616 | 24 | 10.1 | 0 | 0 | 0 | 0 | 0 | 109 | 2616 | 1440 | 107.5068 | 11.0414 | 15.3166 | 1414.284 | 23.8267 | -177.4002 | -32.1338 | 0 | 106.2399 | 286.2399 | 101.4053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4121 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2617 | 1 | 9.4 | 0 | 0 | 0 | 0 | 0 | 110 | 2617 | 60 | 108.4932 | 11.3974 | 15.4666 | 34.284 | 0.82918 | 167.5624 | -30.7682 | 0 | 106.7716 | 73.2284 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4444 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2618 | 2 | 8.7 | 0 | 0 | 0 | 0 | 0 | 110 | 2618 | 120 | 108.4932 | 11.3974 | 15.4666 | 94.284 | 1.8292 | 152.5624 | -26.8596 | 0 | 106.7716 | 73.2284 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.714 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2619 | 3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 110 | 2619 | 180 | 108.4932 | 11.3974 | 15.4666 | 154.284 | 2.8292 | 137.5624 | -20.5756 | 0 | 106.7716 | 73.2284 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7456 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2620 | 4 | 6.5 | 0 | 0 | 0 | 0 | 0 | 110 | 2620 | 240 | 108.4932 | 11.3974 | 15.4666 | 214.284 | 3.8292 | 122.5624 | -12.5514 | 0 | 106.7716 | 73.2284 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2696 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2621 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 110 | 2621 | 300 | 108.4932 | 11.3974 | 15.4666 | 274.284 | 4.8292 | 107.5624 | -3.3575 | 0 | 106.7716 | 73.2284 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.3103 | 1.3103 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2622 | 6 | 5.6 | 0 | 0 | 0 | 0 | 0 | 110 | 2622 | 360 | 108.4932 | 11.3974 | 15.4666 | 334.284 | 5.8292 | 92.5624 | 6.5453 | 6.5453 | 99.6927 | 80.3073 | 92.159 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 14.9776 | 14.9776 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2623 | 7 | 5.8 | 15.08 | 27.22 | 42.3 | 27.22 | 13.61 | 110 | 2623 | 420 | 108.4932 | 11.3974 | 15.4666 | 394.284 | 6.8292 | 77.5624 | 16.7735 | 16.7735 | 88.8916 | 91.1084 | 77.4578 | 11.3475 | 11.3475 | 23.2337 | 34.5812 | -3.4573 | 0% | 15.6376 | 0 | 0 | 191.5727 | 191.5727 | 0% | 11.95% | 11.95% | 80% | 9.56% | 1.4949 | 8.449 | 6 | 8.9696 | 3.3059 | 4.682% | 4.682%
4 | 110 | 20 | 2624 | 8 | 8.1 | 92.78 | 78.25 | 171.03 | 78.25 | 39.13 | 110 | 2624 | 480 | 108.4932 | 11.3974 | 15.4666 | 454.284 | 7.8292 | 62.5624 | 26.9579 | 26.9579 | 77.4406 | 102.5594 | 62.767 | 93.655 | 93.655 | 66.7906 | 160.4455 | -0.080401 | 0% | 72.5535 | 0 | 0 | 170.6518 | 170.6518 | 0% | 11.77% | 11.77% | 80% | 9.416% | 6.832 | 7.7853 | 6 | 40.9919 | 15.1083 | 24.02% | 24.02%
4 | 110 | 20 | 2625 | 9 | 11.4 | 272.14 | 92.5 | 364.64 | 92.5 | 46.25 | 110 | 2625 | 540 | 108.4932 | 11.3974 | 15.4666 | 514.284 | 8.8292 | 47.5624 | 36.6554 | 36.6554 | 64.3954 | 115.6046 | 48.1415 | 304.1825 | 304.1825 | 78.9537 | 383.1362 | 0.45378 | 45.38% | 173.2542 | 78.6194 | 55.0336 | 186.1914 | 186.1914 | 29.56% | 11.55% | 11.55% | 85% | 9.817% | 17.008 | 6.8978 | 6 | 102.0481 | 37.6117 | 54.81% | 54.81%
4 | 110 | 20 | 2626 | 10 | 15.6 | 418.53 | 103.14 | 521.67 | 103.14 | 51.57 | 110 | 2626 | 600 | 108.4932 | 11.3974 | 15.4666 | 574.284 | 9.8292 | 32.5624 | 45.2183 | 45.2183 | 48.5041 | 131.4959 | 33.7035 | 490.5402 | 490.5402 | 88.0355 | 578.5757 | 0.58869 | 58.87% | 261.6319 | 154.0208 | 107.8146 | 194.9094 | 194.9094 | 55.32% | 11.41% | 11.41% | 90% | 10.27% | 26.8566 | 5.8784 | 5.8784 | 157.8748 | 59.3909 | 81% | 81%
4 | 110 | 20 | 2627 | 11 | 17.1 | 527.14 | 129.44 | 656.58 | 129.44 | 64.72 | 110 | 2627 | 660 | 108.4932 | 11.3974 | 15.4666 | 634.284 | 10.8292 | 17.5624 | 51.6313 | 51.6313 | 28.4592 | 151.5408 | 19.9031 | 632.1853 | 632.1853 | 110.484 | 742.6692 | 0.64081 | 64.08% | 335.835 | 215.2062 | 150.6443 | 190.6621 | 190.6621 | 79.01% | 11.36% | 11.36% | 90% | 10.23% | 34.3392 | 5.5443 | 5.5443 | 190.3875 | 75.9381 | 99.86% | 99.86%
4 | 110 | 20 | 2628 | 12 | 18.7 | 590.08 | 137.5 | 727.58 | 137.5 | 68.75 | 110 | 2628 | 720 | 108.4932 | 11.3974 | 15.4666 | 694.284 | 11.8292 | 2.5624 | 54.553 | 54.553 | 4.3338 | 175.6662 | 9.9497 | 713.4395 | 713.4395 | 117.3636 | 830.8031 | 0.66241 | 66.24% | 375.6892 | 248.8618 | 174.2032 | 178.1894 | 178.1894 | 97.76% | 11.35% | 11.35% | 95% | 10.78% | 40.508 | 5.2053 | 5.2053 | 210.8551 | 89.5797 | 118.3% | 118.3%
4 | 110 | 20 | 2629 | 13 | 19 | 641.47 | 164.53 | 806 | 164.53 | 82.27 | 110 | 2629 | 780 | 108.4932 | 11.3974 | 15.4666 | 754.284 | 12.8292 | -12.4376 | 53.0889 | 53.0889 | 20.5819 | 200.5819 | 15.6464 | 772.5419 | 772.5419 | 140.4351 | 912.9771 | 0.67589 | 67.59% | 412.8482 | 279.0383 | 195.3268 | 177.6284 | 177.6284 | 110% | 11.35% | 11.35% | 95% | 10.78% | 44.4988 | 5.1437 | 5.1437 | 228.8886 | 98.4052 | 128.9% | 128.9%
4 | 110 | 20 | 2630 | 14 | 20.1 | 529.25 | 167.22 | 696.47 | 167.22 | 83.61 | 110 | 2630 | 840 | 108.4932 | 11.3974 | 15.4666 | 814.284 | 13.8292 | -27.4376 | 47.7151 | 47.7151 | 42.1714 | 222.1714 | 28.8693 | 626.4822 | 626.4822 | 142.7312 | 769.2134 | 0.6551 | 65.51% | 347.8383 | 227.8682 | 159.5077 | 172.9745 | 172.9745 | 92.21% | 11.35% | 11.35% | 90% | 10.22% | 35.5374 | 4.9233 | 4.9233 | 174.9619 | 78.5878 | 101.1% | 101.1%
4 | 110 | 20 | 2631 | 15 | 19.3 | 406.31 | 150.19 | 556.5 | 150.19 | 75.1 | 110 | 2631 | 900 | 108.4932 | 11.3974 | 15.4666 | 874.284 | 14.8292 | -42.4376 | 39.7505 | 39.7505 | 59.3577 | 239.3577 | 43.1771 | 463.3676 | 463.3676 | 128.1952 | 591.5628 | 0.6074 | 60.74% | 267.5047 | 162.4822 | 113.7376 | 162.2529 | 162.2529 | 70.1% | 11.36% | 11.36% | 90% | 10.22% | 27.3497 | 5.0828 | 5.0828 | 139.012 | 60.4815 | 85.68% | 85.68%
4 | 110 | 20 | 2632 | 16 | 19.9 | 360.83 | 107.22 | 468.05 | 107.22 | 53.61 | 110 | 2632 | 960 | 108.4932 | 11.3974 | 15.4666 | 934.284 | 15.8292 | -57.4376 | 30.3525 | 30.3525 | 73.2192 | 253.2192 | 57.759 | 380.9399 | 380.9399 | 91.518 | 472.4579 | 0.56064 | 56.06% | 213.6455 | 119.778 | 83.8446 | 156.5696 | 156.5696 | 53.55% | 11.35% | 11.35% | 85% | 9.651% | 20.6183 | 4.9628 | 4.9628 | 102.3238 | 45.5956 | 65.35% | 65.35%
4 | 110 | 20 | 2633 | 17 | 18.6 | 282.42 | 138.61 | 421.03 | 138.61 | 69.31 | 110 | 2633 | 1020 | 108.4932 | 11.3974 | 15.4666 | 994.284 | 16.8292 | -72.4376 | 20.2776 | 20.2776 | 85.0943 | 265.0943 | 72.4353 | 245.9235 | 245.9235 | 118.311 | 364.2346 | 0.48044 | 48.04% | 164.7069 | 79.1316 | 55.3921 | 148.8475 | 148.8475 | 37.21% | 11.39% | 11.39% | 85% | 9.678% | 15.9399 | 5.2259 | 5.2259 | 83.3008 | 35.2496 | 55.96% | 55.96%
4 | 110 | 20 | 2634 | 18 | 19 | 202.03 | 91.67 | 293.7 | 91.67 | 45.84 | 110 | 2634 | 1080 | 108.4932 | 11.3974 | 15.4666 | 1054.284 | 17.8292 | -87.4376 | 10.0213 | 10.0213 | 96.027 | 276.027 | 87.1377 | 57.9748 | 57.9748 | 78.2452 | 136.2201 | -0.054649 | 0% | 61.5987 | 0 | 0 | 137.7945 | 137.7945 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2635 | 19 | 17.7 | 73.14 | 60.19 | 133.33 | 60.19 | 30.1 | 110 | 2635 | 1140 | 108.4932 | 11.3974 | 15.4666 | 1114.284 | 18.8292 | -102.4376 | -0.033587 | 0 | 106.7716 | 286.7716 | 101.7734 | 0 | 0 | 51.3754 | 51.3754 | -1.5289 | 0% | 23.2319 | 0 | 0 | 163.4628 | 163.4628 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2636 | 20 | 16.3 | 0 | 14.92 | 14.92 | 14.92 | 7.46 | 110 | 2636 | 1200 | 108.4932 | 11.3974 | 15.4666 | 1174.284 | 19.8292 | -117.4376 | -9.5166 | 0 | 106.7716 | 286.7716 | 101.7734 | 0 | 0 | 12.735 | 12.735 | -8.8539 | 0% | 5.7588 | 0 | 0 | 143.816 | 143.816 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2637 | 21 | 14.9 | 0 | 0 | 0 | 0 | 0 | 110 | 2637 | 1260 | 108.4932 | 11.3974 | 15.4666 | 1234.284 | 20.8292 | -132.4376 | -17.9989 | 0 | 106.7716 | 286.7716 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.3262 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2638 | 22 | 12.3 | 0 | 0 | 0 | 0 | 0 | 110 | 2638 | 1320 | 108.4932 | 11.3974 | 15.4666 | 1294.284 | 21.8292 | -147.4376 | -24.9479 | 0 | 106.7716 | 286.7716 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4164 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2639 | 23 | 10.4 | 0 | 0 | 0 | 0 | 0 | 110 | 2639 | 1380 | 108.4932 | 11.3974 | 15.4666 | 1354.284 | 22.8292 | -162.4376 | -29.7377 | 0 | 106.7716 | 286.7716 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5147 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
4 | 110 | 20 | 2640 | 24 | 9.3 | 0 | 0 | 0 | 0 | 0 | 110 | 2640 | 1440 | 108.4932 | 11.3974 | 15.4666 | 1414.284 | 23.8292 | -177.4376 | -31.7794 | 0 | 106.7716 | 286.7716 | 101.7734 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3939 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2641 | 1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 111 | 2641 | 60 | 109.4795 | 11.75 | 15.6044 | 34.284 | 0.83147 | 167.5279 | -30.415 | 0 | 107.2992 | 72.7008 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4634 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2642 | 2 | 7.5 | 0 | 0 | 0 | 0 | 0 | 111 | 2642 | 120 | 109.4795 | 11.75 | 15.6044 | 94.284 | 1.8315 | 152.5279 | -26.5178 | 0 | 107.2992 | 72.7008 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.1284 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2643 | 3 | 7.2 | 0 | 0 | 0 | 0 | 0 | 111 | 2643 | 180 | 109.4795 | 11.75 | 15.6044 | 154.284 | 2.8315 | 137.5279 | -20.2522 | 0 | 107.2992 | 72.7008 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7267 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2644 | 4 | 6.5 | 0 | 0 | 0 | 0 | 0 | 111 | 2644 | 240 | 109.4795 | 11.75 | 15.6044 | 214.284 | 3.8315 | 122.5279 | -12.2471 | 0 | 107.2992 | 72.7008 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7935 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2645 | 5 | 6.7 | 0 | 0 | 0 | 0 | 0 | 111 | 2645 | 300 | 109.4795 | 11.75 | 15.6044 | 274.284 | 4.8315 | 107.5279 | -3.0687 | 0 | 107.2992 | 72.7008 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.0811 | 3.0811 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2646 | 6 | 6.5 | 0 | 0 | 0 | 0 | 0 | 111 | 2646 | 360 | 109.4795 | 11.75 | 15.6044 | 334.284 | 5.8315 | 92.5279 | 6.8241 | 6.8241 | 99.9126 | 80.0874 | 92.1114 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 17.8472 | 17.8472 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2647 | 7 | 7.5 | 21.47 | 28.25 | 49.72 | 28.25 | 14.13 | 111 | 2647 | 420 | 109.4795 | 11.75 | 15.6044 | 394.284 | 6.8315 | 77.5279 | 17.0492 | 17.0492 | 89.1239 | 90.8761 | 77.4287 | 15.9385 | 15.9385 | 24.1129 | 40.0514 | -2.7743 | 0% | 18.1112 | 0 | 0 | 198.225 | 198.225 | 0% | 11.87% | 11.87% | 80% | 9.5% | 1.7205 | 7.9549 | 6 | 10.3229 | 3.8047 | 5.208% | 5.208%
4 | 111 | 21 | 2648 | 8 | 9.6 | 141.19 | 57.78 | 198.97 | 57.78 | 28.89 | 111 | 2648 | 480 | 109.4795 | 11.75 | 15.6044 | 454.284 | 7.8315 | 62.5279 | 27.2386 | 27.2386 | 77.6833 | 102.3167 | 62.7579 | 141.2068 | 141.2068 | 49.3183 | 190.5251 | 0.07773 | 7.773% | 86.1554 | 6.6969 | 4.6878 | 178.901 | 178.901 | 2.62% | 11.7% | 11.7% | 80% | 9.36% | 8.0646 | 7.3724 | 6 | 48.3875 | 17.8341 | 27.05% | 27.05%
4 | 111 | 21 | 2649 | 9 | 12.4 | 305.36 | 71.19 | 376.55 | 71.19 | 35.6 | 111 | 2649 | 540 | 109.4795 | 11.75 | 15.6044 | 514.284 | 8.8315 | 47.5279 | 36.9502 | 36.9502 | 64.6406 | 115.3594 | 48.1578 | 338.8671 | 338.8671 | 60.7645 | 399.6315 | 0.47402 | 47.4% | 180.7134 | 85.661 | 59.9627 | 192.3123 | 192.3123 | 31.18% | 11.52% | 11.52% | 85% | 9.791% | 17.6945 | 6.6439 | 6 | 106.1668 | 39.1297 | 55.21% | 55.21%
4 | 111 | 21 | 2650 | 10 | 16.5 | 467.14 | 77.58 | 544.72 | 77.58 | 38.79 | 111 | 2650 | 600 | 109.4795 | 11.75 | 15.6044 | 574.284 | 9.8315 | 32.5279 | 45.5362 | 45.5362 | 48.7265 | 131.2735 | 33.7589 | 544.1727 | 544.1727 | 66.2187 | 610.3914 | 0.60324 | 60.32% | 276.019 | 166.5053 | 116.5537 | 200.9107 | 200.9107 | 58.01% | 11.39% | 11.39% | 90% | 10.25% | 28.291 | 5.6761 | 5.6761 | 160.5817 | 62.563 | 79.93% | 79.93%
4 | 111 | 21 | 2651 | 11 | 18.7 | 584.36 | 98.81 | 683.17 | 98.81 | 49.41 | 111 | 2651 | 660 | 109.4795 | 11.75 | 15.6044 | 634.284 | 10.8315 | 17.5279 | 51.9749 | 51.9749 | 28.5981 | 151.4019 | 20.0393 | 696.9059 | 696.9059 | 84.3396 | 781.2455 | 0.65343 | 65.34% | 353.2792 | 230.8442 | 161.5909 | 196.9383 | 196.9383 | 82.05% | 11.35% | 11.35% | 90% | 10.22% | 36.0981 | 5.2053 | 5.2053 | 187.9005 | 79.8277 | 95.41% | 95.41%
4 | 111 | 21 | 2652 | 12 | 20.5 | 670.75 | 107.97 | 778.72 | 107.97 | 53.99 | 111 | 2652 | 720 | 109.4795 | 11.75 | 15.6044 | 694.284 | 11.8315 | 2.5279 | 54.9069 | 54.9069 | 4.3076 | 175.6924 | 10.2823 | 806.6033 | 806.6033 | 92.1582 | 898.7615 | 0.67754 | 67.75% | 406.4199 | 275.3652 | 192.7556 | 184.5477 | 184.5477 | 104.4% | 11.35% | 11.35% | 95% | 10.79% | 43.8404 | 4.8453 | 4.8453 | 212.419 | 96.9492 | 115.1% | 115.1%
4 | 111 | 21 | 2653 | 13 | 20 | 717.36 | 113.06 | 830.42 | 113.06 | 56.53 | 111 | 2653 | 780 | 109.4795 | 11.75 | 15.6044 | 754.284 | 12.8315 | -12.4721 | 53.4222 | 53.4222 | 20.7821 | 200.7821 | 15.8878 | 859.1713 | 859.1713 | 96.5027 | 955.674 | 0.68392 | 68.39% | 432.1558 | 295.5599 | 206.8919 | 180.9844 | 180.9844 | 114.3% | 11.35% | 11.35% | 95% | 10.78% | 46.6054 | 4.943 | 4.943 | 230.3705 | 103.0637 | 127.3% | 127.3%
4 | 111 | 21 | 2654 | 14 | 19.9 | 708.14 | 115.08 | 823.22 | 115.08 | 57.54 | 111 | 2654 | 840 | 109.4795 | 11.75 | 15.6044 | 814.284 | 13.8315 | -27.4721 | 48.0103 | 48.0103 | 42.4631 | 222.4631 | 29.0089 | 833.215 | 833.215 | 98.2269 | 931.4419 | 0.68056 | 68.06% | 421.198 | 286.6503 | 200.6552 | 178.3792 | 178.3792 | 112.5% | 11.35% | 11.35% | 95% | 10.78% | 45.4208 | 4.9628 | 4.9628 | 225.4122 | 100.444 | 126.4% | 126.4%
4 | 111 | 21 | 2655 | 15 | 20 | 631.86 | 118.97 | 750.83 | 118.97 | 59.49 | 111 | 2655 | 900 | 109.4795 | 11.75 | 15.6044 | 874.284 | 14.8315 | -42.4721 | 40.0116 | 40.0116 | 59.6696 | 239.6696 | 43.2709 | 715.5704 | 715.5704 | 101.5472 | 817.1176 | 0.66356 | 66.36% | 369.5006 | 245.1851 | 171.6296 | 172.164 | 172.164 | 99.69% | 11.35% | 11.35% | 95% | 10.78% | 39.8484 | 4.943 | 4.943 | 196.9707 | 88.1212 | 114.4% | 114.4%
4 | 111 | 21 | 2656 | 16 | 19 | 527.5 | 120.19 | 647.69 | 120.19 | 60.1 | 111 | 2656 | 960 | 109.4795 | 11.75 | 15.6044 | 934.284 | 15.8315 | -57.4721 | 30.5917 | 30.5917 | 73.5223 | 253.5223 | 57.8249 | 551.9526 | 551.9526 | 102.5886 | 654.5412 | 0.6253 | 62.53% | 295.9835 | 185.0791 | 129.5554 | 163.8512 | 163.8512 | 79.07% | 11.36% | 11.36% | 90% | 10.22% | 30.2614 | 5.1437 | 5.1437 | 155.6553 | 66.9203 | 95% | 95%
4 | 111 | 21 | 2657 | 17 | 19.8 | 340.47 | 125.75 | 466.22 | 125.75 | 62.88 | 111 | 2657 | 1020 | 109.4795 | 11.75 | 15.6044 | 994.284 | 16.8315 | -72.4721 | 20.507 | 20.507 | 85.3822 | 265.3822 | 72.4802 | 292.5699 | 292.5699 | 107.3343 | 399.9042 | 0.51594 | 51.59% | 180.8367 | 93.3002 | 65.3101 | 153.0292 | 153.0292 | 42.68% | 11.36% | 11.36% | 85% | 9.653% | 17.4561 | 4.9826 | 4.9826 | 86.9762 | 38.6025 | 56.84% | 56.84%
4 | 111 | 21 | 2658 | 18 | 20.1 | 175.75 | 107.58 | 283.33 | 107.58 | 53.79 | 111 | 2658 | 1080 | 109.4795 | 11.75 | 15.6044 | 1054.284 | 17.8315 | -87.4721 | 10.2513 | 10.2513 | 96.3006 | 276.3006 | 87.1639 | 48.8632 | 48.8632 | 91.8253 | 140.6885 | -0.010121 | 0% | 63.6193 | 0 | 0 | 138.345 | 138.345 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2659 | 19 | 18 | 59.64 | 57.5 | 117.14 | 57.5 | 28.75 | 111 | 2659 | 1140 | 109.4795 | 11.75 | 15.6044 | 1114.284 | 18.8315 | -102.4721 | 0.20601 | 0.20601 | 107.0698 | 287.0698 | 101.8306 | 0 | 0 | 49.0793 | 49.0793 | -1.6244 | 0% | 22.1937 | 0 | 0 | 162.2931 | 162.2931 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2660 | 20 | 16.6 | 0 | 17.03 | 17.03 | 17.03 | 8.52 | 111 | 2660 | 1200 | 109.4795 | 11.75 | 15.6044 | 1174.284 | 19.8315 | -117.4721 | -9.2596 | 0 | 107.2992 | 287.2992 | 102.138 | 0 | 0 | 14.536 | 14.536 | -7.6108 | 0% | 6.5732 | 0 | 0 | 143.6667 | 143.6667 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2661 | 21 | 14.3 | 0 | 0 | 0 | 0 | 0 | 111 | 2661 | 1260 | 109.4795 | 11.75 | 15.6044 | 1234.284 | 20.8315 | -132.4721 | -17.718 | 0 | 107.2992 | 287.2992 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0091 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2662 | 22 | 12.3 | 0 | 0 | 0 | 0 | 0 | 111 | 2662 | 1320 | 109.4795 | 11.75 | 15.6044 | 1294.284 | 21.8315 | -147.4721 | -24.6393 | 0 | 107.2992 | 287.2992 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2489 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2663 | 23 | 11.1 | 0 | 0 | 0 | 0 | 0 | 111 | 2663 | 1380 | 109.4795 | 11.75 | 15.6044 | 1354.284 | 22.8315 | -162.4721 | -29.4032 | 0 | 107.2992 | 287.2992 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2188 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
4 | 111 | 21 | 2664 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 111 | 2664 | 1440 | 109.4795 | 11.75 | 15.6044 | 1414.284 | 23.8315 | -177.4721 | -31.4282 | 0 | 107.2992 | 287.2992 | 102.138 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0363 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2665 | 1 | 9.4 | 0 | 0 | 0 | 0 | 0 | 112 | 2665 | 60 | 110.4658 | 12.0991 | 15.7298 | 34.284 | 0.83356 | 167.4966 | -30.0658 | 0 | 107.8223 | 72.1777 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3662 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2666 | 2 | 8.3 | 0 | 0 | 0 | 0 | 0 | 112 | 2666 | 120 | 110.4658 | 12.0991 | 15.7298 | 94.284 | 1.8336 | 152.4966 | -26.1804 | 0 | 107.8223 | 72.1777 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4622 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2667 | 3 | 8.1 | 0 | 0 | 0 | 0 | 0 | 112 | 2667 | 180 | 110.4658 | 12.0991 | 15.7298 | 154.284 | 2.8336 | 137.4966 | -19.9333 | 0 | 107.8223 | 72.1777 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1867 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2668 | 4 | 7.3 | 0 | 0 | 0 | 0 | 0 | 112 | 2668 | 240 | 110.4658 | 12.0991 | 15.7298 | 214.284 | 3.8336 | 122.4966 | -11.9473 | 0 | 107.8223 | 72.1777 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4059 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2669 | 5 | 7.4 | 0 | 0 | 0 | 0 | 0 | 112 | 2669 | 300 | 110.4658 | 12.0991 | 15.7298 | 274.284 | 4.8336 | 107.4966 | -2.7845 | 0 | 107.8223 | 72.1777 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.6398 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2670 | 6 | 7.2 | 0 | 0 | 0 | 0 | 0 | 112 | 2670 | 360 | 110.4658 | 12.0991 | 15.7298 | 334.284 | 5.8336 | 92.4966 | 7.0982 | 7.0982 | 100.1326 | 79.8674 | 92.067 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.1472 | 9.1472 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2671 | 7 | 8.1 | 17.03 | 19.81 | 36.84 | 19.81 | 9.91 | 112 | 2671 | 420 | 110.4658 | 12.0991 | 15.7298 | 394.284 | 6.8336 | 77.4966 | 17.3201 | 17.3201 | 89.3567 | 90.6433 | 77.4031 | 12.4756 | 12.4756 | 16.9089 | 29.3844 | -4.025 | 0% | 13.2876 | 0 | 0 | 180.0054 | 180.0054 | 0% | 11.86% | 11.86% | 80% | 9.485% | 1.2603 | 7.7853 | 6 | 7.5621 | 2.7871 | 4.201% | 4.201%
4 | 112 | 22 | 2672 | 8 | 10 | 103.14 | 64.72 | 167.86 | 64.72 | 32.36 | 112 | 2672 | 480 | 110.4658 | 12.0991 | 15.7298 | 454.284 | 7.8336 | 62.4966 | 27.5142 | 27.5142 | 77.927 | 102.073 | 62.7528 | 102.2161 | 102.2161 | 55.242 | 157.4581 | -0.068851 | 0% | 71.2025 | 0 | 0 | 156.2428 | 156.2428 | 0% | 11.71% | 11.71% | 80% | 9.364% | 6.6676 | 7.265 | 6 | 40.0058 | 14.7449 | 25.6% | 25.6%
4 | 112 | 22 | 2673 | 9 | 12.6 | 206.75 | 69.64 | 276.39 | 69.64 | 34.82 | 112 | 2673 | 540 | 110.4658 | 12.0991 | 15.7298 | 514.284 | 8.8336 | 47.4966 | 37.2399 | 37.2399 | 64.8879 | 115.1121 | 48.1785 | 227.8155 | 227.8155 | 59.4415 | 287.257 | 0.34653 | 34.65% | 129.8976 | 45.0133 | 31.5093 | 165.927 | 165.927 | 18.99% | 11.56% | 11.56% | 80% | 9.249% | 12.0136 | 6.5939 | 6 | 72.0819 | 26.5671 | 43.44% | 43.44%
4 | 112 | 22 | 2674 | 10 | 16.1 | 308.42 | 78.69 | 387.11 | 78.69 | 39.35 | 112 | 2674 | 600 | 110.4658 | 12.0991 | 15.7298 | 574.284 | 9.8336 | 32.4966 | 45.8491 | 45.8491 | 48.9525 | 131.0475 | 33.8195 | 357.1165 | 357.1165 | 67.1661 | 424.2826 | 0.51305 | 51.31% | 191.8606 | 98.4348 | 68.9044 | 172.8739 | 172.8739 | 39.86% | 11.43% | 11.43% | 85% | 9.718% | 18.6444 | 5.7653 | 5.7653 | 107.4911 | 41.2305 | 62.18% | 62.18%
4 | 112 | 22 | 2675 | 11 | 18.7 | 404.92 | 93.89 | 498.81 | 93.89 | 46.95 | 112 | 2675 | 660 | 110.4658 | 12.0991 | 15.7298 | 634.284 | 10.8336 | 17.4966 | 52.3141 | 52.3141 | 28.7421 | 151.2579 | 20.1816 | 480.2529 | 480.2529 | 80.1401 | 560.393 | 0.59409 | 59.41% | 253.4097 | 150.5491 | 105.3844 | 172.4729 | 172.4729 | 61.1% | 11.37% | 11.37% | 90% | 10.23% | 25.9294 | 5.2053 | 5.2053 | 134.9699 | 57.3406 | 78.26% | 78.26%
4 | 112 | 22 | 2676 | 12 | 17.6 | 472.58 | 100 | 572.58 | 100 | 50 | 112 | 2676 | 720 | 110.4658 | 12.0991 | 15.7298 | 694.284 | 11.8336 | 2.4966 | 55.2571 | 55.2571 | 4.2861 | 175.7139 | 10.6136 | 565.2732 | 565.2732 | 85.3553 | 650.6285 | 0.61944 | 61.94% | 294.2142 | 182.2487 | 127.5741 | 160.4336 | 160.4336 | 79.52% | 11.37% | 11.37% | 90% | 10.23% | 30.1115 | 5.4364 | 5.4364 | 163.6993 | 66.5889 | 102% | 102%
4 | 112 | 22 | 2677 | 13 | 19.3 | 383.33 | 84.58 | 467.91 | 84.58 | 42.29 | 112 | 2677 | 780 | 110.4658 | 12.0991 | 15.7298 | 754.284 | 12.8336 | -12.5034 | 53.7526 | 53.7526 | 20.9788 | 200.9788 | 16.1287 | 456.6088 | 456.6088 | 72.1935 | 528.8024 | 0.58407 | 58.41% | 239.1244 | 139.6645 | 97.7652 | 155.8943 | 155.8943 | 62.71% | 11.36% | 11.36% | 90% | 10.23% | 24.4533 | 5.0828 | 5.0828 | 124.2903 | 54.0764 | 79.73% | 79.73%
4 | 112 | 22 | 2678 | 14 | 19 | 515 | 148.53 | 663.53 | 148.53 | 74.27 | 112 | 2678 | 840 | 110.4658 | 12.0991 | 15.7298 | 814.284 | 13.8336 | -27.5034 | 48.3032 | 48.3032 | 42.7516 | 222.7516 | 29.1478 | 602.3815 | 602.3815 | 126.7783 | 729.1598 | 0.64359 | 64.36% | 329.7261 | 212.2081 | 148.5457 | 162.5904 | 162.5904 | 91.36% | 11.36% | 11.36% | 90% | 10.22% | 33.699 | 5.1437 | 5.1437 | 173.3376 | 74.5224 | 106.6% | 106.6%
4 | 112 | 22 | 2679 | 15 | 18.1 | 477.78 | 143.42 | 621.2 | 143.42 | 71.71 | 112 | 2679 | 900 | 110.4658 | 12.0991 | 15.7298 | 874.284 | 14.8336 | -42.5034 | 40.271 | 40.271 | 59.9778 | 239.9778 | 43.3631 | 537.3643 | 537.3643 | 122.4166 | 659.781 | 0.62369 | 62.37% | 298.3529 | 186.0804 | 130.2563 | 157.2937 | 157.2937 | 82.81% | 11.37% | 11.37% | 90% | 10.23% | 30.5215 | 5.3303 | 5.3303 | 162.689 | 67.4955 | 103.4% | 103.4%
4 | 112 | 22 | 2680 | 16 | 12.8 | 399.36 | 96.86 | 496.22 | 96.86 | 48.43 | 112 | 2680 | 960 | 110.4658 | 12.0991 | 15.7298 | 934.284 | 15.8336 | -57.5034 | 30.8297 | 30.8297 | 73.8215 | 253.8215 | 57.8887 | 414.2258 | 414.2258 | 82.6752 | 496.901 | 0.54046 | 54.05% | 224.6986 | 121.4412 | 85.0088 | 142.185 | 142.185 | 59.79% | 11.47% | 11.47% | 85% | 9.751% | 21.9109 | 6.5443 | 6 | 131.4652 | 48.4539 | 92.46% | 92.46%
4 | 112 | 22 | 2681 | 17 | 12.8 | 307.86 | 93.14 | 401 | 93.14 | 46.57 | 112 | 2681 | 1020 | 110.4658 | 12.0991 | 15.7298 | 994.284 | 16.8336 | -72.5034 | 20.7357 | 20.7357 | 85.6659 | 265.6659 | 72.5225 | 261.1447 | 261.1447 | 79.5 | 340.6447 | 0.41958 | 41.96% | 154.0395 | 64.6313 | 45.2419 | 135.3354 | 135.3354 | 33.43% | 11.53% | 11.53% | 85% | 9.804% | 15.1018 | 6.5443 | 6 | 90.6105 | 33.3962 | 66.95% | 66.95%
4 | 112 | 22 | 2682 | 18 | 13.9 | 187.97 | 70.56 | 258.53 | 70.56 | 35.28 | 112 | 2682 | 1080 | 110.4658 | 12.0991 | 15.7298 | 1054.284 | 17.8336 | -87.5034 | 10.4808 | 10.4808 | 96.5698 | 276.5698 | 87.1871 | 50.7103 | 50.7103 | 60.2267 | 110.937 | -0.35371 | 0% | 50.1657 | 0 | 0 | 125.628 | 125.628 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2683 | 19 | 13.1 | 80.83 | 44.17 | 125 | 44.17 | 22.09 | 112 | 2683 | 1140 | 110.4658 | 12.0991 | 15.7298 | 1114.284 | 18.8336 | -102.5034 | 0.44508 | 0.44508 | 107.3261 | 287.3261 | 101.8344 | 0 | 0 | 37.7015 | 37.7015 | -2.6511 | 0% | 17.0486 | 0 | 0 | 154.6129 | 154.6129 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2684 | 20 | 12.6 | 0 | 12.86 | 12.86 | 12.86 | 6.43 | 112 | 2684 | 1200 | 110.4658 | 12.0991 | 15.7298 | 1174.284 | 19.8336 | -117.5034 | -9.0033 | 0 | 107.8223 | 287.8223 | 102.4989 | 0 | 0 | 10.9767 | 10.9767 | -11.1679 | 0% | 4.9637 | 0 | 0 | 138.1014 | 138.1014 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2685 | 21 | 11.1 | 0 | 0 | 0 | 0 | 0 | 112 | 2685 | 1260 | 110.4658 | 12.0991 | 15.7298 | 1234.284 | 20.8336 | -132.5034 | -17.4382 | 0 | 107.8223 | 287.8223 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7358 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2686 | 22 | 9.2 | 0 | 0 | 0 | 0 | 0 | 112 | 2686 | 1320 | 110.4658 | 12.0991 | 15.7298 | 1294.284 | 21.8336 | -147.5034 | -24.3324 | 0 | 107.8223 | 287.8223 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.412 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2687 | 23 | 9.4 | 0 | 0 | 0 | 0 | 0 | 112 | 2687 | 1380 | 110.4658 | 12.0991 | 15.7298 | 1354.284 | 22.8336 | -162.5034 | -29.0712 | 0 | 107.8223 | 287.8223 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5268 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
4 | 112 | 22 | 2688 | 24 | 9.3 | 0 | 0 | 0 | 0 | 0 | 112 | 2688 | 1440 | 110.4658 | 12.0991 | 15.7298 | 1414.284 | 23.8336 | -177.5034 | -31.0804 | 0 | 107.8223 | 287.8223 | 102.4989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0989 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2689 | 1 | 8.9 | 0 | 0 | 0 | 0 | 0 | 113 | 2689 | 60 | 111.4521 | 12.4445 | 15.8428 | 34.284 | 0.83545 | 167.4683 | -29.7207 | 0 | 108.3409 | 71.6591 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.22 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2690 | 2 | 8.7 | 0 | 0 | 0 | 0 | 0 | 113 | 2690 | 120 | 111.4521 | 12.4445 | 15.8428 | 94.284 | 1.8354 | 152.4683 | -25.8473 | 0 | 108.3409 | 71.6591 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8952 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2691 | 3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 113 | 2691 | 180 | 111.4521 | 12.4445 | 15.8428 | 154.284 | 2.8354 | 137.4683 | -19.6189 | 0 | 108.3409 | 71.6591 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8751 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2692 | 4 | 7.7 | 0 | 0 | 0 | 0 | 0 | 113 | 2692 | 240 | 111.4521 | 12.4445 | 15.8428 | 214.284 | 3.8354 | 122.4683 | -11.6521 | 0 | 108.3409 | 71.6591 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7895 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2693 | 5 | 7.1 | 0 | 0 | 0 | 0 | 0 | 113 | 2693 | 300 | 111.4521 | 12.4445 | 15.8428 | 274.284 | 4.8354 | 107.4683 | -2.5051 | 0 | 108.3409 | 71.6591 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.73564 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2694 | 6 | 7 | 0 | 0 | 0 | 0 | 0 | 113 | 2694 | 360 | 111.4521 | 12.4445 | 15.8428 | 334.284 | 5.8354 | 92.4683 | 7.3674 | 7.3674 | 100.3526 | 79.6474 | 92.0257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.5742 | 10.5742 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2695 | 7 | 7.1 | 12.58 | 21.58 | 34.16 | 21.58 | 10.79 | 113 | 2695 | 420 | 111.4521 | 12.4445 | 15.8428 | 394.284 | 6.8354 | 77.4683 | 17.5858 | 17.5858 | 89.5899 | 90.4101 | 77.3811 | 9.0963 | 9.0963 | 18.4197 | 27.516 | -4.439 | 0% | 12.4427 | 0 | 0 | 179.7388 | 179.7388 | 0% | 11.9% | 11.9% | 80% | 9.52% | 1.1846 | 8.0693 | 6 | 7.1073 | 2.6195 | 3.954% | 3.954%
4 | 113 | 23 | 2696 | 8 | 8.1 | 75.08 | 84.36 | 159.44 | 84.36 | 42.18 | 113 | 2696 | 480 | 111.4521 | 12.4445 | 15.8428 | 454.284 | 7.8354 | 62.4683 | 27.7846 | 27.7846 | 78.1718 | 101.8282 | 62.7517 | 73.743 | 73.743 | 72.0058 | 145.7488 | -0.16958 | 0% | 65.9076 | 0 | 0 | 154.4305 | 154.4305 | 0% | 11.78% | 11.78% | 80% | 9.424% | 6.2112 | 7.7853 | 6 | 37.2675 | 13.7356 | 24.13% | 24.13%
4 | 113 | 23 | 2697 | 9 | 9.7 | 187.69 | 146.47 | 334.16 | 146.47 | 73.24 | 113 | 2697 | 540 | 111.4521 | 12.4445 | 15.8428 | 514.284 | 8.8354 | 47.4683 | 37.5242 | 37.5242 | 65.1373 | 114.8627 | 48.2037 | 205.3734 | 205.3734 | 125.02 | 330.3934 | 0.3859 | 38.59% | 149.4039 | 57.6545 | 40.3581 | 165.9841 | 165.9841 | 24.31% | 11.62% | 11.62% | 85% | 9.875% | 14.7541 | 7.3455 | 6 | 88.5247 | 32.6274 | 53.33% | 53.33%
4 | 113 | 23 | 2698 | 10 | 11.5 | 238.25 | 189.17 | 427.42 | 189.17 | 94.59 | 113 | 2698 | 600 | 111.4521 | 12.4445 | 15.8428 | 574.284 | 9.8354 | 32.4683 | 46.1568 | 46.1568 | 49.1822 | 130.8178 | 33.8853 | 274.2293 | 274.2293 | 161.4667 | 435.696 | 0.49656 | 49.66% | 197.0217 | 97.8333 | 68.4833 | 169.1447 | 169.1447 | 40.49% | 11.52% | 11.52% | 85% | 9.794% | 19.2962 | 6.8721 | 6 | 115.7774 | 42.6719 | 68.45% | 68.45%
4 | 113 | 23 | 2699 | 11 | 12 | 343.06 | 224.72 | 567.78 | 224.72 | 112.36 | 113 | 2699 | 660 | 111.4521 | 12.4445 | 15.8428 | 634.284 | 10.8354 | 17.4683 | 52.6486 | 52.6486 | 28.891 | 151.109 | 20.3296 | 404.6783 | 404.6783 | 191.8105 | 596.4889 | 0.58137 | 58.14% | 269.7323 | 156.8152 | 109.7706 | 166.6906 | 166.6906 | 65.85% | 11.44% | 11.44% | 90% | 10.3% | 27.7754 | 6.7446 | 6 | 166.6523 | 61.4228 | 99.98% | 99.98%
4 | 113 | 23 | 2700 | 12 | 12.2 | 337.22 | 257.22 | 594.44 | 257.22 | 128.61 | 113 | 2700 | 720 | 111.4521 | 12.4445 | 15.8428 | 694.284 | 11.8354 | 2.4683 | 55.6036 | 55.6036 | 4.2693 | 175.7307 | 10.9433 | 401.2463 | 401.2463 | 219.551 | 620.7973 | 0.59083 | 59.08% | 280.7245 | 165.8616 | 116.1031 | 154.512 | 154.512 | 75.14% | 11.43% | 11.43% | 90% | 10.29% | 28.8753 | 6.6941 | 6 | 173.2518 | 63.8551 | 112.1% | 112.1%
4 | 113 | 23 | 2701 | 13 | 14.9 | 375.47 | 254.25 | 629.72 | 254.25 | 127.13 | 113 | 2701 | 780 | 111.4521 | 12.4445 | 15.8428 | 754.284 | 12.8354 | -12.5317 | 54.08 | 54.08 | 21.172 | 201.172 | 16.3687 | 444.8443 | 444.8443 | 217.0159 | 661.8603 | 0.61339 | 61.34% | 299.2932 | 183.5836 | 128.5085 | 156.786 | 156.786 | 81.96% | 11.39% | 11.39% | 90% | 10.25% | 30.6826 | 6.0398 | 6 | 184.0954 | 67.8518 | 117.4% | 117.4%
4 | 113 | 23 | 2702 | 14 | 15.9 | 304.92 | 264.44 | 569.36 | 264.44 | 132.22 | 113 | 2702 | 840 | 111.4521 | 12.4445 | 15.8428 | 814.284 | 13.8354 | -27.5317 | 48.5937 | 48.5937 | 43.0366 | 223.0366 | 29.2858 | 354.5796 | 354.5796 | 225.7137 | 580.2933 | 0.5905 | 59.05% | 262.4086 | 154.9516 | 108.4661 | 154.2771 | 154.2771 | 70.31% | 11.4% | 11.4% | 90% | 10.26% | 26.9268 | 5.8104 | 5.8104 | 156.4541 | 59.5462 | 101.4% | 101.4%
4 | 113 | 23 | 2703 | 15 | 12.4 | 373.81 | 225.92 | 599.73 | 225.92 | 112.96 | 113 | 2703 | 900 | 111.4521 | 12.4445 | 15.8428 | 874.284 | 14.8354 | -42.5317 | 40.5285 | 40.5285 | 60.2823 | 240.2823 | 43.4538 | 417.5879 | 417.5879 | 192.8348 | 610.4227 | 0.58797 | 58.8% | 276.0331 | 162.2981 | 113.6087 | 147.1377 | 147.1377 | 77.21% | 11.43% | 11.43% | 90% | 10.29% | 28.3986 | 6.6439 | 6 | 170.3917 | 62.801 | 115.8% | 115.8%
4 | 113 | 23 | 2704 | 16 | 15.1 | 304.44 | 205 | 509.44 | 205 | 102.5 | 113 | 2704 | 960 | 111.4521 | 12.4445 | 15.8428 | 934.284 | 15.8354 | -57.5317 | 31.0665 | 31.0665 | 74.1166 | 254.1166 | 57.9504 | 313.0663 | 313.0663 | 174.9784 | 488.0447 | 0.54643 | 54.64% | 220.6938 | 120.5948 | 84.4164 | 145.2328 | 145.2328 | 58.12% | 11.44% | 11.44% | 85% | 9.721% | 21.4529 | 5.9933 | 5.9933 | 128.574 | 47.4412 | 88.53% | 88.53%
4 | 113 | 23 | 2705 | 17 | 13.8 | 94.72 | 170.97 | 265.69 | 170.97 | 85.49 | 113 | 2705 | 1020 | 111.4521 | 12.4445 | 15.8428 | 994.284 | 16.8354 | -72.5317 | 20.9635 | 20.9635 | 85.9455 | 265.9455 | 72.5622 | 79.3376 | 79.3376 | 145.932 | 225.2696 | 0.23286 | 23.29% | 101.8669 | 23.7204 | 16.6043 | 128.6409 | 128.6409 | 12.91% | 11.55% | 11.55% | 80% | 9.238% | 9.4109 | 6.3002 | 6 | 56.4652 | 20.8113 | 43.89% | 43.89%
4 | 113 | 23 | 2706 | 18 | 14.3 | 113.06 | 117.58 | 230.64 | 117.58 | 58.79 | 113 | 2706 | 1080 | 111.4521 | 12.4445 | 15.8428 | 1054.284 | 17.8354 | -87.5317 | 10.7097 | 10.7097 | 96.8346 | 276.8346 | 87.2074 | 29.6416 | 29.6416 | 100.3608 | 130.0024 | -0.17691 | 0% | 58.7871 | 0 | 0 | 123.5944 | 123.5944 | 0% | 11.56% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2707 | 19 | 13.7 | 55.56 | 55.64 | 111.2 | 55.64 | 27.82 | 113 | 2707 | 1140 | 111.4521 | 12.4445 | 15.8428 | 1114.284 | 18.8354 | -102.5317 | 0.68355 | 0.68355 | 107.5776 | 287.5776 | 101.835 | 0 | 0 | 47.4917 | 47.4917 | -1.9099 | 0% | 21.4758 | 0 | 0 | 154.2398 | 154.2398 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2708 | 20 | 12.6 | 0 | 14.53 | 14.53 | 14.53 | 7.27 | 113 | 2708 | 1200 | 111.4521 | 12.4445 | 15.8428 | 1174.284 | 19.8354 | -117.5317 | -8.7477 | 0 | 108.3409 | 288.3409 | 102.8562 | 0 | 0 | 12.4021 | 12.4021 | -9.7919 | 0% | 5.6082 | 0 | 0 | 138.7105 | 138.7105 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2709 | 21 | 9.9 | 0 | 0 | 0 | 0 | 0 | 113 | 2709 | 1260 | 111.4521 | 12.4445 | 15.8428 | 1234.284 | 20.8354 | -132.5317 | -17.1595 | 0 | 108.3409 | 288.3409 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9077 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2710 | 22 | 8.8 | 0 | 0 | 0 | 0 | 0 | 113 | 2710 | 1320 | 111.4521 | 12.4445 | 15.8428 | 1294.284 | 21.8354 | -147.5317 | -24.0274 | 0 | 108.3409 | 288.3409 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.2613 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2711 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 113 | 2711 | 1380 | 111.4521 | 12.4445 | 15.8428 | 1354.284 | 22.8354 | -162.5317 | -28.7419 | 0 | 108.3409 | 288.3409 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8508 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
4 | 113 | 23 | 2712 | 24 | 7.5 | 0 | 0 | 0 | 0 | 0 | 113 | 2712 | 1440 | 111.4521 | 12.4445 | 15.8428 | 1414.284 | 23.8354 | -177.5317 | -30.7361 | 0 | 108.3409 | 288.3409 | 102.8562 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9832 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2713 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 114 | 2713 | 60 | 112.4384 | 12.7863 | 15.9431 | 34.284 | 0.83712 | 167.4432 | -29.3798 | 0 | 108.8547 | 71.1453 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0333 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2714 | 2 | 5.8 | 0 | 0 | 0 | 0 | 0 | 114 | 2714 | 120 | 112.4384 | 12.7863 | 15.9431 | 94.284 | 1.8371 | 152.4432 | -25.5187 | 0 | 108.8547 | 71.1453 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2436 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2715 | 3 | 5.1 | 0 | 0 | 0 | 0 | 0 | 114 | 2715 | 180 | 112.4384 | 12.7863 | 15.9431 | 154.284 | 2.8371 | 137.4432 | -19.3092 | 0 | 108.8547 | 71.1453 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.6919 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2716 | 4 | 4.3 | 0 | 0 | 0 | 0 | 0 | 114 | 2716 | 240 | 112.4384 | 12.7863 | 15.9431 | 214.284 | 3.8371 | 122.4432 | -11.3616 | 0 | 108.8547 | 71.1453 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.911 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2717 | 5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 114 | 2717 | 300 | 112.4384 | 12.7863 | 15.9431 | 274.284 | 4.8371 | 107.4432 | -2.2305 | 0 | 108.8547 | 71.1453 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.0912 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2718 | 6 | 3.4 | 0 | 0 | 0 | 0 | 0 | 114 | 2718 | 360 | 112.4384 | 12.7863 | 15.9431 | 334.284 | 5.8371 | 92.4432 | 7.6317 | 7.6317 | 100.5726 | 79.4274 | 91.9877 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.5849 | 5.5849 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2719 | 7 | 3.2 | 18.81 | 34.17 | 52.98 | 34.17 | 17.09 | 114 | 2719 | 420 | 112.4384 | 12.7863 | 15.9431 | 394.284 | 6.8371 | 77.4432 | 17.8465 | 17.8465 | 89.8234 | 90.1766 | 77.3626 | 13.428 | 13.428 | 29.1659 | 42.5939 | -2.8027 | 0% | 19.261 | 0 | 0 | 175.828 | 175.828 | 0% | 12.05% | 12.05% | 80% | 9.641% | 1.857 | 9.2438 | 6 | 11.1423 | 4.1067 | 6.337% | 6.337%
4 | 114 | 24 | 2720 | 8 | 6.1 | 97.14 | 101.39 | 198.53 | 101.39 | 50.7 | 114 | 2720 | 480 | 112.4384 | 12.7863 | 15.9431 | 454.284 | 7.8371 | 62.4432 | 28.0497 | 28.0497 | 78.4174 | 101.5826 | 62.7545 | 94.5718 | 94.5718 | 86.5418 | 181.1136 | -0.0056904 | 0% | 81.8996 | 0 | 0 | 154.6302 | 154.6302 | 0% | 11.83% | 11.83% | 80% | 9.46% | 7.7478 | 8.3603 | 6 | 46.4867 | 17.1335 | 30.06% | 30.06%
4 | 114 | 24 | 2721 | 9 | 9.5 | 171.39 | 143.06 | 314.45 | 143.06 | 71.53 | 114 | 2721 | 540 | 112.4384 | 12.7863 | 15.9431 | 514.284 | 8.8371 | 47.4432 | 37.8032 | 37.8032 | 65.3886 | 114.6114 | 48.2333 | 186.2508 | 186.2508 | 122.1093 | 308.3602 | 0.3545 | 35.45% | 139.4405 | 49.4322 | 34.6025 | 165.8996 | 165.8996 | 20.86% | 11.64% | 11.64% | 85% | 9.891% | 13.7914 | 7.3995 | 6 | 82.7484 | 30.4985 | 49.88% | 49.88%
4 | 114 | 24 | 2722 | 10 | 11.2 | 312.97 | 153.33 | 466.3 | 153.33 | 76.67 | 114 | 2722 | 600 | 112.4384 | 12.7863 | 15.9431 | 574.284 | 9.8371 | 32.4432 | 46.4592 | 46.4592 | 49.4154 | 130.5846 | 33.956 | 358.1239 | 358.1239 | 130.8753 | 488.9992 | 0.52865 | 52.87% | 221.1254 | 116.8983 | 81.8288 | 172.2482 | 172.2482 | 47.51% | 11.5% | 11.5% | 85% | 9.777% | 21.6198 | 6.9494 | 6 | 129.7185 | 47.8102 | 75.31% | 75.31%
4 | 114 | 24 | 2723 | 11 | 13.6 | 427.69 | 183.06 | 610.75 | 183.06 | 91.53 | 114 | 2723 | 660 | 112.4384 | 12.7863 | 15.9431 | 634.284 | 10.8371 | 17.4432 | 52.9783 | 52.9783 | 29.0451 | 150.9549 | 20.483 | 501.8111 | 501.8111 | 156.2515 | 658.0626 | 0.60779 | 60.78% | 297.5759 | 180.8637 | 126.6046 | 172.8131 | 172.8131 | 73.26% | 11.4% | 11.4% | 90% | 10.26% | 30.5365 | 6.3484 | 6 | 183.2192 | 67.5288 | 106% | 106%
4 | 114 | 24 | 2724 | 12 | 14.3 | 426.19 | 218.06 | 644.25 | 218.06 | 109.03 | 114 | 2724 | 720 | 112.4384 | 12.7863 | 15.9431 | 694.284 | 11.8371 | 2.4432 | 55.9461 | 55.9461 | 4.2575 | 175.7425 | 11.2711 | 504.4833 | 504.4833 | 186.1259 | 690.6092 | 0.61935 | 61.94% | 312.2935 | 193.419 | 135.3933 | 161.576 | 161.576 | 83.8% | 11.39% | 11.39% | 90% | 10.25% | 32.0028 | 6.1808 | 6 | 192.0167 | 70.7713 | 118.8% | 118.8%
4 | 114 | 24 | 2725 | 13 | 15.1 | 429.81 | 238.69 | 668.5 | 238.69 | 119.35 | 114 | 2725 | 780 | 112.4384 | 12.7863 | 15.9431 | 754.284 | 12.8371 | -12.5568 | 54.4043 | 54.4043 | 21.3614 | 201.3614 | 16.6075 | 506.528 | 506.528 | 203.7347 | 710.2627 | 0.62702 | 62.7% | 321.1808 | 201.3863 | 140.9704 | 160.7512 | 160.7512 | 87.69% | 11.38% | 11.38% | 90% | 10.24% | 32.8843 | 5.9933 | 5.9933 | 197.086 | 72.7207 | 122.6% | 122.6%
4 | 114 | 24 | 2726 | 14 | 13.7 | 441.11 | 222.97 | 664.08 | 222.97 | 111.49 | 114 | 2726 | 840 | 112.4384 | 12.7863 | 15.9431 | 814.284 | 13.8371 | -27.5568 | 48.8817 | 48.8817 | 43.318 | 223.318 | 29.4227 | 510.0064 | 510.0064 | 190.3168 | 700.3232 | 0.61996 | 62% | 316.6862 | 196.3317 | 137.4322 | 156.7978 | 156.7978 | 87.65% | 11.39% | 11.39% | 90% | 10.25% | 32.4536 | 6.3243 | 6 | 194.7218 | 71.7683 | 124.2% | 124.2%
4 | 114 | 24 | 2727 | 15 | 14.6 | 533.89 | 174.44 | 708.33 | 174.44 | 87.22 | 114 | 2727 | 900 | 112.4384 | 12.7863 | 15.9431 | 874.284 | 14.8371 | -42.5568 | 40.7843 | 40.7843 | 60.5829 | 240.5829 | 43.5426 | 592.4507 | 592.4507 | 148.8939 | 741.3446 | 0.63291 | 63.29% | 335.236 | 212.1735 | 148.5214 | 157.0723 | 157.0723 | 94.56% | 11.37% | 11.37% | 90% | 10.23% | 34.303 | 6.1099 | 6 | 205.8177 | 75.8579 | 131% | 131%
4 | 114 | 24 | 2728 | 16 | 15 | 384.64 | 174.53 | 559.17 | 174.53 | 87.27 | 114 | 2728 | 960 | 112.4384 | 12.7863 | 15.9431 | 934.284 | 15.8371 | -57.5568 | 31.302 | 31.302 | 74.4076 | 254.4076 | 58.0097 | 392.2115 | 392.2115 | 148.9707 | 541.1822 | 0.57131 | 57.13% | 244.7226 | 139.8114 | 97.868 | 149.4187 | 149.4187 | 65.5% | 11.42% | 11.42% | 90% | 10.28% | 25.1596 | 6.0165 | 6 | 150.9575 | 55.6382 | 101% | 101%
4 | 114 | 24 | 2729 | 17 | 14.1 | 146.86 | 198.81 | 345.67 | 198.81 | 99.41 | 114 | 2729 | 1020 | 112.4384 | 12.7863 | 15.9431 | 994.284 | 16.8371 | -72.5568 | 21.1903 | 21.1903 | 86.2206 | 266.2206 | 72.5993 | 121.5019 | 121.5019 | 169.6949 | 291.1968 | 0.36451 | 36.45% | 131.6792 | 47.999 | 33.5993 | 134.8266 | 134.8266 | 24.92% | 11.52% | 11.52% | 80% | 9.214% | 12.1325 | 6.2283 | 6 | 72.795 | 26.83 | 53.99% | 53.99%
4 | 114 | 24 | 2730 | 18 | 14.9 | 103.61 | 154.92 | 258.53 | 154.92 | 77.46 | 114 | 2730 | 1080 | 112.4384 | 12.7863 | 15.9431 | 1054.284 | 17.8371 | -87.5568 | 10.9378 | 10.9378 | 97.0949 | 277.0949 | 87.2247 | 26.4393 | 26.4393 | 132.2325 | 158.6718 | 0.0089194 | 0.8919% | 71.7514 | 0.63998 | 0.44799 | 127.0607 | 127.0607 | 0.3526% | 11.53% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2731 | 19 | 14.2 | 26.86 | 88.14 | 115 | 88.14 | 44.07 | 114 | 2731 | 1140 | 112.4384 | 12.7863 | 15.9431 | 1114.284 | 18.8371 | -102.5568 | 0.92134 | 0.92134 | 107.8243 | 287.8243 | 101.8322 | 0 | 0 | 75.2322 | 75.2322 | -0.89406 | 0% | 34.02 | 0 | 0 | 155.2093 | 155.2093 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2732 | 20 | 12.4 | 0 | 13.69 | 13.69 | 13.69 | 6.85 | 114 | 2732 | 1200 | 112.4384 | 12.7863 | 15.9431 | 1174.284 | 19.8371 | -117.5568 | -8.4931 | 0 | 108.8547 | 288.8547 | 103.2097 | 0 | 0 | 11.6851 | 11.6851 | -10.4814 | 0% | 5.284 | 0 | 0 | 138.744 | 138.744 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2733 | 21 | 10.8 | 0 | 0 | 0 | 0 | 0 | 114 | 2733 | 1260 | 112.4384 | 12.7863 | 15.9431 | 1234.284 | 20.8371 | -132.5568 | -16.8821 | 0 | 108.8547 | 288.8547 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2976 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2734 | 22 | 10.2 | 0 | 0 | 0 | 0 | 0 | 114 | 2734 | 1320 | 112.4384 | 12.7863 | 15.9431 | 1294.284 | 21.8371 | -147.5568 | -23.7243 | 0 | 108.8547 | 288.8547 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0122 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2735 | 23 | 7.9 | 0 | 0 | 0 | 0 | 0 | 114 | 2735 | 1380 | 112.4384 | 12.7863 | 15.9431 | 1354.284 | 22.8371 | -162.5568 | -28.4153 | 0 | 108.8547 | 288.8547 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8988 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
4 | 114 | 24 | 2736 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 114 | 2736 | 1440 | 112.4384 | 12.7863 | 15.9431 | 1414.284 | 23.8371 | -177.5568 | -30.3954 | 0 | 108.8547 | 288.8547 | 103.2097 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6519 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2737 | 1 | 5.5 | 0 | 0 | 0 | 0 | 0 | 115 | 2737 | 60 | 113.4247 | 13.1242 | 16.0307 | 34.284 | 0.83858 | 167.4213 | -29.0432 | 0 | 109.3637 | 70.6363 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.7668 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2738 | 2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 115 | 2738 | 120 | 113.4247 | 13.1242 | 16.0307 | 94.284 | 1.8386 | 152.4213 | -25.1948 | 0 | 109.3637 | 70.6363 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3136 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2739 | 3 | 4.5 | 0 | 0 | 0 | 0 | 0 | 115 | 2739 | 180 | 113.4247 | 13.1242 | 16.0307 | 154.284 | 2.8386 | 137.4213 | -19.0042 | 0 | 109.3637 | 70.6363 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.946 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2740 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 115 | 2740 | 240 | 113.4247 | 13.1242 | 16.0307 | 214.284 | 3.8386 | 122.4213 | -11.076 | 0 | 109.3637 | 70.6363 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.708 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2741 | 5 | 3.6 | 0 | 0 | 0 | 0 | 0 | 115 | 2741 | 300 | 113.4247 | 13.1242 | 16.0307 | 274.284 | 4.8386 | 107.4213 | -1.9609 | 0 | 109.3637 | 70.6363 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.3424 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2742 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 115 | 2742 | 360 | 113.4247 | 13.1242 | 16.0307 | 334.284 | 5.8386 | 92.4213 | 7.8908 | 7.8908 | 100.7926 | 79.2074 | 91.953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.9568 | 6.9568 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2743 | 7 | 3.9 | 20.19 | 21.31 | 41.5 | 21.31 | 10.66 | 115 | 2743 | 420 | 113.4247 | 13.1242 | 16.0307 | 394.284 | 6.8386 | 77.4213 | 18.1019 | 18.1019 | 90.0571 | 89.9429 | 77.3477 | 14.233 | 14.233 | 18.1892 | 32.4222 | -3.882 | 0% | 14.6613 | 0 | 0 | 179.3382 | 179.3382 | 0% | 12.03% | 12.03% | 80% | 9.625% | 1.4112 | 9.0252 | 6 | 8.4672 | 3.1208 | 4.721% | 4.721%
4 | 115 | 25 | 2744 | 8 | 6.6 | 83.25 | 51.58 | 134.83 | 51.58 | 25.79 | 115 | 2744 | 480 | 113.4247 | 13.1242 | 16.0307 | 454.284 | 7.8386 | 62.4213 | 28.3094 | 28.3094 | 78.6639 | 101.3361 | 62.7611 | 80.348 | 80.348 | 44.0263 | 124.3743 | -0.36549 | 0% | 56.2421 | 0 | 0 | 197.4204 | 197.4204 | 0% | 11.85% | 11.85% | 80% | 9.48% | 5.3317 | 8.2139 | 6 | 31.9903 | 11.7906 | 16.2% | 16.2%
4 | 115 | 25 | 2745 | 9 | 10.3 | 208.89 | 80.08 | 288.97 | 80.08 | 40.04 | 115 | 2745 | 540 | 113.4247 | 13.1242 | 16.0307 | 514.284 | 8.8386 | 47.4213 | 38.0766 | 38.0766 | 65.6419 | 114.3581 | 48.2673 | 225.4675 | 225.4675 | 68.3526 | 293.82 | 0.33862 | 33.86% | 132.8654 | 44.9911 | 31.4937 | 169.299 | 169.299 | 18.6% | 11.62% | 11.62% | 80% | 9.298% | 12.3533 | 7.1852 | 6 | 74.1201 | 27.3183 | 43.78% | 43.78%
4 | 115 | 25 | 2746 | 10 | 13.7 | 313.42 | 106.11 | 419.53 | 106.11 | 53.06 | 115 | 2746 | 600 | 113.4247 | 13.1242 | 16.0307 | 574.284 | 9.8386 | 32.4213 | 46.7562 | 46.7562 | 49.6521 | 130.3479 | 34.0316 | 356.5683 | 356.5683 | 90.5706 | 447.1389 | 0.51575 | 51.57% | 202.1962 | 104.2818 | 72.9973 | 176.5528 | 176.5528 | 41.35% | 11.47% | 11.47% | 85% | 9.753% | 19.7205 | 6.3243 | 6 | 118.3227 | 43.61 | 67.02% | 67.02%
4 | 115 | 25 | 2747 | 11 | 15.1 | 412.03 | 161.19 | 573.22 | 161.19 | 80.6 | 115 | 2747 | 660 | 113.4247 | 13.1242 | 16.0307 | 634.284 | 10.8386 | 17.4213 | 53.3031 | 53.3031 | 29.2044 | 150.7956 | 20.6414 | 480.8876 | 480.8876 | 137.5843 | 618.4719 | 0.60075 | 60.08% | 279.673 | 168.0141 | 117.6098 | 175.4239 | 175.4239 | 67.04% | 11.4% | 11.4% | 90% | 10.26% | 28.6968 | 5.9933 | 5.9933 | 171.9888 | 63.4603 | 98.04% | 98.04%
4 | 115 | 25 | 2748 | 12 | 14.8 | 483.53 | 233.97 | 717.5 | 233.97 | 116.99 | 115 | 2748 | 720 | 113.4247 | 13.1242 | 16.0307 | 694.284 | 11.8386 | 2.4213 | 56.2847 | 56.2847 | 4.2509 | 175.7491 | 11.5966 | 569.4354 | 569.4354 | 199.7059 | 769.1413 | 0.63968 | 63.97% | 347.8057 | 222.485 | 155.7395 | 166.6966 | 166.6966 | 93.43% | 11.36% | 11.36% | 90% | 10.22% | 35.5622 | 6.0631 | 6 | 213.3734 | 78.6427 | 128% | 128%
4 | 115 | 25 | 2749 | 13 | 13.7 | 359.72 | 259.92 | 619.64 | 259.92 | 129.96 | 115 | 2749 | 780 | 113.4247 | 13.1242 | 16.0307 | 754.284 | 12.8386 | -12.5787 | 54.7254 | 54.7254 | 21.5468 | 201.5468 | 16.845 | 421.7148 | 421.7148 | 221.8556 | 643.5704 | 0.60373 | 60.37% | 291.0225 | 175.6982 | 122.9887 | 157.6024 | 157.6024 | 78.04% | 11.41% | 11.41% | 90% | 10.27% | 29.8752 | 6.3243 | 6 | 179.251 | 66.0663 | 113.7% | 113.7%
4 | 115 | 25 | 2750 | 14 | 16.7 | 257.78 | 258.42 | 516.2 | 258.42 | 129.21 | 115 | 2750 | 840 | 113.4247 | 13.1242 | 16.0307 | 814.284 | 13.8386 | -27.5787 | 49.1672 | 49.1672 | 43.5956 | 223.5956 | 29.5584 | 296.3581 | 296.3581 | 220.5753 | 516.9333 | 0.56781 | 56.78% | 233.7573 | 132.73 | 92.911 | 156.0848 | 156.0848 | 59.53% | 11.4% | 11.4% | 90% | 10.26% | 23.9906 | 5.6319 | 5.6319 | 135.1121 | 53.0531 | 86.56% | 86.56%
4 | 115 | 25 | 2751 | 15 | 17.8 | 284.72 | 242.58 | 527.3 | 242.58 | 121.29 | 115 | 2751 | 900 | 113.4247 | 13.1242 | 16.0307 | 874.284 | 14.8386 | -42.5787 | 41.0382 | 41.0382 | 60.8793 | 240.8793 | 43.6296 | 313.8845 | 313.8845 | 207.055 | 520.9395 | 0.57435 | 57.44% | 235.5688 | 135.2997 | 94.7098 | 154.6182 | 154.6182 | 61.25% | 11.39% | 11.39% | 90% | 10.25% | 24.1392 | 5.3938 | 5.3938 | 130.2015 | 53.3817 | 84.21% | 84.21%
4 | 115 | 25 | 2752 | 16 | 15.6 | 321.47 | 212.03 | 533.5 | 212.03 | 106.02 | 115 | 2752 | 960 | 113.4247 | 13.1242 | 16.0307 | 934.284 | 15.8386 | -57.5787 | 31.5361 | 31.5361 | 74.6942 | 254.6942 | 58.0668 | 325.0932 | 325.0932 | 180.9789 | 506.0721 | 0.55785 | 55.78% | 228.8458 | 127.6608 | 89.3625 | 149.1383 | 149.1383 | 59.92% | 11.42% | 11.42% | 90% | 10.28% | 23.5272 | 5.8784 | 5.8784 | 138.3034 | 52.0284 | 92.73% | 92.73%
4 | 115 | 25 | 2753 | 17 | 15.3 | 149.25 | 117.58 | 266.83 | 117.58 | 58.79 | 115 | 2753 | 1020 | 113.4247 | 13.1242 | 16.0307 | 994.284 | 16.8386 | -72.5787 | 21.4163 | 21.4163 | 86.4913 | 266.4913 | 72.6336 | 122.0027 | 122.0027 | 100.3608 | 222.3635 | 0.24073 | 24.07% | 100.5528 | 24.2063 | 16.9444 | 132.9099 | 132.9099 | 12.75% | 11.5% | 11.5% | 80% | 9.201% | 9.2519 | 5.9472 | 5.9472 | 55.0226 | 20.4598 | 41.4% | 41.4%
4 | 115 | 25 | 2754 | 18 | 15 | 96.67 | 107.31 | 203.98 | 107.31 | 53.66 | 115 | 2754 | 1080 | 113.4247 | 13.1242 | 16.0307 | 1054.284 | 17.8386 | -87.5787 | 11.1652 | 11.1652 | 97.3505 | 277.3505 | 87.239 | 24.0475 | 24.0475 | 91.5948 | 115.6423 | -0.28496 | 0% | 52.2934 | 0 | 0 | 124.6148 | 124.6148 | 0% | 11.54% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2755 | 19 | 13.3 | 32.69 | 57.31 | 90 | 57.31 | 28.66 | 115 | 2755 | 1140 | 113.4247 | 13.1242 | 16.0307 | 1114.284 | 18.8386 | -102.5787 | 1.1584 | 1.1584 | 108.0661 | 288.0661 | 101.8262 | 0 | 0 | 48.9171 | 48.9171 | -1.8496 | 0% | 22.1203 | 0 | 0 | 153.092 | 153.092 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2756 | 20 | 12.2 | 0 | 12.22 | 12.22 | 12.22 | 6.11 | 115 | 2756 | 1200 | 113.4247 | 13.1242 | 16.0307 | 1174.284 | 19.8386 | -117.5787 | -8.2393 | 0 | 109.3637 | 289.3637 | 103.5592 | 0 | 0 | 10.4304 | 10.4304 | -11.8832 | 0% | 4.7166 | 0 | 0 | 138.7054 | 138.7054 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2757 | 21 | 11.1 | 0 | 0 | 0 | 0 | 0 | 115 | 2757 | 1260 | 113.4247 | 13.1242 | 16.0307 | 1234.284 | 20.8386 | -132.5787 | -16.6061 | 0 | 109.3637 | 289.3637 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4716 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2758 | 22 | 10.7 | 0 | 0 | 0 | 0 | 0 | 115 | 2758 | 1320 | 113.4247 | 13.1242 | 16.0307 | 1294.284 | 21.8386 | -147.5787 | -23.4232 | 0 | 109.3637 | 289.3637 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8593 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2759 | 23 | 9.7 | 0 | 0 | 0 | 0 | 0 | 115 | 2759 | 1380 | 113.4247 | 13.1242 | 16.0307 | 1354.284 | 22.8386 | -162.5787 | -28.0917 | 0 | 109.3637 | 289.3637 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7109 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
4 | 115 | 25 | 2760 | 24 | 8.2 | 0 | 0 | 0 | 0 | 0 | 115 | 2760 | 1440 | 113.4247 | 13.1242 | 16.0307 | 1414.284 | 23.8386 | -177.5787 | -30.0583 | 0 | 109.3637 | 289.3637 | 103.5592 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3245 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2761 | 1 | 7.4 | 0 | 0 | 0 | 0 | 0 | 116 | 2761 | 60 | 114.411 | 13.4582 | 16.1054 | 34.284 | 0.83982 | 167.4026 | -28.711 | 0 | 109.8675 | 70.1325 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5707 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2762 | 2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 116 | 2762 | 120 | 114.411 | 13.4582 | 16.1054 | 94.284 | 1.8398 | 152.4026 | -24.8756 | 0 | 109.8675 | 70.1325 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0411 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2763 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 116 | 2763 | 180 | 114.411 | 13.4582 | 16.1054 | 154.284 | 2.8398 | 137.4026 | -18.7041 | 0 | 109.8675 | 70.1325 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2067 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2764 | 4 | 5.3 | 0 | 0 | 0 | 0 | 0 | 116 | 2764 | 240 | 114.411 | 13.4582 | 16.1054 | 214.284 | 3.8398 | 122.4026 | -10.7954 | 0 | 109.8675 | 70.1325 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2734 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2765 | 5 | 4.8 | 0 | 0 | 0 | 0 | 0 | 116 | 2765 | 300 | 114.411 | 13.4582 | 16.1054 | 274.284 | 4.8398 | 107.4026 | -1.6963 | 0 | 109.8675 | 70.1325 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.60789 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2766 | 6 | 4.1 | 0 | 0 | 0 | 0 | 0 | 116 | 2766 | 360 | 114.411 | 13.4582 | 16.1054 | 334.284 | 5.8398 | 92.4026 | 8.1448 | 8.1448 | 101.0123 | 78.9877 | 91.9215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 12.0392 | 12.0392 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2767 | 7 | 5.1 | 22.42 | 31.75 | 54.17 | 31.75 | 15.88 | 116 | 2767 | 420 | 114.411 | 13.4582 | 16.1054 | 394.284 | 6.8398 | 77.4026 | 18.352 | 18.352 | 90.2909 | 89.7091 | 77.3363 | 15.6107 | 15.6107 | 27.1003 | 42.711 | -2.6855 | 0% | 19.3139 | 0 | 0 | 189.0594 | 189.0594 | 0% | 11.97% | 11.97% | 80% | 9.578% | 1.8499 | 8.6583 | 6 | 11.0994 | 4.0909 | 5.871% | 5.871%
4 | 116 | 26 | 2768 | 8 | 8.4 | 103.61 | 76.94 | 180.55 | 76.94 | 38.47 | 116 | 2768 | 480 | 114.411 | 13.4582 | 16.1054 | 454.284 | 7.8398 | 62.4026 | 28.5636 | 28.5636 | 78.9111 | 101.0889 | 62.7716 | 99.147 | 99.147 | 65.6724 | 164.8194 | -0.052638 | 0% | 74.5313 | 0 | 0 | 169.1013 | 169.1013 | 0% | 11.76% | 11.76% | 80% | 9.406% | 7.0103 | 7.7015 | 6 | 42.0616 | 15.5026 | 24.87% | 24.87%
4 | 116 | 26 | 2769 | 9 | 10.9 | 276.11 | 110.08 | 386.19 | 110.08 | 55.04 | 116 | 2769 | 540 | 114.411 | 13.4582 | 16.1054 | 514.284 | 8.8398 | 47.4026 | 38.3444 | 38.3444 | 65.8969 | 114.1031 | 48.3054 | 296.0366 | 296.0366 | 93.9592 | 389.9958 | 0.45697 | 45.7% | 176.3561 | 80.5889 | 56.4122 | 183.8258 | 183.8258 | 30.69% | 11.56% | 11.56% | 85% | 9.824% | 17.3246 | 7.0274 | 6 | 103.9474 | 38.3117 | 56.55% | 56.55%
4 | 116 | 26 | 2770 | 10 | 14.3 | 432.97 | 108.53 | 541.5 | 108.53 | 54.27 | 116 | 2770 | 600 | 114.411 | 13.4582 | 16.1054 | 574.284 | 9.8398 | 32.4026 | 47.0476 | 47.0476 | 49.8923 | 130.1077 | 34.1118 | 489.7735 | 489.7735 | 92.6361 | 582.4097 | 0.58505 | 58.5% | 263.3657 | 154.081 | 107.8567 | 191.7362 | 191.7362 | 56.25% | 11.42% | 11.42% | 90% | 10.28% | 27.0692 | 6.1808 | 6 | 162.4154 | 59.8612 | 84.71% | 84.71%
4 | 116 | 26 | 2771 | 11 | 14.7 | 565.64 | 120.92 | 686.56 | 120.92 | 60.46 | 116 | 2771 | 660 | 114.411 | 13.4582 | 16.1054 | 634.284 | 10.8398 | 17.4026 | 53.6229 | 53.6229 | 29.3688 | 150.6312 | 20.8045 | 656.7363 | 656.7363 | 103.2117 | 759.948 | 0.6374 | 63.74% | 343.6485 | 219.0399 | 153.3279 | 186.9294 | 186.9294 | 82.02% | 11.36% | 11.36% | 90% | 10.23% | 35.146 | 6.0865 | 6 | 210.8759 | 77.7222 | 112.8% | 112.8%
4 | 116 | 26 | 2772 | 12 | 16.1 | 664.64 | 125.36 | 790 | 125.36 | 62.68 | 116 | 2772 | 720 | 114.411 | 13.4582 | 16.1054 | 694.284 | 11.8398 | 2.4026 | 56.6192 | 56.6192 | 4.2496 | 175.7504 | 11.9196 | 778.7836 | 778.7836 | 107.0015 | 885.785 | 0.66464 | 66.46% | 400.552 | 266.2227 | 186.3559 | 176.3633 | 176.3633 | 105.7% | 11.33% | 11.33% | 95% | 10.77% | 43.1271 | 5.7653 | 5.7653 | 248.6414 | 95.3718 | 141% | 141%
4 | 116 | 26 | 2773 | 13 | 9 | 709.72 | 130.97 | 840.69 | 130.97 | 65.49 | 116 | 2773 | 780 | 114.411 | 13.4582 | 16.1054 | 754.284 | 12.8398 | -12.5974 | 55.0432 | 55.0432 | 21.728 | 201.728 | 17.0807 | 827.7558 | 827.7558 | 111.7899 | 939.5457 | 0.65523 | 65.52% | 424.8626 | 278.3814 | 194.8669 | 163.4513 | 163.4513 | 119.2% | 11.27% | 11.27% | 95% | 10.7% | 45.4781 | 7.5357 | 6 | 272.8687 | 100.5708 | 166.9% | 166.9%
4 | 116 | 26 | 2774 | 14 | 12.7 | 679.03 | 155.14 | 834.17 | 155.14 | 77.57 | 116 | 2774 | 840 | 114.411 | 13.4582 | 16.1054 | 814.284 | 13.8398 | -27.5974 | 49.4502 | 49.4502 | 43.8691 | 223.8691 | 29.6926 | 776.3075 | 776.3075 | 132.4203 | 908.7278 | 0.65964 | 65.96% | 410.9267 | 271.0646 | 189.7452 | 167.3468 | 167.3468 | 113.4% | 11.31% | 11.31% | 95% | 10.74% | 44.1456 | 6.5691 | 6 | 264.8734 | 97.624 | 158.3% | 158.3%
4 | 116 | 26 | 2775 | 15 | 14.7 | 592.86 | 130.75 | 723.61 | 130.75 | 65.38 | 116 | 2775 | 900 | 114.411 | 13.4582 | 16.1054 | 874.284 | 14.8398 | -42.5974 | 41.2902 | 41.2902 | 61.1714 | 241.1714 | 43.7146 | 649.3878 | 649.3878 | 111.6021 | 760.9899 | 0.63762 | 63.76% | 344.1196 | 219.4187 | 153.5931 | 162.6687 | 162.6687 | 94.42% | 11.36% | 11.36% | 90% | 10.23% | 35.1932 | 6.0865 | 6 | 211.1594 | 77.8267 | 129.8% | 129.8%
4 | 116 | 26 | 2776 | 16 | 14.1 | 408.53 | 165.28 | 573.81 | 165.28 | 82.64 | 116 | 2776 | 960 | 114.411 | 13.4582 | 16.1054 | 934.284 | 15.8398 | -57.5974 | 31.7689 | 31.7689 | 74.9763 | 254.9763 | 58.1214 | 409.7924 | 409.7924 | 141.0753 | 550.8677 | 0.57168 | 57.17% | 249.1024 | 142.4073 | 99.6851 | 153.1117 | 153.1117 | 65.11% | 11.43% | 11.43% | 90% | 10.29% | 25.6315 | 6.2283 | 6 | 153.7892 | 56.6819 | 100.4% | 100.4%
4 | 116 | 26 | 2777 | 17 | 15.7 | 286.19 | 135.36 | 421.55 | 135.36 | 67.68 | 116 | 2777 | 1020 | 114.411 | 13.4582 | 16.1054 | 994.284 | 16.8398 | -72.5974 | 21.6412 | 21.6412 | 86.7574 | 266.7574 | 72.6653 | 231.2169 | 231.2169 | 115.537 | 346.7539 | 0.4454 | 44.54% | 156.8021 | 69.8398 | 48.8879 | 144.9487 | 144.9487 | 33.73% | 11.46% | 11.46% | 85% | 9.74% | 15.273 | 5.8557 | 5.8557 | 89.4338 | 33.7749 | 61.7% | 61.7%
4 | 116 | 26 | 2778 | 18 | 14.3 | 216.19 | 101.19 | 317.38 | 101.19 | 50.6 | 116 | 2778 | 1080 | 114.411 | 13.4582 | 16.1054 | 1054.284 | 17.8398 | -87.5974 | 11.3918 | 11.3918 | 97.6014 | 277.6014 | 87.2504 | 52.5073 | 52.5073 | 86.3711 | 138.8784 | -0.11422 | 0% | 62.8008 | 0 | 0 | 132.4523 | 132.4523 | 0% | 11.56% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2779 | 19 | 12.2 | 103.61 | 61.31 | 164.92 | 61.31 | 30.66 | 116 | 2779 | 1140 | 114.411 | 13.4582 | 16.1054 | 1114.284 | 18.8398 | -102.5974 | 1.3946 | 1.3946 | 108.303 | 288.303 | 101.817 | 0 | 0 | 52.3314 | 52.3314 | -1.7248 | 0% | 23.6642 | 0 | 0 | 115.9832 | 115.9832 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2780 | 20 | 11.8 | 0 | 19.25 | 19.25 | 19.25 | 9.63 | 116 | 2780 | 1200 | 114.411 | 13.4582 | 16.1054 | 1174.284 | 19.8398 | -117.5974 | -7.9866 | 0 | 109.8675 | 289.8675 | 103.9047 | 0 | 0 | 16.4309 | 16.4309 | -7.3061 | 0% | 7.4301 | 0 | 0 | 138.1724 | 138.1724 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2781 | 21 | 11.6 | 0 | 0 | 0 | 0 | 0 | 116 | 2781 | 1260 | 114.411 | 13.4582 | 16.1054 | 1234.284 | 20.8398 | -132.5974 | -16.3316 | 0 | 109.8675 | 289.8675 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.318 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2782 | 22 | 10.2 | 0 | 0 | 0 | 0 | 0 | 116 | 2782 | 1320 | 114.411 | 13.4582 | 16.1054 | 1294.284 | 21.8398 | -147.5974 | -23.1244 | 0 | 109.8675 | 289.8675 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5499 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2783 | 23 | 9.1 | 0 | 0 | 0 | 0 | 0 | 116 | 2783 | 1380 | 114.411 | 13.4582 | 16.1054 | 1354.284 | 22.8398 | -162.5974 | -27.771 | 0 | 109.8675 | 289.8675 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4775 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
4 | 116 | 26 | 2784 | 24 | 8.4 | 0 | 0 | 0 | 0 | 0 | 116 | 2784 | 1440 | 114.411 | 13.4582 | 16.1054 | 1414.284 | 23.8398 | -177.5974 | -29.7252 | 0 | 109.8675 | 289.8675 | 103.9047 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7955 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2785 | 1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 117 | 2785 | 60 | 115.3973 | 13.7881 | 16.1672 | 34.284 | 0.84085 | 167.3872 | -28.3834 | 0 | 110.3661 | 69.6339 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3193 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2786 | 2 | 7.5 | 0 | 0 | 0 | 0 | 0 | 117 | 2786 | 120 | 115.3973 | 13.7881 | 16.1672 | 94.284 | 1.8409 | 152.3872 | -24.5612 | 0 | 110.3661 | 69.6339 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.2527 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2787 | 3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 117 | 2787 | 180 | 115.3973 | 13.7881 | 16.1672 | 154.284 | 2.8409 | 137.3872 | -18.409 | 0 | 110.3661 | 69.6339 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5765 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2788 | 4 | 7.7 | 0 | 0 | 0 | 0 | 0 | 117 | 2788 | 240 | 115.3973 | 13.7881 | 16.1672 | 214.284 | 3.8409 | 122.3872 | -10.5198 | 0 | 110.3661 | 69.6339 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2717 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2789 | 5 | 7.9 | 0 | 0 | 0 | 0 | 0 | 117 | 2789 | 300 | 115.3973 | 13.7881 | 16.1672 | 274.284 | 4.8409 | 107.3872 | -1.4368 | 0 | 110.3661 | 69.6339 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.0774 | 3.0774 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2790 | 6 | 8.1 | 0 | 0.92 | 0.92 | 0.92 | 0.46 | 117 | 2790 | 360 | 115.3973 | 13.7881 | 16.1672 | 334.284 | 5.8409 | 92.3872 | 8.3935 | 8.3935 | 101.2319 | 78.7681 | 91.8933 | 0 | 0 | 0.78527 | 0.78527 | -179.8961 | 0% | 0.3551 | 0 | 0 | 17.2665 | 17.2665 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2791 | 7 | 8.3 | 29.36 | 34.92 | 64.28 | 34.92 | 17.46 | 117 | 2791 | 420 | 115.3973 | 13.7881 | 16.1672 | 394.284 | 6.8409 | 77.3872 | 18.5967 | 18.5967 | 90.5247 | 89.4753 | 77.3285 | 20.1956 | 20.1956 | 29.8061 | 50.0017 | -2.0244 | 0% | 22.6108 | 0 | 0 | 192.4833 | 192.4833 | 0% | 11.83% | 11.83% | 80% | 9.468% | 2.1407 | 7.7294 | 6 | 12.8443 | 4.734 | 6.673% | 6.673%
4 | 117 | 27 | 2792 | 8 | 9.4 | 125.92 | 83.61 | 209.53 | 83.61 | 41.81 | 117 | 2792 | 480 | 115.3973 | 13.7881 | 16.1672 | 454.284 | 7.8409 | 62.3872 | 28.8122 | 28.8122 | 79.1589 | 100.8411 | 62.786 | 119.4862 | 119.4862 | 71.3656 | 190.8518 | 0.07652 | 7.652% | 86.3032 | 6.6039 | 4.6227 | 170.1973 | 170.1973 | 2.716% | 11.71% | 11.71% | 80% | 9.366% | 8.0829 | 7.4266 | 6 | 48.4974 | 17.8746 | 28.49% | 28.49%
4 | 117 | 27 | 2793 | 9 | 10.7 | 235.47 | 110.83 | 346.3 | 110.83 | 55.42 | 117 | 2793 | 540 | 115.3973 | 13.7881 | 16.1672 | 514.284 | 8.8409 | 47.3872 | 38.6065 | 38.6065 | 66.1535 | 113.8465 | 48.3477 | 250.8067 | 250.8067 | 94.5993 | 345.406 | 0.41082 | 41.08% | 156.1926 | 64.1672 | 44.9171 | 179.4989 | 179.4989 | 25.02% | 11.58% | 11.58% | 85% | 9.847% | 15.38 | 7.0797 | 6 | 92.2803 | 34.0116 | 51.41% | 51.41%
4 | 117 | 27 | 2794 | 10 | 12.7 | 332.14 | 168.69 | 500.83 | 168.69 | 84.35 | 117 | 2794 | 600 | 115.3973 | 13.7881 | 16.1672 | 574.284 | 9.8409 | 32.3872 | 47.3334 | 47.3334 | 50.1358 | 129.8642 | 34.1966 | 373.6079 | 373.6079 | 143.9859 | 517.5938 | 0.55055 | 55.06% | 234.0559 | 128.8605 | 90.2024 | 186.0003 | 186.0003 | 48.5% | 11.47% | 11.47% | 90% | 10.32% | 24.1519 | 6.5691 | 6 | 144.9112 | 53.4097 | 77.91% | 77.91%
4 | 117 | 27 | 2795 | 11 | 13.3 | 569.81 | 127.03 | 696.84 | 127.03 | 63.52 | 117 | 2795 | 660 | 115.3973 | 13.7881 | 16.1672 | 634.284 | 10.8409 | 17.3872 | 53.9376 | 53.9376 | 29.5384 | 150.4616 | 20.9719 | 658.1878 | 658.1878 | 108.4269 | 766.6147 | 0.63468 | 63.47% | 346.6632 | 220.0194 | 154.0136 | 184.6057 | 184.6057 | 83.43% | 11.36% | 11.36% | 90% | 10.23% | 35.4563 | 6.4214 | 6 | 212.7376 | 78.4084 | 115.2% | 115.2%
4 | 117 | 27 | 2796 | 12 | 14.4 | 657.86 | 137.97 | 795.83 | 137.97 | 68.99 | 117 | 2796 | 720 | 115.3973 | 13.7881 | 16.1672 | 694.284 | 11.8409 | 2.3872 | 56.9494 | 56.9494 | 4.2537 | 175.7463 | 12.2399 | 767.0174 | 767.0174 | 117.7648 | 884.7822 | 0.66013 | 66.01% | 400.0985 | 264.1172 | 184.882 | 174.3178 | 174.3178 | 106.1% | 11.33% | 11.33% | 95% | 10.76% | 43.049 | 6.1571 | 6 | 258.2938 | 95.199 | 148.2% | 148.2%
4 | 117 | 27 | 2797 | 13 | 18.2 | 389.58 | 287.92 | 677.5 | 287.92 | 143.96 | 117 | 2797 | 780 | 115.3973 | 13.7881 | 16.1672 | 754.284 | 12.8409 | -12.6128 | 55.3577 | 55.3577 | 21.9047 | 201.9047 | 17.3145 | 452.0712 | 452.0712 | 245.7551 | 697.8263 | 0.63384 | 63.38% | 315.557 | 200.0132 | 140.0092 | 173.3864 | 173.3864 | 80.75% | 11.36% | 11.36% | 90% | 10.23% | 32.2686 | 5.3093 | 5.3093 | 171.3235 | 71.359 | 98.81% | 98.81%
4 | 117 | 27 | 2798 | 14 | 18 | 250.83 | 278.47 | 529.3 | 278.47 | 139.24 | 117 | 2798 | 840 | 115.3973 | 13.7881 | 16.1672 | 814.284 | 13.8409 | -27.6128 | 49.7305 | 49.7305 | 44.1384 | 224.1384 | 29.8252 | 285.1941 | 285.1941 | 237.689 | 522.8831 | 0.57606 | 57.61% | 236.4477 | 136.2079 | 95.3456 | 165.871 | 165.871 | 57.48% | 11.38% | 11.38% | 90% | 10.24% | 24.2223 | 5.3514 | 5.3514 | 129.623 | 53.5654 | 78.15% | 78.15%
4 | 117 | 27 | 2799 | 15 | 15.3 | 437.69 | 178.42 | 616.11 | 178.42 | 89.21 | 117 | 2799 | 900 | 115.3973 | 13.7881 | 16.1672 | 874.284 | 14.8409 | -42.6128 | 41.5403 | 41.5403 | 61.4591 | 241.4591 | 43.7976 | 476.3957 | 476.3957 | 152.291 | 628.6867 | 0.60477 | 60.48% | 284.2921 | 171.9327 | 120.3529 | 161.4648 | 161.4648 | 74.54% | 11.4% | 11.4% | 90% | 10.26% | 29.1589 | 5.9472 | 5.9472 | 173.4123 | 64.4822 | 107.4% | 107.4%
4 | 117 | 27 | 2800 | 16 | 16.1 | 461.39 | 135.83 | 597.22 | 135.83 | 67.92 | 117 | 2800 | 960 | 115.3973 | 13.7881 | 16.1672 | 934.284 | 15.8409 | -57.6128 | 32.0002 | 32.0002 | 75.2539 | 255.2539 | 58.1736 | 459.1476 | 459.1476 | 115.9382 | 575.0858 | 0.58935 | 58.93% | 260.0538 | 153.2622 | 107.2835 | 159.8447 | 159.8447 | 67.12% | 11.4% | 11.4% | 90% | 10.26% | 26.6821 | 5.7653 | 5.7653 | 153.8307 | 59.0051 | 96.24% | 96.24%
4 | 117 | 27 | 2801 | 17 | 15.3 | 399.36 | 121.58 | 520.94 | 121.58 | 60.79 | 117 | 2801 | 1020 | 115.3973 | 13.7881 | 16.1672 | 994.284 | 16.8409 | -72.6128 | 21.8651 | 21.8651 | 87.0188 | 267.0188 | 72.6942 | 318.9884 | 318.9884 | 103.775 | 422.7634 | 0.50773 | 50.77% | 191.1736 | 97.0654 | 67.9458 | 152.07 | 152.07 | 44.68% | 11.45% | 11.45% | 85% | 9.732% | 18.6052 | 5.9472 | 5.9472 | 110.6479 | 41.1437 | 72.76% | 72.76%
4 | 117 | 27 | 2802 | 18 | 15.3 | 198.53 | 79.36 | 277.89 | 79.36 | 39.68 | 117 | 2802 | 1080 | 115.3973 | 13.7881 | 16.1672 | 1054.284 | 17.8409 | -87.6128 | 11.6175 | 11.6175 | 97.8474 | 277.8474 | 87.2586 | 47.1514 | 47.1514 | 67.738 | 114.8894 | -0.28618 | 0% | 51.953 | 0 | 0 | 134.2877 | 134.2877 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2803 | 19 | 14.5 | 126.19 | 50.75 | 176.94 | 50.75 | 25.38 | 117 | 2803 | 1140 | 115.3973 | 13.7881 | 16.1672 | 1114.284 | 18.8409 | -102.6128 | 1.6299 | 1.6299 | 108.5348 | 288.5348 | 101.8045 | 0 | 0 | 43.3178 | 43.3178 | -2.1293 | 0% | 19.5883 | 0 | 0 | 121.9533 | 121.9533 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2804 | 20 | 13.3 | 0 | 19.36 | 19.36 | 19.36 | 9.68 | 117 | 2804 | 1200 | 115.3973 | 13.7881 | 16.1672 | 1174.284 | 19.8409 | -117.6128 | -7.7351 | 0 | 110.3661 | 290.3661 | 104.246 | 0 | 0 | 16.5248 | 16.5248 | -7.0512 | 0% | 7.4725 | 0 | 0 | 140.7114 | 140.7114 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2805 | 21 | 12.4 | 0 | 0 | 0 | 0 | 0 | 117 | 2805 | 1260 | 115.3973 | 13.7881 | 16.1672 | 1234.284 | 20.8409 | -132.6128 | -16.0586 | 0 | 110.3661 | 290.3661 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1465 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2806 | 22 | 11.9 | 0 | 0 | 0 | 0 | 0 | 117 | 2806 | 1320 | 115.3973 | 13.7881 | 16.1672 | 1294.284 | 21.8409 | -147.6128 | -22.8278 | 0 | 110.3661 | 290.3661 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2518 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2807 | 23 | 11.5 | 0 | 0 | 0 | 0 | 0 | 117 | 2807 | 1380 | 115.3973 | 13.7881 | 16.1672 | 1354.284 | 22.8409 | -162.6128 | -27.4535 | 0 | 110.3661 | 290.3661 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1853 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
4 | 117 | 27 | 2808 | 24 | 11.1 | 0 | 0 | 0 | 0 | 0 | 117 | 2808 | 1440 | 115.3973 | 13.7881 | 16.1672 | 1414.284 | 23.8409 | -177.6128 | -29.3959 | 0 | 110.3661 | 290.3661 | 104.246 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1187 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2809 | 1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 118 | 2809 | 60 | 116.3836 | 14.1138 | 16.2159 | 34.284 | 0.84167 | 167.375 | -28.0604 | 0 | 110.8593 | 69.1407 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2905 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2810 | 2 | 9.9 | 0 | 0 | 0 | 0 | 0 | 118 | 2810 | 120 | 116.3836 | 14.1138 | 16.2159 | 94.284 | 1.8417 | 152.375 | -24.2518 | 0 | 110.8593 | 69.1407 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0219 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2811 | 3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 118 | 2811 | 180 | 116.3836 | 14.1138 | 16.2159 | 154.284 | 2.8417 | 137.375 | -18.119 | 0 | 110.8593 | 69.1407 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.601 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2812 | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 118 | 2812 | 240 | 116.3836 | 14.1138 | 16.2159 | 214.284 | 3.8417 | 122.375 | -10.2494 | 0 | 110.8593 | 69.1407 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9058 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2813 | 5 | 9.2 | 0 | 0 | 0 | 0 | 0 | 118 | 2813 | 300 | 116.3836 | 14.1138 | 16.2159 | 274.284 | 4.8417 | 107.375 | -1.1826 | 0 | 110.8593 | 69.1407 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.5539 | 6.5539 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2814 | 6 | 8.9 | 0 | 1.11 | 1.11 | 1.11 | 0.56 | 118 | 2814 | 360 | 116.3836 | 14.1138 | 16.2159 | 334.284 | 5.8417 | 92.375 | 8.6369 | 8.6369 | 101.4511 | 78.5489 | 91.8684 | 0 | 0 | 0.94744 | 0.94744 | -146.9768 | 0% | 0.42843 | 0 | 0 | 20.4105 | 20.4105 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2815 | 7 | 8.6 | 28.53 | 28.61 | 57.14 | 28.61 | 14.31 | 118 | 2815 | 420 | 116.3836 | 14.1138 | 16.2159 | 394.284 | 6.8417 | 77.375 | 18.8358 | 18.8358 | 90.7586 | 89.2414 | 77.3242 | 19.3908 | 19.3908 | 24.4202 | 43.811 | -2.408 | 0% | 19.8113 | 0 | 0 | 195.8811 | 195.8811 | 0% | 11.83% | 11.83% | 80% | 9.461% | 1.8743 | 7.6459 | 6 | 11.246 | 4.1449 | 5.741% | 5.741%
4 | 118 | 28 | 2816 | 8 | 8.8 | 131.31 | 71.19 | 202.5 | 71.19 | 35.6 | 118 | 2816 | 480 | 116.3836 | 14.1138 | 16.2159 | 454.284 | 7.8417 | 62.375 | 29.0551 | 29.0551 | 79.4072 | 100.5928 | 62.8041 | 123.5728 | 123.5728 | 60.7645 | 184.3372 | 0.043171 | 4.317% | 83.3573 | 3.5986 | 2.519 | 172.5554 | 172.5554 | 1.46% | 11.73% | 11.73% | 80% | 9.385% | 7.8231 | 7.5907 | 6 | 46.9385 | 17.3 | 27.2% | 27.2%
4 | 118 | 28 | 2817 | 9 | 9.8 | 265.92 | 122.78 | 388.7 | 122.78 | 61.39 | 118 | 2817 | 540 | 116.3836 | 14.1138 | 16.2159 | 514.284 | 8.8417 | 47.375 | 38.8628 | 38.8628 | 66.4117 | 113.5883 | 48.394 | 281.4087 | 281.4087 | 104.7993 | 386.208 | 0.44693 | 44.69% | 174.6433 | 78.0526 | 54.6368 | 183.6745 | 183.6745 | 29.75% | 11.58% | 11.58% | 85% | 9.847% | 17.1963 | 7.3186 | 6 | 103.1777 | 38.028 | 56.17% | 56.17%
4 | 118 | 28 | 2818 | 10 | 10.3 | 418.14 | 137.03 | 555.17 | 137.03 | 68.52 | 118 | 2818 | 600 | 116.3836 | 14.1138 | 16.2159 | 574.284 | 9.8417 | 32.375 | 47.6134 | 47.6134 | 50.3826 | 129.6174 | 34.2858 | 467.7458 | 467.7458 | 116.9624 | 584.7083 | 0.57014 | 57.01% | 264.4051 | 150.7489 | 105.5243 | 187.5907 | 187.5907 | 56.25% | 11.47% | 11.47% | 90% | 10.32% | 27.2871 | 7.1852 | 6 | 163.7224 | 60.3429 | 87.28% | 87.28%
4 | 118 | 28 | 2819 | 11 | 10.3 | 579.08 | 123.81 | 702.89 | 123.81 | 61.91 | 118 | 2819 | 660 | 116.3836 | 14.1138 | 16.2159 | 634.284 | 10.8417 | 17.375 | 54.247 | 54.247 | 29.7133 | 150.2867 | 21.1433 | 665.5184 | 665.5184 | 105.6784 | 771.1969 | 0.62669 | 62.67% | 348.7352 | 218.5504 | 152.9853 | 182.1224 | 182.1224 | 84% | 11.37% | 11.37% | 90% | 10.23% | 35.6778 | 7.1852 | 6 | 214.0669 | 78.8983 | 117.5% | 117.5%
4 | 118 | 28 | 2820 | 12 | 12.2 | 618.53 | 163.61 | 782.14 | 163.61 | 81.81 | 118 | 2820 | 720 | 116.3836 | 14.1138 | 16.2159 | 694.284 | 11.8417 | 2.375 | 57.2753 | 57.2753 | 4.2634 | 175.7366 | 12.5572 | 717.6397 | 717.6397 | 139.6499 | 857.2895 | 0.64964 | 64.96% | 387.6663 | 251.8428 | 176.2899 | 171.3264 | 171.3264 | 102.9% | 11.33% | 11.33% | 95% | 10.76% | 41.717 | 6.6941 | 6 | 250.3018 | 92.2534 | 146.1% | 146.1%
4 | 118 | 28 | 2821 | 13 | 13.1 | 444.03 | 244.31 | 688.34 | 244.31 | 122.16 | 118 | 2821 | 780 | 116.3836 | 14.1138 | 16.2159 | 754.284 | 12.8417 | -12.625 | 55.6687 | 55.6687 | 22.0768 | 202.0768 | 17.5461 | 512.6864 | 512.6864 | 208.5316 | 721.218 | 0.62338 | 62.34% | 326.1348 | 203.3073 | 142.3151 | 166.2114 | 166.2114 | 85.62% | 11.38% | 11.38% | 90% | 10.24% | 33.4083 | 6.4703 | 6 | 200.4498 | 73.8795 | 120.6% | 120.6%
4 | 118 | 28 | 2822 | 14 | 14.4 | 352.08 | 239.17 | 591.25 | 239.17 | 119.59 | 118 | 2822 | 840 | 116.3836 | 14.1138 | 16.2159 | 814.284 | 13.8417 | -27.625 | 50.0082 | 50.0082 | 44.4033 | 224.4033 | 29.9561 | 398.1604 | 398.1604 | 204.1444 | 602.3048 | 0.59266 | 59.27% | 272.3622 | 161.4172 | 112.9921 | 163.0175 | 163.0175 | 69.31% | 11.41% | 11.41% | 90% | 10.27% | 27.976 | 6.1571 | 6 | 167.8558 | 61.8663 | 103% | 103%
4 | 118 | 28 | 2823 | 15 | 14.5 | 435.47 | 158.33 | 593.8 | 158.33 | 79.17 | 118 | 2823 | 900 | 116.3836 | 14.1138 | 16.2159 | 874.284 | 14.8417 | -42.625 | 41.7883 | 41.7883 | 61.7421 | 241.7421 | 43.8784 | 471.0409 | 471.0409 | 135.1431 | 606.184 | 0.59438 | 59.44% | 274.1164 | 162.9305 | 114.0513 | 159.7091 | 159.7091 | 71.41% | 11.41% | 11.41% | 90% | 10.27% | 28.1506 | 6.1335 | 6 | 168.9034 | 62.2525 | 105.8% | 105.8%
4 | 118 | 28 | 2824 | 16 | 16.2 | 408.61 | 127.58 | 536.19 | 127.58 | 63.79 | 118 | 2824 | 960 | 116.3836 | 14.1138 | 16.2159 | 934.284 | 15.8417 | -57.625 | 32.2301 | 32.2301 | 75.5267 | 255.5267 | 58.2233 | 403.4686 | 403.4686 | 108.8963 | 512.3649 | 0.56351 | 56.35% | 231.6914 | 130.5607 | 91.3925 | 157.5816 | 157.5816 | 58% | 11.41% | 11.41% | 90% | 10.27% | 23.7968 | 5.7429 | 5.7429 | 136.6627 | 52.6245 | 86.73% | 86.73%
4 | 118 | 28 | 2825 | 17 | 16.5 | 416.94 | 116.11 | 533.05 | 116.11 | 58.06 | 118 | 2825 | 1020 | 116.3836 | 14.1138 | 16.2159 | 994.284 | 16.8417 | -72.625 | 22.0878 | 22.0878 | 87.2754 | 267.2754 | 72.7203 | 329.3551 | 329.3551 | 99.1061 | 428.4612 | 0.51799 | 51.8% | 193.7502 | 100.3611 | 70.2528 | 154.9472 | 154.9472 | 45.34% | 11.42% | 11.42% | 85% | 9.71% | 18.8131 | 5.6761 | 5.6761 | 106.7847 | 41.6036 | 68.92% | 68.92%
4 | 118 | 28 | 2826 | 18 | 15.1 | 205.08 | 99.53 | 304.61 | 99.53 | 49.77 | 118 | 2826 | 1080 | 116.3836 | 14.1138 | 16.2159 | 1054.284 | 17.8417 | -87.625 | 11.8422 | 11.8422 | 98.0885 | 278.0885 | 87.2639 | 47.7038 | 47.7038 | 84.9542 | 132.658 | -0.14357 | 0% | 59.988 | 0 | 0 | 135.5925 | 135.5925 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2827 | 19 | 15.9 | 83.42 | 57.03 | 140.45 | 57.03 | 28.52 | 118 | 2827 | 1140 | 116.3836 | 14.1138 | 16.2159 | 1114.284 | 18.8417 | -102.625 | 1.8642 | 1.8642 | 108.7615 | 288.7615 | 101.7887 | 0 | 0 | 48.6781 | 48.6781 | -1.7412 | 0% | 22.0123 | 0 | 0 | 163.5644 | 163.5644 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2828 | 20 | 13 | 0 | 19.17 | 19.17 | 19.17 | 9.59 | 118 | 2828 | 1200 | 116.3836 | 14.1138 | 16.2159 | 1174.284 | 19.8417 | -117.625 | -7.4847 | 0 | 110.8593 | 290.8593 | 104.583 | 0 | 0 | 16.3626 | 16.3626 | -7.1711 | 0% | 7.3992 | 0 | 0 | 140.6049 | 140.6049 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2829 | 21 | 11.6 | 0 | 0 | 0 | 0 | 0 | 118 | 2829 | 1260 | 116.3836 | 14.1138 | 16.2159 | 1234.284 | 20.8417 | -132.625 | -15.7874 | 0 | 110.8593 | 290.8593 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9961 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2830 | 22 | 10.3 | 0 | 0 | 0 | 0 | 0 | 118 | 2830 | 1320 | 116.3836 | 14.1138 | 16.2159 | 1294.284 | 21.8417 | -147.625 | -22.5336 | 0 | 110.8593 | 290.8593 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3153 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2831 | 23 | 9.1 | 0 | 0 | 0 | 0 | 0 | 118 | 2831 | 1380 | 116.3836 | 14.1138 | 16.2159 | 1354.284 | 22.8417 | -162.625 | -27.1393 | 0 | 110.8593 | 290.8593 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4183 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
4 | 118 | 28 | 2832 | 24 | 7.9 | 0 | 0 | 0 | 0 | 0 | 118 | 2832 | 1440 | 116.3836 | 14.1138 | 16.2159 | 1414.284 | 23.8417 | -177.625 | -29.0708 | 0 | 110.8593 | 290.8593 | 104.583 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5214 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2833 | 1 | 6.9 | 0 | 0 | 0 | 0 | 0 | 119 | 2833 | 60 | 117.3699 | 14.4353 | 16.2515 | 34.284 | 0.84226 | 167.3661 | -27.7421 | 0 | 111.3469 | 68.6531 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9793 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2834 | 2 | 5.9 | 0 | 0 | 0 | 0 | 0 | 119 | 2834 | 120 | 117.3699 | 14.4353 | 16.2515 | 94.284 | 1.8423 | 152.3661 | -23.9474 | 0 | 111.3469 | 68.6531 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6856 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2835 | 3 | 5.3 | 0 | 0 | 0 | 0 | 0 | 119 | 2835 | 180 | 117.3699 | 14.4353 | 16.2515 | 154.284 | 2.8423 | 137.3661 | -17.8341 | 0 | 111.3469 | 68.6531 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7824 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2836 | 4 | 4.8 | 0 | 0 | 0 | 0 | 0 | 119 | 2836 | 240 | 117.3699 | 14.4353 | 16.2515 | 214.284 | 3.8423 | 122.3661 | -9.9842 | 0 | 111.3469 | 68.6531 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5444 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2837 | 5 | 4.1 | 0 | 0 | 0 | 0 | 0 | 119 | 2837 | 300 | 117.3699 | 14.4353 | 16.2515 | 274.284 | 4.8423 | 107.3661 | -0.93369 | 0 | 111.3469 | 68.6531 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.90599 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2838 | 6 | 4.1 | 0 | 1.19 | 1.19 | 1.19 | 0.6 | 119 | 2838 | 360 | 117.3699 | 14.4353 | 16.2515 | 334.284 | 5.8423 | 92.3661 | 8.8748 | 8.8748 | 101.67 | 78.33 | 91.8468 | 0 | 0 | 1.0157 | 1.0157 | -148.2981 | 0% | 0.45931 | 0 | 0 | 13.2831 | 13.2831 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2839 | 7 | 5.5 | 26.03 | 35 | 61.03 | 35 | 17.5 | 119 | 2839 | 420 | 117.3699 | 14.4353 | 16.2515 | 394.284 | 6.8423 | 77.3661 | 19.0694 | 19.0694 | 90.9923 | 89.0077 | 77.3234 | 17.4839 | 17.4839 | 29.8744 | 47.3583 | -2.3228 | 0% | 21.4154 | 0 | 0 | 190.7038 | 190.7038 | 0% | 11.95% | 11.95% | 80% | 9.562% | 2.0477 | 8.5383 | 6 | 12.2862 | 4.5283 | 6.443% | 6.443%
4 | 119 | 29 | 2840 | 8 | 7.7 | 124.53 | 79.64 | 204.17 | 79.64 | 39.82 | 119 | 2840 | 480 | 117.3699 | 14.4353 | 16.2515 | 454.284 | 7.8423 | 62.3661 | 29.2923 | 29.2923 | 79.6559 | 100.3441 | 62.8259 | 116.2402 | 116.2402 | 67.977 | 184.2172 | 0.028592 | 2.859% | 83.303 | 2.3818 | 1.6673 | 169.9084 | 169.9084 | 0.9813% | 11.77% | 11.77% | 80% | 9.415% | 7.8429 | 7.8981 | 6 | 47.0572 | 17.3438 | 27.7% | 27.7%
4 | 119 | 29 | 2841 | 9 | 10.4 | 245.83 | 120.08 | 365.91 | 120.08 | 60.04 | 119 | 2841 | 540 | 117.3699 | 14.4353 | 16.2515 | 514.284 | 8.8423 | 47.3661 | 39.1131 | 39.1131 | 66.6714 | 113.3286 | 48.4444 | 258.4919 | 258.4919 | 102.4947 | 360.9866 | 0.42586 | 42.59% | 163.2382 | 69.5161 | 48.6613 | 182.0565 | 182.0565 | 26.73% | 11.58% | 11.58% | 85% | 9.846% | 16.0728 | 7.1587 | 6 | 96.4368 | 35.5436 | 52.97% | 52.97%
4 | 119 | 29 | 2842 | 10 | 11.3 | 311.75 | 137.22 | 448.97 | 137.22 | 68.61 | 119 | 2842 | 600 | 117.3699 | 14.4353 | 16.2515 | 574.284 | 9.8423 | 32.3661 | 47.8876 | 47.8876 | 50.6325 | 129.3675 | 34.3791 | 346.8359 | 346.8359 | 117.1246 | 463.9605 | 0.51429 | 51.43% | 209.8029 | 107.8999 | 75.5299 | 181.5241 | 181.5241 | 41.61% | 11.51% | 11.51% | 85% | 9.786% | 20.5311 | 6.9236 | 6 | 123.1863 | 45.4026 | 67.86% | 67.86%
4 | 119 | 29 | 2843 | 11 | 14.1 | 244.17 | 179.25 | 423.42 | 179.25 | 89.63 | 119 | 2843 | 660 | 117.3699 | 14.4353 | 16.2515 | 634.284 | 10.8423 | 17.3661 | 54.551 | 54.551 | 29.8934 | 150.1066 | 21.3183 | 279.2214 | 279.2214 | 152.9994 | 432.2209 | 0.50791 | 50.79% | 195.4503 | 99.271 | 69.4897 | 172.5228 | 172.5228 | 40.28% | 11.47% | 11.47% | 85% | 9.751% | 19.0577 | 6.2283 | 6 | 114.3459 | 42.1443 | 66.28% | 66.28%
4 | 119 | 29 | 2844 | 12 | 16.9 | 289.81 | 170.47 | 460.28 | 170.47 | 85.24 | 119 | 2844 | 720 | 117.3699 | 14.4353 | 16.2515 | 694.284 | 11.8423 | 2.3661 | 57.5968 | 57.5968 | 4.2788 | 175.7212 | 12.8713 | 334.6306 | 334.6306 | 145.5052 | 480.1359 | 0.55064 | 55.06% | 217.1174 | 119.5546 | 83.6882 | 161.319 | 161.319 | 51.88% | 11.41% | 11.41% | 85% | 9.696% | 21.0507 | 5.588 | 5.588 | 117.6306 | 46.5518 | 72.92% | 72.92%
4 | 119 | 29 | 2845 | 13 | 18.1 | 188.06 | 343.19 | 531.25 | 343.19 | 171.6 | 119 | 2845 | 780 | 117.3699 | 14.4353 | 16.2515 | 754.284 | 12.8423 | -12.6339 | 55.9762 | 55.9762 | 22.2442 | 202.2442 | 17.7752 | 216.0728 | 216.0728 | 292.931 | 509.0038 | 0.57028 | 57.03% | 230.1715 | 131.2626 | 91.8838 | 163.0123 | 163.0123 | 56.37% | 11.38% | 11.38% | 90% | 10.24% | 23.5792 | 5.3303 | 5.3303 | 125.6843 | 52.1432 | 77.1% | 77.1%
4 | 119 | 29 | 2846 | 14 | 18.1 | 274.72 | 277.14 | 551.86 | 277.14 | 138.57 | 119 | 2846 | 840 | 117.3699 | 14.4353 | 16.2515 | 814.284 | 13.8423 | -27.6339 | 50.2831 | 50.2831 | 44.6636 | 224.6636 | 30.0851 | 309.0314 | 309.0314 | 236.5538 | 545.5851 | 0.58595 | 58.6% | 246.7136 | 144.5624 | 101.1937 | 160.8051 | 160.8051 | 62.93% | 11.38% | 11.38% | 90% | 10.24% | 25.2653 | 5.3303 | 5.3303 | 134.6718 | 55.8719 | 83.75% | 83.75%
4 | 119 | 29 | 2847 | 15 | 18.4 | 211.11 | 260.92 | 472.03 | 260.92 | 130.46 | 119 | 2847 | 900 | 117.3699 | 14.4353 | 16.2515 | 874.284 | 14.8423 | -42.6339 | 42.0343 | 42.0343 | 62.0204 | 242.0204 | 43.9569 | 226.9649 | 226.9649 | 222.7092 | 449.674 | 0.54093 | 54.09% | 203.3426 | 109.9939 | 76.9957 | 154.0253 | 154.0253 | 49.99% | 11.38% | 11.38% | 85% | 9.675% | 19.6742 | 5.2675 | 5.2675 | 103.6336 | 43.5078 | 67.28% | 67.28%
4 | 119 | 29 | 2848 | 16 | 18.5 | 242.42 | 274.08 | 516.5 | 274.08 | 137.04 | 119 | 2848 | 960 | 117.3699 | 14.4353 | 16.2515 | 934.284 | 15.8423 | -57.6339 | 32.4585 | 32.4585 | 75.7946 | 255.7946 | 58.2703 | 237.552 | 237.552 | 233.9419 | 471.4939 | 0.55357 | 55.36% | 213.2096 | 118.0274 | 82.6192 | 153.0984 | 153.0984 | 53.96% | 11.38% | 11.38% | 85% | 9.672% | 20.6221 | 5.2467 | 5.2467 | 108.1976 | 45.604 | 70.67% | 70.67%
4 | 119 | 29 | 2849 | 17 | 19.2 | 124.64 | 210.36 | 335 | 210.36 | 105.18 | 119 | 2849 | 1020 | 117.3699 | 14.4353 | 16.2515 | 994.284 | 16.8423 | -72.6339 | 22.3094 | 22.3094 | 87.5271 | 267.5271 | 72.7436 | 97.4013 | 97.4013 | 179.5535 | 276.9548 | 0.38327 | 38.33% | 125.239 | 48.0006 | 33.6004 | 142.1932 | 142.1932 | 23.63% | 11.38% | 11.38% | 80% | 9.1% | 11.3968 | 5.103 | 5.103 | 58.1577 | 25.2029 | 40.9% | 40.9%
4 | 119 | 29 | 2850 | 18 | 19.2 | 85.36 | 164.81 | 250.17 | 164.81 | 82.41 | 119 | 2850 | 1080 | 117.3699 | 14.4353 | 16.2515 | 1054.284 | 17.8423 | -87.6339 | 12.0659 | 12.0659 | 98.3246 | 278.3246 | 87.2661 | 19.477 | 19.477 | 140.6741 | 160.1511 | 0.076421 | 7.642% | 72.4203 | 5.5344 | 3.8741 | 133.1359 | 133.1359 | 2.91% | 11.38% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2851 | 19 | 17.4 | 50 | 85.36 | 135.36 | 85.36 | 42.68 | 119 | 2851 | 1140 | 117.3699 | 14.4353 | 16.2515 | 1114.284 | 18.8423 | -102.6339 | 2.0975 | 2.0975 | 108.983 | 288.983 | 101.7697 | 0 | 0 | 72.8593 | 72.8593 | -0.85022 | 0% | 32.947 | 0 | 0 | 161.9034 | 161.9034 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2852 | 20 | 16.2 | 2.31 | 19.72 | 22.03 | 19.72 | 9.86 | 119 | 2852 | 1200 | 117.3699 | 14.4353 | 16.2515 | 1174.284 | 19.8423 | -117.6339 | -7.2357 | 0 | 111.3469 | 291.3469 | 104.9156 | 0 | 0 | 16.8321 | 16.8321 | -6.5164 | 0% | 7.6115 | 0 | 0 | 144.9415 | 144.9415 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2853 | 21 | 15.3 | 0 | 0 | 0 | 0 | 0 | 119 | 2853 | 1260 | 117.3699 | 14.4353 | 16.2515 | 1234.284 | 20.8423 | -132.6339 | -15.518 | 0 | 111.3469 | 291.3469 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.75 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2854 | 22 | 13.5 | 0 | 0 | 0 | 0 | 0 | 119 | 2854 | 1320 | 117.3699 | 14.4353 | 16.2515 | 1294.284 | 21.8423 | -147.6339 | -22.2419 | 0 | 111.3469 | 291.3469 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.374 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2855 | 23 | 13.1 | 0 | 0 | 0 | 0 | 0 | 119 | 2855 | 1380 | 117.3699 | 14.4353 | 16.2515 | 1354.284 | 22.8423 | -162.6339 | -26.8284 | 0 | 111.3469 | 291.3469 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1659 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
4 | 119 | 29 | 2856 | 24 | 13.1 | 0 | 0 | 0 | 0 | 0 | 119 | 2856 | 1440 | 117.3699 | 14.4353 | 16.2515 | 1414.284 | 23.8423 | -177.6339 | -28.7498 | 0 | 111.3469 | 291.3469 | 104.9156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3482 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2857 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 120 | 2857 | 60 | 118.3562 | 14.7524 | 16.2739 | 34.284 | 0.84263 | 167.3605 | -27.4287 | 0 | 111.8287 | 68.1713 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3229 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2858 | 2 | 9.9 | 0 | 0 | 0 | 0 | 0 | 120 | 2858 | 120 | 118.3562 | 14.7524 | 16.2739 | 94.284 | 1.8426 | 152.3605 | -23.6482 | 0 | 111.8287 | 68.1713 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3101 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2859 | 3 | 10.9 | 0 | 0 | 0 | 0 | 0 | 120 | 2859 | 180 | 118.3562 | 14.7524 | 16.2739 | 154.284 | 2.8426 | 137.3605 | -17.5546 | 0 | 111.8287 | 68.1713 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0968 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2860 | 4 | 12 | 0 | 0 | 0 | 0 | 0 | 120 | 2860 | 240 | 118.3562 | 14.7524 | 16.2739 | 214.284 | 3.8426 | 122.3605 | -9.7243 | 0 | 111.8287 | 68.1713 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4204 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2861 | 5 | 10.6 | 0 | 0 | 0 | 0 | 0 | 120 | 2861 | 300 | 118.3562 | 14.7524 | 16.2739 | 274.284 | 4.8426 | 107.3605 | -0.69021 | 0 | 111.8287 | 68.1713 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.1695 | 6.1695 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2862 | 6 | 10.7 | 0.19 | 1.86 | 2.05 | 1.86 | 0.93 | 120 | 2862 | 360 | 118.3562 | 14.7524 | 16.2739 | 334.284 | 5.8426 | 92.3605 | 9.1072 | 9.1072 | 101.8884 | 78.1116 | 91.8286 | 0 | 0 | 1.5876 | 1.5876 | -84.7374 | 0% | 0.71792 | 0 | 0 | 19.2485 | 19.2485 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2863 | 7 | 10.7 | 24.53 | 35.36 | 59.89 | 35.36 | 17.68 | 120 | 2863 | 420 | 118.3562 | 14.7524 | 16.2739 | 394.284 | 6.8426 | 77.3605 | 19.2973 | 19.2973 | 91.2257 | 88.7743 | 77.3261 | 16.2856 | 16.2856 | 30.1816 | 46.4673 | -2.1186 | 0% | 21.0125 | 0 | 0 | 191.7166 | 191.7166 | 0% | 11.74% | 11.74% | 80% | 9.39% | 1.9731 | 7.0797 | 6 | 11.8384 | 4.3633 | 6.175% | 6.175%
4 | 120 | 30 | 2864 | 8 | 10.7 | 105.08 | 82.58 | 187.66 | 82.58 | 41.29 | 120 | 2864 | 480 | 118.3562 | 14.7524 | 16.2739 | 454.284 | 7.8426 | 62.3605 | 29.5236 | 29.5236 | 79.9049 | 100.0951 | 62.8515 | 97.3004 | 97.3004 | 70.4864 | 167.7869 | -0.0053976 | 0% | 75.8732 | 0 | 0 | 166.0655 | 166.0655 | 0% | 11.68% | 11.68% | 80% | 9.34% | 7.0868 | 7.0797 | 6 | 42.5207 | 15.6718 | 25.6% | 25.6%
4 | 120 | 30 | 2865 | 9 | 11.8 | 218.81 | 127.86 | 346.67 | 127.86 | 63.93 | 120 | 2865 | 540 | 118.3562 | 14.7524 | 16.2739 | 514.284 | 8.8426 | 47.3605 | 39.3575 | 39.3575 | 66.9323 | 113.0677 | 48.4986 | 228.6374 | 228.6374 | 109.1353 | 337.7727 | 0.40949 | 40.95% | 152.7408 | 62.5452 | 43.7816 | 176.0559 | 176.0559 | 24.87% | 11.56% | 11.56% | 85% | 9.826% | 15.0089 | 6.7954 | 6 | 90.0535 | 33.1909 | 51.15% | 51.15%
4 | 120 | 30 | 2866 | 10 | 12.8 | 203.61 | 187.78 | 391.39 | 187.78 | 93.89 | 120 | 2866 | 600 | 118.3562 | 14.7524 | 16.2739 | 574.284 | 9.8426 | 32.3605 | 48.1558 | 48.1558 | 50.8856 | 129.1144 | 34.4764 | 225.3109 | 225.3109 | 160.2803 | 385.5911 | 0.46439 | 46.44% | 174.3643 | 80.9724 | 56.6807 | 175.6547 | 175.6547 | 32.27% | 11.52% | 11.52% | 85% | 9.789% | 17.068 | 6.5443 | 6 | 102.4079 | 37.7443 | 58.3% | 58.3%
4 | 120 | 30 | 2867 | 11 | 14.6 | 254.64 | 228.97 | 483.61 | 228.97 | 114.49 | 120 | 2867 | 660 | 118.3562 | 14.7524 | 16.2739 | 634.284 | 10.8426 | 17.3605 | 54.8495 | 54.8495 | 30.0787 | 149.9213 | 21.4965 | 289.7686 | 289.7686 | 195.4381 | 485.2067 | 0.54259 | 54.26% | 219.4105 | 119.0498 | 83.3348 | 172.4802 | 172.4802 | 48.32% | 11.45% | 11.45% | 85% | 9.729% | 21.3457 | 6.1099 | 6 | 128.0743 | 47.2042 | 74.25% | 74.25%
4 | 120 | 30 | 2868 | 12 | 14.6 | 526.58 | 227.86 | 754.44 | 227.86 | 113.93 | 120 | 2868 | 720 | 118.3562 | 14.7524 | 16.2739 | 694.284 | 11.8426 | 2.3605 | 57.9137 | 57.9137 | 4.3001 | 175.6999 | 13.182 | 605.1408 | 605.1408 | 194.4907 | 799.6315 | 0.64538 | 64.54% | 361.5934 | 233.3648 | 163.3554 | 168.9764 | 168.9764 | 96.67% | 11.35% | 11.35% | 90% | 10.22% | 36.9436 | 6.1099 | 6 | 221.6618 | 81.6975 | 131.2% | 131.2%
4 | 120 | 30 | 2869 | 13 | 12.7 | 286.03 | 241.75 | 527.78 | 241.75 | 120.88 | 120 | 2869 | 780 | 118.3562 | 14.7524 | 16.2739 | 754.284 | 12.8426 | -12.6395 | 56.2802 | 56.2802 | 22.4065 | 202.4065 | 18.0018 | 327.0503 | 327.0503 | 206.3465 | 533.3968 | 0.55806 | 55.81% | 241.202 | 134.606 | 94.2242 | 153.5147 | 153.5147 | 61.38% | 11.46% | 11.46% | 90% | 10.31% | 24.8755 | 6.5691 | 6 | 149.253 | 55.0099 | 97.22% | 97.22%
4 | 120 | 30 | 2870 | 14 | 16.6 | 259.53 | 193.06 | 452.59 | 193.06 | 96.53 | 120 | 2870 | 840 | 118.3562 | 14.7524 | 16.2739 | 814.284 | 13.8426 | -27.6395 | 50.5552 | 50.5552 | 44.9191 | 224.9191 | 30.212 | 290.4262 | 290.4262 | 164.787 | 455.2132 | 0.53529 | 53.53% | 205.8474 | 110.189 | 77.1323 | 154.1699 | 154.1699 | 50.03% | 11.42% | 11.42% | 85% | 9.704% | 19.9754 | 5.6539 | 5.6539 | 112.9399 | 44.1739 | 73.26% | 73.26%
4 | 120 | 30 | 2871 | 15 | 12.6 | 137.42 | 308.53 | 445.95 | 308.53 | 154.27 | 120 | 2871 | 900 | 118.3562 | 14.7524 | 16.2739 | 874.284 | 14.8426 | -42.6395 | 42.2782 | 42.2782 | 62.2938 | 242.2938 | 44.033 | 146.8589 | 146.8589 | 263.3468 | 410.2057 | 0.48364 | 48.36% | 185.495 | 89.7136 | 62.7995 | 144.5508 | 144.5508 | 43.44% | 11.51% | 11.51% | 85% | 9.784% | 18.1489 | 6.5939 | 6 | 108.8935 | 40.1347 | 75.33% | 75.33%
4 | 120 | 30 | 2872 | 16 | 12 | 169.17 | 291.86 | 461.03 | 291.86 | 145.93 | 120 | 2872 | 960 | 118.3562 | 14.7524 | 16.2739 | 934.284 | 15.8426 | -57.6395 | 32.6854 | 32.6854 | 76.0575 | 256.0575 | 58.3148 | 164.542 | 164.542 | 249.1181 | 413.6601 | 0.48298 | 48.3% | 187.0571 | 90.3443 | 63.241 | 141.3031 | 141.3031 | 44.76% | 11.52% | 11.52% | 85% | 9.794% | 18.3198 | 6.7446 | 6 | 109.9188 | 40.5126 | 77.79% | 77.79%
4 | 120 | 30 | 2873 | 17 | 13.97 | 190.47 | 193.97 | 384.44 | 193.97 | 96.99 | 120 | 2873 | 1020 | 118.3562 | 14.7524 | 16.2739 | 994.284 | 16.8426 | -72.6395 | 22.5298 | 22.5298 | 87.7738 | 267.7738 | 72.764 | 147.2947 | 147.2947 | 165.5638 | 312.8584 | 0.394 | 39.4% | 141.4746 | 55.7405 | 39.0183 | 137.2917 | 137.2917 | 28.42% | 11.51% | 11.51% | 85% | 9.787% | 13.8454 | 6.2594 | 6 | 83.0727 | 30.618 | 60.51% | 60.51%
4 | 120 | 30 | 2874 | 18 | 14.83 | 145.47 | 116.03 | 261.5 | 116.03 | 58.02 | 120 | 2874 | 1080 | 118.3562 | 14.7524 | 16.2739 | 1054.284 | 17.8426 | -87.6395 | 12.2886 | 12.2886 | 98.5557 | 278.5557 | 87.2653 | 32.6099 | 32.6099 | 99.0378 | 131.6477 | -0.1555 | 0% | 59.5311 | 0 | 0 | 127.9232 | 127.9232 | 0% | 11.54% | 0% | 80% | 0% | 0 | 6.0561 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2875 | 19 | 14.37 | 44.17 | 72.14 | 116.31 | 72.14 | 36.07 | 120 | 2875 | 1140 | 118.3562 | 14.7524 | 16.2739 | 1114.284 | 18.8426 | -102.6395 | 2.3296 | 2.3296 | 109.1992 | 289.1992 | 101.7475 | 0 | 0 | 61.5753 | 61.5753 | -1.2644 | 0% | 27.8444 | 0 | 0 | 156.1341 | 156.1341 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1642 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2876 | 20 | 13.26 | 8.25 | 21.67 | 29.92 | 21.67 | 10.84 | 120 | 2876 | 1200 | 118.3562 | 14.7524 | 16.2739 | 1174.284 | 19.8426 | -117.6395 | -6.9882 | 0 | 111.8287 | 291.8287 | 105.2438 | 0 | 0 | 18.4965 | 18.4965 | -6.2188 | 0% | 8.3641 | 0 | 0 | 141.3383 | 141.3383 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4311 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2877 | 21 | 12.17 | 0 | 0 | 0 | 0 | 0 | 120 | 2877 | 1260 | 118.3562 | 14.7524 | 16.2739 | 1234.284 | 20.8426 | -132.6395 | -15.2505 | 0 | 111.8287 | 291.8287 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6857 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7017 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2878 | 22 | 11.62 | 0 | 0 | 0 | 0 | 0 | 120 | 2878 | 1320 | 118.3562 | 14.7524 | 16.2739 | 1294.284 | 21.8426 | -147.6395 | -21.9528 | 0 | 111.8287 | 291.8287 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4458 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8413 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2879 | 23 | 11.44 | 0 | 0 | 0 | 0 | 0 | 120 | 2879 | 1380 | 118.3562 | 14.7524 | 16.2739 | 1354.284 | 22.8426 | -162.6395 | -26.521 | 0 | 111.8287 | 291.8287 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0309 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8875 | 6 | 0 | 0 | 0% | 0%
4 | 120 | 30 | 2880 | 24 | 11.18 | 0 | 0 | 0 | 0 | 0 | 120 | 2880 | 1440 | 118.3562 | 14.7524 | 16.2739 | 1414.284 | 23.8426 | -177.6395 | -28.433 | 0 | 111.8287 | 291.8287 | 105.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7379 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9546 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2881 | 1 | 10.49 | 0 | 0 | 0 | 0 | 0 | 121 | 2881 | 60 | 119.3425 | 15.0649 | 16.2831 | 34.284 | 0.84278 | 167.3582 | -27.1202 | 0 | 112.3047 | 67.6953 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4243 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1349 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2882 | 2 | 9.49 | 0 | 0 | 0 | 0 | 0 | 121 | 2882 | 120 | 119.3425 | 15.0649 | 16.2831 | 94.284 | 1.8428 | 152.3582 | -23.3542 | 0 | 112.3047 | 67.6953 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5188 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.4022 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2883 | 3 | 8.34 | 0 | 0 | 0 | 0 | 0 | 121 | 2883 | 180 | 119.3425 | 15.0649 | 16.2831 | 154.284 | 2.8428 | 137.3582 | -17.2803 | 0 | 112.3047 | 67.6953 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8419 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7182 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2884 | 4 | 7.26 | 0 | 0 | 0 | 0 | 0 | 121 | 2884 | 240 | 119.3425 | 15.0649 | 16.2831 | 214.284 | 3.8428 | 122.3582 | -9.4699 | 0 | 112.3047 | 67.6953 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4878 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.0234 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2885 | 5 | 6.38 | 0 | 0 | 0 | 0 | 0 | 121 | 2885 | 300 | 119.3425 | 15.0649 | 16.2831 | 274.284 | 4.8428 | 107.3582 | -0.45221 | 0 | 112.3047 | 67.6953 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7716 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2781 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2886 | 6 | 6.13 | 0.19 | 1.58 | 1.77 | 1.58 | 0.79 | 121 | 2886 | 360 | 119.3425 | 15.0649 | 16.2831 | 334.284 | 5.8428 | 92.3582 | 9.334 | 9.334 | 102.1063 | 77.8937 | 91.8137 | 0 | 0 | 1.3486 | 1.3486 | -107.8811 | 0% | 0.60984 | 0 | 0 | 0.075387 | 0.075387 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3515 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2887 | 7 | 7.16 | 5.64 | 28.61 | 34.25 | 28.61 | 14.31 | 121 | 2887 | 420 | 119.3425 | 15.0649 | 16.2831 | 394.284 | 6.8428 | 77.3582 | 19.5195 | 19.5195 | 91.4589 | 88.5411 | 77.3323 | 3.7017 | 3.7017 | 24.4202 | 28.1218 | -4.3209 | 0% | 12.7167 | 0 | 0 | 163.8613 | 163.8613 | 0% | 11.9% | 11.9% | 80% | 9.518% | 1.2103 | 8.0521 | 6 | 7.262 | 2.6765 | 4.432% | 4.432%
5 | 121 | 1 | 2888 | 8 | 9.4 | 12.86 | 85.47 | 98.33 | 85.47 | 42.74 | 121 | 2888 | 480 | 119.3425 | 15.0649 | 16.2831 | 454.284 | 7.8428 | 62.3582 | 29.749 | 29.749 | 80.1541 | 99.8459 | 62.8806 | 11.8141 | 11.8141 | 72.9532 | 84.7673 | -0.83391 | 0% | 38.3318 | 0 | 0 | 177.607 | 177.607 | 0% | 11.77% | 11.77% | 80% | 9.415% | 3.609 | 7.4266 | 6 | 21.654 | 7.981 | 12.19% | 12.19%
5 | 121 | 1 | 2889 | 9 | 12.8 | 103.33 | 166.47 | 269.8 | 166.47 | 83.24 | 121 | 2889 | 540 | 119.3425 | 15.0649 | 16.2831 | 514.284 | 8.8428 | 47.3582 | 39.5958 | 39.5958 | 67.1944 | 112.8056 | 48.5566 | 107.3041 | 107.3041 | 142.091 | 249.3952 | 0.27892 | 27.89% | 112.7765 | 31.4558 | 22.0191 | 150.2505 | 150.2505 | 14.65% | 11.57% | 11.57% | 80% | 9.256% | 10.4386 | 6.5443 | 6 | 62.6318 | 23.0841 | 41.68% | 41.68%
5 | 121 | 1 | 2890 | 10 | 14.4 | 144.72 | 230.47 | 375.19 | 230.47 | 115.24 | 121 | 2890 | 600 | 119.3425 | 15.0649 | 16.2831 | 574.284 | 9.8428 | 32.3582 | 48.4178 | 48.4178 | 51.1416 | 128.8584 | 34.5776 | 159.299 | 159.299 | 196.7184 | 356.0175 | 0.44645 | 44.65% | 160.9911 | 71.8749 | 50.3124 | 155.7293 | 155.7293 | 32.31% | 11.49% | 11.49% | 85% | 9.765% | 15.7215 | 6.1571 | 6 | 94.3289 | 34.7667 | 60.57% | 60.57%
5 | 121 | 1 | 2891 | 11 | 15 | 188.97 | 260.92 | 449.89 | 260.92 | 130.46 | 121 | 2891 | 660 | 119.3425 | 15.0649 | 16.2831 | 634.284 | 10.8428 | 17.3582 | 55.1424 | 55.1424 | 30.2691 | 149.7309 | 21.6778 | 214.0027 | 214.0027 | 222.7092 | 436.7119 | 0.51564 | 51.56% | 197.4811 | 101.8293 | 71.2805 | 153.6899 | 153.6899 | 46.38% | 11.45% | 11.45% | 85% | 9.734% | 19.223 | 6.0165 | 6 | 115.3383 | 42.5101 | 75.05% | 75.05%
5 | 121 | 1 | 2892 | 12 | 17 | 325.47 | 320.19 | 645.66 | 320.19 | 160.1 | 121 | 2892 | 720 | 119.3425 | 15.0649 | 16.2831 | 694.284 | 11.8428 | 2.3582 | 58.2259 | 58.2259 | 4.3274 | 175.6726 | 13.4892 | 372.2856 | 372.2856 | 273.2993 | 645.5848 | 0.61592 | 61.59% | 291.9335 | 179.808 | 125.8656 | 155.7096 | 155.7096 | 80.83% | 11.38% | 11.38% | 90% | 10.24% | 29.8932 | 5.5661 | 5.5661 | 166.3885 | 66.1061 | 106.9% | 106.9%
5 | 121 | 1 | 2893 | 13 | 18.5 | 153.47 | 364.72 | 518.19 | 364.72 | 182.36 | 121 | 2893 | 780 | 119.3425 | 15.0649 | 16.2831 | 754.284 | 12.8428 | -12.6418 | 56.5804 | 56.5804 | 22.5635 | 202.5635 | 18.2254 | 174.6471 | 174.6471 | 311.308 | 485.9551 | 0.56103 | 56.1% | 219.7489 | 123.285 | 86.2995 | 151.3656 | 151.3656 | 57.01% | 11.38% | 11.38% | 85% | 9.671% | 21.2524 | 5.2467 | 5.2467 | 111.5045 | 46.9978 | 73.67% | 73.67%
5 | 121 | 1 | 2894 | 14 | 19.7 | 224.92 | 291.11 | 516.03 | 291.11 | 145.56 | 121 | 2894 | 840 | 119.3425 | 15.0649 | 16.2831 | 814.284 | 13.8428 | -27.6418 | 50.8245 | 50.8245 | 45.1695 | 225.1695 | 30.3367 | 250.4108 | 250.4108 | 248.4779 | 498.8888 | 0.57265 | 57.26% | 225.5975 | 129.1882 | 90.4317 | 151.5531 | 151.5531 | 59.67% | 11.36% | 11.36% | 85% | 9.653% | 21.7779 | 5.0025 | 5.0025 | 108.9433 | 48.1598 | 71.88% | 71.88%
5 | 121 | 1 | 2895 | 15 | 20.3 | 169.81 | 227.31 | 397.12 | 227.31 | 113.66 | 121 | 2895 | 900 | 119.3425 | 15.0649 | 16.2831 | 874.284 | 14.8428 | -42.6418 | 42.5201 | 42.5201 | 62.562 | 242.562 | 44.1067 | 180.412 | 180.412 | 194.0212 | 374.4332 | 0.49928 | 49.93% | 169.3187 | 84.5372 | 59.1761 | 144.6602 | 144.6602 | 40.91% | 11.34% | 11.34% | 85% | 9.643% | 16.3278 | 4.8842 | 4.8842 | 79.7475 | 36.1075 | 55.13% | 55.13%
5 | 121 | 1 | 2896 | 16 | 20.7 | 198.25 | 217.86 | 416.11 | 217.86 | 108.93 | 121 | 2896 | 960 | 119.3425 | 15.0649 | 16.2831 | 934.284 | 15.8428 | -57.6418 | 32.9107 | 32.9107 | 76.3153 | 256.3153 | 58.3565 | 191.4274 | 191.4274 | 185.9551 | 377.3826 | 0.50399 | 50.4% | 170.6524 | 86.0064 | 60.2045 | 144.3699 | 144.3699 | 41.7% | 11.34% | 11.34% | 85% | 9.635% | 16.443 | 4.8067 | 4.8067 | 79.0361 | 36.3622 | 54.75% | 54.75%
5 | 121 | 1 | 2897 | 17 | 20.6 | 150.56 | 177.86 | 328.42 | 177.86 | 88.93 | 121 | 2897 | 1020 | 119.3425 | 15.0649 | 16.2831 | 994.284 | 16.8428 | -72.6418 | 22.7489 | 22.7489 | 88.0153 | 268.0153 | 72.7815 | 115.255 | 115.255 | 151.813 | 267.068 | 0.37924 | 37.92% | 120.7682 | 45.8003 | 32.0602 | 137.7595 | 137.7595 | 23.27% | 11.33% | 11.33% | 80% | 9.068% | 10.9507 | 4.8259 | 4.8259 | 52.8474 | 24.2165 | 38.36% | 38.36%
5 | 121 | 1 | 2898 | 18 | 20.4 | 90.08 | 125.92 | 216 | 125.92 | 62.96 | 121 | 2898 | 1080 | 119.3425 | 15.0649 | 16.2831 | 1054.284 | 17.8428 | -87.6418 | 12.51 | 12.51 | 98.7815 | 278.7815 | 87.2615 | 19.8692 | 19.8692 | 107.4794 | 127.3486 | -0.090224 | 0% | 57.587 | 0 | 0 | 128.4489 | 128.4489 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.8647 | 4.8647 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2899 | 19 | 20 | 58.14 | 85.47 | 143.61 | 85.47 | 42.74 | 121 | 2899 | 1140 | 119.3425 | 15.0649 | 16.2831 | 1114.284 | 18.8428 | -102.6418 | 2.5605 | 2.5605 | 109.4101 | 289.4101 | 101.7222 | 0 | 0 | 72.9532 | 72.9532 | -0.76903 | 0% | 32.9894 | 0 | 0 | 162.1326 | 162.1326 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2900 | 20 | 18.5 | 11.67 | 25.28 | 36.95 | 25.28 | 12.64 | 121 | 2900 | 1200 | 119.3425 | 15.0649 | 16.2831 | 1174.284 | 19.8428 | -117.6418 | -6.7421 | 0 | 112.3047 | 292.3047 | 105.5673 | 0 | 0 | 21.5778 | 21.5778 | -4.668 | 0% | 9.7575 | 0 | 0 | 147.6017 | 147.6017 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2901 | 21 | 16.8 | 0 | 0 | 0 | 0 | 0 | 121 | 2901 | 1260 | 119.3425 | 15.0649 | 16.2831 | 1234.284 | 20.8428 | -132.6418 | -14.985 | 0 | 112.3047 | 292.3047 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.571 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2902 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 121 | 2902 | 1320 | 119.3425 | 15.0649 | 16.2831 | 1294.284 | 21.8428 | -147.6418 | -21.6665 | 0 | 112.3047 | 292.3047 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3635 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2903 | 23 | 11.6 | 0 | 0 | 0 | 0 | 0 | 121 | 2903 | 1380 | 119.3425 | 15.0649 | 16.2831 | 1354.284 | 22.8428 | -162.6418 | -26.2171 | 0 | 112.3047 | 292.3047 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5916 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
5 | 121 | 1 | 2904 | 24 | 10.5 | 0 | 0 | 0 | 0 | 0 | 121 | 2904 | 1440 | 119.3425 | 15.0649 | 16.2831 | 1414.284 | 23.8428 | -177.6418 | -28.1207 | 0 | 112.3047 | 292.3047 | 105.5673 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8385 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2905 | 1 | 9.6 | 0 | 0 | 0 | 0 | 0 | 122 | 2905 | 60 | 120.3288 | 15.3729 | 16.279 | 34.284 | 0.84272 | 167.3593 | -26.8168 | 0 | 112.7745 | 67.2255 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5239 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2906 | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 122 | 2906 | 120 | 120.3288 | 15.3729 | 16.279 | 94.284 | 1.8427 | 152.3593 | -23.0656 | 0 | 112.7745 | 67.2255 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7795 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2907 | 3 | 7.8 | 0 | 0 | 0 | 0 | 0 | 122 | 2907 | 180 | 120.3288 | 15.3729 | 16.279 | 154.284 | 2.8427 | 137.3593 | -17.0116 | 0 | 112.7745 | 67.2255 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9495 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2908 | 4 | 6.9 | 0 | 0 | 0 | 0 | 0 | 122 | 2908 | 240 | 120.3288 | 15.3729 | 16.279 | 214.284 | 3.8427 | 122.3593 | -9.221 | 0 | 112.7745 | 67.2255 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3211 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2909 | 5 | 6.9 | 0 | 0 | 0 | 0 | 0 | 122 | 2909 | 300 | 120.3288 | 15.3729 | 16.279 | 274.284 | 4.8427 | 107.3593 | -0.21978 | 0 | 112.7745 | 67.2255 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.7296 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2910 | 6 | 6.6 | 0.28 | 1.75 | 2.03 | 1.75 | 0.88 | 122 | 2910 | 360 | 120.3288 | 15.3729 | 16.279 | 334.284 | 5.8427 | 92.3593 | 9.5552 | 9.5552 | 102.3236 | 77.6764 | 91.8021 | 0 | 0 | 1.4937 | 1.4937 | -96.5731 | 0% | 0.67546 | 0 | 0 | 7.7639 | 7.7639 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2911 | 7 | 7.7 | 19.36 | 31.86 | 51.22 | 31.86 | 15.93 | 122 | 2911 | 420 | 120.3288 | 15.3729 | 16.279 | 394.284 | 6.8427 | 77.3593 | 19.7358 | 19.7358 | 91.6916 | 88.3084 | 77.342 | 12.5632 | 12.5632 | 27.1942 | 39.7574 | -2.7889 | 0% | 17.9783 | 0 | 0 | 180.0152 | 180.0152 | 0% | 11.87% | 11.87% | 80% | 9.493% | 1.7067 | 7.8981 | 6 | 10.2401 | 3.7742 | 5.688% | 5.688%
5 | 122 | 2 | 2912 | 8 | 11.3 | 105.75 | 83.69 | 189.44 | 83.69 | 41.85 | 122 | 2912 | 480 | 120.3288 | 15.3729 | 16.279 | 454.284 | 7.8427 | 62.3593 | 29.9684 | 29.9684 | 80.4033 | 99.5967 | 62.9134 | 96.396 | 96.396 | 71.4339 | 167.8299 | 0.0031097 | 0.311% | 75.8927 | 0.23601 | 0.1652 | 159.7663 | 159.7663 | 0.1034% | 11.65% | 11.65% | 80% | 9.324% | 7.0759 | 6.9236 | 6 | 42.4556 | 15.6478 | 26.57% | 26.57%
5 | 122 | 2 | 2913 | 9 | 14.2 | 221.58 | 144.72 | 366.3 | 144.72 | 72.36 | 122 | 2913 | 540 | 120.3288 | 15.3729 | 16.279 | 514.284 | 8.8427 | 47.3593 | 39.8279 | 39.8279 | 67.4576 | 112.5424 | 48.6182 | 228.7033 | 228.7033 | 123.5262 | 352.2295 | 0.44131 | 44.13% | 159.2782 | 70.2917 | 49.2042 | 173.1452 | 173.1452 | 28.42% | 11.49% | 11.49% | 85% | 9.771% | 15.5625 | 6.2045 | 6 | 93.3747 | 34.415 | 53.93% | 53.93%
5 | 122 | 2 | 2914 | 10 | 16.6 | 265.47 | 128.33 | 393.8 | 128.33 | 64.17 | 122 | 2914 | 600 | 120.3288 | 15.3729 | 16.279 | 574.284 | 9.8427 | 32.3593 | 48.6738 | 48.6738 | 51.4004 | 128.5996 | 34.6824 | 290.6952 | 290.6952 | 109.5365 | 400.2317 | 0.49838 | 49.84% | 180.9848 | 90.1994 | 63.1396 | 173.9076 | 173.9076 | 36.31% | 11.43% | 11.43% | 85% | 9.713% | 17.5786 | 5.6539 | 5.6539 | 99.3883 | 38.8735 | 57.15% | 57.15%
5 | 122 | 2 | 2915 | 11 | 19.6 | 241.47 | 153.53 | 395 | 153.53 | 76.77 | 122 | 2915 | 660 | 120.3288 | 15.3729 | 16.279 | 634.284 | 10.8427 | 17.3593 | 55.4295 | 55.4295 | 30.4648 | 149.5352 | 21.8617 | 272.1606 | 272.1606 | 131.0461 | 403.2066 | 0.5172 | 51.72% | 182.33 | 94.3014 | 66.011 | 168.7024 | 168.7024 | 39.13% | 11.36% | 11.36% | 85% | 9.657% | 17.6069 | 5.0224 | 5.0224 | 88.4297 | 38.9361 | 52.42% | 52.42%
5 | 122 | 2 | 2916 | 12 | 22.5 | 377.69 | 250.64 | 628.33 | 250.64 | 125.32 | 122 | 2916 | 720 | 120.3288 | 15.3729 | 16.279 | 694.284 | 11.8427 | 2.3593 | 58.5334 | 58.5334 | 4.3609 | 175.6391 | 13.7926 | 430.0388 | 430.0388 | 213.9346 | 643.9734 | 0.63428 | 63.43% | 291.2048 | 184.7046 | 129.2932 | 169.3093 | 169.3093 | 76.37% | 11.33% | 11.33% | 90% | 10.2% | 29.6956 | 4.4719 | 4.4719 | 132.7949 | 65.6691 | 78.43% | 78.43%
5 | 122 | 2 | 2917 | 13 | 23 | 452.78 | 188.19 | 640.97 | 188.19 | 94.1 | 122 | 2917 | 780 | 120.3288 | 15.3729 | 16.279 | 754.284 | 12.8427 | -12.6407 | 56.877 | 56.877 | 22.7152 | 202.7152 | 18.4461 | 512.8566 | 512.8566 | 160.6302 | 673.4868 | 0.64332 | 64.33% | 304.5507 | 195.9241 | 137.1468 | 166.6577 | 166.6577 | 82.29% | 11.33% | 11.33% | 90% | 10.2% | 31.0581 | 4.3829 | 4.3829 | 136.1247 | 68.6823 | 81.68% | 81.68%
5 | 122 | 2 | 2918 | 14 | 23.6 | 405.83 | 156.25 | 562.08 | 156.25 | 78.13 | 122 | 2918 | 840 | 120.3288 | 15.3729 | 16.279 | 814.284 | 13.8427 | -27.6407 | 51.091 | 51.091 | 45.4148 | 225.4148 | 30.459 | 449.5597 | 449.5597 | 133.3677 | 582.9274 | 0.62058 | 62.06% | 263.5998 | 163.5847 | 114.5093 | 295.4094 | 295.4094 | 38.76% | 11.31% | 11.31% | 90% | 10.18% | 26.8295 | 4.2784 | 4.2784 | 114.7884 | 59.331 | 38.86% | 38.86%
5 | 122 | 2 | 2919 | 15 | 23.5 | 462.14 | 181.03 | 643.17 | 181.03 | 90.52 | 122 | 2919 | 900 | 120.3288 | 15.3729 | 16.279 | 874.284 | 14.8427 | -42.6407 | 42.7597 | 42.7597 | 62.825 | 242.825 | 44.1779 | 488.1797 | 488.1797 | 154.5188 | 642.6985 | 0.6373 | 63.73% | 290.6283 | 185.2182 | 129.6527 | 295.6156 | 295.6156 | 43.86% | 11.32% | 11.32% | 90% | 10.19% | 29.6137 | 4.2957 | 4.2957 | 127.2109 | 65.4881 | 43.03% | 43.03%
5 | 122 | 2 | 2920 | 16 | 24.2 | 331.03 | 226.75 | 557.78 | 226.75 | 113.38 | 122 | 2920 | 960 | 120.3288 | 15.3729 | 16.279 | 934.284 | 15.8427 | -57.6407 | 33.1343 | 33.1343 | 76.5679 | 256.5679 | 58.3955 | 317.3735 | 317.3735 | 193.5432 | 510.9167 | 0.59725 | 59.73% | 231.0365 | 137.9868 | 96.5908 | 290.8217 | 290.8217 | 33.21% | 11.29% | 11.29% | 90% | 10.16% | 23.4657 | 4.1765 | 4.1765 | 98.0044 | 51.8923 | 33.7% | 33.7%
5 | 122 | 2 | 2921 | 17 | 24.1 | 191.67 | 150.75 | 342.42 | 150.75 | 75.38 | 122 | 2921 | 1020 | 120.3288 | 15.3729 | 16.279 | 994.284 | 16.8427 | -72.6407 | 22.9667 | 22.9667 | 88.2516 | 268.2516 | 72.7961 | 145.2885 | 145.2885 | 128.6732 | 273.9616 | 0.41765 | 41.76% | 123.8855 | 51.7403 | 36.2182 | 287.3715 | 287.3715 | 12.6% | 11.23% | 11.23% | 80% | 8.987% | 11.1332 | 4.1933 | 4.1933 | 46.6851 | 24.6201 | 16.25% | 16.25%
5 | 122 | 2 | 2922 | 18 | 23.9 | 132.42 | 111.75 | 244.17 | 111.75 | 55.88 | 122 | 2922 | 1080 | 120.3288 | 15.3729 | 16.279 | 1054.284 | 17.8427 | -87.6407 | 12.7303 | 12.7303 | 99.0021 | 279.0021 | 87.2546 | 28.7831 | 28.7831 | 95.3846 | 124.1677 | -0.051903 | 0% | 56.1486 | 0 | 0 | 279.7717 | 279.7717 | 0% | 11.21% | 0% | 80% | 0% | 0 | 4.2272 | 4.2272 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2923 | 19 | 23.1 | 57.97 | 56.47 | 114.44 | 56.47 | 28.24 | 122 | 2923 | 1140 | 120.3288 | 15.3729 | 16.279 | 1114.284 | 18.8427 | -102.6407 | 2.7901 | 2.7901 | 109.6156 | 289.6156 | 101.6938 | 0 | 0 | 48.2002 | 48.2002 | -1.4366 | 0% | 21.7961 | 0 | 0 | 309.0574 | 309.0574 | 0% | 11.22% | 0% | 80% | 0% | 0 | 4.3653 | 4.3653 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2924 | 20 | 21.7 | 12.31 | 20 | 32.31 | 20 | 10 | 122 | 2924 | 1200 | 120.3288 | 15.3729 | 16.279 | 1174.284 | 19.8427 | -117.6407 | -6.4976 | 0 | 112.7745 | 292.7745 | 105.886 | 0 | 0 | 17.0711 | 17.0711 | -5.7003 | 0% | 7.7195 | 0 | 0 | 151.2184 | 151.2184 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.6179 | 4.6179 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2925 | 21 | 18.9 | 0 | 0 | 0 | 0 | 0 | 122 | 2925 | 1260 | 120.3288 | 15.3729 | 16.279 | 1234.284 | 20.8427 | -132.6407 | -14.7216 | 0 | 112.7745 | 292.7745 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.6076 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2926 | 22 | 15.3 | 0 | 0 | 0 | 0 | 0 | 122 | 2926 | 1320 | 120.3288 | 15.3729 | 16.279 | 1294.284 | 21.8427 | -147.6407 | -21.3831 | 0 | 112.7745 | 292.7745 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8136 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2927 | 23 | 13.7 | 0 | 0 | 0 | 0 | 0 | 122 | 2927 | 1380 | 120.3288 | 15.3729 | 16.279 | 1354.284 | 22.8427 | -162.6407 | -25.917 | 0 | 112.7745 | 292.7745 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5932 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
5 | 122 | 2 | 2928 | 24 | 12.9 | 0 | 0 | 0 | 0 | 0 | 122 | 2928 | 1440 | 120.3288 | 15.3729 | 16.279 | 1414.284 | 23.8427 | -177.6407 | -27.8128 | 0 | 112.7745 | 292.7745 | 105.886 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1536 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2929 | 1 | 12.2 | 0 | 0 | 0 | 0 | 0 | 123 | 2929 | 60 | 121.3151 | 15.6762 | 16.2616 | 34.284 | 0.84243 | 167.3636 | -26.5185 | 0 | 113.2381 | 66.7619 | 106.2 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9084 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2930 | 2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 123 | 2930 | 120 | 121.3151 | 15.6762 | 16.2616 | 94.284 | 1.8424 | 152.3636 | -22.7823 | 0 | 113.2381 | 66.7619 | 106.2 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6593 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2931 | 3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 123 | 2931 | 180 | 121.3151 | 15.6762 | 16.2616 | 154.284 | 2.8424 | 137.3636 | -16.7483 | 0 | 113.2381 | 66.7619 | 106.2 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8674 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2932 | 4 | 9.2 | 0 | 0 | 0 | 0 | 0 | 123 | 2932 | 240 | 121.3151 | 15.6762 | 16.2616 | 214.284 | 3.8424 | 122.3636 | -8.9777 | 0 | 113.2381 | 66.7619 | 106.2 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9342 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2933 | 5 | 8.4 | 0 | 0 | 0 | 0 | 0 | 123 | 2933 | 300 | 121.3151 | 15.6762 | 16.2616 | 274.284 | 4.8424 | 107.3636 | 0.0070179 | 0.0070179 | 113.23 | 66.77 | 106.1893 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.91817 | 0.91817 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2934 | 6 | 8.1 | 0.56 | 2.58 | 3.14 | 2.58 | 1.29 | 123 | 2934 | 360 | 121.3151 | 15.6762 | 16.2616 | 334.284 | 5.8424 | 92.3636 | 9.7706 | 9.7706 | 102.5402 | 77.4598 | 91.7939 | 0 | 0 | 2.2022 | 2.2022 | -63.6317 | 0% | 0.99582 | 0 | 0 | 14.7851 | 14.7851 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2935 | 7 | 9.8 | 28.53 | 44.17 | 72.7 | 44.17 | 22.09 | 123 | 2935 | 420 | 121.3151 | 15.6762 | 16.2616 | 394.284 | 6.8424 | 77.3636 | 19.9463 | 19.9463 | 91.9238 | 88.0762 | 77.3551 | 18.3076 | 18.3076 | 37.7015 | 56.0091 | -1.6582 | 0% | 25.3273 | 0 | 0 | 194.1727 | 194.1727 | 0% | 11.77% | 11.77% | 80% | 9.416% | 2.3847 | 7.3186 | 6 | 14.3082 | 5.2735 | 7.369% | 7.369%
5 | 123 | 3 | 2936 | 8 | 12.7 | 132.42 | 95.28 | 227.7 | 95.28 | 47.64 | 123 | 2936 | 480 | 121.3151 | 15.6762 | 16.2616 | 454.284 | 7.8424 | 62.3636 | 30.1817 | 30.1817 | 80.6525 | 99.3475 | 62.9496 | 119.7849 | 119.7849 | 81.3266 | 201.1115 | 0.15172 | 15.17% | 90.9426 | 13.7974 | 9.6582 | 175.4009 | 175.4009 | 5.506% | 11.59% | 11.59% | 80% | 9.274% | 8.434 | 6.5691 | 6 | 50.6039 | 18.651 | 28.85% | 28.85%
5 | 123 | 3 | 2937 | 9 | 16.5 | 297.5 | 127.86 | 425.36 | 127.86 | 63.93 | 123 | 2937 | 540 | 121.3151 | 15.6762 | 16.2616 | 514.284 | 8.8424 | 47.3636 | 40.0537 | 40.0537 | 67.7216 | 112.2784 | 48.6835 | 305.2265 | 305.2265 | 109.1353 | 414.3619 | 0.50826 | 50.83% | 187.3744 | 95.2351 | 66.6645 | 191.3194 | 191.3194 | 34.84% | 11.43% | 11.43% | 85% | 9.712% | 18.1984 | 5.6761 | 5.6761 | 103.2953 | 40.2441 | 53.99% | 53.99%
5 | 123 | 3 | 2938 | 10 | 18.3 | 442.42 | 136.03 | 578.45 | 136.03 | 68.02 | 123 | 2938 | 600 | 121.3151 | 15.6762 | 16.2616 | 574.284 | 9.8424 | 32.3636 | 48.9234 | 48.9234 | 51.6619 | 128.3381 | 34.7907 | 481.9825 | 481.9825 | 116.1089 | 598.0914 | 0.60584 | 60.58% | 270.4569 | 163.8533 | 114.6973 | 196.0754 | 196.0754 | 58.5% | 11.37% | 11.37% | 90% | 10.23% | 27.678 | 5.2884 | 5.2884 | 146.3711 | 61.2074 | 74.65% | 74.65%
5 | 123 | 3 | 2939 | 11 | 20.6 | 573.14 | 136.39 | 709.53 | 136.39 | 68.2 | 123 | 2939 | 660 | 121.3151 | 15.6762 | 16.2616 | 634.284 | 10.8424 | 17.3636 | 55.7108 | 55.7108 | 30.6656 | 149.3344 | 22.0479 | 642.9725 | 642.9725 | 116.4161 | 759.3886 | 0.65462 | 65.46% | 343.3955 | 224.7928 | 157.3549 | 192.9654 | 192.9654 | 81.55% | 11.35% | 11.35% | 90% | 10.22% | 35.0799 | 4.8259 | 4.8259 | 169.2935 | 77.5761 | 87.73% | 87.73%
5 | 123 | 3 | 2940 | 12 | 23.4 | 656.31 | 154.44 | 810.75 | 154.44 | 77.22 | 123 | 2940 | 720 | 121.3151 | 15.6762 | 16.2616 | 694.284 | 11.8424 | 2.3636 | 58.836 | 58.836 | 4.4006 | 175.5994 | 14.0922 | 743.9128 | 743.9128 | 131.8228 | 875.7356 | 0.68142 | 68.14% | 396.0076 | 269.8458 | 188.892 | 287.0702 | 287.0702 | 65.8% | 11.37% | 11.37% | 95% | 10.8% | 42.7603 | 4.313 | 4.313 | 184.4244 | 94.5607 | 64.24% | 64.24%
5 | 123 | 3 | 2941 | 13 | 24.7 | 613.89 | 177.58 | 791.47 | 177.58 | 88.79 | 123 | 2941 | 780 | 121.3151 | 15.6762 | 16.2616 | 754.284 | 12.8424 | -12.6364 | 57.1697 | 57.1697 | 22.8612 | 202.8612 | 18.6635 | 692.16 | 692.16 | 151.574 | 843.734 | 0.68007 | 68.01% | 381.5365 | 259.473 | 181.6311 | 315.1298 | 315.1298 | 57.64% | 11.36% | 11.36% | 95% | 10.8% | 41.1874 | 4.0935 | 4.0935 | 168.5996 | 91.0823 | 53.5% | 53.5%
5 | 123 | 3 | 2942 | 14 | 26 | 516.31 | 197.03 | 713.34 | 197.03 | 98.52 | 123 | 2942 | 840 | 121.3151 | 15.6762 | 16.2616 | 814.284 | 13.8424 | -27.6364 | 51.3545 | 51.3545 | 45.6547 | 225.6547 | 30.5789 | 569.1328 | 569.1328 | 168.1756 | 737.3085 | 0.66594 | 66.59% | 333.4109 | 222.0317 | 155.4222 | 327.2317 | 327.2317 | 47.5% | 11.33% | 11.33% | 90% | 10.2% | 34.0018 | 3.8858 | 3.8858 | 132.1244 | 75.192 | 40.38% | 40.38%
5 | 123 | 3 | 2943 | 15 | 26.3 | 429.64 | 205 | 634.64 | 205 | 102.5 | 123 | 2943 | 900 | 121.3151 | 15.6762 | 16.2616 | 874.284 | 14.8424 | -42.6364 | 42.9971 | 42.9971 | 63.0825 | 243.0825 | 44.2464 | 451.3021 | 451.3021 | 174.9784 | 626.2806 | 0.64248 | 64.25% | 283.2041 | 181.9528 | 127.367 | 330.8427 | 330.8427 | 38.5% | 11.29% | 11.29% | 90% | 10.16% | 28.781 | 3.8396 | 3.8396 | 110.5061 | 63.6466 | 33.4% | 33.4%
5 | 123 | 3 | 2944 | 16 | 25.9 | 384.44 | 204.44 | 588.88 | 204.44 | 102.22 | 123 | 2944 | 960 | 121.3151 | 15.6762 | 16.2616 | 934.284 | 15.8424 | -57.6364 | 33.3562 | 33.3562 | 76.8151 | 256.8151 | 58.4317 | 366.0324 | 366.0324 | 174.5005 | 540.5328 | 0.61529 | 61.53% | 244.4289 | 150.3943 | 105.276 | 324.3295 | 324.3295 | 32.46% | 11.27% | 11.27% | 90% | 10.14% | 24.7876 | 3.9014 | 3.9014 | 96.7052 | 54.8156 | 29.82% | 29.82%
5 | 123 | 3 | 2945 | 17 | 26 | 362.31 | 159.25 | 521.56 | 159.25 | 79.63 | 123 | 2945 | 1020 | 121.3151 | 15.6762 | 16.2616 | 994.284 | 16.8424 | -72.6364 | 23.1831 | 23.1831 | 88.4827 | 268.4827 | 72.8077 | 272.0327 | 272.0327 | 135.9284 | 407.9611 | 0.55448 | 55.45% | 184.48 | 102.2913 | 71.6039 | 321.463 | 321.463 | 22.27% | 11.22% | 11.22% | 85% | 9.539% | 17.598 | 3.8858 | 3.8858 | 68.3822 | 38.9164 | 21.27% | 21.27%
5 | 123 | 3 | 2946 | 18 | 26.1 | 220.36 | 113.89 | 334.25 | 113.89 | 56.95 | 123 | 2946 | 1080 | 121.3151 | 15.6762 | 16.2616 | 1054.284 | 17.8424 | -87.6364 | 12.9493 | 12.9493 | 99.2173 | 279.2173 | 87.2447 | 47.2714 | 47.2714 | 97.2112 | 144.4826 | 0.10093 | 10.09% | 65.335 | 6.5946 | 4.6162 | 319.7456 | 319.7456 | 1.444% | 11.13% | 0% | 80% | 0% | 0 | 3.8703 | 3.8703 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2947 | 19 | 24.9 | 85.64 | 73.69 | 159.33 | 73.69 | 36.85 | 123 | 2947 | 1140 | 121.3151 | 15.6762 | 16.2616 | 1114.284 | 18.8424 | -102.6364 | 3.0183 | 3.0183 | 109.8157 | 289.8157 | 101.6622 | 0 | 0 | 62.8983 | 62.8983 | -0.85158 | 0% | 28.4426 | 0 | 0 | 288.7664 | 288.7664 | 0% | 11.15% | 0% | 80% | 0% | 0 | 4.0608 | 4.0608 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2948 | 20 | 22.6 | 7.97 | 25.56 | 33.53 | 25.56 | 12.78 | 123 | 2948 | 1200 | 121.3151 | 15.6762 | 16.2616 | 1174.284 | 19.8424 | -117.6364 | -6.2548 | 0 | 113.2381 | 293.2381 | 106.2 | 0 | 0 | 21.8168 | 21.8168 | -4.1958 | 0% | 9.8656 | 0 | 0 | 151.4407 | 151.4407 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4539 | 4.4539 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2949 | 21 | 19.5 | 0 | 0 | 0 | 0 | 0 | 123 | 2949 | 1260 | 121.3151 | 15.6762 | 16.2616 | 1234.284 | 20.8424 | -132.6364 | -14.4605 | 0 | 113.2381 | 293.2381 | 106.2 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.9421 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0425 | 5.0425 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2950 | 22 | 16.8 | 0 | 0 | 0 | 0 | 0 | 123 | 2950 | 1320 | 121.3151 | 15.6762 | 16.2616 | 1294.284 | 21.8424 | -147.6364 | -21.1026 | 0 | 113.2381 | 293.2381 | 106.2 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2174 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2951 | 23 | 15.3 | 0 | 0 | 0 | 0 | 0 | 123 | 2951 | 1380 | 121.3151 | 15.6762 | 16.2616 | 1354.284 | 22.8424 | -162.6364 | -25.6207 | 0 | 113.2381 | 293.2381 | 106.2 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7303 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
5 | 123 | 3 | 2952 | 24 | 14.7 | 0 | 0 | 0 | 0 | 0 | 123 | 2952 | 1440 | 121.3151 | 15.6762 | 16.2616 | 1414.284 | 23.8424 | -177.6364 | -27.5096 | 0 | 113.2381 | 293.2381 | 106.2 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8716 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2953 | 1 | 13.7 | 0 | 0 | 0 | 0 | 0 | 124 | 2953 | 60 | 122.3014 | 15.9747 | 16.2309 | 34.284 | 0.84192 | 167.3713 | -26.2254 | 0 | 113.6952 | 66.3048 | 106.509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8541 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2954 | 2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 124 | 2954 | 120 | 122.3014 | 15.9747 | 16.2309 | 94.284 | 1.8419 | 152.3713 | -22.5046 | 0 | 113.6952 | 66.3048 | 106.509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1406 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2955 | 3 | 11.1 | 0 | 0 | 0 | 0 | 0 | 124 | 2955 | 180 | 122.3014 | 15.9747 | 16.2309 | 154.284 | 2.8419 | 137.3713 | -16.4907 | 0 | 113.6952 | 66.3048 | 106.509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4272 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2956 | 4 | 10.7 | 0 | 0 | 0 | 0 | 0 | 124 | 2956 | 240 | 122.3014 | 15.9747 | 16.2309 | 214.284 | 3.8419 | 122.3713 | -8.74 | 0 | 113.6952 | 66.3048 | 106.509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0368 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2957 | 5 | 9.7 | 0 | 0 | 0 | 0 | 0 | 124 | 2957 | 300 | 122.3014 | 15.9747 | 16.2309 | 274.284 | 4.8419 | 107.3713 | 0.2281 | 0.2281 | 113.4306 | 66.5694 | 106.1621 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.012512 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2958 | 6 | 8.9 | 0.47 | 3.25 | 3.72 | 3.25 | 1.63 | 124 | 2958 | 360 | 122.3014 | 15.9747 | 16.2309 | 334.284 | 5.8419 | 92.3713 | 9.9802 | 9.9802 | 102.756 | 77.244 | 91.789 | 0 | 0 | 2.774 | 2.774 | -49.6688 | 0% | 1.2544 | 0 | 0 | 11.4513 | 11.4513 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2959 | 7 | 10.8 | 21.94 | 42.97 | 64.91 | 42.97 | 21.49 | 124 | 2959 | 420 | 122.3014 | 15.9747 | 16.2309 | 394.284 | 6.8419 | 77.3713 | 20.1508 | 20.1508 | 92.1553 | 87.8447 | 77.3716 | 13.9239 | 13.9239 | 36.6772 | 50.6011 | -1.8753 | 0% | 22.8818 | 0 | 0 | 186.8016 | 186.8016 | 0% | 11.73% | 11.73% | 80% | 9.385% | 2.1474 | 7.0535 | 6 | 12.8847 | 4.7489 | 6.898% | 6.898%
5 | 124 | 4 | 2960 | 8 | 13.3 | 119.08 | 86.19 | 205.27 | 86.19 | 43.1 | 124 | 2960 | 480 | 122.3014 | 15.9747 | 16.2309 | 454.284 | 7.8419 | 62.3713 | 30.3889 | 30.3889 | 80.9014 | 99.0986 | 62.9893 | 106.9075 | 106.9075 | 73.5678 | 180.4753 | 0.08476 | 8.476% | 81.6109 | 6.9174 | 4.8422 | 165.5333 | 165.5333 | 2.925% | 11.58% | 11.58% | 80% | 9.264% | 7.5606 | 6.4214 | 6 | 45.3638 | 16.7197 | 27.4% | 27.4%
5 | 124 | 4 | 2961 | 9 | 17.5 | 240.36 | 133.25 | 373.61 | 133.25 | 66.63 | 124 | 2961 | 540 | 122.3014 | 15.9747 | 16.2309 | 514.284 | 8.8419 | 47.3713 | 40.2733 | 40.2733 | 67.9864 | 112.0136 | 48.7521 | 245.1503 | 245.1503 | 113.736 | 358.8863 | 0.46879 | 46.88% | 162.2884 | 76.0794 | 53.2556 | 180.4413 | 180.4413 | 29.51% | 11.41% | 11.41% | 85% | 9.701% | 15.7432 | 5.4579 | 5.4579 | 85.9244 | 34.8147 | 47.62% | 47.62%
5 | 124 | 4 | 2962 | 10 | 20 | 316.58 | 159.92 | 476.5 | 159.92 | 79.96 | 124 | 2962 | 600 | 122.3014 | 15.9747 | 16.2309 | 574.284 | 9.8419 | 32.3713 | 49.1667 | 49.1667 | 51.9259 | 128.0741 | 34.9023 | 343.1552 | 343.1552 | 136.5003 | 479.6554 | 0.56475 | 56.48% | 216.9002 | 122.4944 | 85.7461 | 184.5759 | 184.5759 | 46.46% | 11.35% | 11.35% | 85% | 9.649% | 20.9291 | 4.943 | 4.943 | 103.4527 | 46.2829 | 56.05% | 56.05%
5 | 124 | 4 | 2963 | 11 | 21.5 | 454.17 | 212.5 | 666.67 | 212.5 | 106.25 | 124 | 2963 | 660 | 122.3014 | 15.9747 | 16.2309 | 634.284 | 10.8419 | 17.3713 | 55.9861 | 55.9861 | 30.8714 | 149.1286 | 22.2361 | 507.1704 | 507.1704 | 181.3801 | 688.5505 | 0.64211 | 64.21% | 311.3626 | 199.9283 | 139.9498 | 184.7307 | 184.7307 | 75.76% | 11.34% | 11.34% | 90% | 10.21% | 31.7855 | 4.6551 | 4.6551 | 147.964 | 70.2909 | 80.1% | 80.1%
5 | 124 | 4 | 2964 | 12 | 22.9 | 492.03 | 243.25 | 735.28 | 243.25 | 121.63 | 124 | 2964 | 720 | 122.3014 | 15.9747 | 16.2309 | 694.284 | 11.8419 | 2.3713 | 59.1337 | 59.1337 | 4.4467 | 175.5533 | 14.3876 | 555.2388 | 555.2388 | 207.6269 | 762.8657 | 0.66186 | 66.19% | 344.9679 | 228.3217 | 159.8252 | 174.5685 | 174.5685 | 91.55% | 11.35% | 11.35% | 90% | 10.21% | 35.2263 | 4.4006 | 4.4006 | 155.0152 | 77.8998 | 88.8% | 88.8%
5 | 124 | 4 | 2965 | 13 | 24.9 | 388.75 | 259.86 | 648.61 | 259.86 | 129.93 | 124 | 2965 | 780 | 122.3014 | 15.9747 | 16.2309 | 754.284 | 12.8419 | -12.6287 | 57.4585 | 57.4585 | 23.0013 | 203.0013 | 18.8775 | 436.3453 | 436.3453 | 221.8044 | 658.1497 | 0.64578 | 64.58% | 297.6153 | 192.1935 | 134.5355 | 302.651 | 302.651 | 44.45% | 11.31% | 11.31% | 90% | 10.18% | 30.3044 | 4.0608 | 4.0608 | 123.0586 | 67.0154 | 40.66% | 40.66%
5 | 124 | 4 | 2966 | 14 | 25.1 | 409.08 | 218.81 | 627.89 | 218.81 | 109.41 | 124 | 2966 | 840 | 122.3014 | 15.9747 | 16.2309 | 814.284 | 13.8419 | -27.6287 | 51.615 | 51.615 | 45.889 | 225.889 | 30.6961 | 448.7593 | 448.7593 | 186.766 | 635.5253 | 0.64082 | 64.08% | 287.3845 | 184.161 | 128.9127 | 310.8528 | 310.8528 | 41.47% | 11.31% | 11.31% | 90% | 10.18% | 29.2422 | 4.0283 | 4.0283 | 117.7967 | 64.6665 | 37.89% | 37.89%
5 | 124 | 4 | 2967 | 15 | 25.6 | 293.69 | 217.78 | 511.47 | 217.78 | 108.89 | 124 | 2967 | 900 | 122.3014 | 15.9747 | 16.2309 | 874.284 | 14.8419 | -42.6287 | 43.2323 | 43.2323 | 63.3345 | 243.3345 | 44.3122 | 306.8042 | 306.8042 | 185.8869 | 492.6911 | 0.59567 | 59.57% | 222.7949 | 132.7124 | 92.8987 | 305.2554 | 305.2554 | 30.43% | 11.26% | 11.26% | 85% | 9.569% | 21.3187 | 3.9484 | 3.9484 | 84.1755 | 47.1444 | 27.58% | 27.58%
5 | 124 | 4 | 2968 | 16 | 26.2 | 280.56 | 211.67 | 492.23 | 211.67 | 105.84 | 124 | 2968 | 960 | 122.3014 | 15.9747 | 16.2309 | 934.284 | 15.8419 | -57.6287 | 33.5764 | 33.5764 | 77.0568 | 257.0568 | 58.465 | 265.3262 | 265.3262 | 180.6716 | 445.9978 | 0.57671 | 57.67% | 201.6802 | 116.3119 | 81.4183 | 307.6133 | 307.6133 | 26.47% | 11.23% | 11.23% | 85% | 9.547% | 19.2536 | 3.8549 | 3.8549 | 74.2207 | 42.5776 | 24.13% | 24.13%
5 | 124 | 4 | 2969 | 17 | 25.9 | 235.83 | 186.86 | 422.69 | 186.86 | 93.43 | 124 | 2969 | 1020 | 122.3014 | 15.9747 | 16.2309 | 994.284 | 16.8419 | -72.6287 | 23.3981 | 23.3981 | 88.7083 | 268.7083 | 72.8165 | 175.4449 | 175.4449 | 159.495 | 334.9399 | 0.49945 | 49.95% | 151.4598 | 75.6471 | 52.953 | 297.1435 | 297.1435 | 17.82% | 11.2% | 11.2% | 85% | 9.521% | 14.4204 | 3.9014 | 3.9014 | 56.259 | 31.8894 | 18.93% | 18.93%
5 | 124 | 4 | 2970 | 18 | 25.2 | 102.14 | 132.78 | 234.92 | 132.78 | 66.39 | 124 | 2970 | 1080 | 122.3014 | 15.9747 | 16.2309 | 1054.284 | 17.8419 | -87.6287 | 13.1669 | 13.1669 | 99.4271 | 279.4271 | 87.2317 | 21.6561 | 21.6561 | 113.3348 | 134.9909 | 0.03733 | 3.733% | 61.0429 | 2.2787 | 1.5951 | 276.9611 | 276.9611 | 0.5759% | 11.16% | 0% | 80% | 0% | 0 | 4.0122 | 4.0122 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2971 | 19 | 23.9 | 23.97 | 82.42 | 106.39 | 82.42 | 41.21 | 124 | 2971 | 1140 | 122.3014 | 15.9747 | 16.2309 | 1114.284 | 18.8419 | -102.6287 | 3.245 | 3.245 | 110.0102 | 290.0102 | 101.6276 | 0 | 0 | 70.3499 | 70.3499 | -0.70667 | 0% | 31.8122 | 0 | 0 | 300.7135 | 300.7135 | 0% | 11.2% | 0% | 80% | 0% | 0 | 4.2272 | 4.2272 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2972 | 20 | 21.1 | 2.69 | 23.06 | 25.75 | 23.06 | 11.53 | 124 | 2972 | 1200 | 122.3014 | 15.9747 | 16.2309 | 1174.284 | 19.8419 | -117.6287 | -6.0139 | 0 | 113.6952 | 293.6952 | 106.509 | 0 | 0 | 19.6829 | 19.6829 | -4.9037 | 0% | 8.9006 | 0 | 0 | 147.589 | 147.589 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.7303 | 4.7303 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2973 | 21 | 20.1 | 0 | 0 | 0 | 0 | 0 | 124 | 2973 | 1260 | 122.3014 | 15.9747 | 16.2309 | 1234.284 | 20.8419 | -132.6287 | -14.2017 | 0 | 113.6952 | 293.6952 | 106.509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.3605 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2974 | 22 | 18.9 | 0 | 0 | 0 | 0 | 0 | 124 | 2974 | 1320 | 122.3014 | 15.9747 | 16.2309 | 1294.284 | 21.8419 | -147.6287 | -20.8252 | 0 | 113.6952 | 293.6952 | 106.509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.0132 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2975 | 23 | 17.5 | 0 | 0 | 0 | 0 | 0 | 124 | 2975 | 1380 | 122.3014 | 15.9747 | 16.2309 | 1354.284 | 22.8419 | -162.6287 | -25.3283 | 0 | 113.6952 | 293.6952 | 106.509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4522 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
5 | 124 | 4 | 2976 | 24 | 16.2 | 0 | 0 | 0 | 0 | 0 | 124 | 2976 | 1440 | 122.3014 | 15.9747 | 16.2309 | 1414.284 | 23.8419 | -177.6287 | -27.211 | 0 | 113.6952 | 293.6952 | 106.509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.7387 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2977 | 1 | 15.3 | 0 | 0 | 0 | 0 | 0 | 125 | 2977 | 60 | 123.2877 | 16.2683 | 16.187 | 34.284 | 0.84118 | 167.3823 | -25.9377 | 0 | 114.1458 | 65.8542 | 106.813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6019 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2978 | 2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 125 | 2978 | 120 | 123.2877 | 16.2683 | 16.187 | 94.284 | 1.8412 | 152.3823 | -22.2325 | 0 | 114.1458 | 65.8542 | 106.813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1304 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2979 | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 125 | 2979 | 180 | 123.2877 | 16.2683 | 16.187 | 154.284 | 2.8412 | 137.3823 | -16.2388 | 0 | 114.1458 | 65.8542 | 106.813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8113 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2980 | 4 | 13.1 | 0 | 0 | 0 | 0 | 0 | 125 | 2980 | 240 | 123.2877 | 16.2683 | 16.187 | 214.284 | 3.8412 | 122.3823 | -8.508 | 0 | 114.1458 | 65.8542 | 106.813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1829 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2981 | 5 | 12.4 | 0 | 0 | 0 | 0 | 0 | 125 | 2981 | 300 | 123.2877 | 16.2683 | 16.187 | 274.284 | 4.8412 | 107.3823 | 0.44341 | 0.44341 | 113.6305 | 66.3695 | 106.1381 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.8678 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2982 | 6 | 12 | 0.14 | 1.39 | 1.53 | 1.39 | 0.7 | 125 | 2982 | 360 | 123.2877 | 16.2683 | 16.187 | 334.284 | 5.8412 | 92.3823 | 10.184 | 10.184 | 102.971 | 77.029 | 91.7874 | -0.024697 | 0 | 1.1864 | 1.1864 | -111.1228 | 0% | 0.53651 | 0 | 0 | 5.1821 | 5.1821 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2983 | 7 | 13.1 | 10.64 | 22.58 | 33.22 | 22.58 | 11.29 | 125 | 2983 | 420 | 123.2877 | 16.2683 | 16.187 | 394.284 | 6.8412 | 77.3823 | 20.3494 | 20.3494 | 92.3861 | 87.6139 | 77.3914 | 6.6791 | 6.6791 | 19.2732 | 25.9523 | -4.2153 | 0% | 11.7356 | 0 | 0 | 168.5564 | 168.5564 | 0% | 11.65% | 11.65% | 80% | 9.317% | 1.0934 | 6.4703 | 6 | 6.5602 | 2.4179 | 3.892% | 3.892%
5 | 125 | 5 | 2984 | 8 | 14.5 | 45.47 | 63.42 | 108.89 | 63.42 | 31.71 | 125 | 2984 | 480 | 123.2877 | 16.2683 | 16.187 | 454.284 | 7.8412 | 62.3823 | 30.59 | 30.59 | 81.15 | 98.85 | 63.0324 | 40.5196 | 40.5196 | 54.1324 | 94.652 | -0.53845 | 0% | 42.8016 | 0 | 0 | 181.3777 | 181.3777 | 0% | 11.57% | 11.57% | 80% | 9.252% | 3.9601 | 6.1335 | 6 | 23.7608 | 8.7575 | 13.1% | 13.1%
5 | 125 | 5 | 2985 | 9 | 15.7 | 97.5 | 101.94 | 199.44 | 101.94 | 50.97 | 125 | 2985 | 540 | 123.2877 | 16.2683 | 16.187 | 514.284 | 8.8412 | 47.3823 | 40.4865 | 40.4865 | 68.2517 | 111.7483 | 48.8242 | 98.867 | 98.867 | 87.0112 | 185.8782 | 0.13504 | 13.5% | 84.0541 | 11.3504 | 7.9453 | 167.4009 | 167.4009 | 4.746% | 11.5% | 11.5% | 80% | 9.198% | 7.7311 | 5.8557 | 5.8557 | 45.271 | 17.0967 | 27.04% | 27.04%
5 | 125 | 5 | 2986 | 10 | 17.2 | 173.14 | 203.25 | 376.39 | 203.25 | 101.63 | 125 | 2986 | 600 | 123.2877 | 16.2683 | 16.187 | 574.284 | 9.8412 | 32.3823 | 49.4036 | 49.4036 | 52.1923 | 127.8077 | 35.017 | 186.7461 | 186.7461 | 173.4847 | 360.2308 | 0.46818 | 46.82% | 162.8964 | 76.2648 | 53.3853 | 155.3934 | 155.3934 | 34.35% | 11.42% | 11.42% | 85% | 9.707% | 15.812 | 5.5226 | 5.5226 | 87.3232 | 34.9668 | 56.19% | 56.19%
5 | 125 | 5 | 2987 | 11 | 18.8 | 207.5 | 234.08 | 441.58 | 234.08 | 117.04 | 125 | 2987 | 660 | 123.2877 | 16.2683 | 16.187 | 634.284 | 10.8412 | 17.3823 | 56.2553 | 56.2553 | 31.0823 | 148.9177 | 22.4261 | 230.6704 | 230.6704 | 199.7998 | 430.4702 | 0.53126 | 53.13% | 194.6586 | 103.4135 | 72.3894 | 154.8407 | 154.8407 | 46.75% | 11.38% | 11.38% | 85% | 9.67% | 18.8234 | 5.1847 | 5.1847 | 97.5931 | 41.6262 | 63.03% | 63.03%
5 | 125 | 5 | 2988 | 12 | 20.1 | 401.11 | 261.47 | 662.58 | 261.47 | 130.74 | 125 | 2988 | 720 | 123.2877 | 16.2683 | 16.187 | 694.284 | 11.8412 | 2.3823 | 59.4262 | 59.4262 | 4.4993 | 175.5007 | 14.679 | 450.673 | 450.673 | 223.1786 | 673.8516 | 0.63403 | 63.4% | 304.7157 | 193.1976 | 135.2383 | 157.2078 | 157.2078 | 86.03% | 11.35% | 11.35% | 90% | 10.22% | 31.1303 | 4.9233 | 4.9233 | 153.2642 | 68.8419 | 97.49% | 97.49%
5 | 125 | 5 | 2989 | 13 | 20.2 | 361.25 | 288.61 | 649.86 | 288.61 | 144.31 | 125 | 2989 | 780 | 123.2877 | 16.2683 | 16.187 | 754.284 | 12.8412 | -12.6177 | 57.7434 | 57.7434 | 23.1355 | 203.1355 | 19.088 | 403.6907 | 403.6907 | 246.344 | 650.0348 | 0.62814 | 62.81% | 293.9457 | 184.638 | 129.2466 | 155.3703 | 155.3703 | 83.19% | 11.35% | 11.35% | 90% | 10.22% | 30.0275 | 4.9037 | 4.9037 | 147.2458 | 66.4031 | 94.77% | 94.77%
5 | 125 | 5 | 2990 | 14 | 21.4 | 275.64 | 283.06 | 558.7 | 283.06 | 141.53 | 125 | 2990 | 840 | 123.2877 | 16.2683 | 16.187 | 814.284 | 13.8412 | -27.6177 | 51.8724 | 51.8724 | 46.1175 | 226.1175 | 30.8106 | 300.9485 | 300.9485 | 241.6068 | 542.5553 | 0.59814 | 59.81% | 245.3435 | 146.7503 | 102.7252 | 152.9588 | 152.9588 | 67.16% | 11.33% | 11.33% | 90% | 10.2% | 25.0225 | 4.6738 | 4.6738 | 116.9496 | 55.335 | 76.46% | 76.46%
5 | 125 | 5 | 2991 | 15 | 22.1 | 153.97 | 301.75 | 455.72 | 301.75 | 150.88 | 125 | 2991 | 900 | 123.2877 | 16.2683 | 16.187 | 874.284 | 14.8412 | -42.6177 | 43.4652 | 43.4652 | 63.5808 | 243.5808 | 44.3753 | 159.9821 | 159.9821 | 257.5597 | 417.5418 | 0.54016 | 54.02% | 188.8124 | 101.9886 | 71.392 | 147.6778 | 147.6778 | 48.34% | 11.31% | 11.31% | 85% | 9.612% | 18.148 | 4.5443 | 4.5443 | 82.4702 | 40.1327 | 55.84% | 55.84%
5 | 125 | 5 | 2992 | 16 | 22 | 330.08 | 217.58 | 547.66 | 217.58 | 108.79 | 125 | 2992 | 960 | 123.2877 | 16.2683 | 16.187 | 934.284 | 15.8412 | -57.6177 | 33.7948 | 33.7948 | 77.293 | 257.293 | 58.4955 | 310.1082 | 310.1082 | 185.7161 | 495.8244 | 0.58138 | 58.14% | 224.2118 | 130.3514 | 91.246 | 150.0541 | 150.0541 | 60.81% | 11.32% | 11.32% | 85% | 9.621% | 21.5709 | 4.5626 | 4.5626 | 98.4193 | 47.7021 | 65.59% | 65.59%
5 | 125 | 5 | 2993 | 17 | 22.1 | 220.36 | 156.75 | 377.11 | 156.75 | 78.38 | 125 | 2993 | 1020 | 123.2877 | 16.2683 | 16.187 | 994.284 | 16.8412 | -72.6177 | 23.6115 | 23.6115 | 88.9284 | 268.9284 | 72.8222 | 162.4847 | 162.4847 | 133.7945 | 296.2792 | 0.43217 | 43.22% | 133.9775 | 57.9013 | 40.5309 | 140.2423 | 140.2423 | 28.9% | 11.29% | 11.29% | 80% | 9.035% | 12.1049 | 4.5443 | 4.5443 | 55.0087 | 26.769 | 39.22% | 39.22%
5 | 125 | 5 | 2994 | 18 | 21.7 | 64.17 | 116.39 | 180.56 | 116.39 | 58.2 | 125 | 2994 | 1080 | 123.2877 | 16.2683 | 16.187 | 1054.284 | 17.8412 | -87.6177 | 13.3832 | 13.3832 | 99.6315 | 279.6315 | 87.2158 | 13.4667 | 13.4667 | 99.3451 | 112.8117 | -0.18025 | 0% | 51.0135 | 0 | 0 | 126.1255 | 126.1255 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6179 | 4.6179 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2995 | 19 | 20.5 | 48.53 | 93.81 | 142.34 | 93.81 | 46.91 | 125 | 2995 | 1140 | 123.2877 | 16.2683 | 16.187 | 1114.284 | 18.8412 | -102.6177 | 3.4701 | 3.4701 | 110.1993 | 290.1993 | 101.59 | 0 | 0 | 80.0718 | 80.0718 | -0.61546 | 0% | 36.2085 | 0 | 0 | 160.0602 | 160.0602 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8453 | 4.8453 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2996 | 20 | 18.5 | 13.53 | 35.83 | 49.36 | 35.83 | 17.92 | 125 | 2996 | 1200 | 123.2877 | 16.2683 | 16.187 | 1174.284 | 19.8412 | -117.6177 | -5.7748 | 0 | 114.1458 | 294.1458 | 106.813 | 0 | 0 | 30.5828 | 30.5828 | -3.0568 | 0% | 13.8296 | 0 | 0 | 145.7715 | 145.7715 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2997 | 21 | 17.4 | 0 | 0 | 0 | 0 | 0 | 125 | 2997 | 1260 | 123.2877 | 16.2683 | 16.187 | 1234.284 | 20.8412 | -132.6177 | -13.9454 | 0 | 114.1458 | 294.1458 | 106.813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.0404 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2998 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 125 | 2998 | 1320 | 123.2877 | 16.2683 | 16.187 | 1294.284 | 21.8412 | -147.6177 | -20.5509 | 0 | 114.1458 | 294.1458 | 106.813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6929 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 2999 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 125 | 2999 | 1380 | 123.2877 | 16.2683 | 16.187 | 1354.284 | 22.8412 | -162.6177 | -25.0399 | 0 | 114.1458 | 294.1458 | 106.813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.831 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
5 | 125 | 5 | 3000 | 24 | 13.7 | 0 | 0 | 0 | 0 | 0 | 125 | 3000 | 1440 | 123.2877 | 16.2683 | 16.187 | 1414.284 | 23.8412 | -177.6177 | -26.9172 | 0 | 114.1458 | 294.1458 | 106.813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4262 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3001 | 1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 126 | 3001 | 60 | 124.274 | 16.5569 | 16.1298 | 34.284 | 0.84023 | 167.3966 | -25.6554 | 0 | 114.5896 | 65.4104 | 107.1118 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8626 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3002 | 2 | 9.4 | 0 | 0 | 0 | 0 | 0 | 126 | 3002 | 120 | 124.274 | 16.5569 | 16.1298 | 94.284 | 1.8402 | 152.3966 | -21.9661 | 0 | 114.5896 | 65.4104 | 107.1118 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6241 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3003 | 3 | 8.8 | 0 | 0 | 0 | 0 | 0 | 126 | 3003 | 180 | 124.274 | 16.5569 | 16.1298 | 154.284 | 2.8402 | 137.3966 | -15.9926 | 0 | 114.5896 | 65.4104 | 107.1118 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0809 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3004 | 4 | 8.1 | 0 | 0 | 0 | 0 | 0 | 126 | 3004 | 240 | 124.274 | 16.5569 | 16.1298 | 214.284 | 3.8402 | 122.3966 | -8.2819 | 0 | 114.5896 | 65.4104 | 107.1118 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1477 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3005 | 5 | 7.7 | 0 | 0 | 0 | 0 | 0 | 126 | 3005 | 300 | 124.274 | 16.5569 | 16.1298 | 274.284 | 4.8402 | 107.3966 | 0.65289 | 0.65289 | 113.8295 | 66.1705 | 106.1174 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.4647 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3006 | 6 | 7.8 | 0.19 | 1.75 | 1.94 | 1.75 | 0.88 | 126 | 3006 | 360 | 124.274 | 16.5569 | 16.1298 | 334.284 | 5.8402 | 92.3966 | 10.3819 | 10.3819 | 103.185 | 76.815 | 91.7891 | -0.032917 | 0 | 1.4937 | 1.4937 | -94.6671 | 0% | 0.67546 | 0 | 0 | 1.901 | 1.901 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3007 | 7 | 8.8 | 4.72 | 28.53 | 33.25 | 28.53 | 14.27 | 126 | 3007 | 420 | 124.274 | 16.5569 | 16.1298 | 394.284 | 6.8402 | 77.3966 | 20.5419 | 20.5419 | 92.6161 | 87.3839 | 77.4145 | 2.931 | 2.931 | 24.3519 | 27.2829 | -4.3366 | 0% | 12.3373 | 0 | 0 | 166.2287 | 166.2287 | 0% | 11.83% | 11.83% | 80% | 9.462% | 1.1674 | 7.5907 | 6 | 7.0044 | 2.5816 | 4.214% | 4.214%
5 | 126 | 6 | 3008 | 8 | 11.2 | 51.11 | 70.08 | 121.19 | 70.08 | 35.04 | 126 | 3008 | 480 | 124.274 | 16.5569 | 16.1298 | 454.284 | 7.8402 | 62.3966 | 30.7848 | 30.7848 | 81.3982 | 98.6018 | 63.0787 | 45.2133 | 45.2133 | 59.817 | 105.0304 | -0.47796 | 0% | 47.4947 | 0 | 0 | 181.8278 | 181.8278 | 0% | 11.69% | 11.69% | 80% | 9.351% | 4.4411 | 6.9494 | 6 | 26.6465 | 9.8211 | 14.65% | 14.65%
5 | 126 | 6 | 3009 | 9 | 16 | 127.58 | 109.36 | 236.94 | 109.36 | 54.68 | 126 | 3009 | 540 | 124.274 | 16.5569 | 16.1298 | 514.284 | 8.8402 | 47.3966 | 40.6933 | 40.6933 | 68.5175 | 111.4825 | 48.8994 | 128.6314 | 128.6314 | 93.3446 | 221.976 | 0.24687 | 24.69% | 100.3775 | 24.7806 | 17.3464 | 153.5167 | 153.5167 | 11.3% | 11.48% | 11.48% | 80% | 9.183% | 9.218 | 5.7878 | 5.7878 | 53.352 | 20.3848 | 34.75% | 34.75%
5 | 126 | 6 | 3010 | 10 | 17.9 | 170.19 | 135.19 | 305.38 | 135.19 | 67.6 | 126 | 3010 | 600 | 124.274 | 16.5569 | 16.1298 | 574.284 | 9.8402 | 32.3966 | 49.634 | 49.634 | 52.461 | 127.539 | 35.1346 | 182.672 | 182.672 | 115.3919 | 298.0639 | 0.40338 | 40.34% | 134.7845 | 54.3699 | 38.0589 | 157.4528 | 157.4528 | 24.17% | 11.41% | 11.41% | 80% | 9.128% | 12.3031 | 5.3726 | 5.3726 | 66.0991 | 27.2072 | 41.98% | 41.98%
5 | 126 | 6 | 3011 | 11 | 18.7 | 238.69 | 198.53 | 437.22 | 198.53 | 99.27 | 126 | 3011 | 660 | 124.274 | 16.5569 | 16.1298 | 634.284 | 10.8402 | 17.3966 | 56.5184 | 56.5184 | 31.2981 | 148.7019 | 22.6174 | 264.1685 | 264.1685 | 169.456 | 433.6245 | 0.53273 | 53.27% | 196.085 | 104.46 | 73.122 | 157.9599 | 157.9599 | 46.29% | 11.38% | 11.38% | 85% | 9.671% | 18.9643 | 5.2053 | 5.2053 | 98.7144 | 41.9378 | 62.49% | 62.49%
5 | 126 | 6 | 3012 | 12 | 19.4 | 302.03 | 228.14 | 530.17 | 228.14 | 114.07 | 126 | 3012 | 720 | 124.274 | 16.5569 | 16.1298 | 694.284 | 11.8402 | 2.3966 | 59.7136 | 59.7136 | 4.5585 | 175.4415 | 14.9659 | 337.9037 | 337.9037 | 194.7297 | 532.6334 | 0.58606 | 58.61% | 240.8568 | 141.1573 | 98.8101 | 153.0601 | 153.0601 | 64.56% | 11.36% | 11.36% | 90% | 10.22% | 24.627 | 5.0626 | 5.0626 | 124.6761 | 54.4604 | 81.46% | 81.46%
5 | 126 | 6 | 3013 | 13 | 20.6 | 333.89 | 320 | 653.89 | 320 | 160 | 126 | 3013 | 780 | 124.274 | 16.5569 | 16.1298 | 754.284 | 12.8402 | -12.6034 | 58.0242 | 58.0242 | 23.2634 | 203.2634 | 19.2947 | 371.5035 | 371.5035 | 273.1371 | 644.6405 | 0.62803 | 62.8% | 291.5065 | 183.0739 | 128.1518 | 158.2723 | 158.2723 | 80.97% | 11.35% | 11.35% | 90% | 10.21% | 29.7692 | 4.8259 | 4.8259 | 143.6643 | 65.8319 | 90.77% | 90.77%
5 | 126 | 6 | 3014 | 14 | 21.3 | 387.58 | 292.03 | 679.61 | 292.03 | 146.02 | 126 | 3014 | 840 | 124.274 | 16.5569 | 16.1298 | 814.284 | 13.8402 | -27.6034 | 52.1268 | 52.1268 | 46.3401 | 226.3401 | 30.9223 | 421.2104 | 421.2104 | 249.2632 | 670.4736 | 0.63709 | 63.71% | 303.1881 | 193.1587 | 135.2111 | 159.0421 | 159.0421 | 85.02% | 11.34% | 11.34% | 90% | 10.21% | 30.9509 | 4.6926 | 4.6926 | 145.2386 | 68.4451 | 91.32% | 91.32%
5 | 126 | 6 | 3015 | 15 | 22 | 335.47 | 250.64 | 586.11 | 250.64 | 125.32 | 126 | 3015 | 900 | 124.274 | 16.5569 | 16.1298 | 874.284 | 14.8402 | -42.6034 | 43.6957 | 43.6957 | 63.8213 | 243.8213 | 44.4355 | 346.7415 | 346.7415 | 213.9346 | 560.6762 | 0.60713 | 60.71% | 253.5378 | 153.9295 | 107.7506 | 153.7169 | 153.7169 | 70.1% | 11.33% | 11.33% | 90% | 10.19% | 25.8434 | 4.5626 | 4.5626 | 117.913 | 57.1503 | 76.71% | 76.71%
5 | 126 | 6 | 3016 | 16 | 22.2 | 224.92 | 156.31 | 381.23 | 156.31 | 78.16 | 126 | 3016 | 960 | 124.274 | 16.5569 | 16.1298 | 934.284 | 15.8402 | -57.6034 | 34.0114 | 34.0114 | 77.5234 | 257.5234 | 58.523 | 209.9609 | 209.9609 | 133.4189 | 343.3799 | 0.48381 | 48.38% | 155.2764 | 75.1238 | 52.5867 | 143.1093 | 143.1093 | 36.75% | 11.3% | 11.3% | 85% | 9.602% | 14.91 | 4.5261 | 4.5261 | 67.4842 | 32.9721 | 47.16% | 47.16%
5 | 126 | 6 | 3017 | 17 | 21.8 | 145.47 | 124.08 | 269.55 | 124.08 | 62.04 | 126 | 3017 | 1020 | 124.274 | 16.5569 | 16.1298 | 994.284 | 16.8402 | -72.6034 | 23.8234 | 23.8234 | 89.1429 | 269.1429 | 72.825 | 106.3477 | 106.3477 | 105.9089 | 212.2566 | 0.28191 | 28.19% | 95.9824 | 27.0582 | 18.9408 | 134.8438 | 134.8438 | 14.05% | 11.29% | 11.29% | 80% | 9.035% | 8.6721 | 4.5994 | 4.5994 | 39.8861 | 19.1775 | 29.58% | 29.58%
5 | 126 | 6 | 3018 | 18 | 21.4 | 99.44 | 173.25 | 272.69 | 173.25 | 86.63 | 126 | 3018 | 1080 | 124.274 | 16.5569 | 16.1298 | 1054.284 | 17.8402 | -87.6034 | 13.5979 | 13.5979 | 99.8303 | 279.8303 | 87.1969 | 20.6844 | 20.6844 | 147.8781 | 168.5625 | 0.1414 | 14.14% | 76.224 | 10.7782 | 7.5447 | 130.7519 | 130.7519 | 5.77% | 11.3% | 0% | 80% | 0% | 0 | 4.6738 | 4.6738 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3019 | 19 | 19.1 | 10 | 72.97 | 82.97 | 72.97 | 36.49 | 126 | 3019 | 1140 | 124.274 | 16.5569 | 16.1298 | 1114.284 | 18.8402 | -102.6034 | 3.6937 | 3.6937 | 110.3827 | 290.3827 | 101.5494 | 0 | 0 | 62.2838 | 62.2838 | -1.0704 | 0% | 28.1647 | 0 | 0 | 155.1037 | 155.1037 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1233 | 5.1233 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3020 | 20 | 17.8 | 8.33 | 22.69 | 31.02 | 22.69 | 11.35 | 126 | 3020 | 1200 | 124.274 | 16.5569 | 16.1298 | 1174.284 | 19.8402 | -117.6034 | -5.5377 | 0 | 114.5896 | 294.5896 | 107.1118 | 0 | 0 | 19.3671 | 19.3671 | -5.3731 | 0% | 8.7578 | 0 | 0 | 144.5164 | 144.5164 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3021 | 21 | 16.5 | 0 | 1.67 | 1.67 | 1.67 | 0.84 | 126 | 3021 | 1260 | 124.274 | 16.5569 | 16.1298 | 1234.284 | 20.8402 | -132.6034 | -13.6916 | 0 | 114.5896 | 294.5896 | 107.1118 | 0 | 0 | 1.4254 | 1.4254 | -85.1649 | 0% | 0.64458 | 0 | 0 | -7.1198 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3022 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 126 | 3022 | 1320 | 124.274 | 16.5569 | 16.1298 | 1294.284 | 21.8402 | -147.6034 | -20.28 | 0 | 114.5896 | 294.5896 | 107.1118 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9202 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3023 | 23 | 14.1 | 0 | 0 | 0 | 0 | 0 | 126 | 3023 | 1380 | 124.274 | 16.5569 | 16.1298 | 1354.284 | 22.8402 | -162.6034 | -24.7556 | 0 | 114.5896 | 294.5896 | 107.1118 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8342 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
5 | 126 | 6 | 3024 | 24 | 12.7 | 0 | 0 | 0 | 0 | 0 | 126 | 3024 | 1440 | 124.274 | 16.5569 | 16.1298 | 1414.284 | 23.8402 | -177.6034 | -26.6283 | 0 | 114.5896 | 294.5896 | 107.1118 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5102 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3025 | 1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 127 | 3025 | 60 | 125.2603 | 16.8404 | 16.0594 | 34.284 | 0.83906 | 167.4142 | -25.3786 | 0 | 115.0264 | 64.9736 | 107.4055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7662 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3026 | 2 | 8.9 | 0 | 0 | 0 | 0 | 0 | 127 | 3026 | 120 | 125.2603 | 16.8404 | 16.0594 | 94.284 | 1.8391 | 152.4142 | -21.7054 | 0 | 115.0264 | 64.9736 | 107.4055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.63 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3027 | 3 | 8.1 | 0 | 0 | 0 | 0 | 0 | 127 | 3027 | 180 | 125.2603 | 16.8404 | 16.0594 | 154.284 | 2.8391 | 137.4142 | -15.7523 | 0 | 115.0264 | 64.9736 | 107.4055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4269 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3028 | 4 | 7.2 | 0 | 0 | 0 | 0 | 0 | 127 | 3028 | 240 | 125.2603 | 16.8404 | 16.0594 | 214.284 | 3.8391 | 122.4142 | -8.0616 | 0 | 115.0264 | 64.9736 | 107.4055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7985 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3029 | 5 | 6.8 | 0 | 0 | 0 | 0 | 0 | 127 | 3029 | 300 | 125.2603 | 16.8404 | 16.0594 | 274.284 | 4.8391 | 107.4142 | 0.85646 | 0.85646 | 114.0276 | 65.9724 | 106.1001 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6302 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3030 | 6 | 6.5 | 0.19 | 3.33 | 3.52 | 3.33 | 1.67 | 127 | 3030 | 360 | 125.2603 | 16.8404 | 16.0594 | 334.284 | 5.8391 | 92.4142 | 10.5738 | 10.5738 | 103.3979 | 76.6021 | 91.7941 | -0.032417 | 0 | 2.8423 | 2.8423 | -50.4539 | 0% | 1.2853 | 0 | 0 | 0.53254 | 0.53254 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3031 | 7 | 7.5 | 7.31 | 35.92 | 43.23 | 35.92 | 17.96 | 127 | 3031 | 420 | 125.2603 | 16.8404 | 16.0594 | 394.284 | 6.8391 | 77.4142 | 20.7283 | 20.7283 | 92.845 | 87.155 | 77.4409 | 4.491 | 4.491 | 30.6596 | 35.1506 | -3.2732 | 0% | 15.8951 | 0 | 0 | 166.0048 | 166.0048 | 0% | 11.88% | 11.88% | 80% | 9.502% | 1.5104 | 7.9549 | 6 | 9.0624 | 3.3401 | 5.459% | 5.459%
5 | 127 | 7 | 3032 | 8 | 10.9 | 44.81 | 94.81 | 139.62 | 94.81 | 47.41 | 127 | 3032 | 480 | 125.2603 | 16.8404 | 16.0594 | 454.284 | 7.8391 | 62.4142 | 30.9733 | 30.9733 | 81.6457 | 98.3543 | 63.1283 | 39.3554 | 39.3554 | 80.9254 | 120.2808 | -0.32121 | 0% | 54.391 | 0 | 0 | 183.5675 | 183.5675 | 0% | 11.69% | 11.69% | 80% | 9.354% | 5.0876 | 7.0274 | 6 | 30.5256 | 11.2508 | 16.63% | 16.63%
5 | 127 | 7 | 3033 | 9 | 14.8 | 97.97 | 118.53 | 216.5 | 118.53 | 59.27 | 127 | 3033 | 540 | 125.2603 | 16.8404 | 16.0594 | 514.284 | 8.8391 | 47.4142 | 40.8936 | 40.8936 | 68.7835 | 111.2165 | 48.9778 | 98.2237 | 98.2237 | 101.1717 | 199.3954 | 0.17016 | 17.02% | 90.1666 | 15.3432 | 10.7402 | 152.0787 | 152.0787 | 7.062% | 11.52% | 11.52% | 80% | 9.219% | 8.3125 | 6.0631 | 6 | 49.8749 | 18.3823 | 32.8% | 32.8%
5 | 127 | 7 | 3034 | 10 | 16.9 | 180.92 | 138.25 | 319.17 | 138.25 | 69.13 | 127 | 3034 | 600 | 125.2603 | 16.8404 | 16.0594 | 574.284 | 9.8391 | 32.4142 | 49.8577 | 49.8577 | 52.7317 | 127.2683 | 35.2549 | 193.2613 | 193.2613 | 118.0038 | 311.2651 | 0.41319 | 41.32% | 140.7541 | 58.1584 | 40.7109 | 157.9146 | 157.9146 | 25.78% | 11.44% | 11.44% | 85% | 9.72% | 13.6813 | 5.588 | 5.588 | 76.4507 | 30.2551 | 48.41% | 48.41%
5 | 127 | 7 | 3035 | 11 | 19.2 | 391.39 | 162.14 | 553.53 | 162.14 | 81.07 | 127 | 3035 | 660 | 125.2603 | 16.8404 | 16.0594 | 634.284 | 10.8391 | 17.4142 | 56.7752 | 56.7752 | 31.5187 | 148.4813 | 22.8099 | 431.2852 | 431.2852 | 138.3951 | 569.6804 | 0.59946 | 59.95% | 257.6095 | 154.4265 | 108.0985 | 164.8174 | 164.8174 | 65.59% | 11.36% | 11.36% | 90% | 10.23% | 26.3429 | 5.103 | 5.103 | 134.428 | 58.2551 | 81.56% | 81.56%
5 | 127 | 7 | 3036 | 12 | 20.2 | 381.94 | 224.17 | 606.11 | 224.17 | 112.09 | 127 | 3036 | 720 | 125.2603 | 16.8404 | 16.0594 | 694.284 | 11.8391 | 2.4142 | 59.9957 | 59.9957 | 4.6243 | 175.3757 | 15.2485 | 425.5182 | 425.5182 | 191.3411 | 616.8593 | 0.61868 | 61.87% | 278.9438 | 172.5764 | 120.8035 | 158.3307 | 158.3307 | 76.3% | 11.35% | 11.35% | 90% | 10.21% | 28.4941 | 4.9037 | 4.9037 | 139.7264 | 63.0121 | 88.25% | 88.25%
5 | 127 | 7 | 3037 | 13 | 21 | 344.36 | 210.47 | 554.83 | 210.47 | 105.24 | 127 | 3037 | 780 | 125.2603 | 16.8404 | 16.0594 | 754.284 | 12.8391 | -12.5858 | 58.3009 | 58.3009 | 23.3849 | 203.3849 | 19.4976 | 381.5298 | 381.5298 | 179.6474 | 561.1772 | 0.60342 | 60.34% | 253.7643 | 153.1254 | 107.1878 | 155.9312 | 155.9312 | 68.74% | 11.34% | 11.34% | 90% | 10.2% | 25.8966 | 4.7493 | 4.7493 | 122.9907 | 57.268 | 78.87% | 78.87%
5 | 127 | 7 | 3038 | 14 | 21.9 | 422.78 | 191.47 | 614.25 | 191.47 | 95.74 | 127 | 3038 | 840 | 125.2603 | 16.8404 | 16.0594 | 814.284 | 13.8391 | -27.5858 | 52.378 | 52.378 | 46.5565 | 226.5565 | 31.0309 | 457.3865 | 457.3865 | 163.4299 | 620.8163 | 0.62585 | 62.58% | 280.7331 | 175.6962 | 122.9874 | 159.2649 | 159.2649 | 77.22% | 11.33% | 11.33% | 90% | 10.2% | 28.6346 | 4.581 | 4.581 | 131.174 | 63.3229 | 82.36% | 82.36%
5 | 127 | 7 | 3039 | 15 | 22.1 | 416.19 | 193.61 | 609.8 | 193.61 | 96.81 | 127 | 3039 | 900 | 125.2603 | 16.8404 | 16.0594 | 874.284 | 14.8391 | -42.5858 | 43.9238 | 43.9238 | 64.0557 | 244.0557 | 44.4927 | 427.9718 | 427.9718 | 165.2565 | 593.2283 | 0.6183 | 61.83% | 268.2578 | 165.8627 | 116.1039 | 157.9976 | 157.9976 | 73.48% | 11.33% | 11.33% | 90% | 10.2% | 27.3497 | 4.5443 | 4.5443 | 124.2857 | 60.4814 | 78.66% | 78.66%
5 | 127 | 7 | 3040 | 16 | 22.8 | 396.39 | 143.25 | 539.64 | 143.25 | 71.63 | 127 | 3040 | 960 | 125.2603 | 16.8404 | 16.0594 | 934.284 | 15.8391 | -57.5858 | 34.2261 | 34.2261 | 77.748 | 257.748 | 58.5476 | 367.7278 | 367.7278 | 122.2715 | 489.9993 | 0.58227 | 58.23% | 221.5777 | 129.0182 | 90.3127 | 154.9928 | 154.9928 | 58.27% | 11.3% | 11.3% | 85% | 9.609% | 21.2906 | 4.4183 | 4.4183 | 94.0677 | 47.0822 | 60.69% | 60.69%
5 | 127 | 7 | 3041 | 17 | 21.7 | 324.81 | 97.5 | 422.31 | 97.5 | 48.75 | 127 | 3041 | 1020 | 125.2603 | 16.8404 | 16.0594 | 994.284 | 16.8391 | -72.5858 | 24.0337 | 24.0337 | 89.3517 | 269.3517 | 72.8249 | 235.5026 | 235.5026 | 83.2215 | 318.724 | 0.45563 | 45.56% | 144.127 | 65.668 | 45.9676 | 146.0301 | 146.0301 | 31.48% | 11.31% | 11.31% | 85% | 9.611% | 13.852 | 4.6179 | 4.6179 | 63.9667 | 30.6324 | 43.8% | 43.8%
5 | 127 | 7 | 3042 | 18 | 21.8 | 218.61 | 74.25 | 292.86 | 74.25 | 37.13 | 127 | 3042 | 1080 | 125.2603 | 16.8404 | 16.0594 | 1054.284 | 17.8391 | -87.5858 | 13.811 | 13.811 | 100.0235 | 280.0235 | 87.175 | 45.1335 | 45.1335 | 63.3763 | 108.5099 | -0.21727 | 0% | 49.0682 | 0 | 0 | 136.2395 | 136.2395 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.5994 | 4.5994 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3043 | 19 | 21.3 | 119.25 | 55.08 | 174.33 | 55.08 | 27.54 | 127 | 3043 | 1140 | 125.2603 | 16.8404 | 16.0594 | 1114.284 | 18.8391 | -102.5858 | 3.9155 | 3.9155 | 110.5605 | 290.5605 | 101.5059 | 0 | 0 | 47.0137 | 47.0137 | -1.5763 | 0% | 21.2596 | 0 | 0 | 124.8806 | 124.8806 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.6926 | 4.6926 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3044 | 20 | 19.3 | 24.17 | 24.72 | 48.89 | 24.72 | 12.36 | 127 | 3044 | 1200 | 125.2603 | 16.8404 | 16.0594 | 1174.284 | 19.8391 | -117.5858 | -5.3027 | 0 | 115.0264 | 295.0264 | 107.4055 | 0 | 0 | 21.0998 | 21.0998 | -4.708 | 0% | 9.5413 | 0 | 0 | 149.336 | 149.336 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0828 | 5.0828 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3045 | 21 | 18 | 0 | 0 | 0 | 0 | 0 | 127 | 3045 | 1260 | 125.2603 | 16.8404 | 16.0594 | 1234.284 | 20.8391 | -132.5858 | -13.4404 | 0 | 115.0264 | 295.0264 | 107.4055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7299 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3046 | 22 | 15.1 | 0 | 0 | 0 | 0 | 0 | 127 | 3046 | 1320 | 125.2603 | 16.8404 | 16.0594 | 1294.284 | 21.8391 | -147.5858 | -20.0124 | 0 | 115.0264 | 295.0264 | 107.4055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.87 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3047 | 23 | 12.6 | 0 | 0 | 0 | 0 | 0 | 127 | 3047 | 1380 | 125.2603 | 16.8404 | 16.0594 | 1354.284 | 22.8391 | -162.5858 | -24.4756 | 0 | 115.0264 | 295.0264 | 107.4055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2578 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
5 | 127 | 7 | 3048 | 24 | 12.1 | 0 | 0 | 0 | 0 | 0 | 127 | 3048 | 1440 | 125.2603 | 16.8404 | 16.0594 | 1414.284 | 23.8391 | -177.5858 | -26.3444 | 0 | 115.0264 | 295.0264 | 107.4055 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5976 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3049 | 1 | 10.7 | 0 | 0 | 0 | 0 | 0 | 128 | 3049 | 60 | 126.2466 | 17.1188 | 15.9757 | 34.284 | 0.83766 | 167.4351 | -25.1073 | 0 | 115.4562 | 64.5438 | 107.6938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9036 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3050 | 2 | 9.7 | 0 | 0 | 0 | 0 | 0 | 128 | 3050 | 120 | 126.2466 | 17.1188 | 15.9757 | 94.284 | 1.8377 | 152.4351 | -21.4505 | 0 | 115.4562 | 64.5438 | 107.6938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.478 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3051 | 3 | 9.1 | 0 | 0 | 0 | 0 | 0 | 128 | 3051 | 180 | 126.2466 | 17.1188 | 15.9757 | 154.284 | 2.8377 | 137.4351 | -15.5179 | 0 | 115.4562 | 64.5438 | 107.6938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4427 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3052 | 4 | 8.1 | 0 | 0 | 0 | 0 | 0 | 128 | 3052 | 240 | 126.2466 | 17.1188 | 15.9757 | 214.284 | 3.8377 | 122.4351 | -7.8473 | 0 | 115.4562 | 64.5438 | 107.6938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9667 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3053 | 5 | 7.2 | 0 | 0 | 0 | 0 | 0 | 128 | 3053 | 300 | 126.2466 | 17.1188 | 15.9757 | 274.284 | 4.8377 | 107.4351 | 1.0541 | 1.0541 | 114.2247 | 65.7753 | 106.086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.6902 | 5.6902 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3054 | 6 | 6.9 | 0.75 | 4.92 | 5.67 | 4.92 | 2.46 | 128 | 3054 | 360 | 126.2466 | 17.1188 | 15.9757 | 334.284 | 5.8377 | 92.4351 | 10.7597 | 10.7597 | 103.6097 | 76.3903 | 91.8024 | -0.12636 | 0 | 4.1995 | 4.1995 | -33.6622 | 0% | 1.899 | 0 | 0 | 22.6349 | 22.6349 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3055 | 7 | 8.3 | 48.69 | 38.33 | 87.02 | 38.33 | 19.17 | 128 | 3055 | 420 | 126.2466 | 17.1188 | 15.9757 | 394.284 | 6.8377 | 77.4351 | 20.9086 | 20.9086 | 93.0729 | 86.9271 | 77.4706 | 29.5979 | 29.5979 | 32.7167 | 62.3146 | -1.4656 | 0% | 28.1787 | 0 | 0 | 207.2291 | 207.2291 | 0% | 11.83% | 11.83% | 80% | 9.461% | 2.6661 | 7.7294 | 6 | 15.9965 | 5.8958 | 7.719% | 7.719%
5 | 128 | 8 | 3056 | 8 | 13.7 | 191.03 | 85.75 | 276.78 | 85.75 | 42.88 | 128 | 3056 | 480 | 126.2466 | 17.1188 | 15.9757 | 454.284 | 7.8377 | 62.4351 | 31.1555 | 31.1555 | 81.8924 | 98.1076 | 63.1811 | 166.5898 | 166.5898 | 73.1922 | 239.782 | 0.26647 | 26.65% | 108.4294 | 28.8933 | 20.2253 | 195.8052 | 195.8052 | 10.33% | 11.55% | 11.55% | 80% | 9.237% | 10.0155 | 6.3243 | 6 | 60.0931 | 22.1484 | 30.69% | 30.69%
5 | 128 | 8 | 3057 | 9 | 16.2 | 347.31 | 96.86 | 444.17 | 96.86 | 48.43 | 128 | 3057 | 540 | 126.2466 | 17.1188 | 15.9757 | 514.284 | 8.8377 | 47.4351 | 41.0873 | 41.0873 | 69.0496 | 110.9504 | 49.0592 | 346.2905 | 346.2905 | 82.6752 | 428.9657 | 0.51676 | 51.68% | 193.9783 | 100.2393 | 70.1675 | 207.7846 | 207.7846 | 33.77% | 11.43% | 11.43% | 85% | 9.715% | 18.8452 | 5.7429 | 5.7429 | 108.2262 | 41.6745 | 52.09% | 52.09%
5 | 128 | 8 | 3058 | 10 | 19.1 | 481.31 | 117.31 | 598.62 | 117.31 | 58.66 | 128 | 3058 | 600 | 126.2466 | 17.1188 | 15.9757 | 574.284 | 9.8377 | 32.4351 | 50.0749 | 50.0749 | 53.0042 | 126.9958 | 35.3778 | 511.7299 | 511.7299 | 100.1303 | 611.8602 | 0.6132 | 61.32% | 276.6832 | 169.6617 | 118.7632 | 212.3643 | 212.3643 | 55.92% | 11.36% | 11.36% | 90% | 10.23% | 28.2914 | 5.1233 | 5.1233 | 144.9455 | 62.5638 | 68.25% | 68.25%
5 | 128 | 8 | 3059 | 11 | 20.2 | 447.42 | 206.86 | 654.28 | 206.86 | 103.43 | 128 | 3059 | 660 | 126.2466 | 17.1188 | 15.9757 | 634.284 | 10.8377 | 17.4351 | 57.0257 | 57.0257 | 31.744 | 148.256 | 23.0032 | 490.9231 | 490.9231 | 176.5661 | 667.4891 | 0.63273 | 63.27% | 301.8386 | 190.9838 | 133.6887 | 201.7408 | 201.7408 | 66.27% | 11.35% | 11.35% | 90% | 10.22% | 30.8343 | 4.9037 | 4.9037 | 151.2021 | 68.1873 | 74.95% | 74.95%
5 | 128 | 8 | 3060 | 12 | 21 | 420.47 | 259.72 | 680.19 | 259.72 | 129.86 | 128 | 3060 | 720 | 126.2466 | 17.1188 | 15.9757 | 694.284 | 11.8377 | 2.4351 | 60.2724 | 60.2724 | 4.6969 | 175.3031 | 15.5265 | 466.5237 | 466.5237 | 221.6849 | 688.2086 | 0.64044 | 64.04% | 311.2079 | 199.3101 | 139.5171 | 183.5267 | 183.5267 | 76.02% | 11.35% | 11.35% | 90% | 10.21% | 31.7783 | 4.7493 | 4.7493 | 150.9245 | 70.2748 | 82.24% | 82.24%
5 | 128 | 8 | 3061 | 13 | 22.3 | 347.36 | 335.42 | 682.78 | 335.42 | 167.71 | 128 | 3061 | 780 | 126.2466 | 17.1188 | 15.9757 | 754.284 | 12.8377 | -12.5649 | 58.5734 | 58.5734 | 23.4997 | 203.4997 | 19.6964 | 383.257 | 383.257 | 286.2989 | 669.5558 | 0.64011 | 64.01% | 302.7732 | 193.8094 | 135.6666 | 181.7146 | 181.7146 | 74.66% | 11.34% | 11.34% | 90% | 10.2% | 30.8888 | 4.508 | 4.508 | 139.2452 | 68.3077 | 76.63% | 76.63%
5 | 128 | 8 | 3062 | 14 | 23.6 | 218.61 | 323.47 | 542.08 | 323.47 | 161.74 | 128 | 3062 | 840 | 126.2466 | 17.1188 | 15.9757 | 814.284 | 13.8377 | -27.5649 | 52.6261 | 52.6261 | 46.7666 | 226.7666 | 31.1365 | 235.4583 | 235.4583 | 276.0989 | 511.5572 | 0.59499 | 59.5% | 231.3262 | 137.6367 | 96.3457 | 311.0736 | 311.0736 | 30.97% | 11.29% | 11.29% | 90% | 10.17% | 23.5152 | 4.2784 | 4.2784 | 100.6085 | 52.0018 | 32.34% | 32.34%
5 | 128 | 8 | 3063 | 15 | 24.3 | 455 | 214.53 | 669.53 | 214.53 | 107.27 | 128 | 3063 | 900 | 126.2466 | 17.1188 | 15.9757 | 874.284 | 14.8377 | -42.5649 | 44.1496 | 44.1496 | 64.284 | 244.284 | 44.547 | 465.5443 | 465.5443 | 183.1128 | 648.6571 | 0.64148 | 64.15% | 293.3227 | 188.1619 | 131.7133 | 325.5178 | 325.5178 | 40.46% | 11.32% | 11.32% | 90% | 10.18% | 29.8737 | 4.1598 | 4.1598 | 124.2673 | 66.063 | 38.18% | 38.18%
5 | 128 | 8 | 3064 | 16 | 23.6 | 462.78 | 163.25 | 626.03 | 163.25 | 81.63 | 128 | 3064 | 960 | 126.2466 | 17.1188 | 15.9757 | 934.284 | 15.8377 | -57.5649 | 34.4389 | 34.4389 | 77.9667 | 257.9667 | 58.5692 | 426.7259 | 426.7259 | 139.3426 | 566.0685 | 0.61512 | 61.51% | 255.9762 | 157.4553 | 110.2187 | 316.9351 | 316.9351 | 34.78% | 11.31% | 11.31% | 90% | 10.18% | 26.0459 | 4.2784 | 4.2784 | 111.4357 | 57.5981 | 35.16% | 35.16%
5 | 128 | 8 | 3065 | 17 | 24.1 | 352.58 | 144.25 | 496.83 | 144.25 | 72.13 | 128 | 3065 | 1020 | 126.2466 | 17.1188 | 15.9757 | 994.284 | 16.8377 | -72.5649 | 24.2424 | 24.2424 | 89.5548 | 269.5548 | 72.8218 | 253.6132 | 253.6132 | 123.1251 | 376.7383 | 0.52305 | 52.3% | 170.361 | 89.1067 | 62.3747 | 315.4018 | 315.4018 | 19.78% | 11.26% | 11.26% | 85% | 9.568% | 16.3003 | 4.1933 | 4.1933 | 68.3521 | 36.0466 | 21.67% | 21.67%
5 | 128 | 8 | 3066 | 18 | 23.9 | 188.61 | 70.47 | 259.08 | 70.47 | 35.24 | 128 | 3066 | 1080 | 126.2466 | 17.1188 | 15.9757 | 1054.284 | 17.8377 | -87.5649 | 14.0226 | 14.0226 | 100.2111 | 280.2111 | 87.1502 | 38.7007 | 38.7007 | 60.1499 | 98.8506 | -0.27111 | 0% | 44.7002 | 0 | 0 | 296.4955 | 296.4955 | 0% | 11.2% | 0% | 80% | 0% | 0 | 4.2272 | 4.2272 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3067 | 19 | 23 | 119.92 | 67.69 | 187.61 | 67.69 | 33.85 | 128 | 3067 | 1140 | 126.2466 | 17.1188 | 15.9757 | 1114.284 | 18.8377 | -102.5649 | 4.1355 | 4.1355 | 110.7326 | 290.7326 | 101.4595 | 0 | 0 | 57.777 | 57.777 | -1.069 | 0% | 26.1268 | 0 | 0 | 133.1258 | 133.1258 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.3829 | 4.3829 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3068 | 20 | 20.8 | 23.42 | 23.06 | 46.48 | 23.06 | 11.53 | 128 | 3068 | 1200 | 126.2466 | 17.1188 | 15.9757 | 1174.284 | 19.8377 | -117.5649 | -5.0698 | 0 | 115.4562 | 295.4562 | 107.6938 | 0 | 0 | 19.6829 | 19.6829 | -4.9371 | 0% | 8.9006 | 0 | 0 | 152.7588 | 152.7588 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.7875 | 4.7875 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3069 | 21 | 19.6 | 0 | 0 | 0 | 0 | 0 | 128 | 3069 | 1260 | 126.2466 | 17.1188 | 15.9757 | 1234.284 | 20.8377 | -132.5649 | -13.192 | 0 | 115.4562 | 295.4562 | 107.6938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.7092 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0224 | 5.0224 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3070 | 22 | 18.1 | 0 | 0 | 0 | 0 | 0 | 128 | 3070 | 1320 | 126.2466 | 17.1188 | 15.9757 | 1294.284 | 21.8377 | -147.5649 | -19.7484 | 0 | 115.4562 | 295.4562 | 107.6938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.4751 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3071 | 23 | 16.5 | 0 | 0 | 0 | 0 | 0 | 128 | 3071 | 1380 | 126.2466 | 17.1188 | 15.9757 | 1354.284 | 22.8377 | -162.5649 | -24.1999 | 0 | 115.4562 | 295.4562 | 107.6938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9638 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
5 | 128 | 8 | 3072 | 24 | 11.9 | 0 | 0 | 0 | 0 | 0 | 128 | 3072 | 1440 | 126.2466 | 17.1188 | 15.9757 | 1414.284 | 23.8377 | -177.5649 | -26.0655 | 0 | 115.4562 | 295.4562 | 107.6938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0245 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3073 | 1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 129 | 3073 | 60 | 127.2329 | 17.3918 | 15.879 | 34.284 | 0.83605 | 167.4592 | -24.8417 | 0 | 115.8787 | 64.1213 | 107.9766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2364 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3074 | 2 | 13.9 | 0 | 0 | 0 | 0 | 0 | 129 | 3074 | 120 | 127.2329 | 17.3918 | 15.879 | 94.284 | 1.8361 | 152.4592 | -21.2015 | 0 | 115.8787 | 64.1213 | 107.9766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9608 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3075 | 3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 129 | 3075 | 180 | 127.2329 | 17.3918 | 15.879 | 154.284 | 2.8361 | 137.4592 | -15.2895 | 0 | 115.8787 | 64.1213 | 107.9766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.228 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3076 | 4 | 12.7 | 0 | 0 | 0 | 0 | 0 | 129 | 3076 | 240 | 127.2329 | 17.3918 | 15.879 | 214.284 | 3.8361 | 122.4592 | -7.6389 | 0 | 115.8787 | 64.1213 | 107.9766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.99 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3077 | 5 | 9.9 | 0 | 0 | 0 | 0 | 0 | 129 | 3077 | 300 | 127.2329 | 17.3918 | 15.879 | 274.284 | 4.8361 | 107.4592 | 1.2457 | 1.2457 | 114.4206 | 65.5794 | 106.0752 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.6991 | 3.6991 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3078 | 6 | 7.4 | 0.75 | 5.75 | 6.5 | 5.75 | 2.88 | 129 | 3078 | 360 | 127.2329 | 17.3918 | 15.879 | 334.284 | 5.8361 | 92.4592 | 10.9395 | 10.9395 | 103.8203 | 76.1797 | 91.8139 | -0.1251 | 0 | 4.9079 | 4.9079 | -28.4453 | 0% | 2.2194 | 0 | 0 | 14.4329 | 14.4329 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3079 | 7 | 9.3 | 25.64 | 44.36 | 70 | 44.36 | 22.18 | 129 | 3079 | 420 | 127.2329 | 17.3918 | 15.879 | 394.284 | 6.8361 | 77.4592 | 21.0827 | 21.0827 | 93.2996 | 86.7004 | 77.5034 | 15.4234 | 15.4234 | 37.8636 | 53.287 | -1.8059 | 0% | 24.0964 | 0 | 0 | 192.9106 | 192.9106 | 0% | 11.79% | 11.79% | 80% | 9.433% | 2.273 | 7.4538 | 6 | 13.6383 | 5.0266 | 7.07% | 7.07%
5 | 129 | 9 | 3080 | 8 | 14.4 | 92.86 | 95.64 | 188.5 | 95.64 | 47.82 | 129 | 3080 | 480 | 127.2329 | 17.3918 | 15.879 | 454.284 | 7.8361 | 62.4592 | 31.3314 | 31.3314 | 82.1383 | 97.8617 | 63.2369 | 80.4156 | 80.4156 | 81.6338 | 162.0494 | 0.018479 | 1.848% | 73.2788 | 1.3541 | 0.94789 | 175.5284 | 175.5284 | 0.54% | 11.55% | 11.55% | 80% | 9.239% | 6.7701 | 6.1571 | 6 | 40.6204 | 14.9714 | 23.14% | 23.14%
5 | 129 | 9 | 3081 | 9 | 17.4 | 220.19 | 151.58 | 371.77 | 151.58 | 75.79 | 129 | 3081 | 540 | 127.2329 | 17.3918 | 15.879 | 514.284 | 8.8361 | 47.4592 | 41.2745 | 41.2745 | 69.3155 | 110.6845 | 49.1434 | 218.3544 | 218.3544 | 129.3816 | 347.7361 | 0.4574 | 45.74% | 157.2462 | 71.9244 | 50.3471 | 189.7031 | 189.7031 | 26.54% | 11.42% | 11.42% | 85% | 9.704% | 15.2594 | 5.4794 | 5.4794 | 83.6123 | 33.7449 | 44.08% | 44.08%
5 | 129 | 9 | 3082 | 10 | 19.7 | 425.92 | 137.86 | 563.78 | 137.86 | 68.93 | 129 | 3082 | 600 | 127.2329 | 17.3918 | 15.879 | 574.284 | 9.8361 | 32.4592 | 50.2853 | 50.2853 | 53.2784 | 126.7216 | 35.503 | 450.7529 | 450.7529 | 117.6709 | 568.4238 | 0.60095 | 60.1% | 257.0412 | 154.4689 | 108.1283 | 197.2326 | 197.2326 | 54.82% | 11.36% | 11.36% | 90% | 10.22% | 26.2702 | 5.0025 | 5.0025 | 131.4162 | 58.0943 | 66.63% | 66.63%
5 | 129 | 9 | 3083 | 11 | 21 | 567.86 | 146.11 | 713.97 | 146.11 | 73.06 | 129 | 3083 | 660 | 127.2329 | 17.3918 | 15.879 | 634.284 | 10.8361 | 17.4592 | 57.2697 | 57.2697 | 31.974 | 148.026 | 23.1971 | 620.466 | 620.466 | 124.7127 | 745.1787 | 0.65294 | 65.29% | 336.9698 | 220.0227 | 154.0159 | 193.5531 | 193.5531 | 79.57% | 11.35% | 11.35% | 90% | 10.21% | 34.4184 | 4.7493 | 4.7493 | 163.4633 | 76.1132 | 84.45% | 84.45%
5 | 129 | 9 | 3084 | 12 | 22.4 | 515.28 | 165.47 | 680.75 | 165.47 | 82.74 | 129 | 3084 | 720 | 127.2329 | 17.3918 | 15.879 | 694.284 | 11.8361 | 2.4592 | 60.5436 | 60.5436 | 4.7763 | 175.2237 | 15.7998 | 569.421 | 569.421 | 141.2375 | 710.6585 | 0.6499 | 64.99% | 321.3598 | 208.8512 | 146.1958 | 176.9329 | 176.9329 | 82.63% | 11.34% | 11.34% | 90% | 10.21% | 32.7986 | 4.4899 | 4.4899 | 147.2617 | 72.5311 | 83.23% | 83.23%
5 | 129 | 9 | 3085 | 13 | 23.1 | 553.19 | 252.22 | 805.41 | 252.22 | 126.11 | 129 | 3085 | 780 | 127.2329 | 17.3918 | 15.879 | 754.284 | 12.8361 | -12.5408 | 58.8416 | 58.8416 | 23.6078 | 203.6078 | 19.8911 | 607.8796 | 607.8796 | 215.2832 | 823.1629 | 0.6728 | 67.28% | 372.2342 | 250.4393 | 175.3075 | 320.4196 | 320.4196 | 54.71% | 11.36% | 11.36% | 95% | 10.79% | 40.1572 | 4.3653 | 4.3653 | 175.2988 | 88.8041 | 54.71% | 54.71%
5 | 129 | 9 | 3086 | 14 | 23.6 | 362.08 | 264.44 | 626.52 | 264.44 | 132.22 | 129 | 3086 | 840 | 127.2329 | 17.3918 | 15.879 | 814.284 | 13.8361 | -27.5408 | 52.8709 | 52.8709 | 46.9702 | 226.9702 | 31.2389 | 388.3002 | 388.3002 | 225.7137 | 614.0139 | 0.62987 | 62.99% | 277.6571 | 174.8867 | 122.4207 | 313.7475 | 313.7475 | 39.02% | 11.32% | 11.32% | 90% | 10.18% | 28.2756 | 4.2784 | 4.2784 | 120.9757 | 62.5291 | 38.56% | 38.56%
5 | 129 | 9 | 3087 | 15 | 24.4 | 376.39 | 320.14 | 696.53 | 320.14 | 160.07 | 129 | 3087 | 900 | 127.2329 | 17.3918 | 15.879 | 874.284 | 14.8361 | -42.5408 | 44.3728 | 44.3728 | 64.506 | 244.506 | 44.5982 | 383.2383 | 383.2383 | 273.2566 | 656.4949 | 0.64375 | 64.38% | 296.867 | 191.1083 | 133.7758 | 317.1236 | 317.1236 | 42.18% | 11.32% | 11.32% | 90% | 10.19% | 30.2375 | 4.1431 | 4.1431 | 125.2765 | 66.8676 | 39.5% | 39.5%
5 | 129 | 9 | 3088 | 16 | 22.5 | 371.94 | 187.58 | 559.52 | 187.58 | 93.79 | 129 | 3088 | 960 | 127.2329 | 17.3918 | 15.879 | 934.284 | 15.8361 | -57.5408 | 34.6497 | 34.6497 | 78.1793 | 258.1793 | 58.5878 | 340.9539 | 340.9539 | 160.1095 | 501.0634 | 0.58587 | 58.59% | 226.5809 | 132.747 | 92.9229 | 159.2628 | 159.2628 | 58.35% | 11.31% | 11.31% | 90% | 10.18% | 23.0655 | 4.4719 | 4.4719 | 103.146 | 51.0073 | 64.76% | 64.76%
5 | 129 | 9 | 3089 | 17 | 23.6 | 188.89 | 206.19 | 395.08 | 206.19 | 103.1 | 129 | 3089 | 1020 | 127.2329 | 17.3918 | 15.879 | 994.284 | 16.8361 | -72.5408 | 24.4493 | 24.4493 | 89.7521 | 269.7521 | 72.8156 | 134.8363 | 134.8363 | 175.9942 | 310.8305 | 0.46002 | 46% | 140.5575 | 64.6587 | 45.2611 | 292.5895 | 292.5895 | 15.47% | 11.26% | 11.26% | 85% | 9.567% | 13.447 | 4.2784 | 4.2784 | 57.532 | 29.7368 | 19.66% | 19.66%
5 | 129 | 9 | 3090 | 18 | 21.5 | 77.69 | 165.08 | 242.77 | 165.08 | 82.54 | 129 | 3090 | 1080 | 127.2329 | 17.3918 | 15.879 | 1054.284 | 17.8361 | -87.5408 | 14.2324 | 14.2324 | 100.3929 | 280.3929 | 87.1225 | 15.8636 | 15.8636 | 140.9046 | 156.7682 | 0.092943 | 9.294% | 70.8906 | 6.5888 | 4.6122 | 133.2942 | 133.2942 | 3.46% | 11.3% | 0% | 80% | 0% | 0 | 4.6551 | 4.6551 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3091 | 19 | 21.2 | 84.44 | 101.75 | 186.19 | 101.75 | 50.88 | 129 | 3091 | 1140 | 127.2329 | 17.3918 | 15.879 | 1114.284 | 18.8361 | -102.5408 | 4.3537 | 4.3537 | 110.8989 | 290.8989 | 101.4103 | 0 | 0 | 86.8491 | 86.8491 | -0.48704 | 0% | 39.2731 | 0 | 0 | 125.1628 | 125.1628 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.7114 | 4.7114 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3092 | 20 | 19.7 | 13.69 | 28.89 | 42.58 | 28.89 | 14.45 | 129 | 3092 | 1200 | 127.2329 | 17.3918 | 15.879 | 1174.284 | 19.8361 | -117.5408 | -4.8392 | 0 | 115.8787 | 295.8787 | 107.9766 | 0 | 0 | 24.6592 | 24.6592 | -3.8765 | 0% | 11.1509 | 0 | 0 | 147.918 | 147.918 | 0% | 11.36% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3093 | 21 | 18.4 | 0 | 0 | 0 | 0 | 0 | 129 | 3093 | 1260 | 127.2329 | 17.3918 | 15.879 | 1234.284 | 20.8361 | -132.5408 | -12.9464 | 0 | 115.8787 | 295.8787 | 107.9766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.2625 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3094 | 22 | 17.6 | 0 | 0 | 0 | 0 | 0 | 129 | 3094 | 1320 | 127.2329 | 17.3918 | 15.879 | 1294.284 | 21.8361 | -147.5408 | -19.4879 | 0 | 115.8787 | 295.8787 | 107.9766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5205 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3095 | 23 | 16.6 | 0 | 0 | 0 | 0 | 0 | 129 | 3095 | 1380 | 127.2329 | 17.3918 | 15.879 | 1354.284 | 22.8361 | -162.5408 | -23.9286 | 0 | 115.8787 | 295.8787 | 107.9766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2449 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
5 | 129 | 9 | 3096 | 24 | 13.9 | 0 | 0 | 0 | 0 | 0 | 129 | 3096 | 1440 | 127.2329 | 17.3918 | 15.879 | 1414.284 | 23.8361 | -177.5408 | -25.7919 | 0 | 115.8787 | 295.8787 | 107.9766 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.56 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3097 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 130 | 3097 | 60 | 128.2192 | 17.6596 | 15.7693 | 34.284 | 0.83422 | 167.4867 | -24.5819 | 0 | 116.2938 | 63.7062 | 108.254 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0383 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3098 | 2 | 11.1 | 0 | 0 | 0 | 0 | 0 | 130 | 3098 | 120 | 128.2192 | 17.6596 | 15.7693 | 94.284 | 1.8342 | 152.4867 | -20.9585 | 0 | 116.2938 | 63.7062 | 108.254 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7926 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3099 | 3 | 10.6 | 0 | 0 | 0 | 0 | 0 | 130 | 3099 | 180 | 128.2192 | 17.6596 | 15.7693 | 154.284 | 2.8342 | 137.4867 | -15.0671 | 0 | 116.2938 | 63.7062 | 108.254 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9372 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3100 | 4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 130 | 3100 | 240 | 128.2192 | 17.6596 | 15.7693 | 214.284 | 3.8342 | 122.4867 | -7.4366 | 0 | 116.2938 | 63.7062 | 108.254 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4612 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3101 | 5 | 9 | 0 | 0 | 0 | 0 | 0 | 130 | 3101 | 300 | 128.2192 | 17.6596 | 15.7693 | 274.284 | 4.8342 | 107.4867 | 1.4313 | 1.4313 | 114.6154 | 65.3846 | 106.0677 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.2519 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3102 | 6 | 9.9 | 0.75 | 6.03 | 6.78 | 6.03 | 3.02 | 130 | 3102 | 360 | 128.2192 | 17.6596 | 15.7693 | 334.284 | 5.8342 | 92.4867 | 11.1132 | 11.1132 | 104.0295 | 75.9705 | 91.8286 | -0.12417 | 0 | 5.1469 | 5.1469 | -25.9442 | 0% | 2.3274 | 0 | 0 | 12.1086 | 12.1086 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3103 | 7 | 10.6 | 37.97 | 42.03 | 80 | 42.03 | 21.02 | 130 | 3103 | 420 | 128.2192 | 17.6596 | 15.7693 | 394.284 | 6.8342 | 77.4867 | 21.2506 | 21.2506 | 93.525 | 86.475 | 77.5393 | 22.604 | 22.604 | 35.8748 | 58.4788 | -1.5223 | 0% | 26.4441 | 0 | 0 | 184.4407 | 184.4407 | 0% | 11.74% | 11.74% | 80% | 9.388% | 2.4827 | 7.1059 | 6 | 14.8959 | 5.4902 | 8.076% | 8.076%
5 | 130 | 10 | 3104 | 8 | 12.8 | 141.03 | 83.42 | 224.45 | 83.42 | 41.71 | 130 | 3104 | 480 | 128.2192 | 17.6596 | 15.7693 | 454.284 | 7.8342 | 62.4867 | 31.5009 | 31.5009 | 82.3831 | 97.6169 | 63.2957 | 121.2928 | 121.2928 | 71.2034 | 192.4962 | 0.12372 | 12.37% | 87.0468 | 10.7691 | 7.5384 | 161.9604 | 161.9604 | 4.654% | 11.59% | 11.59% | 80% | 9.274% | 8.0728 | 6.5443 | 6 | 48.4366 | 17.8522 | 29.91% | 29.91%
5 | 130 | 10 | 3105 | 9 | 14.7 | 206.67 | 163.97 | 370.64 | 163.97 | 81.99 | 130 | 3105 | 540 | 128.2192 | 17.6596 | 15.7693 | 514.284 | 8.8342 | 47.4867 | 41.4551 | 41.4551 | 69.5812 | 110.4188 | 49.2304 | 203.8563 | 203.8563 | 139.9571 | 343.8134 | 0.43575 | 43.57% | 155.4724 | 67.7463 | 47.4224 | 172.0035 | 172.0035 | 27.57% | 11.48% | 11.48% | 85% | 9.762% | 15.1776 | 6.0865 | 6 | 91.0655 | 33.5639 | 52.94% | 52.94%
5 | 130 | 10 | 3106 | 10 | 16.7 | 311.47 | 131.67 | 443.14 | 131.67 | 65.84 | 130 | 3106 | 600 | 128.2192 | 17.6596 | 15.7693 | 574.284 | 9.8342 | 32.4867 | 50.4889 | 50.4889 | 53.5541 | 126.4459 | 35.6304 | 328.1396 | 328.1396 | 112.3874 | 440.5269 | 0.52685 | 52.68% | 199.2063 | 104.951 | 73.4657 | 174.6652 | 174.6652 | 42.06% | 11.42% | 11.42% | 85% | 9.705% | 19.3323 | 5.6319 | 5.6319 | 108.877 | 42.7516 | 62.33% | 62.33%
5 | 130 | 10 | 3107 | 11 | 18.5 | 423.14 | 117.22 | 540.36 | 117.22 | 58.61 | 130 | 3107 | 660 | 128.2192 | 17.6596 | 15.7693 | 634.284 | 10.8342 | 17.4867 | 57.5072 | 57.5072 | 32.2084 | 147.7916 | 23.3913 | 460.4423 | 460.4423 | 100.0535 | 560.4958 | 0.59334 | 59.33% | 253.4562 | 150.3857 | 105.27 | 172.0543 | 172.0543 | 61.18% | 11.37% | 11.37% | 90% | 10.23% | 25.9402 | 5.2467 | 5.2467 | 136.0997 | 57.3644 | 79.1% | 79.1%
5 | 130 | 10 | 3108 | 12 | 20.8 | 466.75 | 127.22 | 593.97 | 127.22 | 63.61 | 130 | 3108 | 720 | 128.2192 | 17.6596 | 15.7693 | 694.284 | 11.8342 | 2.4867 | 60.8093 | 60.8093 | 4.8627 | 175.1373 | 16.0683 | 513.7624 | 513.7624 | 108.5891 | 622.3514 | 0.62243 | 62.24% | 281.4273 | 175.1685 | 122.618 | 164.0318 | 164.0318 | 74.75% | 11.34% | 11.34% | 90% | 10.21% | 28.7331 | 4.7875 | 4.7875 | 137.559 | 63.5406 | 83.86% | 83.86%
5 | 130 | 10 | 3109 | 13 | 20 | 422.42 | 203.42 | 625.84 | 203.42 | 101.71 | 130 | 3109 | 780 | 128.2192 | 17.6596 | 15.7693 | 754.284 | 12.8342 | -12.5133 | 59.1056 | 59.1056 | 23.7089 | 203.7089 | 20.0815 | 462.338 | 462.338 | 173.6298 | 635.9678 | 0.62355 | 62.36% | 287.5847 | 179.3247 | 125.5273 | 161.5115 | 161.5115 | 77.72% | 11.35% | 11.35% | 90% | 10.22% | 29.3819 | 4.943 | 4.943 | 145.235 | 64.9756 | 89.92% | 89.92%
5 | 130 | 10 | 3110 | 14 | 20.3 | 519.25 | 235.28 | 754.53 | 235.28 | 117.64 | 130 | 3110 | 840 | 128.2192 | 17.6596 | 15.7693 | 814.284 | 13.8342 | -27.5133 | 53.1124 | 53.1124 | 47.1671 | 227.1671 | 31.338 | 554.5024 | 554.5024 | 200.824 | 755.3264 | 0.65294 | 65.29% | 341.5586 | 223.0181 | 156.1127 | 165.9303 | 165.9303 | 94.08% | 11.35% | 11.35% | 90% | 10.22% | 34.8941 | 4.8842 | 4.8842 | 170.4282 | 77.1652 | 102.7% | 102.7%
5 | 130 | 10 | 3111 | 15 | 20.6 | 328.25 | 222.22 | 550.47 | 222.22 | 111.11 | 130 | 3111 | 900 | 128.2192 | 17.6596 | 15.7693 | 874.284 | 14.8342 | -42.5133 | 44.5935 | 44.5935 | 64.7216 | 244.7216 | 44.6463 | 332.6383 | 332.6383 | 189.6766 | 522.3149 | 0.58681 | 58.68% | 236.1908 | 138.6002 | 97.0201 | 155.202 | 155.202 | 62.51% | 11.34% | 11.34% | 90% | 10.21% | 24.1117 | 4.8259 | 4.8259 | 116.3614 | 53.3208 | 74.97% | 74.97%
5 | 130 | 10 | 3112 | 16 | 20.8 | 175.92 | 198.25 | 374.17 | 198.25 | 99.13 | 130 | 3112 | 960 | 128.2192 | 17.6596 | 15.7693 | 934.284 | 15.8342 | -57.5133 | 34.8584 | 34.8584 | 78.3858 | 258.3858 | 58.6034 | 160.3482 | 160.3482 | 169.217 | 329.5652 | 0.46112 | 46.11% | 149.0294 | 68.7206 | 48.1044 | 145.377 | 145.377 | 33.09% | 11.33% | 11.33% | 85% | 9.632% | 14.3539 | 4.7875 | 4.7875 | 68.7191 | 31.7424 | 47.27% | 47.27%
5 | 130 | 10 | 3113 | 17 | 21.3 | 265.19 | 170.75 | 435.94 | 170.75 | 85.38 | 130 | 3113 | 1020 | 128.2192 | 17.6596 | 15.7693 | 994.284 | 16.8342 | -72.5133 | 24.6544 | 24.6544 | 89.9435 | 269.9435 | 72.8066 | 187.9205 | 187.9205 | 145.7442 | 333.6648 | 0.46861 | 46.86% | 150.8832 | 70.7055 | 49.4939 | 146.1955 | 146.1955 | 33.85% | 11.32% | 11.32% | 85% | 9.621% | 14.5163 | 4.6926 | 4.6926 | 68.1183 | 32.1014 | 46.59% | 46.59%
5 | 130 | 10 | 3114 | 18 | 21.2 | 133.61 | 104.72 | 238.33 | 104.72 | 52.36 | 130 | 3114 | 1080 | 128.2192 | 17.6596 | 15.7693 | 1054.284 | 17.8342 | -87.5133 | 14.4404 | 14.4404 | 100.5689 | 280.5689 | 87.0918 | 27.183 | 27.183 | 89.3841 | 116.5671 | -0.1579 | 0% | 52.7116 | 0 | 0 | 131.9099 | 131.9099 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7114 | 4.7114 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3115 | 19 | 20.3 | 59.72 | 73.06 | 132.78 | 73.06 | 36.53 | 130 | 3115 | 1140 | 128.2192 | 17.6596 | 15.7693 | 1114.284 | 18.8342 | -102.5133 | 4.5698 | 4.5698 | 111.0595 | 291.0595 | 101.3583 | 0 | 0 | 62.3606 | 62.3606 | -1.0256 | 0% | 28.1995 | 0 | 0 | 162.16 | 162.16 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.8842 | 4.8842 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3116 | 20 | 18.3 | 5.36 | 30.47 | 35.83 | 30.47 | 15.24 | 130 | 3116 | 1200 | 128.2192 | 17.6596 | 15.7693 | 1174.284 | 19.8342 | -117.5133 | -4.611 | 0 | 116.2938 | 296.2938 | 108.254 | 0 | 0 | 26.0078 | 26.0078 | -3.753 | 0% | 11.7607 | 0 | 0 | 145.4985 | 145.4985 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3117 | 21 | 16.9 | 0 | 1.11 | 1.11 | 1.11 | 0.56 | 130 | 3117 | 1260 | 128.2192 | 17.6596 | 15.7693 | 1234.284 | 20.8342 | -132.5133 | -12.7038 | 0 | 116.2938 | 296.2938 | 108.254 | 0 | 0 | 0.94744 | 0.94744 | -127.5888 | 0% | 0.42843 | 0 | 0 | -6.5983 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3118 | 22 | 16.1 | 0 | 0 | 0 | 0 | 0 | 130 | 3118 | 1320 | 128.2192 | 17.6596 | 15.7693 | 1294.284 | 21.8342 | -147.5133 | -19.2311 | 0 | 116.2938 | 296.2938 | 108.254 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.642 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3119 | 23 | 15.3 | 0 | 0 | 0 | 0 | 0 | 130 | 3119 | 1380 | 128.2192 | 17.6596 | 15.7693 | 1354.284 | 22.8342 | -162.5133 | -23.6618 | 0 | 116.2938 | 296.2938 | 108.254 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2439 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
5 | 130 | 10 | 3120 | 24 | 14.7 | 0 | 0 | 0 | 0 | 0 | 130 | 3120 | 1440 | 128.2192 | 17.6596 | 15.7693 | 1414.284 | 23.8342 | -177.5133 | -25.5234 | 0 | 116.2938 | 296.2938 | 108.254 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5409 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3121 | 1 | 10.7 | 0 | 0 | 0 | 0 | 0 | 131 | 3121 | 60 | 129.2055 | 17.9219 | 15.6466 | 34.284 | 0.83218 | 167.5174 | -24.3278 | 0 | 116.7013 | 63.2987 | 108.5258 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9918 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3122 | 2 | 13.4 | 0 | 0 | 0 | 0 | 0 | 131 | 3122 | 120 | 129.2055 | 17.9219 | 15.6466 | 94.284 | 1.8322 | 152.5174 | -20.7216 | 0 | 116.7013 | 63.2987 | 108.5258 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2085 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3123 | 3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 131 | 3123 | 180 | 129.2055 | 17.9219 | 15.6466 | 154.284 | 2.8322 | 137.5174 | -14.8508 | 0 | 116.7013 | 63.2987 | 108.5258 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8447 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3124 | 4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 131 | 3124 | 240 | 129.2055 | 17.9219 | 15.6466 | 214.284 | 3.8322 | 122.5174 | -7.2404 | 0 | 116.7013 | 63.2987 | 108.5258 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2163 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3125 | 5 | 12.2 | 0 | 0 | 0 | 0 | 0 | 131 | 3125 | 300 | 129.2055 | 17.9219 | 15.6466 | 274.284 | 4.8322 | 107.5174 | 1.6108 | 1.6108 | 114.809 | 65.191 | 106.0636 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.1204 | 5.1204 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3126 | 6 | 11.9 | 0.56 | 4.81 | 5.37 | 4.81 | 2.41 | 131 | 3126 | 360 | 129.2055 | 17.9219 | 15.6466 | 334.284 | 5.8322 | 92.5174 | 11.2808 | 11.2808 | 104.2374 | 75.7626 | 91.8466 | -0.092246 | 0 | 4.1056 | 4.1056 | -31.597 | 0% | 1.8565 | 0 | 0 | 17.4773 | 17.4773 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3127 | 7 | 12.3 | 28.69 | 43.69 | 72.38 | 43.69 | 21.85 | 131 | 3127 | 420 | 129.2055 | 17.9219 | 15.6466 | 394.284 | 6.8322 | 77.5174 | 21.4123 | 21.4123 | 93.749 | 86.251 | 77.5783 | 16.9043 | 16.9043 | 37.2917 | 54.196 | -1.6335 | 0% | 24.5074 | 0 | 0 | 190.7412 | 190.7412 | 0% | 11.67% | 11.67% | 80% | 9.334% | 2.2876 | 6.669 | 6 | 13.7256 | 5.0588 | 7.196% | 7.196%
5 | 131 | 11 | 3128 | 8 | 13.1 | 135.08 | 81.31 | 216.39 | 81.31 | 40.66 | 131 | 3128 | 480 | 129.2055 | 17.9219 | 15.6466 | 454.284 | 7.8322 | 62.5174 | 31.664 | 31.664 | 82.6267 | 97.3733 | 63.3574 | 115.3913 | 115.3913 | 69.4024 | 184.7937 | 0.099087 | 9.909% | 83.5637 | 8.2801 | 5.7961 | 167.2442 | 167.2442 | 3.466% | 11.59% | 11.59% | 80% | 9.268% | 7.745 | 6.4703 | 6 | 46.47 | 17.1274 | 27.79% | 27.79%
5 | 131 | 11 | 3129 | 9 | 15.5 | 250.19 | 114.17 | 364.36 | 114.17 | 57.09 | 131 | 3129 | 540 | 129.2055 | 17.9219 | 15.6466 | 514.284 | 8.8322 | 47.5174 | 41.629 | 41.629 | 69.8465 | 110.1535 | 49.32 | 245.4935 | 245.4935 | 97.4502 | 342.9436 | 0.4401 | 44.01% | 155.0791 | 68.2501 | 47.7751 | 178.5346 | 178.5346 | 26.76% | 11.47% | 11.47% | 85% | 9.745% | 15.113 | 5.9013 | 5.9013 | 89.186 | 33.4211 | 49.95% | 49.95%
5 | 131 | 11 | 3130 | 10 | 17.3 | 391.86 | 160.28 | 552.14 | 160.28 | 80.14 | 131 | 3130 | 600 | 129.2055 | 17.9219 | 15.6466 | 574.284 | 9.8322 | 32.5174 | 50.6858 | 50.6858 | 53.8311 | 126.1689 | 35.7598 | 411.0007 | 411.0007 | 136.8075 | 547.8083 | 0.58358 | 58.36% | 247.7189 | 144.5633 | 101.1943 | 186.2951 | 186.2951 | 54.32% | 11.39% | 11.39% | 90% | 10.25% | 25.3924 | 5.501 | 5.501 | 139.6827 | 56.1531 | 74.98% | 74.98%
5 | 131 | 11 | 3131 | 11 | 19.5 | 524.53 | 179.53 | 704.06 | 179.53 | 89.77 | 131 | 3131 | 660 | 129.2055 | 17.9219 | 15.6466 | 634.284 | 10.8322 | 17.5174 | 57.7381 | 57.7381 | 32.4471 | 147.5529 | 23.5855 | 568.4756 | 568.4756 | 153.2384 | 721.714 | 0.64347 | 64.35% | 326.3591 | 210.001 | 147.0007 | 186.0198 | 186.0198 | 79.02% | 11.35% | 11.35% | 90% | 10.22% | 33.3498 | 5.0425 | 5.0425 | 168.1654 | 73.7501 | 90.4% | 90.4%
5 | 131 | 11 | 3132 | 12 | 19.5 | 634.44 | 153.81 | 788.25 | 153.81 | 76.91 | 131 | 3132 | 720 | 129.2055 | 17.9219 | 15.6466 | 694.284 | 11.8322 | 2.5174 | 61.0693 | 61.0693 | 4.9559 | 175.0441 | 16.3319 | 695.6531 | 695.6531 | 131.285 | 826.9381 | 0.66389 | 66.39% | 373.9414 | 248.2572 | 173.78 | 174.3131 | 174.3131 | 99.69% | 11.35% | 11.35% | 95% | 10.78% | 40.3247 | 5.0425 | 5.0425 | 203.3363 | 89.1745 | 116.7% | 116.7%
5 | 131 | 11 | 3133 | 13 | 18.3 | 722.92 | 119.86 | 842.78 | 119.86 | 59.93 | 131 | 3133 | 780 | 129.2055 | 17.9219 | 15.6466 | 754.284 | 12.8322 | -12.4826 | 59.3651 | 59.3651 | 23.8028 | 203.8028 | 20.2675 | 788.1637 | 788.1637 | 102.3069 | 890.4706 | 0.6709 | 67.09% | 402.6708 | 270.1532 | 189.1073 | 170.6754 | 170.6754 | 110.8% | 11.34% | 11.34% | 95% | 10.78% | 43.3933 | 5.2884 | 5.2884 | 229.479 | 95.9603 | 134.5% | 134.5%
5 | 131 | 11 | 3134 | 14 | 15 | 640 | 193.42 | 833.42 | 193.42 | 96.71 | 131 | 3134 | 840 | 129.2055 | 17.9219 | 15.6466 | 814.284 | 13.8322 | -27.4826 | 53.3505 | 53.3505 | 47.3572 | 227.3572 | 31.4337 | 680.637 | 680.637 | 165.0943 | 845.7313 | 0.6551 | 65.51% | 382.4397 | 250.536 | 175.3752 | 164.3668 | 164.3668 | 106.7% | 11.34% | 11.34% | 95% | 10.77% | 41.1981 | 6.0165 | 6 | 247.1888 | 91.106 | 150.4% | 150.4%
5 | 131 | 11 | 3135 | 15 | 13.9 | 440.08 | 237.78 | 677.86 | 237.78 | 118.89 | 131 | 3135 | 900 | 129.2055 | 17.9219 | 15.6466 | 874.284 | 14.8322 | -42.4826 | 44.8117 | 44.8117 | 64.9306 | 244.9306 | 44.6913 | 443.9067 | 443.9067 | 202.9579 | 646.8646 | 0.60545 | 60.55% | 292.5122 | 177.1024 | 123.9717 | 153.4634 | 153.4634 | 80.78% | 11.4% | 11.4% | 90% | 10.26% | 30.0206 | 6.2762 | 6 | 180.1238 | 66.388 | 117.4% | 117.4%
5 | 131 | 11 | 3136 | 16 | 15.7 | 368.06 | 172.69 | 540.75 | 172.69 | 86.35 | 131 | 3136 | 960 | 129.2055 | 17.9219 | 15.6466 | 934.284 | 15.8322 | -57.4826 | 35.0651 | 35.0651 | 78.5861 | 258.5861 | 58.6159 | 333.635 | 333.635 | 147.4001 | 481.0352 | 0.5455 | 54.55% | 217.5241 | 118.6603 | 83.0622 | 147.7838 | 147.7838 | 56.21% | 11.43% | 11.43% | 85% | 9.713% | 21.1288 | 5.8557 | 5.8557 | 123.7235 | 46.7245 | 83.72% | 83.72%
5 | 131 | 11 | 3137 | 17 | 17.9 | 297.14 | 163.33 | 460.47 | 163.33 | 81.67 | 131 | 3137 | 1020 | 129.2055 | 17.9219 | 15.6466 | 994.284 | 16.8322 | -72.4826 | 24.8576 | 24.8576 | 90.1289 | 270.1289 | 72.7945 | 209.0894 | 209.0894 | 139.4109 | 348.5003 | 0.46136 | 46.14% | 157.5918 | 72.707 | 50.8949 | 144.2626 | 144.2626 | 35.28% | 11.4% | 11.4% | 85% | 9.694% | 15.2762 | 5.3726 | 5.3726 | 82.0722 | 33.782 | 56.89% | 56.89%
5 | 131 | 11 | 3138 | 18 | 17.3 | 195.36 | 125.47 | 320.83 | 125.47 | 62.74 | 131 | 3138 | 1080 | 129.2055 | 17.9219 | 15.6466 | 1054.284 | 17.8322 | -87.4826 | 14.6466 | 14.6466 | 100.7391 | 280.7391 | 87.0584 | 39.6491 | 39.6491 | 107.0953 | 146.7444 | -0.018853 | 0% | 66.3578 | 0 | 0 | 131.6853 | 131.6853 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3139 | 19 | 16.2 | 88.33 | 73.53 | 161.86 | 73.53 | 36.77 | 131 | 3139 | 1140 | 129.2055 | 17.9219 | 15.6466 | 1114.284 | 18.8322 | -102.4826 | 4.784 | 4.784 | 111.2144 | 291.2144 | 101.3037 | 0 | 0 | 62.7618 | 62.7618 | -1.1593 | 0% | 28.3809 | 0 | 0 | 116.6984 | 116.6984 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3140 | 20 | 15.2 | 16.67 | 25.75 | 42.42 | 25.75 | 12.88 | 131 | 3140 | 1200 | 129.2055 | 17.9219 | 15.6466 | 1174.284 | 19.8322 | -117.4826 | -4.3852 | 0 | 116.7013 | 296.7013 | 108.5258 | 0 | 0 | 21.979 | 21.979 | -4.9049 | 0% | 9.9389 | 0 | 0 | 142.0329 | 142.0329 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3141 | 21 | 14.3 | 0 | 0 | 0 | 0 | 0 | 131 | 3141 | 1260 | 129.2055 | 17.9219 | 15.6466 | 1234.284 | 20.8322 | -132.4826 | -12.4642 | 0 | 116.7013 | 296.7013 | 108.5258 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5712 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3142 | 22 | 14.2 | 0 | 0 | 0 | 0 | 0 | 131 | 3142 | 1320 | 129.2055 | 17.9219 | 15.6466 | 1294.284 | 21.8322 | -147.4826 | -18.9782 | 0 | 116.7013 | 296.7013 | 108.5258 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6636 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3143 | 23 | 13 | 0 | 0 | 0 | 0 | 0 | 131 | 3143 | 1380 | 129.2055 | 17.9219 | 15.6466 | 1354.284 | 22.8322 | -162.4826 | -23.3997 | 0 | 116.7013 | 296.7013 | 108.5258 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8238 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
5 | 131 | 11 | 3144 | 24 | 12.1 | 0 | 0 | 0 | 0 | 0 | 131 | 3144 | 1440 | 129.2055 | 17.9219 | 15.6466 | 1414.284 | 23.8322 | -177.4826 | -25.2603 | 0 | 116.7013 | 296.7013 | 108.5258 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5268 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3145 | 1 | 11.4 | 0 | 0 | 0 | 0 | 0 | 132 | 3145 | 60 | 130.1918 | 18.1787 | 15.511 | 34.284 | 0.82992 | 167.5512 | -24.0796 | 0 | 117.1011 | 62.8989 | 108.7919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9977 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3146 | 2 | 8.1 | 0 | 0 | 0 | 0 | 0 | 132 | 3146 | 120 | 130.1918 | 18.1787 | 15.511 | 94.284 | 1.8299 | 152.5512 | -20.4907 | 0 | 117.1011 | 62.8989 | 108.7919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4593 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3147 | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 132 | 3147 | 180 | 130.1918 | 18.1787 | 15.511 | 154.284 | 2.8299 | 137.5512 | -14.6407 | 0 | 117.1011 | 62.8989 | 108.7919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9961 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3148 | 4 | 8.1 | 0 | 0 | 0 | 0 | 0 | 132 | 3148 | 240 | 130.1918 | 18.1787 | 15.511 | 214.284 | 3.8299 | 122.5512 | -7.0503 | 0 | 117.1011 | 62.8989 | 108.7919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8917 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3149 | 5 | 9.6 | 0 | 0 | 0 | 0 | 0 | 132 | 3149 | 300 | 130.1918 | 18.1787 | 15.511 | 274.284 | 4.8299 | 107.5512 | 1.7842 | 1.7842 | 115.0012 | 64.9988 | 106.0627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.11663 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3150 | 6 | 9.7 | 0.36 | 5.75 | 6.11 | 5.75 | 2.88 | 132 | 3150 | 360 | 130.1918 | 18.1787 | 15.511 | 334.284 | 5.8299 | 92.5512 | 11.4423 | 11.4423 | 104.4437 | 75.5563 | 91.8677 | -0.059143 | 0 | 4.9079 | 4.9079 | -27.342 | 0% | 2.2194 | 0 | 0 | 11.7536 | 11.7536 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3151 | 7 | 10.6 | 28.06 | 61.75 | 89.81 | 61.75 | 30.88 | 132 | 3151 | 420 | 130.1918 | 18.1787 | 15.511 | 394.284 | 6.8299 | 77.5512 | 21.5677 | 21.5677 | 93.9714 | 86.0286 | 77.6204 | 16.3649 | 16.3649 | 52.7069 | 69.0718 | -1.1655 | 0% | 31.2343 | 0 | 0 | 183.1656 | 183.1656 | 0% | 11.73% | 11.73% | 80% | 9.384% | 2.931 | 7.1059 | 6 | 17.586 | 6.4816 | 9.601% | 9.601%
5 | 132 | 12 | 3152 | 8 | 11.2 | 118.81 | 117.31 | 236.12 | 117.31 | 58.66 | 132 | 3152 | 480 | 130.1918 | 18.1787 | 15.511 | 454.284 | 7.8299 | 62.5512 | 31.8206 | 31.8206 | 82.8689 | 97.1311 | 63.4219 | 100.8184 | 100.8184 | 100.1303 | 200.9487 | 0.13395 | 13.4% | 90.869 | 12.1721 | 8.5205 | 158.2632 | 158.2632 | 5.384% | 11.64% | 11.64% | 80% | 9.314% | 8.4631 | 6.9494 | 6 | 50.7788 | 18.7155 | 32.09% | 32.09%
5 | 132 | 12 | 3153 | 9 | 15.2 | 157.78 | 184.53 | 342.31 | 184.53 | 92.27 | 132 | 3153 | 540 | 130.1918 | 18.1787 | 15.511 | 514.284 | 8.8299 | 47.5512 | 41.7962 | 41.7962 | 70.111 | 109.889 | 49.412 | 154.0233 | 154.0233 | 157.5062 | 311.5295 | 0.40122 | 40.12% | 140.8736 | 56.5219 | 39.5653 | 169.7456 | 169.7456 | 23.31% | 11.48% | 11.48% | 85% | 9.759% | 13.7476 | 5.9702 | 5.9702 | 82.0759 | 30.4016 | 48.35% | 48.35%
5 | 132 | 12 | 3154 | 10 | 18.1 | 223.81 | 197.97 | 421.78 | 197.97 | 98.99 | 132 | 3154 | 600 | 130.1918 | 18.1787 | 15.511 | 574.284 | 9.8299 | 32.5512 | 50.8757 | 50.8757 | 54.1091 | 125.8909 | 35.891 | 233.7212 | 233.7212 | 168.978 | 402.6992 | 0.50858 | 50.86% | 182.1006 | 92.6135 | 64.8295 | 174.552 | 174.552 | 37.14% | 11.39% | 11.39% | 85% | 9.684% | 17.6355 | 5.3303 | 5.3303 | 94.0028 | 38.9994 | 53.85% | 53.85%
5 | 132 | 12 | 3155 | 11 | 20.4 | 200.92 | 185.56 | 386.48 | 185.56 | 92.78 | 132 | 3155 | 660 | 130.1918 | 18.1787 | 15.511 | 634.284 | 10.8299 | 17.5512 | 57.9623 | 57.9623 | 32.6901 | 147.3099 | 23.7796 | 216.8958 | 216.8958 | 158.3854 | 375.2812 | 0.50055 | 50.06% | 169.7022 | 84.9448 | 59.4614 | 167.7318 | 167.7318 | 35.45% | 11.34% | 11.34% | 85% | 9.641% | 16.3614 | 4.8647 | 4.8647 | 79.5931 | 36.1818 | 47.45% | 47.45%
5 | 132 | 12 | 3156 | 12 | 20.1 | 214.92 | 256.94 | 471.86 | 256.94 | 128.47 | 132 | 3156 | 720 | 130.1918 | 18.1787 | 15.511 | 694.284 | 11.8299 | 2.5512 | 61.3236 | 61.3236 | 5.0562 | 174.9438 | 16.5906 | 234.7686 | 234.7686 | 219.312 | 454.0806 | 0.55176 | 55.18% | 205.3352 | 113.2957 | 79.307 | 158.6557 | 158.6557 | 49.99% | 11.35% | 11.35% | 85% | 9.648% | 19.8099 | 4.9233 | 4.9233 | 97.5303 | 43.8078 | 61.47% | 61.47%
5 | 132 | 12 | 3157 | 13 | 17.3 | 211.11 | 300.47 | 511.58 | 300.47 | 150.24 | 132 | 3157 | 780 | 130.1918 | 18.1787 | 15.511 | 754.284 | 12.8299 | -12.4488 | 59.6201 | 59.6201 | 23.8894 | 203.8894 | 20.4489 | 229.2902 | 229.2902 | 256.4672 | 485.7574 | 0.55542 | 55.54% | 219.6595 | 122.0035 | 85.4025 | 154.1041 | 154.1041 | 55.42% | 11.4% | 11.4% | 85% | 9.689% | 21.2825 | 5.501 | 5.501 | 117.0741 | 47.0644 | 75.97% | 75.97%
5 | 132 | 12 | 3158 | 14 | 15.3 | 348.69 | 325.28 | 673.97 | 325.28 | 162.64 | 132 | 3158 | 840 | 130.1918 | 18.1787 | 15.511 | 814.284 | 13.8299 | -27.4488 | 53.5853 | 53.5853 | 47.5402 | 227.5402 | 31.5258 | 369.3422 | 369.3422 | 277.6438 | 646.9861 | 0.61041 | 61.04% | 292.5671 | 178.5858 | 125.0101 | 156.5337 | 156.5337 | 79.86% | 11.39% | 11.39% | 90% | 10.25% | 29.9951 | 5.9472 | 5.9472 | 178.3858 | 66.3316 | 114% | 114%
5 | 132 | 12 | 3159 | 15 | 16.4 | 413.81 | 215.83 | 629.64 | 215.83 | 107.92 | 132 | 3159 | 900 | 130.1918 | 18.1787 | 15.511 | 874.284 | 14.8299 | -42.4488 | 45.0272 | 45.0272 | 65.1329 | 245.1329 | 44.733 | 415.537 | 415.537 | 184.2224 | 599.7594 | 0.5993 | 59.93% | 271.2112 | 162.5382 | 113.7767 | 153.3704 | 153.3704 | 74.18% | 11.39% | 11.39% | 90% | 10.25% | 27.8059 | 5.6983 | 5.6983 | 158.4457 | 61.4902 | 103.3% | 103.3%
5 | 132 | 12 | 3160 | 16 | 17.6 | 298.89 | 195 | 493.89 | 195 | 97.5 | 132 | 3160 | 960 | 130.1918 | 18.1787 | 15.511 | 934.284 | 15.8299 | -57.4488 | 35.2696 | 35.2696 | 78.7801 | 258.7801 | 58.6253 | 269.4925 | 269.4925 | 166.4429 | 435.9354 | 0.52855 | 52.85% | 197.13 | 104.193 | 72.9351 | 147.4372 | 147.4372 | 49.47% | 11.4% | 11.4% | 85% | 9.69% | 19.102 | 5.4364 | 5.4364 | 103.8468 | 42.2424 | 70.43% | 70.43%
5 | 132 | 12 | 3161 | 17 | 19.3 | 211.94 | 190.92 | 402.86 | 190.92 | 95.46 | 132 | 3161 | 1020 | 130.1918 | 18.1787 | 15.511 | 994.284 | 16.8299 | -72.4488 | 25.059 | 25.059 | 90.3083 | 270.3083 | 72.7795 | 148.1398 | 148.1398 | 162.9604 | 311.1002 | 0.43016 | 43.02% | 140.6795 | 60.5148 | 42.3603 | 143.1216 | 143.1216 | 29.6% | 11.37% | 11.37% | 85% | 9.665% | 13.597 | 5.0828 | 5.0828 | 69.11 | 30.0685 | 48.29% | 48.29%
5 | 132 | 12 | 3162 | 18 | 18.4 | 175.47 | 144.92 | 320.39 | 144.92 | 72.46 | 132 | 3162 | 1080 | 130.1918 | 18.1787 | 15.511 | 1054.284 | 17.8299 | -87.4488 | 14.8509 | 14.8509 | 100.9034 | 280.9034 | 87.0221 | 35.5662 | 35.5662 | 123.697 | 159.2632 | 0.061228 | 6.123% | 72.0188 | 4.4096 | 3.0867 | 133.6051 | 133.6051 | 2.31% | 11.41% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3163 | 19 | 16.9 | 102.97 | 86.39 | 189.36 | 86.39 | 43.2 | 132 | 3163 | 1140 | 130.1918 | 18.1787 | 15.511 | 1114.284 | 18.8299 | -102.4488 | 4.9959 | 4.9959 | 111.3634 | 291.3634 | 101.2464 | 0 | 0 | 73.7385 | 73.7385 | -0.84568 | 0% | 33.3445 | 0 | 0 | 119.995 | 119.995 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3164 | 20 | 16.3 | 23.33 | 29.72 | 53.05 | 29.72 | 14.86 | 132 | 3164 | 1200 | 130.1918 | 18.1787 | 15.511 | 1174.284 | 19.8299 | -117.4488 | -4.162 | 0 | 117.1011 | 297.1011 | 108.7919 | 0 | 0 | 25.3676 | 25.3676 | -4.0444 | 0% | 11.4712 | 0 | 0 | 145.6484 | 145.6484 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3165 | 21 | 15.1 | 0 | 1.67 | 1.67 | 1.67 | 0.84 | 132 | 3165 | 1260 | 130.1918 | 18.1787 | 15.511 | 1234.284 | 20.8299 | -132.4488 | -12.2278 | 0 | 117.1011 | 297.1011 | 108.7919 | 0 | 0 | 1.4254 | 1.4254 | -87.382 | 0% | 0.64458 | 0 | 0 | -8.1603 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3166 | 22 | 13.8 | 0 | 0 | 0 | 0 | 0 | 132 | 3166 | 1320 | 130.1918 | 18.1787 | 15.511 | 1294.284 | 21.8299 | -147.4488 | -18.7291 | 0 | 117.1011 | 297.1011 | 108.7919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.043 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3167 | 23 | 13.6 | 0 | 0 | 0 | 0 | 0 | 132 | 3167 | 1380 | 130.1918 | 18.1787 | 15.511 | 1354.284 | 22.8299 | -162.4488 | -23.1422 | 0 | 117.1011 | 297.1011 | 108.7919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7802 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
5 | 132 | 12 | 3168 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 132 | 3168 | 1440 | 130.1918 | 18.1787 | 15.511 | 1414.284 | 23.8299 | -177.4488 | -25.0025 | 0 | 117.1011 | 297.1011 | 108.7919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.127 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3169 | 1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 133 | 3169 | 60 | 131.1781 | 18.4299 | 15.3627 | 34.284 | 0.82745 | 167.5883 | -23.8374 | 0 | 117.493 | 62.507 | 109.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5885 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3170 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 133 | 3170 | 120 | 131.1781 | 18.4299 | 15.3627 | 94.284 | 1.8274 | 152.5883 | -20.266 | 0 | 117.493 | 62.507 | 109.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3398 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3171 | 3 | 13.4 | 0 | 0 | 0 | 0 | 0 | 133 | 3171 | 180 | 131.1781 | 18.4299 | 15.3627 | 154.284 | 2.8274 | 137.5883 | -14.4368 | 0 | 117.493 | 62.507 | 109.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.7863 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3172 | 4 | 11.9 | 0 | 0 | 0 | 0 | 0 | 133 | 3172 | 240 | 131.1781 | 18.4299 | 15.3627 | 214.284 | 3.8274 | 122.5883 | -6.8663 | 0 | 117.493 | 62.507 | 109.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0722 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3173 | 5 | 12.8 | 0 | 0 | 0 | 0 | 0 | 133 | 3173 | 300 | 131.1781 | 18.4299 | 15.3627 | 274.284 | 4.8274 | 107.5883 | 1.9514 | 1.9514 | 115.1921 | 64.8079 | 106.0652 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 13.8807 | 13.8807 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3174 | 6 | 12.8 | 3.42 | 8.61 | 12.03 | 8.61 | 4.31 | 133 | 3174 | 360 | 131.1781 | 18.4299 | 15.3627 | 334.284 | 5.8274 | 92.5883 | 11.5975 | 11.5975 | 104.6484 | 75.3516 | 91.8919 | -0.56162 | 0 | 7.3491 | 7.3491 | -17.0148 | 0% | 3.3233 | 0 | 0 | 31.9899 | 31.9899 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3175 | 7 | 13.4 | 83.25 | 41.19 | 124.44 | 41.19 | 20.6 | 133 | 3175 | 420 | 131.1781 | 18.4299 | 15.3627 | 394.284 | 6.8274 | 77.5883 | 21.7168 | 21.7168 | 94.1921 | 85.8079 | 77.6653 | 48.0623 | 48.0623 | 35.1579 | 83.2202 | -0.75303 | 0% | 37.6322 | 0 | 0 | 218.5318 | 218.5318 | 0% | 11.61% | 11.61% | 80% | 9.29% | 3.4959 | 6.397 | 6 | 20.9756 | 7.731 | 9.598% | 9.598%
5 | 133 | 13 | 3176 | 8 | 15 | 233.97 | 56.58 | 290.55 | 56.58 | 28.29 | 133 | 3176 | 480 | 131.1781 | 18.4299 | 15.3627 | 454.284 | 7.8274 | 62.5883 | 31.9708 | 31.9708 | 83.1097 | 96.8903 | 63.4892 | 197.2411 | 197.2411 | 48.2941 | 245.5352 | 0.29112 | 29.11% | 111.031 | 32.3234 | 22.6264 | 199.9679 | 199.9679 | 11.31% | 11.5% | 11.5% | 80% | 9.204% | 10.2188 | 6.0165 | 6 | 61.313 | 22.598 | 30.66% | 30.66%
5 | 133 | 13 | 3177 | 9 | 18.1 | 406.03 | 64.25 | 470.28 | 64.25 | 32.13 | 133 | 3177 | 540 | 131.1781 | 18.4299 | 15.3627 | 514.284 | 8.8274 | 47.5883 | 41.9568 | 41.9568 | 70.3748 | 109.6252 | 49.5065 | 394.3648 | 394.3648 | 54.8408 | 449.2056 | 0.53917 | 53.92% | 203.1308 | 109.5218 | 76.6653 | 213.3404 | 213.3404 | 35.94% | 11.39% | 11.39% | 85% | 9.68% | 19.6638 | 5.3303 | 5.3303 | 104.8142 | 43.4847 | 49.13% | 49.13%
5 | 133 | 13 | 3178 | 10 | 19.3 | 547.58 | 73.06 | 620.64 | 73.06 | 36.53 | 133 | 3178 | 600 | 131.1781 | 18.4299 | 15.3627 | 574.284 | 9.8274 | 32.5883 | 51.0588 | 51.0588 | 54.3879 | 125.6121 | 36.0238 | 569.3915 | 569.3915 | 62.3606 | 631.7521 | 0.61991 | 61.99% | 285.6783 | 177.0938 | 123.9657 | 215.2588 | 215.2588 | 57.59% | 11.36% | 11.36% | 90% | 10.22% | 29.2038 | 5.0828 | 5.0828 | 148.4359 | 64.5817 | 68.96% | 68.96%
5 | 133 | 13 | 3179 | 11 | 20.3 | 636.39 | 107.42 | 743.81 | 107.42 | 53.71 | 133 | 3179 | 660 | 131.1781 | 18.4299 | 15.3627 | 634.284 | 10.8274 | 17.5883 | 58.1798 | 58.1798 | 32.937 | 147.063 | 23.9733 | 684.344 | 684.344 | 91.6887 | 776.0327 | 0.65697 | 65.7% | 350.922 | 230.5462 | 161.3824 | 207.0256 | 207.0256 | 77.95% | 11.35% | 11.35% | 90% | 10.22% | 35.8517 | 4.8842 | 4.8842 | 175.1055 | 79.2829 | 84.58% | 84.58%
5 | 133 | 13 | 3180 | 12 | 21.3 | 726.11 | 111.94 | 838.05 | 111.94 | 55.97 | 133 | 3180 | 720 | 131.1781 | 18.4299 | 15.3627 | 694.284 | 11.8274 | 2.5883 | 61.572 | 61.572 | 5.1634 | 174.8366 | 16.8442 | 790.2483 | 790.2483 | 95.5468 | 885.7951 | 0.67766 | 67.77% | 400.5565 | 271.4429 | 190.01 | 191.0255 | 191.0255 | 99.47% | 11.36% | 11.36% | 95% | 10.79% | 43.221 | 4.6926 | 4.6926 | 202.8167 | 95.5793 | 106.2% | 106.2%
5 | 133 | 13 | 3181 | 13 | 22.4 | 521.11 | 207.22 | 728.33 | 207.22 | 103.61 | 133 | 3181 | 780 | 131.1781 | 18.4299 | 15.3627 | 754.284 | 12.8274 | -12.4117 | 59.8706 | 59.8706 | 23.9685 | 203.9685 | 20.6257 | 563.8927 | 563.8927 | 176.8733 | 740.766 | 0.65616 | 65.62% | 334.9744 | 219.7973 | 153.8581 | 184.4404 | 184.4404 | 83.42% | 11.34% | 11.34% | 90% | 10.21% | 34.2001 | 4.4899 | 4.4899 | 153.5543 | 75.6305 | 83.25% | 83.25%
5 | 133 | 13 | 3182 | 14 | 22.9 | 533.89 | 200.56 | 734.45 | 200.56 | 100.28 | 133 | 3182 | 840 | 131.1781 | 18.4299 | 15.3627 | 814.284 | 13.8274 | -27.4117 | 53.8166 | 53.8166 | 47.716 | 227.716 | 31.6144 | 563.3013 | 563.3013 | 171.1887 | 734.4899 | 0.65637 | 65.64% | 332.1364 | 218.0052 | 152.6036 | 183.4857 | 183.4857 | 83.17% | 11.34% | 11.34% | 90% | 10.21% | 33.9025 | 4.4006 | 4.4006 | 149.1897 | 74.9723 | 81.31% | 81.31%
5 | 133 | 13 | 3183 | 15 | 23.6 | 502.58 | 202.42 | 705 | 202.42 | 101.21 | 133 | 3183 | 900 | 131.1781 | 18.4299 | 15.3627 | 874.284 | 14.8274 | -42.4117 | 45.2401 | 45.2401 | 65.3284 | 245.3284 | 44.7714 | 502.4802 | 502.4802 | 172.7763 | 675.2565 | 0.64566 | 64.57% | 305.351 | 197.1527 | 138.0069 | 327.9142 | 327.9142 | 42.09% | 11.33% | 11.33% | 90% | 10.19% | 31.1292 | 4.2784 | 4.2784 | 133.1845 | 68.8395 | 40.62% | 40.62%
5 | 133 | 13 | 3184 | 16 | 23.9 | 504.81 | 149.36 | 654.17 | 149.36 | 74.68 | 133 | 3184 | 960 | 131.1781 | 18.4299 | 15.3627 | 934.284 | 15.8274 | -57.4117 | 35.472 | 35.472 | 78.9676 | 258.9676 | 58.6317 | 452.8182 | 452.8182 | 127.4867 | 580.3049 | 0.62086 | 62.09% | 262.4139 | 162.923 | 114.0461 | 321.5985 | 321.5985 | 35.46% | 11.3% | 11.3% | 90% | 10.17% | 26.699 | 4.2272 | 4.2272 | 112.8608 | 59.0425 | 35.09% | 35.09%
5 | 133 | 13 | 3185 | 17 | 23.7 | 490.92 | 100 | 590.92 | 100 | 50 | 133 | 3185 | 1020 | 131.1781 | 18.4299 | 15.3627 | 994.284 | 16.8274 | -72.4117 | 25.2583 | 25.2583 | 90.4815 | 270.4815 | 72.7616 | 340.9498 | 340.9498 | 85.3553 | 426.3051 | 0.5537 | 55.37% | 192.7752 | 106.739 | 74.7173 | 325.0401 | 325.0401 | 22.99% | 11.28% | 11.28% | 85% | 9.585% | 18.4767 | 4.2613 | 4.2613 | 78.7341 | 40.8595 | 24.22% | 24.22%
5 | 133 | 13 | 3186 | 18 | 23.5 | 230.19 | 94.81 | 325 | 94.81 | 47.41 | 133 | 3186 | 1080 | 131.1781 | 18.4299 | 15.3627 | 1054.284 | 17.8274 | -87.4117 | 15.0532 | 15.0532 | 101.0618 | 281.0618 | 86.983 | 46.6481 | 46.6481 | 80.9254 | 127.5735 | -0.035799 | 0% | 57.6887 | 0 | 0 | 306.9946 | 306.9946 | 0% | 11.22% | 11.22% | 80% | 8.978% | 5.1793 | 4.2957 | 4.2957 | 22.2487 | 11.4536 | 7.247% | 7.247%
5 | 133 | 13 | 3187 | 19 | 20.1 | 114.72 | 65 | 179.72 | 65 | 32.5 | 133 | 3187 | 1140 | 131.1781 | 18.4299 | 15.3627 | 1114.284 | 18.8274 | -102.4117 | 5.2057 | 5.2057 | 111.5065 | 291.5065 | 101.1865 | 0 | 0 | 55.481 | 55.481 | -1.2604 | 0% | 25.0885 | 0 | 0 | 128.291 | 128.291 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3188 | 20 | 18.9 | 34.08 | 34.08 | 68.16 | 34.08 | 17.04 | 133 | 3188 | 1200 | 131.1781 | 18.4299 | 15.3627 | 1174.284 | 19.8274 | -117.4117 | -3.9413 | 0 | 117.493 | 297.493 | 109.0522 | 0 | 0 | 29.0891 | 29.0891 | -3.2245 | 0% | 13.1541 | 0 | 0 | 150.8095 | 150.8095 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3189 | 21 | 17.1 | 0 | 1.81 | 1.81 | 1.81 | 0.91 | 133 | 3189 | 1260 | 131.1781 | 18.4299 | 15.3627 | 1234.284 | 20.8274 | -132.4117 | -11.9945 | 0 | 117.493 | 297.493 | 109.0522 | 0 | 0 | 1.5449 | 1.5449 | -77.644 | 0% | 0.69862 | 0 | 0 | -6.1405 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3190 | 22 | 14.4 | 0 | 0 | 0 | 0 | 0 | 133 | 3190 | 1320 | 131.1781 | 18.4299 | 15.3627 | 1294.284 | 21.8274 | -147.4117 | -18.484 | 0 | 117.493 | 297.493 | 109.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9818 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3191 | 23 | 9 | 0 | 0 | 0 | 0 | 0 | 133 | 3191 | 1380 | 131.1781 | 18.4299 | 15.3627 | 1354.284 | 22.8274 | -162.4117 | -22.8895 | 0 | 117.493 | 297.493 | 109.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2675 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
5 | 133 | 13 | 3192 | 24 | 12.4 | 0 | 0 | 0 | 0 | 0 | 133 | 3192 | 1440 | 131.1781 | 18.4299 | 15.3627 | 1414.284 | 23.8274 | -177.4117 | -24.7503 | 0 | 117.493 | 297.493 | 109.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.142 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3193 | 1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 134 | 3193 | 60 | 132.1644 | 18.6754 | 15.2018 | 34.284 | 0.82476 | 167.6285 | -23.6012 | 0 | 117.8768 | 62.1232 | 109.3066 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5778 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3194 | 2 | 11.3 | 0 | 0 | 0 | 0 | 0 | 134 | 3194 | 120 | 132.1644 | 18.6754 | 15.2018 | 94.284 | 1.8248 | 152.6285 | -20.0476 | 0 | 117.8768 | 62.1232 | 109.3066 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5197 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3195 | 3 | 10.8 | 0 | 0 | 0 | 0 | 0 | 134 | 3195 | 180 | 132.1644 | 18.6754 | 15.2018 | 154.284 | 2.8248 | 137.6285 | -14.2391 | 0 | 117.8768 | 62.1232 | 109.3066 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3092 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3196 | 4 | 10.3 | 0 | 0 | 0 | 0 | 0 | 134 | 3196 | 240 | 132.1644 | 18.6754 | 15.2018 | 214.284 | 3.8248 | 122.6285 | -6.6887 | 0 | 117.8768 | 62.1232 | 109.3066 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0711 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3197 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 134 | 3197 | 300 | 132.1644 | 18.6754 | 15.2018 | 274.284 | 4.8248 | 107.6285 | 2.1124 | 2.1124 | 115.3814 | 64.6186 | 106.0709 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.8068 | 9.8068 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3198 | 6 | 10.1 | 2.86 | 9.92 | 12.78 | 9.92 | 4.96 | 134 | 3198 | 360 | 132.1644 | 18.6754 | 15.2018 | 334.284 | 5.8248 | 92.6285 | 11.7466 | 11.7466 | 104.8514 | 75.1486 | 91.9192 | -0.47048 | 0 | 8.4672 | 8.4672 | -15.4001 | 0% | 3.8289 | 0 | 0 | 26.4949 | 26.4949 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3199 | 7 | 11.4 | 66.11 | 54.72 | 120.83 | 54.72 | 27.36 | 134 | 3199 | 420 | 132.1644 | 18.6754 | 15.2018 | 394.284 | 6.8248 | 77.6285 | 21.8596 | 21.8596 | 94.4111 | 85.5889 | 77.7132 | 37.7848 | 37.7848 | 46.7064 | 84.4912 | -0.78411 | 0% | 38.2069 | 0 | 0 | 210.3062 | 210.3062 | 0% | 11.69% | 11.69% | 80% | 9.352% | 3.5732 | 6.8978 | 6 | 21.4395 | 7.9019 | 10.19% | 10.19%
5 | 134 | 14 | 3200 | 8 | 12.8 | 183.69 | 84.92 | 268.61 | 84.92 | 42.46 | 134 | 3200 | 480 | 132.1644 | 18.6754 | 15.2018 | 454.284 | 7.8248 | 62.6285 | 32.1145 | 32.1145 | 83.3488 | 96.6512 | 63.559 | 153.8576 | 153.8576 | 72.4838 | 226.3414 | 0.22544 | 22.54% | 102.3516 | 23.0742 | 16.1519 | 189.3849 | 189.3849 | 8.529% | 11.58% | 11.58% | 80% | 9.263% | 9.4812 | 6.5443 | 6 | 56.887 | 20.9668 | 30.04% | 30.04%
5 | 134 | 14 | 3201 | 9 | 16.3 | 354.81 | 90 | 444.81 | 90 | 45 | 134 | 3201 | 540 | 132.1644 | 18.6754 | 15.2018 | 514.284 | 8.8248 | 47.6285 | 42.1106 | 42.1106 | 70.6375 | 109.3625 | 49.6032 | 342.9121 | 342.9121 | 76.8198 | 419.7319 | 0.51097 | 51.1% | 189.8028 | 96.984 | 67.8888 | 203.3014 | 203.3014 | 33.39% | 11.43% | 11.43% | 85% | 9.715% | 18.4393 | 5.7206 | 5.7206 | 105.483 | 40.7769 | 51.89% | 51.89%
5 | 134 | 14 | 3202 | 10 | 20.1 | 499.25 | 104.25 | 603.5 | 104.25 | 52.13 | 134 | 3202 | 600 | 132.1644 | 18.6754 | 15.2018 | 574.284 | 9.8248 | 32.6285 | 51.2349 | 51.2349 | 54.6673 | 125.3327 | 36.1581 | 516.9687 | 516.9687 | 88.9829 | 605.9516 | 0.61498 | 61.5% | 274.0113 | 168.5113 | 117.9579 | 209.9113 | 209.9113 | 56.19% | 11.35% | 11.35% | 90% | 10.22% | 27.9926 | 4.9233 | 4.9233 | 137.8162 | 61.903 | 65.65% | 65.65%
5 | 134 | 14 | 3203 | 11 | 21.1 | 581.31 | 139.36 | 720.67 | 139.36 | 69.68 | 134 | 3203 | 660 | 132.1644 | 18.6754 | 15.2018 | 634.284 | 10.8248 | 17.6285 | 58.3904 | 58.3904 | 33.1877 | 146.8123 | 24.1664 | 622.7571 | 622.7571 | 118.9512 | 741.7083 | 0.65253 | 65.25% | 335.4005 | 218.8598 | 153.2019 | 202.4333 | 202.4333 | 75.68% | 11.35% | 11.35% | 90% | 10.21% | 34.2566 | 4.7303 | 4.7303 | 162.0443 | 75.7553 | 80.05% | 80.05%
5 | 134 | 14 | 3204 | 12 | 21.5 | 643.42 | 162.86 | 806.28 | 162.86 | 81.43 | 134 | 3204 | 720 | 132.1644 | 18.6754 | 15.2018 | 694.284 | 11.8248 | 2.6285 | 61.8145 | 61.8145 | 5.2777 | 174.7223 | 17.0927 | 697.736 | 697.736 | 139.0097 | 836.7457 | 0.67078 | 67.08% | 378.3764 | 253.8074 | 177.6652 | 186.766 | 186.766 | 95.13% | 11.36% | 11.36% | 95% | 10.79% | 40.8165 | 4.6551 | 4.6551 | 190.004 | 90.2621 | 101.7% | 101.7%
5 | 134 | 14 | 3205 | 13 | 20.4 | 518.06 | 256.86 | 774.92 | 256.86 | 128.43 | 134 | 3205 | 780 | 132.1644 | 18.6754 | 15.2018 | 754.284 | 12.8248 | -12.3715 | 60.1165 | 60.1165 | 24.0399 | 204.0399 | 20.7978 | 558.5699 | 558.5699 | 219.2437 | 777.8136 | 0.65759 | 65.76% | 351.7273 | 231.2931 | 161.9051 | 178.43 | 178.43 | 90.74% | 11.35% | 11.35% | 90% | 10.22% | 35.9337 | 4.8647 | 4.8647 | 174.8061 | 79.4642 | 97.97% | 97.97%
5 | 134 | 14 | 3206 | 14 | 20.1 | 384.25 | 262.31 | 646.56 | 262.31 | 131.16 | 134 | 3206 | 840 | 132.1644 | 18.6754 | 15.2018 | 814.284 | 13.8248 | -27.3715 | 54.0444 | 54.0444 | 47.8844 | 227.8844 | 31.6994 | 403.8761 | 403.8761 | 223.8956 | 627.7716 | 0.62155 | 62.15% | 283.8783 | 176.4443 | 123.511 | 169.4325 | 169.4325 | 72.9% | 11.35% | 11.35% | 90% | 10.22% | 29.0009 | 4.9233 | 4.9233 | 142.7804 | 64.1328 | 84.27% | 84.27%
5 | 134 | 14 | 3207 | 15 | 16.9 | 129.72 | 162.69 | 292.41 | 162.69 | 81.35 | 134 | 3207 | 900 | 132.1644 | 18.6754 | 15.2018 | 874.284 | 14.8248 | -42.3715 | 45.4502 | 45.4502 | 65.517 | 245.517 | 44.8065 | 129.1464 | 129.1464 | 138.8646 | 268.011 | 0.35012 | 35.01% | 121.1946 | 42.4326 | 29.7028 | 144.0798 | 144.0798 | 20.62% | 11.44% | 11.44% | 80% | 9.154% | 11.0944 | 5.588 | 5.588 | 61.9947 | 24.5342 | 43.03% | 43.03%
5 | 134 | 14 | 3208 | 16 | 15.7 | 74.64 | 98.89 | 173.53 | 98.89 | 49.45 | 134 | 3208 | 960 | 132.1644 | 18.6754 | 15.2018 | 934.284 | 15.8248 | -57.3715 | 35.6721 | 35.6721 | 79.1486 | 259.1486 | 58.6349 | 66.6203 | 66.6203 | 84.4079 | 151.0282 | -0.019328 | 0% | 68.2949 | 0 | 0 | 132.3627 | 132.3627 | 0% | 11.51% | 11.51% | 80% | 9.204% | 6.2861 | 5.8557 | 5.8557 | 36.8095 | 13.9012 | 27.81% | 27.81%
5 | 134 | 14 | 3209 | 17 | 15.5 | 110.36 | 91.75 | 202.11 | 91.75 | 45.88 | 134 | 3209 | 1020 | 132.1644 | 18.6754 | 15.2018 | 994.284 | 16.8248 | -72.3715 | 25.4557 | 25.4557 | 90.6486 | 270.6486 | 72.7407 | 76.1806 | 76.1806 | 78.3135 | 154.4942 | -0.0037825 | 0% | 69.8623 | 0 | 0 | 129.0229 | 129.0229 | 0% | 11.51% | 11.51% | 80% | 9.209% | 6.4339 | 5.9013 | 5.9013 | 37.9682 | 14.228 | 29.43% | 29.43%
5 | 134 | 14 | 3210 | 18 | 15 | 33.81 | 99.08 | 132.89 | 99.08 | 49.54 | 134 | 3210 | 1080 | 132.1644 | 18.6754 | 15.2018 | 1054.284 | 17.8248 | -87.3715 | 15.2534 | 15.2534 | 101.2142 | 281.2142 | 86.9412 | 6.8574 | 6.8574 | 84.5701 | 91.4275 | -0.57338 | 0% | 41.3435 | 0 | 0 | 161.184 | 161.184 | 0% | 11.55% | 11.55% | 80% | 9.237% | 3.8191 | 6.0165 | 6 | 22.9146 | 8.4456 | 14.22% | 14.22%
5 | 134 | 14 | 3211 | 19 | 14.6 | 49.25 | 60.83 | 110.08 | 60.83 | 30.42 | 134 | 3211 | 1140 | 132.1644 | 18.6754 | 15.2018 | 1114.284 | 18.8248 | -102.3715 | 5.4132 | 5.4132 | 111.6438 | 291.6438 | 101.1241 | 0 | 0 | 51.9217 | 51.9217 | -1.6389 | 0% | 23.479 | 0 | 0 | 154.8637 | 154.8637 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3212 | 20 | 14.3 | 21.19 | 31.94 | 53.13 | 31.94 | 15.97 | 134 | 3212 | 1200 | 132.1644 | 18.6754 | 15.2018 | 1174.284 | 19.8248 | -117.3715 | -3.7234 | 0 | 117.8768 | 297.8768 | 109.3066 | 0 | 0 | 27.2625 | 27.2625 | -3.8735 | 0% | 12.3281 | 0 | 0 | 142.9839 | 142.9839 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3213 | 21 | 13.5 | 0 | 1.58 | 1.58 | 1.58 | 0.79 | 134 | 3213 | 1260 | 132.1644 | 18.6754 | 15.2018 | 1234.284 | 20.8248 | -132.3715 | -11.7646 | 0 | 117.8768 | 297.8768 | 109.3066 | 0 | 0 | 1.3486 | 1.3486 | -95.1071 | 0% | 0.60984 | 0 | 0 | -10.0516 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3214 | 22 | 13 | 0 | 0 | 0 | 0 | 0 | 134 | 3214 | 1320 | 132.1644 | 18.6754 | 15.2018 | 1294.284 | 21.8248 | -147.3715 | -18.2429 | 0 | 117.8768 | 297.8768 | 109.3066 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.819 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3215 | 23 | 12.3 | 0 | 0 | 0 | 0 | 0 | 134 | 3215 | 1380 | 132.1644 | 18.6754 | 15.2018 | 1354.284 | 22.8248 | -162.3715 | -22.6417 | 0 | 117.8768 | 297.8768 | 109.3066 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9133 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
5 | 134 | 14 | 3216 | 24 | 12.7 | 0 | 0 | 0 | 0 | 0 | 134 | 3216 | 1440 | 132.1644 | 18.6754 | 15.2018 | 1414.284 | 23.8248 | -177.3715 | -24.5036 | 0 | 117.8768 | 297.8768 | 109.3066 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3311 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3217 | 1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 135 | 3217 | 60 | 133.1507 | 18.9152 | 15.0285 | 34.284 | 0.82187 | 167.6719 | -23.371 | 0 | 118.2525 | 61.7475 | 109.5552 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1125 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3218 | 2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 135 | 3218 | 120 | 133.1507 | 18.9152 | 15.0285 | 94.284 | 1.8219 | 152.6719 | -19.8353 | 0 | 118.2525 | 61.7475 | 109.5552 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2821 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3219 | 3 | 12.5 | 0 | 0 | 0 | 0 | 0 | 135 | 3219 | 180 | 133.1507 | 18.9152 | 15.0285 | 154.284 | 2.8219 | 137.6719 | -14.0477 | 0 | 118.2525 | 61.7475 | 109.5552 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9088 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3220 | 4 | 12.7 | 0 | 0 | 0 | 0 | 0 | 135 | 3220 | 240 | 133.1507 | 18.9152 | 15.0285 | 214.284 | 3.8219 | 122.6719 | -6.5172 | 0 | 118.2525 | 61.7475 | 109.5552 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.604 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3221 | 5 | 12.1 | 0 | 0 | 0 | 0 | 0 | 135 | 3221 | 300 | 133.1507 | 18.9152 | 15.0285 | 274.284 | 4.8219 | 107.6719 | 2.2672 | 2.2672 | 115.5692 | 64.4308 | 106.0798 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.5816 | 9.5816 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3222 | 6 | 11.8 | 1.86 | 10 | 11.86 | 10 | 5 | 135 | 3222 | 360 | 133.1507 | 18.9152 | 15.0285 | 334.284 | 5.8219 | 92.6719 | 11.8894 | 11.8894 | 105.0526 | 74.9474 | 91.9496 | -0.30714 | 0 | 8.5355 | 8.5355 | -14.8079 | 0% | 3.8598 | 0 | 0 | 24.1973 | 24.1973 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3223 | 7 | 12.5 | 39.92 | 55.75 | 95.67 | 55.75 | 27.88 | 135 | 3223 | 420 | 133.1507 | 18.9152 | 15.0285 | 394.284 | 6.8219 | 77.6719 | 21.9962 | 21.9962 | 94.6281 | 85.3719 | 77.7639 | 22.5892 | 22.5892 | 47.5856 | 70.1748 | -1.0719 | 0% | 31.7331 | 0 | 0 | 202.1482 | 202.1482 | 0% | 11.65% | 11.65% | 80% | 9.322% | 2.9583 | 6.6189 | 6 | 17.7498 | 6.542 | 8.781% | 8.781%
5 | 135 | 15 | 3224 | 8 | 12.9 | 177.42 | 89.25 | 266.67 | 89.25 | 44.63 | 135 | 3224 | 480 | 133.1507 | 18.9152 | 15.0285 | 454.284 | 7.8219 | 62.6719 | 32.2517 | 32.2517 | 83.5861 | 96.4139 | 63.6314 | 147.665 | 147.665 | 76.1796 | 223.8447 | 0.22001 | 22% | 101.2226 | 22.2703 | 15.5892 | 180.2637 | 180.2637 | 8.648% | 11.58% | 11.58% | 80% | 9.262% | 9.3748 | 6.5196 | 6 | 56.2489 | 20.7316 | 31.2% | 31.2%
5 | 135 | 15 | 3225 | 9 | 14.4 | 314.08 | 129.25 | 443.33 | 129.25 | 64.63 | 135 | 3225 | 540 | 133.1507 | 18.9152 | 15.0285 | 514.284 | 8.8219 | 47.6719 | 42.2577 | 42.2577 | 70.8989 | 109.1011 | 49.7019 | 302.0754 | 302.0754 | 110.3218 | 412.3972 | 0.49533 | 49.53% | 186.486 | 92.3728 | 64.6609 | 191.0034 | 191.0034 | 33.85% | 11.47% | 11.47% | 85% | 9.751% | 18.1836 | 6.1571 | 6 | 109.1019 | 40.2115 | 57.12% | 57.12%
5 | 135 | 15 | 3226 | 10 | 17 | 304.17 | 170.36 | 474.53 | 170.36 | 85.18 | 135 | 3226 | 600 | 133.1507 | 18.9152 | 15.0285 | 574.284 | 9.8219 | 32.6719 | 51.404 | 51.404 | 54.947 | 125.053 | 36.2936 | 313.6776 | 313.6776 | 145.4114 | 459.089 | 0.53952 | 53.95% | 207.6 | 112.0039 | 78.4028 | 190.6443 | 190.6443 | 41.13% | 11.41% | 11.41% | 85% | 9.697% | 20.131 | 5.5661 | 5.5661 | 112.0512 | 44.5179 | 58.77% | 58.77%
5 | 135 | 15 | 3227 | 11 | 19 | 569.64 | 151.39 | 721.03 | 151.39 | 75.7 | 135 | 3227 | 660 | 133.1507 | 18.9152 | 15.0285 | 634.284 | 10.8219 | 17.6719 | 58.5941 | 58.5941 | 33.442 | 146.558 | 24.3585 | 608.0063 | 608.0063 | 129.2194 | 737.2258 | 0.64534 | 64.53% | 333.3735 | 215.1406 | 150.5984 | 191.9134 | 191.9134 | 78.47% | 11.36% | 11.36% | 90% | 10.22% | 34.0705 | 5.1437 | 5.1437 | 175.2482 | 75.3438 | 91.32% | 91.32%
5 | 135 | 15 | 3228 | 12 | 19.9 | 494.17 | 224.53 | 718.7 | 224.53 | 112.27 | 135 | 3228 | 720 | 133.1507 | 18.9152 | 15.0285 | 694.284 | 11.8219 | 2.6719 | 62.051 | 62.051 | 5.399 | 174.601 | 17.3359 | 534.0057 | 534.0057 | 191.6483 | 725.6541 | 0.64555 | 64.56% | 328.1408 | 211.8323 | 148.2826 | 175.6897 | 175.6897 | 84.4% | 11.35% | 11.35% | 90% | 10.22% | 33.5267 | 4.9628 | 4.9628 | 166.3848 | 74.1413 | 94.7% | 94.7%
5 | 135 | 15 | 3229 | 13 | 18 | 140.42 | 236.94 | 377.36 | 236.94 | 118.47 | 135 | 3229 | 780 | 133.1507 | 18.9152 | 15.0285 | 754.284 | 12.8219 | -12.3281 | 60.3577 | 60.3577 | 24.1034 | 204.1034 | 20.9651 | 150.8681 | 150.8681 | 202.2409 | 353.109 | 0.46647 | 46.65% | 159.6759 | 74.4834 | 52.1384 | 154.9229 | 154.9229 | 33.65% | 11.4% | 11.4% | 85% | 9.691% | 15.4742 | 5.3514 | 5.3514 | 82.8084 | 34.2197 | 53.45% | 53.45%
5 | 135 | 15 | 3230 | 14 | 15.6 | 223.06 | 245.64 | 468.7 | 245.64 | 122.82 | 135 | 3230 | 840 | 133.1507 | 18.9152 | 15.0285 | 814.284 | 13.8219 | -27.3281 | 54.2687 | 54.2687 | 48.0453 | 228.0453 | 31.7805 | 233.5863 | 233.5863 | 209.6669 | 443.2531 | 0.52296 | 52.3% | 200.4391 | 104.8217 | 73.3752 | 152.3585 | 152.3585 | 48.16% | 11.44% | 11.44% | 85% | 9.723% | 19.4879 | 5.8784 | 5.8784 | 114.5582 | 43.0957 | 75.19% | 75.19%
5 | 135 | 15 | 3231 | 15 | 16.7 | 290.08 | 259.53 | 549.61 | 259.53 | 129.77 | 135 | 3231 | 900 | 133.1507 | 18.9152 | 15.0285 | 874.284 | 14.8219 | -42.3281 | 45.6576 | 45.6576 | 65.6985 | 245.6985 | 44.8383 | 287.6152 | 287.6152 | 221.5227 | 509.1379 | 0.5642 | 56.42% | 230.2322 | 129.8959 | 90.9271 | 153.4688 | 153.4688 | 59.25% | 11.4% | 11.4% | 90% | 10.26% | 23.6317 | 5.6319 | 5.6319 | 133.0911 | 52.2595 | 86.72% | 86.72%
5 | 135 | 15 | 3232 | 16 | 17.9 | 243.25 | 254.64 | 497.89 | 254.64 | 127.32 | 135 | 3232 | 960 | 133.1507 | 18.9152 | 15.0285 | 934.284 | 15.8219 | -57.3281 | 35.87 | 35.87 | 79.3231 | 259.3231 | 58.635 | 216.0752 | 216.0752 | 217.3488 | 433.424 | 0.5285 | 52.85% | 195.9943 | 103.5826 | 72.5078 | 149.8962 | 149.8962 | 48.37% | 11.39% | 11.39% | 85% | 9.685% | 18.9824 | 5.3726 | 5.3726 | 101.9841 | 41.9779 | 68.04% | 68.04%
5 | 135 | 15 | 3233 | 17 | 16.2 | 225.83 | 161.47 | 387.3 | 161.47 | 80.74 | 135 | 3233 | 1020 | 133.1507 | 18.9152 | 15.0285 | 994.284 | 16.8219 | -72.3281 | 25.6509 | 25.6509 | 90.8094 | 270.8094 | 72.7169 | 154.9883 | 154.9883 | 137.8233 | 292.8116 | 0.38319 | 38.32% | 132.4094 | 50.738 | 35.5166 | 138.7064 | 138.7064 | 25.61% | 11.46% | 11.46% | 80% | 9.166% | 12.1372 | 5.7429 | 5.7429 | 69.7026 | 26.8403 | 50.25% | 50.25%
5 | 135 | 15 | 3234 | 18 | 16.6 | 124.44 | 129.64 | 254.08 | 129.64 | 64.82 | 135 | 3234 | 1080 | 133.1507 | 18.9152 | 15.0285 | 1054.284 | 17.8219 | -87.3281 | 15.4515 | 15.4515 | 101.3606 | 281.3606 | 86.8967 | 25.2855 | 25.2855 | 110.6547 | 135.9402 | -0.095795 | 0% | 61.4721 | 0 | 0 | 127.6828 | 127.6828 | 0% | 11.48% | 11.48% | 80% | 9.181% | 5.6437 | 5.6539 | 5.6539 | 31.9093 | 12.4806 | 24.99% | 24.99%
5 | 135 | 15 | 3235 | 19 | 16.4 | 66.39 | 95 | 161.39 | 95 | 47.5 | 135 | 3235 | 1140 | 133.1507 | 18.9152 | 15.0285 | 1114.284 | 18.8219 | -102.3281 | 5.6184 | 5.6184 | 111.7752 | 291.7752 | 101.0593 | 0 | 0 | 81.0876 | 81.0876 | -0.71002 | 0% | 36.6678 | 0 | 0 | 117.6907 | 117.6907 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3236 | 20 | 15.3 | 23.06 | 39.44 | 62.5 | 39.44 | 19.72 | 135 | 3236 | 1200 | 133.1507 | 18.9152 | 15.0285 | 1174.284 | 19.8219 | -117.3281 | -3.5083 | 0 | 118.2525 | 298.2525 | 109.5552 | 0 | 0 | 33.6641 | 33.6641 | -2.9166 | 0% | 15.2229 | 0 | 0 | 144.5234 | 144.5234 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3237 | 21 | 14.8 | 0 | 1.67 | 1.67 | 1.67 | 0.84 | 135 | 3237 | 1260 | 133.1507 | 18.9152 | 15.0285 | 1234.284 | 20.8219 | -132.3281 | -11.5382 | 0 | 118.2525 | 298.2525 | 109.5552 | 0 | 0 | 1.4254 | 1.4254 | -87.8594 | 0% | 0.64458 | 0 | 0 | -8.5711 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3238 | 22 | 13.5 | 0 | 0 | 0 | 0 | 0 | 135 | 3238 | 1320 | 133.1507 | 18.9152 | 15.0285 | 1294.284 | 21.8219 | -147.3281 | -18.0061 | 0 | 118.2525 | 298.2525 | 109.5552 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5372 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3239 | 23 | 12.3 | 0 | 0 | 0 | 0 | 0 | 135 | 3239 | 1380 | 133.1507 | 18.9152 | 15.0285 | 1354.284 | 22.8219 | -162.3281 | -22.3988 | 0 | 118.2525 | 298.2525 | 109.5552 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5355 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
5 | 135 | 15 | 3240 | 24 | 11.4 | 0 | 0 | 0 | 0 | 0 | 135 | 3240 | 1440 | 133.1507 | 18.9152 | 15.0285 | 1414.284 | 23.8219 | -177.3281 | -24.2625 | 0 | 118.2525 | 298.2525 | 109.5552 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0766 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3241 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 136 | 3241 | 60 | 134.137 | 19.1491 | 14.8428 | 34.284 | 0.81878 | 167.7183 | -23.147 | 0 | 118.6197 | 61.3803 | 109.7977 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3744 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3242 | 2 | 10.6 | 0 | 0 | 0 | 0 | 0 | 136 | 3242 | 120 | 134.137 | 19.1491 | 14.8428 | 94.284 | 1.8188 | 152.7183 | -19.6294 | 0 | 118.6197 | 61.3803 | 109.7977 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4025 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3243 | 3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 136 | 3243 | 180 | 134.137 | 19.1491 | 14.8428 | 154.284 | 2.8188 | 137.7183 | -13.8627 | 0 | 118.6197 | 61.3803 | 109.7977 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9735 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3244 | 4 | 10.2 | 0 | 0 | 0 | 0 | 0 | 136 | 3244 | 240 | 134.137 | 19.1491 | 14.8428 | 214.284 | 3.8188 | 122.7183 | -6.3521 | 0 | 118.6197 | 61.3803 | 109.7977 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4306 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3245 | 5 | 9.4 | 0 | 0 | 0 | 0 | 0 | 136 | 3245 | 300 | 134.137 | 19.1491 | 14.8428 | 274.284 | 4.8188 | 107.7183 | 2.4157 | 2.4157 | 115.7554 | 64.2446 | 106.0921 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.6386 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3246 | 6 | 9.6 | 0.56 | 7.5 | 8.06 | 7.5 | 3.75 | 136 | 3246 | 360 | 134.137 | 19.1491 | 14.8428 | 334.284 | 5.8188 | 92.7183 | 12.026 | 12.026 | 105.2519 | 74.7481 | 91.983 | -0.093001 | 0 | 6.4017 | 6.4017 | -20.8111 | 0% | 2.8948 | 0 | 0 | 10.0802 | 10.0802 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3247 | 7 | 10.8 | 19.81 | 40.83 | 60.64 | 40.83 | 20.42 | 136 | 3247 | 420 | 134.137 | 19.1491 | 14.8428 | 394.284 | 6.8188 | 77.7183 | 22.1264 | 22.1264 | 94.8431 | 85.1569 | 77.8173 | 11.0991 | 11.0991 | 34.8506 | 45.9497 | -2.1465 | 0% | 20.7784 | 0 | 0 | 179.6995 | 179.6995 | 0% | 11.73% | 11.73% | 80% | 9.387% | 1.9504 | 7.0535 | 6 | 11.7026 | 4.3132 | 6.512% | 6.512%
5 | 136 | 16 | 3248 | 8 | 13.4 | 90.36 | 86.67 | 177.03 | 86.67 | 43.34 | 136 | 3248 | 480 | 134.137 | 19.1491 | 14.8428 | 454.284 | 7.8188 | 62.7183 | 32.3825 | 32.3825 | 83.8215 | 96.1785 | 63.7063 | 74.7374 | 74.7374 | 73.9775 | 148.7149 | -0.067304 | 0% | 67.2489 | 0 | 0 | 156.0173 | 156.0173 | 0% | 11.59% | 11.59% | 80% | 9.271% | 6.2345 | 6.397 | 6 | 37.4068 | 13.787 | 23.98% | 23.98%
5 | 136 | 16 | 3249 | 9 | 15.7 | 157.86 | 141.86 | 299.72 | 141.86 | 70.93 | 136 | 3249 | 540 | 134.137 | 19.1491 | 14.8428 | 514.284 | 8.8188 | 47.7183 | 42.3981 | 42.3981 | 71.159 | 108.841 | 49.8027 | 151.1043 | 151.1043 | 121.0851 | 272.1894 | 0.34716 | 34.72% | 123.084 | 42.7304 | 29.9113 | 165.8688 | 165.8688 | 18.03% | 11.48% | 11.48% | 80% | 9.181% | 11.3009 | 5.8557 | 5.8557 | 66.1745 | 24.991 | 39.9% | 39.9%
5 | 136 | 16 | 3250 | 10 | 17.8 | 287.42 | 214.36 | 501.78 | 214.36 | 107.18 | 136 | 3250 | 600 | 134.137 | 19.1491 | 14.8428 | 574.284 | 9.8188 | 32.7183 | 51.5661 | 51.5661 | 55.2269 | 124.7731 | 36.4303 | 295.2185 | 295.2185 | 182.9677 | 478.1862 | 0.55382 | 55.38% | 216.2358 | 119.7559 | 83.8292 | 175.0325 | 175.0325 | 47.89% | 11.39% | 11.39% | 85% | 9.682% | 20.9366 | 5.3938 | 5.3938 | 112.9274 | 46.2994 | 64.52% | 64.52%
5 | 136 | 16 | 3251 | 11 | 18.6 | 434.17 | 204.08 | 638.25 | 204.08 | 102.04 | 136 | 3251 | 660 | 134.137 | 19.1491 | 14.8428 | 634.284 | 10.8188 | 17.7183 | 58.7909 | 58.7909 | 33.6998 | 146.3002 | 24.5497 | 461.7442 | 461.7442 | 174.1932 | 635.9374 | 0.61868 | 61.87% | 287.5709 | 177.9143 | 124.54 | 173.2504 | 173.2504 | 71.88% | 11.36% | 11.36% | 90% | 10.23% | 29.4132 | 5.2259 | 5.2259 | 153.7118 | 65.0448 | 88.72% | 88.72%
5 | 136 | 16 | 3252 | 12 | 19.9 | 259.53 | 273.97 | 533.5 | 273.97 | 136.99 | 136 | 3252 | 720 | 134.137 | 19.1491 | 14.8428 | 694.284 | 11.8188 | 2.7183 | 62.2813 | 62.2813 | 5.5273 | 174.4727 | 17.5739 | 279.4911 | 279.4911 | 233.848 | 513.3391 | 0.58002 | 58% | 232.132 | 134.6412 | 94.2488 | 158.4552 | 158.4552 | 59.48% | 11.35% | 11.35% | 90% | 10.22% | 23.7198 | 4.9628 | 4.9628 | 117.7153 | 52.4541 | 74.29% | 74.29%
5 | 136 | 16 | 3253 | 13 | 19.8 | 162.03 | 331.11 | 493.14 | 331.11 | 165.56 | 136 | 3253 | 780 | 134.137 | 19.1491 | 14.8428 | 754.284 | 12.8188 | -12.2817 | 60.5942 | 60.5942 | 24.159 | 204.159 | 21.1274 | 173.4903 | 173.4903 | 282.6201 | 456.1104 | 0.55143 | 55.14% | 206.2531 | 113.735 | 79.6145 | 154.4809 | 154.4809 | 51.54% | 11.36% | 11.36% | 85% | 9.652% | 19.9084 | 4.9826 | 4.9826 | 99.1952 | 44.0257 | 64.21% | 64.21%
5 | 136 | 16 | 3254 | 14 | 20.8 | 343.06 | 312.97 | 656.03 | 312.97 | 156.49 | 136 | 3254 | 840 | 134.137 | 19.1491 | 14.8428 | 814.284 | 13.8188 | -27.2817 | 54.4894 | 54.4894 | 48.1986 | 228.1986 | 31.8579 | 357.9592 | 357.9592 | 267.1366 | 625.0958 | 0.62323 | 62.32% | 282.6683 | 176.1663 | 123.3164 | 160.7773 | 160.7773 | 76.7% | 11.34% | 11.34% | 90% | 10.21% | 28.8601 | 4.7875 | 4.7875 | 138.167 | 63.8215 | 85.94% | 85.94%
5 | 136 | 16 | 3255 | 15 | 20.1 | 164.72 | 263.42 | 428.14 | 263.42 | 131.71 | 136 | 3255 | 900 | 134.137 | 19.1491 | 14.8428 | 874.284 | 14.8188 | -42.2817 | 45.8623 | 45.8623 | 65.8729 | 245.8729 | 44.8667 | 162.6732 | 162.6732 | 224.843 | 387.5163 | 0.50843 | 50.84% | 175.2349 | 89.095 | 62.3665 | 147.1404 | 147.1404 | 42.39% | 11.35% | 11.35% | 85% | 9.647% | 16.9054 | 4.9233 | 4.9233 | 83.2305 | 37.3847 | 56.57% | 56.57%
5 | 136 | 16 | 3256 | 16 | 19.8 | 288.89 | 255.08 | 543.97 | 255.08 | 127.54 | 136 | 3256 | 960 | 134.137 | 19.1491 | 14.8428 | 934.284 | 15.8188 | -57.2817 | 36.0655 | 36.0655 | 79.4909 | 259.4909 | 58.6319 | 255.4347 | 255.4347 | 217.7244 | 473.1591 | 0.56053 | 56.05% | 213.9626 | 119.9334 | 83.9534 | 149.5541 | 149.5541 | 56.14% | 11.36% | 11.36% | 85% | 9.652% | 20.6522 | 4.9826 | 4.9826 | 102.9013 | 45.6705 | 68.81% | 68.81%
5 | 136 | 16 | 3257 | 17 | 20.1 | 187.31 | 187.42 | 374.73 | 187.42 | 93.71 | 136 | 3257 | 1020 | 134.137 | 19.1491 | 14.8428 | 994.284 | 16.8188 | -72.2817 | 25.844 | 25.844 | 90.964 | 270.964 | 72.6903 | 127.8477 | 127.8477 | 159.973 | 287.8207 | 0.40605 | 40.61% | 130.1525 | 52.8488 | 36.9942 | 139.4978 | 139.4978 | 26.52% | 11.35% | 11.35% | 80% | 9.079% | 11.817 | 4.9233 | 4.9233 | 58.1788 | 26.1322 | 41.71% | 41.71%
5 | 136 | 16 | 3258 | 18 | 19.7 | 48.14 | 140.36 | 188.5 | 140.36 | 70.18 | 136 | 3258 | 1080 | 134.137 | 19.1491 | 14.8428 | 1054.284 | 17.8188 | -87.2817 | 15.6474 | 15.6474 | 101.501 | 281.501 | 86.8496 | 9.809 | 9.809 | 119.8048 | 129.6138 | -0.08648 | 0% | 58.6113 | 0 | 0 | 125.3922 | 125.3922 | 0% | 11.36% | 11.36% | 80% | 9.09% | 5.328 | 5.0025 | 5.0025 | 26.6534 | 11.7825 | 21.26% | 21.26%
5 | 136 | 16 | 3259 | 19 | 19.3 | 47.22 | 89.31 | 136.53 | 89.31 | 44.66 | 136 | 3259 | 1140 | 134.137 | 19.1491 | 14.8428 | 1114.284 | 18.8188 | -102.2817 | 5.821 | 5.821 | 111.9006 | 291.9006 | 100.9921 | 0 | 0 | 76.2309 | 76.2309 | -0.72165 | 0% | 34.4716 | 0 | 0 | 159.8315 | 159.8315 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0828 | 5.0828 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3260 | 20 | 17.8 | 4.72 | 42.31 | 47.03 | 42.31 | 21.16 | 136 | 3260 | 1200 | 134.137 | 19.1491 | 14.8428 | 1174.284 | 19.8188 | -117.2817 | -3.2961 | 0 | 118.6197 | 298.6197 | 109.7977 | 0 | 0 | 36.1138 | 36.1138 | -2.5086 | 0% | 16.3307 | 0 | 0 | 145.1593 | 145.1593 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3261 | 21 | 15.5 | 0 | 3.06 | 3.06 | 3.06 | 1.53 | 136 | 3261 | 1260 | 134.137 | 19.1491 | 14.8428 | 1234.284 | 20.8188 | -132.2817 | -11.3152 | 0 | 118.6197 | 298.6197 | 109.7977 | 0 | 0 | 2.6119 | 2.6119 | -46.9769 | 0% | 1.1811 | 0 | 0 | -8.5069 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3262 | 22 | 13.6 | 0 | 0 | 0 | 0 | 0 | 136 | 3262 | 1320 | 134.137 | 19.1491 | 14.8428 | 1294.284 | 21.8188 | -147.2817 | -17.7735 | 0 | 118.6197 | 298.6197 | 109.7977 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1564 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3263 | 23 | 11.8 | 0 | 0 | 0 | 0 | 0 | 136 | 3263 | 1380 | 134.137 | 19.1491 | 14.8428 | 1354.284 | 22.8188 | -162.2817 | -22.161 | 0 | 118.6197 | 298.6197 | 109.7977 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3181 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
5 | 136 | 16 | 3264 | 24 | 15.6 | 0 | 0 | 0 | 0 | 0 | 136 | 3264 | 1440 | 134.137 | 19.1491 | 14.8428 | 1414.284 | 23.8188 | -177.2817 | -24.0272 | 0 | 118.6197 | 298.6197 | 109.7977 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.9455 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3265 | 1 | 11.1 | 0 | 0 | 0 | 0 | 0 | 137 | 3265 | 60 | 135.1233 | 19.3772 | 14.6449 | 34.284 | 0.81548 | 167.7678 | -22.9292 | 0 | 118.9785 | 61.0215 | 110.0341 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1797 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3266 | 2 | 10.1 | 0 | 0 | 0 | 0 | 0 | 137 | 3266 | 120 | 135.1233 | 19.3772 | 14.6449 | 94.284 | 1.8155 | 152.7678 | -19.4299 | 0 | 118.9785 | 61.0215 | 110.0341 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0359 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3267 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 137 | 3267 | 180 | 135.1233 | 19.3772 | 14.6449 | 154.284 | 2.8155 | 137.7678 | -13.684 | 0 | 118.9785 | 61.0215 | 110.0341 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2826 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3268 | 4 | 8.9 | 0 | 0 | 0 | 0 | 0 | 137 | 3268 | 240 | 135.1233 | 19.3772 | 14.6449 | 214.284 | 3.8155 | 122.7678 | -6.1933 | 0 | 118.9785 | 61.0215 | 110.0341 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.197 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3269 | 5 | 8.8 | 0 | 0 | 0 | 0 | 0 | 137 | 3269 | 300 | 135.1233 | 19.3772 | 14.6449 | 274.284 | 4.8155 | 107.7678 | 2.558 | 2.558 | 115.9398 | 64.0602 | 106.1075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.79145 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3270 | 6 | 8.4 | 0.75 | 9.44 | 10.19 | 9.44 | 4.72 | 137 | 3270 | 360 | 135.1233 | 19.3772 | 14.6449 | 334.284 | 5.8155 | 92.7678 | 12.1563 | 12.1563 | 105.4492 | 74.5508 | 92.0193 | -0.1255 | 0 | 8.0575 | 8.0575 | -16.7188 | 0% | 3.6436 | 0 | 0 | 11.1766 | 11.1766 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3271 | 7 | 9.8 | 29.53 | 47.31 | 76.84 | 47.31 | 23.66 | 137 | 3271 | 420 | 135.1233 | 19.3772 | 14.6449 | 394.284 | 6.8155 | 77.7678 | 22.2503 | 22.2503 | 95.056 | 84.944 | 77.8735 | 16.3828 | 16.3828 | 40.3816 | 56.7644 | -1.6254 | 0% | 25.6689 | 0 | 0 | 184.1128 | 184.1128 | 0% | 11.77% | 11.77% | 80% | 9.415% | 2.4168 | 7.3186 | 6 | 14.5006 | 5.3445 | 7.876% | 7.876%
5 | 137 | 17 | 3272 | 8 | 13.7 | 86.86 | 92.78 | 179.64 | 92.78 | 46.39 | 137 | 3272 | 480 | 135.1233 | 19.3772 | 14.6449 | 454.284 | 7.8155 | 62.7678 | 32.5067 | 32.5067 | 84.0548 | 95.9452 | 63.7835 | 71.4025 | 71.4025 | 79.1927 | 150.5952 | -0.051869 | 0% | 68.0991 | 0 | 0 | 162.1932 | 162.1932 | 0% | 11.58% | 11.58% | 80% | 9.262% | 6.3071 | 6.3243 | 6 | 37.8425 | 13.9475 | 23.33% | 23.33%
5 | 137 | 17 | 3273 | 9 | 17.1 | 181.31 | 128.97 | 310.28 | 128.97 | 64.49 | 137 | 3273 | 540 | 135.1233 | 19.3772 | 14.6449 | 514.284 | 8.8155 | 47.7678 | 42.5317 | 42.5317 | 71.4174 | 108.5826 | 49.9053 | 172.7419 | 172.7419 | 110.0828 | 282.8247 | 0.37548 | 37.55% | 127.8933 | 48.0211 | 33.6147 | 174.1975 | 174.1975 | 19.3% | 11.43% | 11.43% | 80% | 9.148% | 11.6992 | 5.5443 | 5.5443 | 64.8638 | 25.8716 | 37.24% | 37.24%
5 | 137 | 17 | 3274 | 10 | 18.4 | 344.72 | 146.31 | 491.03 | 146.31 | 73.16 | 137 | 3274 | 600 | 135.1233 | 19.3772 | 14.6449 | 574.284 | 9.8155 | 32.7678 | 51.7213 | 51.7213 | 55.5067 | 124.4933 | 36.5678 | 352.6884 | 352.6884 | 124.8834 | 477.5718 | 0.5563 | 55.63% | 215.958 | 120.1366 | 84.0956 | 180.4477 | 180.4477 | 46.6% | 11.38% | 11.38% | 85% | 9.673% | 20.8903 | 5.2675 | 5.2675 | 110.0392 | 46.197 | 60.98% | 60.98%
5 | 137 | 17 | 3275 | 11 | 20.4 | 424.92 | 207.03 | 631.95 | 207.03 | 103.52 | 137 | 3275 | 660 | 135.1233 | 19.3772 | 14.6449 | 634.284 | 10.8155 | 17.7678 | 58.9807 | 58.9807 | 33.9607 | 146.0393 | 24.7395 | 450.319 | 450.319 | 176.7112 | 627.0302 | 0.62238 | 62.24% | 283.543 | 176.4729 | 123.531 | 179.7721 | 179.7721 | 68.72% | 11.35% | 11.35% | 90% | 10.21% | 28.9593 | 4.8647 | 4.8647 | 140.8778 | 64.0409 | 78.36% | 78.36%
5 | 137 | 17 | 3276 | 12 | 21.6 | 233.47 | 314.86 | 548.33 | 314.86 | 157.43 | 137 | 3276 | 720 | 135.1233 | 19.3772 | 14.6449 | 694.284 | 11.8155 | 2.7678 | 62.5055 | 62.5055 | 5.6626 | 174.3374 | 17.8065 | 250.5882 | 250.5882 | 268.7498 | 519.338 | 0.58978 | 58.98% | 234.8446 | 138.5065 | 96.9545 | 164.4956 | 164.4956 | 58.94% | 11.33% | 11.33% | 90% | 10.19% | 23.9414 | 4.6364 | 4.6364 | 111.0029 | 52.9443 | 67.48% | 67.48%
5 | 137 | 17 | 3277 | 13 | 22.1 | 166.39 | 212.78 | 379.17 | 212.78 | 106.39 | 137 | 3277 | 780 | 135.1233 | 19.3772 | 14.6449 | 754.284 | 12.8155 | -12.2322 | 60.8258 | 60.8258 | 24.2064 | 204.2064 | 21.2847 | 177.5659 | 177.5659 | 181.6191 | 359.1849 | 0.49729 | 49.73% | 162.4234 | 80.7718 | 56.5403 | 154.5408 | 154.5408 | 36.59% | 11.3% | 11.3% | 85% | 9.606% | 15.6023 | 4.5443 | 4.5443 | 70.9016 | 34.503 | 45.88% | 45.88%
5 | 137 | 17 | 3278 | 14 | 22.2 | 415.83 | 162.78 | 578.61 | 162.78 | 81.39 | 137 | 3278 | 840 | 135.1233 | 19.3772 | 14.6449 | 814.284 | 13.8155 | -27.2322 | 54.7064 | 54.7064 | 48.344 | 228.344 | 31.9313 | 432.378 | 432.378 | 138.9414 | 571.3195 | 0.61155 | 61.16% | 258.3507 | 157.9956 | 110.5969 | 160.2064 | 160.2064 | 69.03% | 11.32% | 11.32% | 90% | 10.19% | 26.3308 | 4.5261 | 4.5261 | 119.176 | 58.2283 | 74.39% | 74.39%
5 | 137 | 17 | 3279 | 15 | 23.1 | 411.03 | 139.17 | 550.2 | 139.17 | 69.59 | 137 | 3279 | 900 | 135.1233 | 19.3772 | 14.6449 | 874.284 | 14.8155 | -42.2322 | 46.064 | 46.064 | 66.0399 | 246.0399 | 44.8916 | 404.3674 | 404.3674 | 118.789 | 523.1565 | 0.59756 | 59.76% | 236.5713 | 141.3663 | 98.9564 | 279.3279 | 279.3279 | 35.43% | 11.3% | 11.3% | 90% | 10.17% | 24.0695 | 4.3653 | 4.3653 | 105.071 | 53.2276 | 37.62% | 37.62%
5 | 137 | 17 | 3280 | 16 | 23.9 | 243.33 | 127.42 | 370.75 | 127.42 | 63.71 | 137 | 3280 | 960 | 135.1233 | 19.3772 | 14.6449 | 934.284 | 15.8155 | -57.2322 | 36.2586 | 36.2586 | 79.6519 | 259.6519 | 58.6258 | 214.1987 | 214.1987 | 108.7598 | 322.9585 | 0.47493 | 47.49% | 146.0418 | 69.3598 | 48.5519 | 277.3134 | 277.3134 | 17.51% | 11.25% | 11.25% | 85% | 9.562% | 13.9648 | 4.2272 | 4.2272 | 59.0316 | 30.882 | 21.29% | 21.29%
5 | 137 | 17 | 3281 | 17 | 23.7 | 152.5 | 127.69 | 280.19 | 127.69 | 63.85 | 137 | 3281 | 1020 | 135.1233 | 19.3772 | 14.6449 | 994.284 | 16.8155 | -72.2322 | 26.0349 | 26.0349 | 91.1122 | 271.1122 | 72.6607 | 103.5489 | 103.5489 | 108.9902 | 212.5392 | 0.30195 | 30.19% | 96.1102 | 29.0204 | 20.3143 | 264.5064 | 264.5064 | 7.68% | 11.23% | 11.23% | 80% | 8.986% | 8.6364 | 4.2613 | 4.2613 | 36.8022 | 19.0987 | 13.91% | 13.91%
5 | 137 | 17 | 3282 | 18 | 23.5 | 110.83 | 67.14 | 177.97 | 67.14 | 33.57 | 137 | 3282 | 1080 | 135.1233 | 19.3772 | 14.6449 | 1054.284 | 17.8155 | -87.2322 | 15.8411 | 15.8411 | 101.6353 | 281.6353 | 86.7998 | 22.6658 | 22.6658 | 57.3076 | 79.9734 | -0.53565 | 0% | 36.164 | 0 | 0 | 247.6338 | 247.6338 | 0% | 11.21% | 11.21% | 80% | 8.971% | 3.2442 | 4.2957 | 4.2957 | 13.9359 | 7.1742 | 5.628% | 5.628%
5 | 137 | 17 | 3283 | 19 | 22.5 | 65.08 | 36.39 | 101.47 | 36.39 | 18.2 | 137 | 3283 | 1140 | 135.1233 | 19.3772 | 14.6449 | 1114.284 | 18.8155 | -102.2322 | 6.0212 | 6.0212 | 112.0202 | 292.0202 | 100.9226 | 0 | 0 | 31.0608 | 31.0608 | -2.7148 | 0% | 14.0457 | 0 | 0 | 163.4981 | 163.4981 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.4719 | 4.4719 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3284 | 20 | 20.9 | 18.33 | 25 | 43.33 | 25 | 12.5 | 137 | 3284 | 1200 | 135.1233 | 19.3772 | 14.6449 | 1174.284 | 19.8155 | -117.2322 | -3.0869 | 0 | 118.9785 | 298.9785 | 110.0341 | 0 | 0 | 21.3388 | 21.3388 | -4.4813 | 0% | 9.6494 | 0 | 0 | 150.3414 | 150.3414 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7684 | 4.7684 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3285 | 21 | 18.4 | 0 | 1.81 | 1.81 | 1.81 | 0.91 | 137 | 3285 | 1260 | 135.1233 | 19.3772 | 14.6449 | 1234.284 | 20.8155 | -132.2322 | -11.0958 | 0 | 118.9785 | 298.9785 | 110.0341 | 0 | 0 | 1.5449 | 1.5449 | -75.7665 | 0% | 0.69862 | 0 | 0 | -4.3034 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3286 | 22 | 15.4 | 0 | 0 | 0 | 0 | 0 | 137 | 3286 | 1320 | 135.1233 | 19.3772 | 14.6449 | 1294.284 | 21.8155 | -147.2322 | -17.5452 | 0 | 118.9785 | 298.9785 | 110.0341 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6296 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3287 | 23 | 14.2 | 0 | 0 | 0 | 0 | 0 | 137 | 3287 | 1380 | 135.1233 | 19.3772 | 14.6449 | 1354.284 | 22.8155 | -162.2322 | -21.9283 | 0 | 118.9785 | 298.9785 | 110.0341 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7907 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
5 | 137 | 17 | 3288 | 24 | 13.2 | 0 | 0 | 0 | 0 | 0 | 137 | 3288 | 1440 | 135.1233 | 19.3772 | 14.6449 | 1414.284 | 23.8155 | -177.2322 | -23.7976 | 0 | 118.9785 | 298.9785 | 110.0341 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.647 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3289 | 1 | 12.2 | 0 | 0 | 0 | 0 | 0 | 138 | 3289 | 60 | 136.1096 | 19.5993 | 14.4351 | 34.284 | 0.81198 | 167.8202 | -22.7176 | 0 | 119.3286 | 60.6714 | 110.2644 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4486 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3290 | 2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 138 | 3290 | 120 | 136.1096 | 19.5993 | 14.4351 | 94.284 | 1.812 | 152.8202 | -19.2368 | 0 | 119.3286 | 60.6714 | 110.2644 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5198 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3291 | 3 | 11.1 | 0 | 0 | 0 | 0 | 0 | 138 | 3291 | 180 | 136.1096 | 19.5993 | 14.4351 | 154.284 | 2.812 | 137.8202 | -13.5118 | 0 | 119.3286 | 60.6714 | 110.2644 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7435 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3292 | 4 | 10.4 | 0 | 0 | 0 | 0 | 0 | 138 | 3292 | 240 | 136.1096 | 19.5993 | 14.4351 | 214.284 | 3.812 | 122.8202 | -6.0408 | 0 | 119.3286 | 60.6714 | 110.2644 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8103 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3293 | 5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 138 | 3293 | 300 | 136.1096 | 19.5993 | 14.4351 | 274.284 | 4.812 | 107.8202 | 2.694 | 2.694 | 116.1225 | 63.8775 | 106.1262 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.36982 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3294 | 6 | 8.7 | 1.47 | 10.83 | 12.3 | 10.83 | 5.42 | 138 | 3294 | 360 | 136.1096 | 19.5993 | 14.4351 | 334.284 | 5.812 | 92.8202 | 12.2803 | 12.2803 | 105.6444 | 74.3556 | 92.0586 | -0.24827 | 0 | 9.244 | 9.244 | -14.3934 | 0% | 4.1801 | 0 | 0 | 13.1082 | 13.1082 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3295 | 7 | 10.1 | 43.69 | 57.5 | 101.19 | 57.5 | 28.75 | 138 | 3295 | 420 | 136.1096 | 19.5993 | 14.4351 | 394.284 | 6.812 | 77.8202 | 22.3678 | 22.3678 | 95.2666 | 84.7334 | 77.9323 | 24.0025 | 24.0025 | 49.0793 | 73.0818 | -1.0734 | 0% | 33.0476 | 0 | 0 | 188.525 | 188.525 | 0% | 11.75% | 11.75% | 80% | 9.398% | 3.1059 | 7.2383 | 6 | 18.6354 | 6.8684 | 9.885% | 9.885%
5 | 138 | 18 | 3296 | 8 | 14 | 147.78 | 100.75 | 248.53 | 100.75 | 50.38 | 138 | 3296 | 480 | 136.1096 | 19.5993 | 14.4351 | 454.284 | 7.812 | 62.8202 | 32.6245 | 32.6245 | 84.2858 | 95.7142 | 63.863 | 120.7497 | 120.7497 | 85.9955 | 206.7452 | 0.18389 | 18.39% | 93.4902 | 17.1919 | 12.0343 | 169.7167 | 169.7167 | 7.091% | 11.55% | 11.55% | 80% | 9.238% | 8.6368 | 6.2522 | 6 | 51.821 | 19.0996 | 30.53% | 30.53%
5 | 138 | 18 | 3297 | 9 | 17.4 | 191.39 | 162.31 | 353.7 | 162.31 | 81.16 | 138 | 3297 | 540 | 136.1096 | 19.5993 | 14.4351 | 514.284 | 8.812 | 47.8202 | 42.6586 | 42.6586 | 71.674 | 108.326 | 50.0096 | 181.5131 | 181.5131 | 138.5403 | 320.0534 | 0.42742 | 42.74% | 144.7281 | 61.8598 | 43.3019 | 180.1519 | 180.1519 | 24.04% | 11.42% | 11.42% | 85% | 9.708% | 14.0495 | 5.4794 | 5.4794 | 76.9828 | 31.0693 | 42.73% | 42.73%
5 | 138 | 18 | 3298 | 10 | 18.2 | 346.58 | 183.69 | 530.27 | 183.69 | 91.85 | 138 | 3298 | 600 | 136.1096 | 19.5993 | 14.4351 | 574.284 | 9.812 | 32.8202 | 51.8693 | 51.8693 | 55.786 | 124.214 | 36.7061 | 353.2362 | 353.2362 | 156.7892 | 510.0254 | 0.57119 | 57.12% | 230.6335 | 131.7346 | 92.2142 | 185.4535 | 185.4535 | 49.72% | 11.38% | 11.38% | 90% | 10.24% | 23.6229 | 5.3093 | 5.3093 | 125.4213 | 52.24 | 67.63% | 67.63%
5 | 138 | 18 | 3299 | 11 | 20.9 | 283.69 | 211.03 | 494.72 | 211.03 | 105.52 | 138 | 3299 | 660 | 136.1096 | 19.5993 | 14.4351 | 634.284 | 10.812 | 17.8202 | 59.1635 | 59.1635 | 34.2246 | 145.7754 | 24.9279 | 299.6169 | 299.6169 | 180.1254 | 479.7423 | 0.56891 | 56.89% | 216.9395 | 123.4193 | 86.3935 | 177.7039 | 177.7039 | 48.62% | 11.34% | 11.34% | 85% | 9.636% | 20.9037 | 4.7684 | 4.7684 | 99.6762 | 46.2266 | 56.09% | 56.09%
5 | 138 | 18 | 3300 | 12 | 22.1 | 152.5 | 360.97 | 513.47 | 360.97 | 180.49 | 138 | 3300 | 720 | 136.1096 | 19.5993 | 14.4351 | 694.284 | 11.812 | 2.8202 | 62.7235 | 62.7235 | 5.8049 | 174.1951 | 18.0336 | 163.1499 | 163.1499 | 308.1072 | 471.2571 | 0.57023 | 57.02% | 213.1024 | 121.5178 | 85.0624 | 166.5045 | 166.5045 | 51.09% | 11.31% | 11.31% | 85% | 9.617% | 20.4939 | 4.5443 | 4.5443 | 93.1308 | 45.3204 | 55.93% | 55.93%
5 | 138 | 18 | 3301 | 13 | 22.6 | 350.28 | 291.53 | 641.81 | 291.53 | 145.77 | 138 | 3301 | 780 | 136.1096 | 19.5993 | 14.4351 | 754.284 | 12.812 | -12.1798 | 61.0526 | 61.0526 | 24.2455 | 204.2455 | 21.4369 | 372.5986 | 372.5986 | 248.8364 | 621.435 | 0.62847 | 62.85% | 281.0129 | 176.6083 | 123.6258 | 168.7472 | 168.7472 | 73.26% | 11.33% | 11.33% | 90% | 10.19% | 28.6459 | 4.4539 | 4.4539 | 127.5873 | 63.348 | 75.61% | 75.61%
5 | 138 | 18 | 3302 | 14 | 24.7 | 251.39 | 344.03 | 595.42 | 344.03 | 172.02 | 138 | 3302 | 840 | 136.1096 | 19.5993 | 14.4351 | 814.284 | 13.812 | -27.1798 | 54.9197 | 54.9197 | 48.4813 | 228.4813 | 32.0008 | 260.5116 | 260.5116 | 293.648 | 554.1596 | 0.61532 | 61.53% | 250.591 | 154.1927 | 107.9349 | 288.1864 | 288.1864 | 37.45% | 11.29% | 11.29% | 90% | 10.16% | 25.4591 | 4.0935 | 4.0935 | 104.216 | 56.3004 | 36.16% | 36.16%
5 | 138 | 18 | 3303 | 15 | 24.4 | 495 | 217.78 | 712.78 | 217.78 | 108.89 | 138 | 3303 | 900 | 136.1096 | 19.5993 | 14.4351 | 874.284 | 14.812 | -42.1798 | 46.2629 | 46.2629 | 66.1996 | 246.1996 | 44.9131 | 485.1747 | 485.1747 | 185.8869 | 671.0615 | 0.64723 | 64.72% | 303.454 | 196.4043 | 137.483 | 283.1949 | 283.1949 | 48.55% | 11.32% | 11.32% | 90% | 10.19% | 30.9181 | 4.1431 | 4.1431 | 128.096 | 68.3726 | 45.23% | 45.23%
5 | 138 | 18 | 3304 | 16 | 24.7 | 313.81 | 178.25 | 492.06 | 178.25 | 89.13 | 138 | 3304 | 960 | 136.1096 | 19.5993 | 14.4351 | 934.284 | 15.812 | -57.1798 | 36.4493 | 36.4493 | 79.8061 | 259.8061 | 58.6165 | 275.0678 | 275.0678 | 152.1459 | 427.2136 | 0.55925 | 55.92% | 193.186 | 108.0392 | 75.6274 | 274.6084 | 274.6084 | 27.54% | 11.26% | 11.26% | 85% | 9.567% | 18.4827 | 4.0935 | 4.0935 | 75.6583 | 40.8728 | 27.55% | 27.55%
5 | 138 | 18 | 3305 | 17 | 24.5 | 220.08 | 198.61 | 418.69 | 198.61 | 99.31 | 138 | 3305 | 1020 | 136.1096 | 19.5993 | 14.4351 | 994.284 | 16.812 | -72.1798 | 26.2235 | 26.2235 | 91.254 | 271.254 | 72.6283 | 148.7058 | 148.7058 | 169.5242 | 318.23 | 0.47409 | 47.41% | 143.9036 | 68.2226 | 47.7558 | 262.8099 | 262.8099 | 18.17% | 11.23% | 11.23% | 85% | 9.548% | 13.7397 | 4.1265 | 4.1265 | 56.6965 | 30.3841 | 21.57% | 21.57%
5 | 138 | 18 | 3306 | 18 | 23.2 | 133.97 | 130.47 | 264.44 | 130.47 | 65.24 | 138 | 3306 | 1080 | 136.1096 | 19.5993 | 14.4351 | 1054.284 | 17.812 | -87.1798 | 16.0324 | 16.0324 | 101.7634 | 281.7634 | 86.7475 | 27.5221 | 27.5221 | 111.3631 | 138.8852 | 0.027942 | 2.794% | 62.8039 | 1.7549 | 1.2284 | 235.0198 | 235.0198 | 0.5227% | 11.24% | 11.24% | 80% | 8.989% | 5.6451 | 4.3478 | 4.3478 | 24.5439 | 12.4837 | 10.44% | 10.44%
5 | 138 | 18 | 3307 | 19 | 23.1 | 80.47 | 74.92 | 155.39 | 74.92 | 37.46 | 138 | 3307 | 1140 | 136.1096 | 19.5993 | 14.4351 | 1114.284 | 18.812 | -102.1798 | 6.2187 | 6.2187 | 112.1338 | 292.1338 | 100.8508 | 0 | 0 | 63.9482 | 63.9482 | -0.88485 | 0% | 28.9174 | 0 | 0 | 222.1235 | 222.1235 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.3653 | 4.3653 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3308 | 20 | 21.4 | 19.08 | 35.47 | 54.55 | 35.47 | 17.74 | 138 | 3308 | 1200 | 136.1096 | 19.5993 | 14.4351 | 1174.284 | 19.812 | -117.1798 | -2.8807 | 0 | 119.3286 | 299.3286 | 110.2644 | 0 | 0 | 30.2755 | 30.2755 | -2.8851 | 0% | 13.6906 | 0 | 0 | 151.1452 | 151.1452 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6738 | 4.6738 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3309 | 21 | 18.6 | 0 | 3.19 | 3.19 | 3.19 | 1.6 | 138 | 3309 | 1260 | 136.1096 | 19.5993 | 14.4351 | 1234.284 | 20.812 | -132.1798 | -10.8801 | 0 | 119.3286 | 299.3286 | 110.2644 | 0 | 0 | 2.7228 | 2.7228 | -42.4788 | 0% | 1.2313 | 0 | 0 | -4.7209 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3310 | 22 | 17.1 | 0 | 0 | 0 | 0 | 0 | 138 | 3310 | 1320 | 136.1096 | 19.5993 | 14.4351 | 1294.284 | 21.812 | -147.1798 | -17.3213 | 0 | 119.3286 | 299.3286 | 110.2644 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0532 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3311 | 23 | 15.7 | 0 | 0 | 0 | 0 | 0 | 138 | 3311 | 1380 | 136.1096 | 19.5993 | 14.4351 | 1354.284 | 22.812 | -162.1798 | -21.7007 | 0 | 119.3286 | 299.3286 | 110.2644 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4961 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
5 | 138 | 18 | 3312 | 24 | 14.8 | 0 | 0 | 0 | 0 | 0 | 138 | 3312 | 1440 | 136.1096 | 19.5993 | 14.4351 | 1414.284 | 23.812 | -177.1798 | -23.5738 | 0 | 119.3286 | 299.3286 | 110.2644 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1769 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3313 | 1 | 13.7 | 0 | 0 | 0 | 0 | 0 | 139 | 3313 | 60 | 137.0959 | 19.8154 | 14.2135 | 34.284 | 0.80829 | 167.8756 | -22.5123 | 0 | 119.6699 | 60.3301 | 110.4885 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5979 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3314 | 2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 139 | 3314 | 120 | 137.0959 | 19.8154 | 14.2135 | 94.284 | 1.8083 | 152.8756 | -19.0501 | 0 | 119.6699 | 60.3301 | 110.4885 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2098 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3315 | 3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 139 | 3315 | 180 | 137.0959 | 19.8154 | 14.2135 | 154.284 | 2.8083 | 137.8756 | -13.346 | 0 | 119.6699 | 60.3301 | 110.4885 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5169 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3316 | 4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 139 | 3316 | 240 | 137.0959 | 19.8154 | 14.2135 | 214.284 | 3.8083 | 122.8756 | -5.8947 | 0 | 119.6699 | 60.3301 | 110.4885 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7361 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3317 | 5 | 10.9 | 0 | 0 | 0 | 0 | 0 | 139 | 3317 | 300 | 137.0959 | 19.8154 | 14.2135 | 274.284 | 4.8083 | 107.8756 | 2.8237 | 2.8237 | 116.3032 | 63.6968 | 106.148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.8532 | 3.8532 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3318 | 6 | 10.7 | 0.92 | 7.78 | 8.7 | 7.78 | 3.89 | 139 | 3318 | 360 | 137.0959 | 19.8154 | 14.2135 | 334.284 | 5.8083 | 92.8756 | 12.3981 | 12.3981 | 105.8374 | 74.1626 | 92.1008 | -0.15708 | 0 | 6.6406 | 6.6406 | -19.6468 | 0% | 3.0029 | 0 | 0 | 17.9916 | 17.9916 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3319 | 7 | 12.5 | 23.69 | 68.69 | 92.38 | 68.69 | 34.35 | 139 | 3319 | 420 | 137.0959 | 19.8154 | 14.2135 | 394.284 | 6.8083 | 77.8756 | 22.479 | 22.479 | 95.4748 | 84.5252 | 77.9936 | 12.8889 | 12.8889 | 58.6306 | 71.5195 | -1.0366 | 0% | 32.3411 | 0 | 0 | 195.4914 | 195.4914 | 0% | 11.65% | 11.65% | 80% | 9.322% | 3.0148 | 6.6189 | 6 | 18.089 | 6.667 | 9.253% | 9.253%
5 | 139 | 19 | 3320 | 8 | 16.4 | 105.92 | 118.89 | 224.81 | 118.89 | 59.45 | 139 | 3320 | 480 | 137.0959 | 19.8154 | 14.2135 | 454.284 | 7.8083 | 62.8756 | 32.7358 | 32.7358 | 84.5144 | 95.4856 | 63.9446 | 86.0339 | 86.0339 | 101.479 | 187.5129 | 0.14928 | 14.93% | 84.7933 | 12.6582 | 8.8607 | 176.8981 | 176.8981 | 5.009% | 11.47% | 11.47% | 80% | 9.179% | 7.7829 | 5.6983 | 5.6983 | 44.3489 | 17.2111 | 25.07% | 25.07%
5 | 139 | 19 | 3321 | 9 | 18 | 259.53 | 150 | 409.53 | 150 | 75 | 139 | 3321 | 540 | 137.0959 | 19.8154 | 14.2135 | 514.284 | 8.8083 | 47.8756 | 42.7788 | 42.7788 | 71.9286 | 108.0714 | 50.1156 | 245.0366 | 245.0366 | 128.033 | 373.0696 | 0.48453 | 48.45% | 168.7021 | 81.7404 | 57.2183 | 188.9385 | 188.9385 | 30.28% | 11.4% | 11.4% | 85% | 9.689% | 16.3457 | 5.3514 | 5.3514 | 87.4726 | 36.1472 | 46.3% | 46.3%
5 | 139 | 19 | 3322 | 10 | 19.4 | 382.78 | 183.81 | 566.59 | 183.81 | 91.91 | 139 | 3322 | 600 | 137.0959 | 19.8154 | 14.2135 | 574.284 | 9.8083 | 32.8756 | 52.0104 | 52.0104 | 56.0648 | 123.9352 | 36.845 | 388.6753 | 388.6753 | 156.8916 | 545.5669 | 0.59123 | 59.12% | 246.7054 | 145.8595 | 102.1017 | 193.724 | 193.724 | 52.7% | 11.36% | 11.36% | 90% | 10.22% | 25.224 | 5.0626 | 5.0626 | 127.6987 | 55.7807 | 65.92% | 65.92%
5 | 139 | 19 | 3323 | 11 | 22.6 | 491.58 | 192.5 | 684.08 | 192.5 | 96.25 | 139 | 3323 | 660 | 137.0959 | 19.8154 | 14.2135 | 634.284 | 10.8083 | 17.8756 | 59.3391 | 59.3391 | 34.4911 | 145.5089 | 25.1147 | 517.4444 | 517.4444 | 164.309 | 681.7535 | 0.644 | 64.4% | 308.2889 | 198.5382 | 138.9768 | 192.2589 | 192.2589 | 72.29% | 11.34% | 11.34% | 90% | 10.2% | 31.4503 | 4.4539 | 4.4539 | 140.078 | 69.5496 | 72.86% | 72.86%
5 | 139 | 19 | 3324 | 12 | 23.8 | 413.81 | 262.31 | 676.12 | 262.31 | 131.16 | 139 | 3324 | 720 | 137.0959 | 19.8154 | 14.2135 | 694.284 | 11.8083 | 2.8756 | 62.9351 | 62.9351 | 5.9541 | 174.0459 | 18.2553 | 441.3103 | 441.3103 | 223.8956 | 665.2059 | 0.64391 | 64.39% | 300.8061 | 193.6931 | 135.5852 | 191.4077 | 191.4077 | 70.84% | 11.32% | 11.32% | 90% | 10.19% | 30.6565 | 4.2442 | 4.2442 | 130.1117 | 67.7941 | 67.98% | 67.98%
5 | 139 | 19 | 3325 | 13 | 22.5 | 322.64 | 338.06 | 660.7 | 338.06 | 169.03 | 139 | 3325 | 780 | 137.0959 | 19.8154 | 14.2135 | 754.284 | 12.8083 | -12.1244 | 61.2744 | 61.2744 | 24.2762 | 204.2762 | 21.584 | 342.1205 | 342.1205 | 288.5523 | 630.6727 | 0.6307 | 63.07% | 285.1902 | 179.8689 | 125.9082 | 171.8871 | 171.8871 | 73.25% | 11.33% | 11.33% | 90% | 10.2% | 29.0776 | 4.4719 | 4.4719 | 130.0312 | 64.3024 | 75.65% | 75.65%
5 | 139 | 19 | 3326 | 14 | 22.9 | 240.28 | 388.19 | 628.47 | 388.19 | 194.1 | 139 | 3326 | 840 | 137.0959 | 19.8154 | 14.2135 | 814.284 | 13.8083 | -27.1244 | 55.1293 | 55.1293 | 48.6106 | 228.6106 | 32.0662 | 248.1847 | 248.1847 | 331.3409 | 579.5256 | 0.6169 | 61.69% | 262.0615 | 161.6649 | 113.1655 | 169.4062 | 169.4062 | 66.8% | 11.32% | 11.32% | 90% | 10.19% | 26.6914 | 4.4006 | 4.4006 | 117.4568 | 59.0256 | 69.33% | 69.33%
5 | 139 | 19 | 3327 | 15 | 23.1 | 570.47 | 261.31 | 831.78 | 261.31 | 130.66 | 139 | 3327 | 900 | 137.0959 | 19.8154 | 14.2135 | 874.284 | 14.8083 | -42.1244 | 46.4589 | 46.4589 | 66.3517 | 246.3517 | 44.9311 | 557.1518 | 557.1518 | 223.042 | 780.1938 | 0.66557 | 66.56% | 352.8036 | 234.8171 | 164.3719 | 175.3571 | 175.3571 | 93.74% | 11.35% | 11.35% | 90% | 10.21% | 36.0345 | 4.3653 | 4.3653 | 157.302 | 79.6871 | 89.7% | 89.7%
5 | 139 | 19 | 3328 | 16 | 22.8 | 342.69 | 216.47 | 559.16 | 216.47 | 108.24 | 139 | 3328 | 960 | 137.0959 | 19.8154 | 14.2135 | 934.284 | 15.8083 | -57.1244 | 36.6375 | 36.6375 | 79.9534 | 259.9534 | 58.6041 | 299.1603 | 299.1603 | 184.7687 | 483.929 | 0.57949 | 57.95% | 218.8327 | 126.8112 | 88.7679 | 158.6451 | 158.6451 | 55.95% | 11.3% | 11.3% | 85% | 9.608% | 21.0251 | 4.4183 | 4.4183 | 92.8946 | 46.4951 | 58.55% | 58.55%
5 | 139 | 19 | 3329 | 17 | 22.6 | 193.89 | 187.5 | 381.39 | 187.5 | 93.75 | 139 | 3329 | 1020 | 137.0959 | 19.8154 | 14.2135 | 994.284 | 16.8083 | -72.1244 | 26.4097 | 26.4097 | 91.3894 | 271.3894 | 72.5931 | 130.407 | 130.407 | 160.0413 | 290.4482 | 0.42844 | 42.84% | 131.3407 | 56.2718 | 39.3903 | 146.5643 | 146.5643 | 26.88% | 11.28% | 11.28% | 80% | 9.023% | 11.8513 | 4.4539 | 4.4539 | 52.7849 | 26.208 | 36.01% | 36.01%
5 | 139 | 19 | 3330 | 18 | 23.3 | 61.19 | 142.5 | 203.69 | 142.5 | 71.25 | 139 | 3330 | 1080 | 137.0959 | 19.8154 | 14.2135 | 1054.284 | 17.8083 | -87.1244 | 16.2212 | 16.2212 | 101.8855 | 281.8855 | 86.6926 | 12.6374 | 12.6374 | 121.6314 | 134.2688 | 0.0028669 | 0.2867% | 60.7163 | 0.17407 | 0.12185 | 236.3675 | 236.3675 | 0.05155% | 11.23% | 11.23% | 80% | 8.985% | 5.4553 | 4.3304 | 4.3304 | 23.6235 | 12.064 | 9.994% | 9.994%
5 | 139 | 19 | 3331 | 19 | 22 | 59.17 | 99.08 | 158.25 | 99.08 | 49.54 | 139 | 3331 | 1140 | 137.0959 | 19.8154 | 14.2135 | 1114.284 | 18.8083 | -102.1244 | 6.4136 | 6.4136 | 112.2414 | 292.2414 | 100.7769 | 0 | 0 | 84.5701 | 84.5701 | -0.50122 | 0% | 38.2426 | 0 | 0 | 123.815 | 123.815 | 0% | 11.27% | 0% | 80% | 0% | 0 | 4.5626 | 4.5626 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3332 | 20 | 20.2 | 11.39 | 34.44 | 45.83 | 34.44 | 17.22 | 139 | 3332 | 1200 | 137.0959 | 19.8154 | 14.2135 | 1174.284 | 19.8083 | -117.1244 | -2.6776 | 0 | 119.6699 | 299.6699 | 110.4885 | 0 | 0 | 29.3964 | 29.3964 | -3.0848 | 0% | 13.293 | 0 | 0 | 148.0122 | 148.0122 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.9037 | 4.9037 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3333 | 21 | 19.5 | 0 | 1.39 | 1.39 | 1.39 | 0.7 | 139 | 3333 | 1260 | 137.0959 | 19.8154 | 14.2135 | 1234.284 | 20.8083 | -132.1244 | -10.6681 | 0 | 119.6699 | 299.6699 | 110.4885 | 0 | 0 | 1.1864 | 1.1864 | -96.8493 | 0% | 0.53651 | 0 | 0 | -3.9651 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0425 | 5.0425 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3334 | 22 | 17.8 | 0 | 0 | 0 | 0 | 0 | 139 | 3334 | 1320 | 137.0959 | 19.8154 | 14.2135 | 1294.284 | 21.8083 | -147.1244 | -17.1019 | 0 | 119.6699 | 299.6699 | 110.4885 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6286 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3335 | 23 | 17.5 | 0 | 0 | 0 | 0 | 0 | 139 | 3335 | 1380 | 137.0959 | 19.8154 | 14.2135 | 1354.284 | 22.8083 | -162.1244 | -21.4784 | 0 | 119.6699 | 299.6699 | 110.4885 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3261 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
5 | 139 | 19 | 3336 | 24 | 16.8 | 0 | 0 | 0 | 0 | 0 | 139 | 3336 | 1440 | 137.0959 | 19.8154 | 14.2135 | 1414.284 | 23.8083 | -177.1244 | -23.3559 | 0 | 119.6699 | 299.6699 | 110.4885 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6332 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3337 | 1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 140 | 3337 | 60 | 138.0822 | 20.0254 | 13.9803 | 34.284 | 0.8044 | 167.9339 | -22.3133 | 0 | 120.0023 | 59.9977 | 110.7063 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1622 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3338 | 2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 140 | 3338 | 120 | 138.0822 | 20.0254 | 13.9803 | 94.284 | 1.8044 | 152.9339 | -18.8699 | 0 | 120.0023 | 59.9977 | 110.7063 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2475 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3339 | 3 | 14.7 | 0 | 0 | 0 | 0 | 0 | 140 | 3339 | 180 | 138.0822 | 20.0254 | 13.9803 | 154.284 | 2.8044 | 137.9339 | -13.1866 | 0 | 120.0023 | 59.9977 | 110.7063 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0176 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3340 | 4 | 14.7 | 0 | 0 | 0 | 0 | 0 | 140 | 3340 | 240 | 138.0822 | 20.0254 | 13.9803 | 214.284 | 3.8044 | 122.9339 | -5.755 | 0 | 120.0023 | 59.9977 | 110.7063 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0176 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3341 | 5 | 13.8 | 0 | 0 | 0 | 0 | 0 | 140 | 3341 | 300 | 138.0822 | 20.0254 | 13.9803 | 274.284 | 4.8044 | 107.9339 | 2.9471 | 2.9471 | 116.482 | 63.518 | 106.1731 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.7877 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3342 | 6 | 14.1 | 0.56 | 7.14 | 7.7 | 7.14 | 3.57 | 140 | 3342 | 360 | 138.0822 | 20.0254 | 13.9803 | 334.284 | 5.8044 | 92.9339 | 12.5096 | 12.5096 | 106.0281 | 73.9719 | 92.1458 | -0.096802 | 0 | 6.0944 | 6.0944 | -20.1952 | 0% | 2.7559 | 0 | 0 | 5.4719 | 5.4719 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3343 | 7 | 14.8 | 6.31 | 53.89 | 60.2 | 53.89 | 26.95 | 140 | 3343 | 420 | 138.0822 | 20.0254 | 13.9803 | 394.284 | 6.8044 | 77.9339 | 22.584 | 22.584 | 95.6806 | 84.3194 | 78.0574 | 3.4 | 3.4 | 45.998 | 49.398 | -1.7545 | 0% | 22.3378 | 0 | 0 | 166.4511 | 166.4511 | 0% | 11.57% | 11.57% | 80% | 9.253% | 2.067 | 6.0631 | 6 | 12.4019 | 4.571 | 7.451% | 7.451%
5 | 140 | 20 | 3344 | 8 | 16.6 | 22.22 | 124.44 | 146.66 | 124.44 | 62.22 | 140 | 3344 | 480 | 138.0822 | 20.0254 | 13.9803 | 454.284 | 7.8044 | 62.9339 | 32.8407 | 32.8407 | 84.7405 | 95.2595 | 64.0283 | 17.9433 | 17.9433 | 106.2162 | 124.1595 | -0.18117 | 0% | 56.1449 | 0 | 0 | 179.3451 | 179.3451 | 0% | 11.48% | 11.48% | 80% | 9.183% | 5.1556 | 5.6539 | 5.6539 | 29.1496 | 11.4012 | 16.25% | 16.25%
5 | 140 | 20 | 3345 | 9 | 16.8 | 53.14 | 176.47 | 229.61 | 176.47 | 88.24 | 140 | 3345 | 540 | 138.0822 | 20.0254 | 13.9803 | 514.284 | 8.8044 | 47.9339 | 42.8922 | 42.8922 | 72.1809 | 107.8191 | 50.223 | 49.953 | 49.953 | 150.6266 | 200.5796 | 0.19641 | 19.64% | 90.7021 | 17.8152 | 12.4706 | 142.4555 | 142.4555 | 8.754% | 11.46% | 11.46% | 80% | 9.166% | 8.3138 | 5.6099 | 5.6099 | 46.6391 | 18.3851 | 32.74% | 32.74%
5 | 140 | 20 | 3346 | 10 | 18.3 | 128.89 | 233.42 | 362.31 | 233.42 | 116.71 | 140 | 3346 | 600 | 138.0822 | 20.0254 | 13.9803 | 574.284 | 9.8044 | 32.9339 | 52.1444 | 52.1444 | 56.3426 | 123.6574 | 36.9844 | 130.3984 | 130.3984 | 199.2364 | 329.6348 | 0.44445 | 44.45% | 149.0609 | 66.2508 | 46.3756 | 149.7927 | 149.7927 | 30.96% | 11.4% | 11.4% | 85% | 9.687% | 14.4389 | 5.2884 | 5.2884 | 76.358 | 31.9303 | 50.98% | 50.98%
5 | 140 | 20 | 3347 | 11 | 19.8 | 101.67 | 291.75 | 393.42 | 291.75 | 145.88 | 140 | 3347 | 660 | 138.0822 | 20.0254 | 13.9803 | 634.284 | 10.8044 | 17.9339 | 59.5076 | 59.5076 | 34.7601 | 145.2399 | 25.2997 | 106.6713 | 106.6713 | 249.0242 | 355.6955 | 0.48013 | 48.01% | 160.8455 | 77.2273 | 54.0591 | 148.8106 | 148.8106 | 36.33% | 11.36% | 11.36% | 85% | 9.653% | 15.527 | 4.9826 | 4.9826 | 77.3645 | 34.3366 | 51.99% | 51.99%
5 | 140 | 20 | 3348 | 12 | 19.1 | 209.08 | 315.92 | 525 | 315.92 | 157.96 | 140 | 3348 | 720 | 138.0822 | 20.0254 | 13.9803 | 694.284 | 11.8044 | 2.9339 | 63.1403 | 63.1403 | 6.1101 | 173.8899 | 18.4714 | 222.2903 | 222.2903 | 269.6546 | 491.9449 | 0.56669 | 56.67% | 222.4575 | 126.0643 | 88.245 | 146.0295 | 146.0295 | 60.43% | 11.37% | 11.37% | 85% | 9.662% | 21.4942 | 5.1233 | 5.1233 | 110.1216 | 47.5325 | 75.41% | 75.41%
5 | 140 | 20 | 3349 | 13 | 19.3 | 351.03 | 311.19 | 662.22 | 311.19 | 155.6 | 140 | 3349 | 780 | 138.0822 | 20.0254 | 13.9803 | 754.284 | 12.8044 | -12.0661 | 61.4912 | 61.4912 | 24.2984 | 204.2984 | 21.7258 | 371.0921 | 371.0921 | 265.6173 | 636.7094 | 0.62134 | 62.13% | 287.92 | 178.8962 | 125.2273 | 150.3262 | 150.3262 | 83.3% | 11.36% | 11.36% | 90% | 10.22% | 29.4325 | 5.0828 | 5.0828 | 149.5982 | 65.0874 | 99.52% | 99.52%
5 | 140 | 20 | 3350 | 14 | 19 | 340.56 | 308.25 | 648.81 | 308.25 | 154.13 | 140 | 3350 | 840 | 138.0822 | 20.0254 | 13.9803 | 814.284 | 13.8044 | -27.0661 | 55.3351 | 55.3351 | 48.7316 | 228.7316 | 32.1275 | 350.6521 | 350.6521 | 263.1078 | 613.76 | 0.61343 | 61.34% | 277.5423 | 170.2523 | 119.1766 | 148.6738 | 148.6738 | 80.16% | 11.36% | 11.36% | 90% | 10.23% | 28.3815 | 5.1437 | 5.1437 | 145.986 | 62.7632 | 98.19% | 98.19%
5 | 140 | 20 | 3351 | 15 | 19.1 | 224.44 | 279.08 | 503.52 | 279.08 | 139.54 | 140 | 3351 | 900 | 138.0822 | 20.0254 | 13.9803 | 874.284 | 14.8044 | -42.0661 | 46.6518 | 46.6518 | 66.4963 | 246.4963 | 44.9456 | 218.4471 | 218.4471 | 238.2097 | 456.6568 | 0.54835 | 54.84% | 206.5002 | 113.2346 | 79.2642 | 140.8235 | 140.8235 | 56.29% | 11.37% | 11.37% | 85% | 9.664% | 19.9554 | 5.1233 | 5.1233 | 102.238 | 44.1297 | 72.6% | 72.6%
5 | 140 | 20 | 3352 | 16 | 18.6 | 183.81 | 254.08 | 437.89 | 254.08 | 127.04 | 140 | 3352 | 960 | 138.0822 | 20.0254 | 13.9803 | 934.284 | 15.8044 | -57.0661 | 36.8231 | 36.8231 | 80.0937 | 260.0937 | 58.5885 | 159.8377 | 159.8377 | 216.8708 | 376.7085 | 0.49115 | 49.12% | 170.3476 | 83.6668 | 58.5667 | 135.812 | 135.812 | 43.12% | 11.38% | 11.38% | 85% | 9.677% | 16.4844 | 5.2259 | 5.2259 | 86.1463 | 36.4537 | 63.43% | 63.43%
5 | 140 | 20 | 3353 | 17 | 17.2 | 143.89 | 231.58 | 375.47 | 231.58 | 115.79 | 140 | 3353 | 1020 | 138.0822 | 20.0254 | 13.9803 | 994.284 | 16.8044 | -72.0661 | 26.5936 | 26.5936 | 91.5183 | 271.5183 | 72.5551 | 96.3605 | 96.3605 | 197.6659 | 294.0264 | 0.39256 | 39.26% | 132.9587 | 52.1949 | 36.5364 | 128.8281 | 128.8281 | 28.36% | 11.43% | 11.43% | 80% | 9.144% | 12.1577 | 5.5226 | 5.5226 | 67.1419 | 26.8856 | 52.12% | 52.12%
5 | 140 | 20 | 3354 | 18 | 17.5 | 51.58 | 168.61 | 220.19 | 168.61 | 84.31 | 140 | 3354 | 1080 | 138.0822 | 20.0254 | 13.9803 | 1054.284 | 17.8044 | -87.0661 | 16.4076 | 16.4076 | 102.0014 | 282.0014 | 86.6353 | 10.7173 | 10.7173 | 143.9176 | 154.6349 | 0.026027 | 2.603% | 69.9259 | 1.8199 | 1.274 | 118.716 | 118.716 | 1.073% | 11.44% | 11.44% | 80% | 9.153% | 6.4 | 5.4579 | 5.4579 | 34.9306 | 14.1531 | 29.42% | 29.42%
5 | 140 | 20 | 3355 | 19 | 16.9 | 57.69 | 96.75 | 154.44 | 96.75 | 48.38 | 140 | 3355 | 1140 | 138.0822 | 20.0254 | 13.9803 | 1114.284 | 18.8044 | -102.0661 | 6.6057 | 6.6057 | 112.3431 | 292.3431 | 100.7009 | 0 | 0 | 82.5813 | 82.5813 | -0.66903 | 0% | 37.3433 | 0 | 0 | 111.3522 | 111.3522 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3356 | 20 | 15.8 | 13.06 | 30.75 | 43.81 | 30.75 | 15.38 | 140 | 3356 | 1200 | 138.0822 | 20.0254 | 13.9803 | 1174.284 | 19.8044 | -117.0661 | -2.4778 | 0 | 120.0023 | 300.0023 | 110.7063 | 0 | 0 | 26.2468 | 26.2468 | -3.925 | 0% | 11.8688 | 0 | 0 | 140.3836 | 140.3836 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3357 | 21 | 15.4 | 0 | 4.03 | 4.03 | 4.03 | 2.02 | 140 | 3357 | 1260 | 138.0822 | 20.0254 | 13.9803 | 1234.284 | 20.8044 | -132.0661 | -10.46 | 0 | 120.0023 | 300.0023 | 110.7063 | 0 | 0 | 3.4398 | 3.4398 | -35.542 | 0% | 1.5555 | 0 | 0 | -10.2106 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3358 | 22 | 14.6 | 0 | 0 | 0 | 0 | 0 | 140 | 3358 | 1320 | 138.0822 | 20.0254 | 13.9803 | 1294.284 | 21.8044 | -147.0661 | -16.8871 | 0 | 120.0023 | 300.0023 | 110.7063 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8414 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3359 | 23 | 14.8 | 0 | 0 | 0 | 0 | 0 | 140 | 3359 | 1380 | 138.0822 | 20.0254 | 13.9803 | 1354.284 | 22.8044 | -162.0661 | -21.2614 | 0 | 120.0023 | 300.0023 | 110.7063 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2024 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
5 | 140 | 20 | 3360 | 24 | 13.8 | 0 | 0 | 0 | 0 | 0 | 140 | 3360 | 1440 | 138.0822 | 20.0254 | 13.9803 | 1414.284 | 23.8044 | -177.0661 | -23.144 | 0 | 120.0023 | 300.0023 | 110.7063 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3921 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3361 | 1 | 13.6 | 0 | 0 | 0 | 0 | 0 | 141 | 3361 | 60 | 139.0685 | 20.2293 | 13.7356 | 34.284 | 0.80033 | 167.9951 | -22.1208 | 0 | 120.3256 | 59.6744 | 110.9178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4435 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3362 | 2 | 13.4 | 0 | 0 | 0 | 0 | 0 | 141 | 3362 | 120 | 139.0685 | 20.2293 | 13.7356 | 94.284 | 1.8003 | 152.9951 | -18.6962 | 0 | 120.3256 | 59.6744 | 110.9178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0585 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3363 | 3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 141 | 3363 | 180 | 139.0685 | 20.2293 | 13.7356 | 154.284 | 2.8003 | 137.9951 | -13.0338 | 0 | 120.3256 | 59.6744 | 110.9178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6735 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3364 | 4 | 13.1 | 0 | 0 | 0 | 0 | 0 | 141 | 3364 | 240 | 139.0685 | 20.2293 | 13.7356 | 214.284 | 3.8003 | 122.9951 | -5.6217 | 0 | 120.3256 | 59.6744 | 110.9178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8259 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3365 | 5 | 13 | 0 | 0 | 0 | 0 | 0 | 141 | 3365 | 300 | 139.0685 | 20.2293 | 13.7356 | 274.284 | 4.8003 | 107.9951 | 3.0641 | 3.0641 | 116.6588 | 63.3412 | 106.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.0423 | 7.0423 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3366 | 6 | 12.8 | 1.94 | 11.31 | 13.25 | 11.31 | 5.66 | 141 | 3366 | 360 | 139.0685 | 20.2293 | 13.7356 | 334.284 | 5.8003 | 92.9951 | 12.6148 | 12.6148 | 106.2164 | 73.7836 | 92.1935 | -0.34 | 0 | 9.6537 | 9.6537 | -12.761 | 0% | 4.3654 | 0 | 0 | 19.8349 | 19.8349 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3367 | 7 | 12.6 | 44.25 | 67.86 | 112.11 | 67.86 | 33.93 | 141 | 3367 | 420 | 139.0685 | 20.2293 | 13.7356 | 394.284 | 6.8003 | 77.9951 | 22.6826 | 22.6826 | 95.8836 | 84.1164 | 78.1237 | 23.6153 | 23.6153 | 57.9221 | 81.5374 | -0.80767 | 0% | 36.8712 | 0 | 0 | 192.9154 | 192.9154 | 0% | 11.64% | 11.64% | 80% | 9.316% | 3.4348 | 6.5939 | 6 | 20.6085 | 7.5956 | 10.68% | 10.68%
5 | 141 | 21 | 3368 | 8 | 12.3 | 144.08 | 107.31 | 251.39 | 107.31 | 53.66 | 141 | 3368 | 480 | 139.0685 | 20.2293 | 13.7356 | 454.284 | 7.8003 | 62.9951 | 32.9391 | 32.9391 | 84.9639 | 95.0361 | 64.114 | 115.6837 | 115.6837 | 91.5948 | 207.2786 | 0.16668 | 16.67% | 93.7314 | 15.6233 | 10.9363 | 166.6904 | 166.6904 | 6.561% | 11.6% | 11.6% | 80% | 9.282% | 8.7005 | 6.669 | 6 | 52.2032 | 19.2405 | 31.32% | 31.32%
5 | 141 | 21 | 3369 | 9 | 12.8 | 270.28 | 136.11 | 406.39 | 136.11 | 68.06 | 141 | 3369 | 540 | 139.0685 | 20.2293 | 13.7356 | 514.284 | 8.8003 | 47.9951 | 42.9989 | 42.9989 | 72.4309 | 107.5691 | 50.3317 | 252.9839 | 252.9839 | 116.1772 | 369.161 | 0.44927 | 44.93% | 166.9346 | 74.9989 | 52.4993 | 175.1433 | 175.1433 | 29.98% | 11.52% | 11.52% | 85% | 9.794% | 16.3499 | 6.5443 | 6 | 98.0997 | 36.1564 | 56.01% | 56.01%
5 | 141 | 21 | 3370 | 10 | 13.2 | 379.92 | 183.14 | 563.06 | 183.14 | 91.57 | 141 | 3370 | 600 | 139.0685 | 20.2293 | 13.7356 | 574.284 | 9.8003 | 32.9951 | 52.2713 | 52.2713 | 56.6193 | 123.3807 | 37.124 | 383.0011 | 383.0011 | 156.3198 | 539.3209 | 0.56289 | 56.29% | 243.8809 | 137.2788 | 96.0952 | 178.7454 | 178.7454 | 53.76% | 11.45% | 11.45% | 90% | 10.3% | 25.1308 | 6.4458 | 6 | 150.7849 | 55.5746 | 84.36% | 84.36%
5 | 141 | 21 | 3371 | 11 | 12.9 | 510.36 | 209.72 | 720.08 | 209.72 | 104.86 | 141 | 3371 | 660 | 139.0685 | 20.2293 | 13.7356 | 634.284 | 10.8003 | 17.9951 | 59.6689 | 59.6689 | 35.0312 | 144.9688 | 25.4827 | 533.7716 | 533.7716 | 179.0072 | 712.7788 | 0.6206 | 62.06% | 322.3186 | 200.0315 | 140.022 | 174.8285 | 174.8285 | 80.09% | 11.39% | 11.39% | 90% | 10.25% | 33.0294 | 6.5196 | 6 | 198.1767 | 73.0417 | 113.4% | 113.4%
5 | 141 | 21 | 3372 | 12 | 12.3 | 560.64 | 225 | 785.64 | 225 | 112.5 | 141 | 3372 | 720 | 139.0685 | 20.2293 | 13.7356 | 694.284 | 11.8003 | 2.9951 | 63.339 | 63.339 | 6.2728 | 173.7272 | 18.6819 | 594.2872 | 594.2872 | 192.0495 | 786.3367 | 0.636 | 63.6% | 355.5814 | 226.1508 | 158.3055 | 161.8099 | 161.8099 | 97.83% | 11.36% | 11.36% | 90% | 10.22% | 36.3476 | 6.669 | 6 | 218.0854 | 80.3794 | 134.8% | 134.8%
5 | 141 | 21 | 3373 | 13 | 11.9 | 533.06 | 217.31 | 750.37 | 217.31 | 108.66 | 141 | 3373 | 780 | 139.0685 | 20.2293 | 13.7356 | 754.284 | 12.8003 | -12.0049 | 61.7029 | 61.7029 | 24.3119 | 204.3119 | 21.8623 | 561.8652 | 561.8652 | 185.4857 | 747.3509 | 0.626 | 62.6% | 337.9521 | 211.5595 | 148.0916 | 155.7334 | 155.7334 | 95.09% | 11.38% | 11.38% | 90% | 10.24% | 34.5992 | 6.77 | 6 | 207.5954 | 76.5131 | 133.3% | 133.3%
5 | 141 | 21 | 3374 | 14 | 12.2 | 622.5 | 215.56 | 838.06 | 215.56 | 107.78 | 141 | 3374 | 840 | 139.0685 | 20.2293 | 13.7356 | 814.284 | 13.8003 | -27.0049 | 55.5371 | 55.5371 | 48.8441 | 228.8441 | 32.1847 | 638.9915 | 638.9915 | 183.992 | 822.9835 | 0.6432 | 64.32% | 372.1531 | 239.3702 | 167.5591 | 157.7132 | 157.7132 | 106.2% | 11.34% | 11.34% | 95% | 10.78% | 40.0996 | 6.6941 | 6 | 240.5977 | 88.6767 | 152.6% | 152.6%
5 | 141 | 21 | 3375 | 15 | 13.1 | 393.33 | 205.19 | 598.52 | 205.19 | 102.6 | 141 | 3375 | 900 | 139.0685 | 20.2293 | 13.7356 | 874.284 | 14.8003 | -42.0049 | 46.8417 | 46.8417 | 66.6331 | 246.6331 | 44.9565 | 381.5629 | 381.5629 | 175.1406 | 556.7035 | 0.57001 | 57% | 251.7413 | 143.4949 | 100.4464 | 146.095 | 146.095 | 68.75% | 11.44% | 11.44% | 90% | 10.3% | 25.9291 | 6.4703 | 6 | 155.5746 | 57.3399 | 106.5% | 106.5%
5 | 141 | 21 | 3376 | 16 | 13.2 | 314.25 | 182.03 | 496.28 | 182.03 | 91.02 | 141 | 3376 | 960 | 139.0685 | 20.2293 | 13.7356 | 934.284 | 15.8003 | -57.0049 | 37.0062 | 37.0062 | 80.227 | 260.227 | 58.5699 | 272.2514 | 272.2514 | 155.3723 | 427.6237 | 0.49991 | 49.99% | 193.3714 | 96.6692 | 67.6684 | 139.2771 | 139.2771 | 48.59% | 11.49% | 11.49% | 85% | 9.768% | 18.8877 | 6.4458 | 6 | 113.3262 | 41.7685 | 81.37% | 81.37%
5 | 141 | 21 | 3377 | 17 | 12.6 | 212.42 | 189.17 | 401.59 | 189.17 | 94.59 | 141 | 3377 | 1020 | 139.0685 | 20.2293 | 13.7356 | 994.284 | 16.8003 | -72.0049 | 26.775 | 26.775 | 91.6407 | 271.6407 | 72.5143 | 141.6807 | 141.6807 | 161.4667 | 303.1474 | 0.37051 | 37.05% | 137.0832 | 50.7905 | 35.5534 | 130.951 | 130.951 | 27.15% | 11.55% | 11.55% | 85% | 9.821% | 13.4631 | 6.5939 | 6 | 80.7784 | 29.7724 | 61.69% | 61.69%
5 | 141 | 21 | 3378 | 18 | 12.8 | 125.28 | 161.94 | 287.22 | 161.94 | 80.97 | 141 | 3378 | 1080 | 139.0685 | 20.2293 | 13.7356 | 1054.284 | 17.8003 | -87.0049 | 16.5915 | 16.5915 | 102.1111 | 282.1111 | 86.5756 | 26.2068 | 26.2068 | 138.2244 | 164.4313 | 0.0076062 | 0.7606% | 74.3558 | 0.56557 | 0.3959 | 121.2093 | 121.2093 | 0.3266% | 11.6% | 11.6% | 80% | 9.283% | 6.9024 | 6.5443 | 6 | 41.4145 | 15.2641 | 34.17% | 34.17%
5 | 141 | 21 | 3379 | 19 | 12.8 | 55.08 | 103.97 | 159.05 | 103.97 | 51.99 | 141 | 3379 | 1140 | 139.0685 | 20.2293 | 13.7356 | 1114.284 | 18.8003 | -102.0049 | 6.7949 | 6.7949 | 112.4389 | 292.4389 | 100.6228 | 0 | 0 | 88.7439 | 88.7439 | -0.67162 | 0% | 40.13 | 0 | 0 | 110.1863 | 110.1863 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3380 | 20 | 12.8 | 18.97 | 52.31 | 71.28 | 52.31 | 26.16 | 141 | 3380 | 1200 | 139.0685 | 20.2293 | 13.7356 | 1174.284 | 19.8003 | -117.0049 | -2.2813 | 0 | 120.3256 | 300.3256 | 110.9178 | 0 | 0 | 44.6494 | 44.6494 | -2.1289 | 0% | 20.1904 | 0 | 0 | 140.1627 | 140.1627 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3381 | 21 | 12.6 | 0 | 3.89 | 3.89 | 3.89 | 1.95 | 141 | 3381 | 1260 | 139.0685 | 20.2293 | 13.7356 | 1234.284 | 20.8003 | -132.0049 | -10.2558 | 0 | 120.3256 | 300.3256 | 110.9178 | 0 | 0 | 3.3203 | 3.3203 | -38.774 | 0% | 1.5014 | 0 | 0 | -12.1391 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3382 | 22 | 12.5 | 0 | 0 | 0 | 0 | 0 | 141 | 3382 | 1320 | 139.0685 | 20.2293 | 13.7356 | 1294.284 | 21.8003 | -147.0049 | -16.677 | 0 | 120.3256 | 300.3256 | 110.9178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1894 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3383 | 23 | 12.3 | 0 | 0 | 0 | 0 | 0 | 141 | 3383 | 1380 | 139.0685 | 20.2293 | 13.7356 | 1354.284 | 22.8003 | -162.0049 | -21.0499 | 0 | 120.3256 | 300.3256 | 110.9178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8044 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
5 | 141 | 21 | 3384 | 24 | 10.5 | 0 | 0 | 0 | 0 | 0 | 141 | 3384 | 1440 | 139.0685 | 20.2293 | 13.7356 | 1414.284 | 23.8003 | -177.0049 | -22.9381 | 0 | 120.3256 | 300.3256 | 110.9178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8577 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3385 | 1 | 11.8 | 0 | 0 | 0 | 0 | 0 | 142 | 3385 | 60 | 140.0548 | 20.427 | 13.4799 | 34.284 | 0.79606 | 168.059 | -21.9346 | 0 | 120.6397 | 59.3603 | 111.1228 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9796 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3386 | 2 | 11.6 | 0 | 0 | 0 | 0 | 0 | 142 | 3386 | 120 | 140.0548 | 20.427 | 13.4799 | 94.284 | 1.7961 | 153.059 | -18.5291 | 0 | 120.6397 | 59.3603 | 111.1228 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6191 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3387 | 3 | 13.1 | 0 | 0 | 0 | 0 | 0 | 142 | 3387 | 180 | 140.0548 | 20.427 | 13.4799 | 154.284 | 2.7961 | 138.059 | -12.8875 | 0 | 120.6397 | 59.3603 | 111.1228 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6678 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3388 | 4 | 11.6 | 0 | 0 | 0 | 0 | 0 | 142 | 3388 | 240 | 140.0548 | 20.427 | 13.4799 | 214.284 | 3.7961 | 123.059 | -5.4948 | 0 | 120.6397 | 59.3603 | 111.1228 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9538 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3389 | 5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 142 | 3389 | 300 | 140.0548 | 20.427 | 13.4799 | 274.284 | 4.7961 | 108.059 | 3.1749 | 3.1749 | 116.8334 | 63.1666 | 106.2324 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.0753 | 3.0753 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3390 | 6 | 11.3 | 2.31 | 11.67 | 13.98 | 11.67 | 5.84 | 142 | 3390 | 360 | 140.0548 | 20.427 | 13.4799 | 334.284 | 5.7961 | 93.059 | 12.7138 | 12.7138 | 106.4023 | 73.5977 | 92.2441 | -0.41099 | 0 | 9.961 | 9.961 | -12.69 | 0% | 4.5043 | 0 | 0 | 15.7615 | 15.7615 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3391 | 7 | 11.5 | 32.22 | 67.78 | 100 | 67.78 | 33.89 | 142 | 3391 | 420 | 140.0548 | 20.427 | 13.4799 | 394.284 | 6.7961 | 78.059 | 22.7749 | 22.7749 | 96.084 | 83.916 | 78.1922 | 17.0316 | 17.0316 | 57.8538 | 74.8855 | -0.98473 | 0% | 33.8632 | 0 | 0 | 187.9114 | 187.9114 | 0% | 11.69% | 11.69% | 80% | 9.353% | 3.1672 | 6.8721 | 6 | 19.0029 | 7.0039 | 10.11% | 10.11%
5 | 142 | 22 | 3392 | 8 | 12.4 | 97.86 | 125.75 | 223.61 | 125.75 | 62.88 | 142 | 3392 | 480 | 140.0548 | 20.427 | 13.4799 | 454.284 | 7.7961 | 63.059 | 33.0311 | 33.0311 | 85.1844 | 94.8156 | 64.2016 | 78.1321 | 78.1321 | 107.3343 | 185.4664 | 0.092971 | 9.297% | 83.8679 | 7.7972 | 5.4581 | 162.116 | 162.116 | 3.367% | 11.61% | 11.61% | 80% | 9.287% | 7.7889 | 6.6439 | 6 | 46.7334 | 17.2245 | 28.83% | 28.83%
5 | 142 | 22 | 3393 | 9 | 13.1 | 253.61 | 155.92 | 409.53 | 155.92 | 77.96 | 142 | 3393 | 540 | 140.0548 | 20.427 | 13.4799 | 514.284 | 8.7961 | 48.059 | 43.0989 | 43.0989 | 72.6782 | 107.3218 | 50.4417 | 236.3886 | 236.3886 | 133.086 | 369.4747 | 0.45144 | 45.14% | 167.0764 | 75.4244 | 52.797 | 172.4934 | 172.4934 | 30.61% | 11.52% | 11.52% | 85% | 9.788% | 16.3536 | 6.4703 | 6 | 98.1214 | 36.1645 | 56.88% | 56.88%
5 | 142 | 22 | 3394 | 10 | 14.5 | 395.08 | 176.75 | 571.83 | 176.75 | 88.38 | 142 | 3394 | 600 | 140.0548 | 20.427 | 13.4799 | 574.284 | 9.7961 | 33.059 | 52.3912 | 52.3912 | 56.8946 | 123.1054 | 37.2637 | 396.906 | 396.906 | 150.8656 | 547.7715 | 0.57203 | 57.2% | 247.7023 | 141.6935 | 99.1855 | 177.4138 | 177.4138 | 55.91% | 11.43% | 11.43% | 90% | 10.29% | 25.4773 | 6.1335 | 6 | 152.8641 | 56.3409 | 86.16% | 86.16%
5 | 142 | 22 | 3395 | 11 | 16.1 | 472.31 | 184.72 | 657.03 | 184.72 | 92.36 | 142 | 3395 | 660 | 140.0548 | 20.427 | 13.4799 | 634.284 | 10.7961 | 18.059 | 59.823 | 59.823 | 35.3042 | 144.6958 | 25.6635 | 492.4573 | 492.4573 | 157.6684 | 650.1256 | 0.61412 | 61.41% | 293.9868 | 180.5443 | 126.381 | 173.1534 | 173.1534 | 72.99% | 11.38% | 11.38% | 90% | 10.25% | 30.1211 | 5.7653 | 5.7653 | 173.6577 | 66.6101 | 100.3% | 100.3%
5 | 142 | 22 | 3396 | 12 | 17.6 | 364.03 | 195 | 559.03 | 195 | 97.5 | 142 | 3396 | 720 | 140.0548 | 20.427 | 13.4799 | 694.284 | 11.7961 | 3.059 | 63.5312 | 63.5312 | 6.4422 | 173.5578 | 18.8867 | 384.7627 | 384.7627 | 166.4429 | 551.2056 | 0.58615 | 58.62% | 249.2552 | 146.1017 | 102.2712 | 156.8783 | 156.8783 | 65.19% | 11.38% | 11.38% | 90% | 10.25% | 25.5396 | 5.4364 | 5.4364 | 138.8444 | 56.4785 | 88.5% | 88.5%
5 | 142 | 22 | 3397 | 13 | 20.2 | 276.67 | 212.92 | 489.59 | 212.92 | 106.46 | 142 | 3397 | 780 | 140.0548 | 20.427 | 13.4799 | 754.284 | 12.7961 | -11.941 | 61.9095 | 61.9095 | 24.3167 | 204.3167 | 21.9934 | 290.7895 | 290.7895 | 181.7386 | 472.5281 | 0.56207 | 56.21% | 213.6772 | 120.1021 | 84.0714 | 154.8456 | 154.8456 | 54.29% | 11.35% | 11.35% | 85% | 9.646% | 20.6116 | 4.9037 | 4.9037 | 101.0731 | 45.5807 | 65.27% | 65.27%
5 | 142 | 22 | 3398 | 14 | 20.5 | 193.75 | 220 | 413.75 | 220 | 110 | 142 | 3398 | 840 | 140.0548 | 20.427 | 13.4799 | 814.284 | 13.7961 | -26.941 | 55.7351 | 55.7351 | 48.9482 | 228.9482 | 32.2377 | 198.2978 | 198.2978 | 187.7817 | 386.0796 | 0.50961 | 50.96% | 174.5852 | 88.97 | 62.279 | 150.5384 | 150.5384 | 41.37% | 11.34% | 11.34% | 85% | 9.64% | 16.8292 | 4.8453 | 4.8453 | 81.542 | 37.2162 | 54.17% | 54.17%
5 | 142 | 22 | 3399 | 15 | 20.2 | 432.03 | 164.53 | 596.56 | 164.53 | 82.27 | 142 | 3399 | 900 | 140.0548 | 20.427 | 13.4799 | 874.284 | 14.7961 | -41.941 | 47.0286 | 47.0286 | 66.7622 | 246.7622 | 44.9638 | 417.7761 | 417.7761 | 140.4351 | 558.2112 | 0.59921 | 59.92% | 252.4231 | 151.2538 | 105.8776 | 154.4186 | 154.4186 | 68.57% | 11.35% | 11.35% | 90% | 10.21% | 25.7835 | 4.9037 | 4.9037 | 126.4347 | 57.018 | 81.88% | 81.88%
5 | 142 | 22 | 3400 | 16 | 20.2 | 347.31 | 196.19 | 543.5 | 196.19 | 98.1 | 142 | 3400 | 960 | 140.0548 | 20.427 | 13.4799 | 934.284 | 15.7961 | -56.941 | 37.1866 | 37.1866 | 80.3533 | 260.3533 | 58.5481 | 299.8293 | 299.8293 | 167.4586 | 467.2879 | 0.55936 | 55.94% | 211.3076 | 118.1969 | 82.7378 | 150.2212 | 150.2212 | 55.08% | 11.35% | 11.35% | 85% | 9.646% | 20.3829 | 4.9037 | 4.9037 | 99.9517 | 45.075 | 66.54% | 66.54%
5 | 142 | 22 | 3401 | 17 | 19.7 | 193.69 | 226.58 | 420.27 | 226.58 | 113.29 | 142 | 3401 | 1020 | 140.0548 | 20.427 | 13.4799 | 994.284 | 16.7961 | -71.941 | 26.9539 | 26.9539 | 91.7565 | 271.7565 | 72.4708 | 128.7038 | 128.7038 | 193.3981 | 322.1019 | 0.44567 | 44.57% | 145.6545 | 64.914 | 45.4398 | 141.1361 | 141.1361 | 32.2% | 11.36% | 11.36% | 85% | 9.656% | 14.0643 | 5.0025 | 5.0025 | 70.3561 | 31.1018 | 49.85% | 49.85%
5 | 142 | 22 | 3402 | 18 | 17.3 | 122.03 | 147.22 | 269.25 | 147.22 | 73.61 | 142 | 3402 | 1080 | 140.0548 | 20.427 | 13.4799 | 1054.284 | 17.7961 | -86.941 | 16.7727 | 16.7727 | 102.2146 | 282.2146 | 86.5135 | 25.7164 | 25.7164 | 125.6601 | 151.3765 | 0.0063263 | 0.6326% | 68.4524 | 0.43305 | 0.30313 | 125.9194 | 125.9194 | 0.2407% | 11.45% | 11.45% | 80% | 9.159% | 6.2693 | 5.501 | 5.501 | 34.4873 | 13.8641 | 27.39% | 27.39%
5 | 142 | 22 | 3403 | 19 | 18.8 | 77.31 | 125.19 | 202.5 | 125.19 | 62.6 | 142 | 3403 | 1140 | 140.0548 | 20.427 | 13.4799 | 1114.284 | 18.7961 | -101.941 | 6.9813 | 6.9813 | 112.5287 | 292.5287 | 100.5429 | 0 | 0 | 106.8563 | 106.8563 | -0.29475 | 0% | 48.3204 | 0 | 0 | 120.6384 | 120.6384 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3404 | 20 | 16.5 | 13.25 | 49.36 | 62.61 | 49.36 | 24.68 | 142 | 3404 | 1200 | 140.0548 | 20.427 | 13.4799 | 1174.284 | 19.7961 | -116.941 | -2.0881 | 0 | 120.6397 | 300.6397 | 111.1228 | 0 | 0 | 42.1314 | 42.1314 | -2.1046 | 0% | 19.0518 | 0 | 0 | 144.2269 | 144.2269 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3405 | 21 | 15 | 0 | 3.89 | 3.89 | 3.89 | 1.95 | 142 | 3405 | 1260 | 140.0548 | 20.427 | 13.4799 | 1234.284 | 20.7961 | -131.941 | -10.0556 | 0 | 120.6397 | 300.6397 | 111.1228 | 0 | 0 | 3.3203 | 3.3203 | -37.123 | 0% | 1.5014 | 0 | 0 | -9.2707 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3406 | 22 | 13.8 | 0 | 0 | 0 | 0 | 0 | 142 | 3406 | 1320 | 140.0548 | 20.427 | 13.4799 | 1294.284 | 21.7961 | -146.941 | -16.4716 | 0 | 120.6397 | 300.6397 | 111.1228 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9276 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3407 | 23 | 12.7 | 0 | 0 | 0 | 0 | 0 | 142 | 3407 | 1380 | 140.0548 | 20.427 | 13.4799 | 1354.284 | 22.7961 | -161.941 | -20.8437 | 0 | 120.6397 | 300.6397 | 111.1228 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9386 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
5 | 142 | 22 | 3408 | 24 | 10.5 | 0 | 0 | 0 | 0 | 0 | 142 | 3408 | 1440 | 140.0548 | 20.427 | 13.4799 | 1414.284 | 23.7961 | -176.941 | -22.7382 | 0 | 120.6397 | 300.6397 | 111.1228 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6261 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3409 | 1 | 11.4 | 0 | 0 | 0 | 0 | 0 | 143 | 3409 | 60 | 141.0411 | 20.6184 | 13.2131 | 34.284 | 0.79162 | 168.1257 | -21.7549 | 0 | 120.9445 | 59.0555 | 111.3214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4071 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3410 | 2 | 10.8 | 0 | 0 | 0 | 0 | 0 | 143 | 3410 | 120 | 141.0411 | 20.6184 | 13.2131 | 94.284 | 1.7916 | 153.1257 | -18.3686 | 0 | 120.9445 | 59.0555 | 111.3214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6617 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3411 | 3 | 10.3 | 0 | 0 | 0 | 0 | 0 | 143 | 3411 | 180 | 141.0411 | 20.6184 | 13.2131 | 154.284 | 2.7916 | 138.1257 | -12.7477 | 0 | 120.9445 | 59.0555 | 111.3214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.764 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3412 | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 143 | 3412 | 240 | 141.0411 | 20.6184 | 13.2131 | 214.284 | 3.7916 | 123.1257 | -5.3743 | 0 | 120.9445 | 59.0555 | 111.3214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9832 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3413 | 5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 143 | 3413 | 300 | 141.0411 | 20.6184 | 13.2131 | 274.284 | 4.7916 | 108.1257 | 3.2793 | 3.2793 | 117.0059 | 62.9941 | 106.2667 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.79219 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3414 | 6 | 8.8 | 1.75 | 13.89 | 15.64 | 13.89 | 6.95 | 143 | 3414 | 360 | 141.0411 | 20.6184 | 13.2131 | 334.284 | 5.7916 | 93.1257 | 12.8065 | 12.8065 | 106.5855 | 73.4145 | 92.2972 | -0.31646 | 0 | 11.8559 | 11.8559 | -11.0255 | 0% | 5.3612 | 0 | 0 | 12.0269 | 12.0269 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3415 | 7 | 10.7 | 29.44 | 63.69 | 93.13 | 63.69 | 31.85 | 143 | 3415 | 420 | 141.0411 | 20.6184 | 13.2131 | 394.284 | 6.7916 | 78.1257 | 22.8609 | 22.8609 | 96.2815 | 83.7185 | 78.2631 | 15.4149 | 15.4149 | 54.3628 | 69.7777 | -1.1423 | 0% | 31.5535 | 0 | 0 | 187.4124 | 187.4124 | 0% | 11.73% | 11.73% | 80% | 9.38% | 2.9598 | 7.0797 | 6 | 17.7591 | 6.5454 | 9.476% | 9.476%
5 | 143 | 23 | 3416 | 8 | 14.6 | 158.81 | 111.03 | 269.84 | 111.03 | 55.52 | 143 | 3416 | 480 | 141.0411 | 20.6184 | 13.2131 | 454.284 | 7.7916 | 63.1257 | 33.1166 | 33.1166 | 85.4019 | 94.5981 | 64.2909 | 126.0963 | 126.0963 | 94.77 | 220.8664 | 0.22972 | 22.97% | 99.8758 | 22.9439 | 16.0607 | 170.2228 | 170.2228 | 9.435% | 11.52% | 11.52% | 80% | 9.219% | 9.2077 | 6.1099 | 6 | 55.2465 | 20.3621 | 32.46% | 32.46%
5 | 143 | 23 | 3417 | 9 | 16.4 | 266.11 | 141.03 | 407.14 | 141.03 | 70.52 | 143 | 3417 | 540 | 141.0411 | 20.6184 | 13.2131 | 514.284 | 8.7916 | 48.1257 | 43.1923 | 43.1923 | 72.9227 | 107.0773 | 50.5527 | 247.0274 | 247.0274 | 120.3766 | 367.4041 | 0.46985 | 46.99% | 166.1401 | 78.061 | 54.6427 | 179.7971 | 179.7971 | 30.39% | 11.44% | 11.44% | 85% | 9.722% | 16.1522 | 5.6983 | 5.6983 | 92.0395 | 35.719 | 51.19% | 51.19%
5 | 143 | 23 | 3418 | 10 | 18.6 | 360.64 | 141.75 | 502.39 | 141.75 | 70.88 | 143 | 3418 | 600 | 141.0411 | 20.6184 | 13.2131 | 574.284 | 9.7916 | 33.1257 | 52.5041 | 52.5041 | 57.1682 | 122.8318 | 37.4034 | 361.0864 | 361.0864 | 120.9912 | 482.0776 | 0.55953 | 55.95% | 217.9955 | 121.9757 | 85.383 | 183.3951 | 183.3951 | 46.56% | 11.38% | 11.38% | 85% | 9.67% | 21.0802 | 5.2259 | 5.2259 | 110.1638 | 46.6169 | 60.07% | 60.07%
5 | 143 | 23 | 3419 | 11 | 20.7 | 410.64 | 187.58 | 598.22 | 187.58 | 93.79 | 143 | 3419 | 660 | 141.0411 | 20.6184 | 13.2131 | 634.284 | 10.7916 | 18.1257 | 59.9699 | 59.9699 | 35.5788 | 144.4212 | 25.8421 | 426.8784 | 426.8784 | 160.1095 | 586.9879 | 0.61112 | 61.11% | 265.4359 | 162.2124 | 113.5487 | 180.5831 | 180.5831 | 62.88% | 11.34% | 11.34% | 90% | 10.21% | 27.0995 | 4.8067 | 4.8067 | 130.2583 | 59.9281 | 72.13% | 72.13%
5 | 143 | 23 | 3420 | 12 | 23.2 | 434.72 | 269.72 | 704.44 | 269.72 | 134.86 | 143 | 3420 | 720 | 141.0411 | 20.6184 | 13.2131 | 694.284 | 11.7916 | 3.1257 | 63.7168 | 63.7168 | 6.6181 | 173.3819 | 19.0858 | 458.1931 | 458.1931 | 230.2204 | 688.4135 | 0.64743 | 64.74% | 311.3006 | 201.5462 | 141.0824 | 281.3838 | 281.3838 | 50.14% | 11.33% | 11.33% | 90% | 10.2% | 31.7499 | 4.3478 | 4.3478 | 138.0424 | 70.2122 | 49.06% | 49.06%
5 | 143 | 23 | 3421 | 13 | 23 | 597.22 | 200.56 | 797.78 | 200.56 | 100.28 | 143 | 3421 | 780 | 141.0411 | 20.6184 | 13.2131 | 754.284 | 12.7916 | -11.8743 | 62.1108 | 62.1108 | 24.3126 | 204.3126 | 22.1191 | 625.9704 | 625.9704 | 171.1887 | 797.1591 | 0.66825 | 66.82% | 360.4753 | 240.8874 | 168.6212 | 174.1662 | 174.1662 | 96.82% | 11.35% | 11.35% | 90% | 10.22% | 36.8275 | 4.3829 | 4.3829 | 161.4114 | 81.4408 | 92.68% | 92.68%
5 | 143 | 23 | 3422 | 14 | 25.3 | 530.14 | 170.83 | 700.97 | 170.83 | 85.42 | 143 | 3422 | 840 | 141.0411 | 20.6184 | 13.2131 | 814.284 | 13.7916 | -26.8743 | 55.9292 | 55.9292 | 49.0436 | 229.0436 | 32.2864 | 541.047 | 541.047 | 145.8125 | 686.8595 | 0.65363 | 65.36% | 310.5979 | 203.0173 | 142.1121 | 300.6633 | 300.6633 | 47.27% | 11.32% | 11.32% | 90% | 10.19% | 31.641 | 3.9962 | 3.9962 | 126.4422 | 69.9712 | 42.05% | 42.05%
5 | 143 | 23 | 3423 | 15 | 25.1 | 564.72 | 191.53 | 756.25 | 191.53 | 95.77 | 143 | 3423 | 900 | 141.0411 | 20.6184 | 13.2131 | 874.284 | 14.7916 | -41.8743 | 47.2123 | 47.2123 | 66.8834 | 246.8834 | 44.9676 | 544.4289 | 544.4289 | 163.4811 | 707.91 | 0.6575 | 65.75% | 320.1169 | 210.4778 | 147.3345 | 302.0792 | 302.0792 | 48.77% | 11.33% | 11.33% | 90% | 10.19% | 32.6313 | 4.0283 | 4.0283 | 131.4491 | 72.1612 | 43.51% | 43.51%
5 | 143 | 23 | 3424 | 16 | 25.1 | 395.64 | 201.94 | 597.58 | 201.94 | 100.97 | 143 | 3424 | 960 | 141.0411 | 20.6184 | 13.2131 | 934.284 | 15.7916 | -56.8743 | 37.3642 | 37.3642 | 80.4724 | 260.4724 | 58.5232 | 340.4049 | 340.4049 | 172.3666 | 512.7715 | 0.60175 | 60.18% | 231.8753 | 139.5316 | 97.6721 | 290.9052 | 290.9052 | 33.58% | 11.27% | 11.27% | 90% | 10.14% | 23.5221 | 4.0283 | 4.0283 | 94.7544 | 52.017 | 32.57% | 32.57%
5 | 143 | 23 | 3425 | 17 | 22.5 | 332.69 | 148.25 | 480.94 | 148.25 | 74.13 | 143 | 3425 | 1020 | 141.0411 | 20.6184 | 13.2131 | 994.284 | 16.7916 | -71.8743 | 27.1302 | 27.1302 | 91.8658 | 271.8658 | 72.4246 | 220.2995 | 220.2995 | 126.5393 | 346.8388 | 0.48888 | 48.89% | 156.8405 | 76.6757 | 53.673 | 150.9269 | 150.9269 | 35.56% | 11.29% | 11.29% | 85% | 9.596% | 15.0508 | 4.4719 | 4.4719 | 67.3052 | 33.2835 | 44.59% | 44.59%
5 | 143 | 23 | 3426 | 18 | 22.7 | 201.75 | 123.61 | 325.36 | 123.61 | 61.81 | 143 | 3426 | 1080 | 141.0411 | 20.6184 | 13.2131 | 1054.284 | 17.7916 | -86.8743 | 16.9513 | 16.9513 | 102.3118 | 282.3118 | 86.4491 | 42.8577 | 42.8577 | 105.5077 | 148.3654 | 0.070247 | 7.025% | 67.0908 | 4.7129 | 3.299 | 138.8546 | 138.8546 | 2.376% | 11.26% | 11.26% | 80% | 9.004% | 6.041 | 4.4361 | 4.4361 | 26.7983 | 13.3591 | 19.3% | 19.3%
5 | 143 | 23 | 3427 | 19 | 22.4 | 66.86 | 100.75 | 167.61 | 100.75 | 50.38 | 143 | 3427 | 1140 | 141.0411 | 20.6184 | 13.2131 | 1114.284 | 18.7916 | -101.8743 | 7.1647 | 7.1647 | 112.6125 | 292.6125 | 100.461 | 0 | 0 | 85.9955 | 85.9955 | -0.46948 | 0% | 38.8872 | 0 | 0 | 124.5716 | 124.5716 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.4899 | 4.4899 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3428 | 20 | 21.1 | 4.53 | 28.61 | 33.14 | 28.61 | 14.31 | 143 | 3428 | 1200 | 141.0411 | 20.6184 | 13.2131 | 1174.284 | 19.7916 | -116.8743 | -1.8984 | 0 | 120.9445 | 300.9445 | 111.3214 | 0 | 0 | 24.4202 | 24.4202 | -3.7965 | 0% | 11.0428 | 0 | 0 | 148.3017 | 148.3017 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7303 | 4.7303 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3429 | 21 | 18.5 | 0 | 4.17 | 4.17 | 4.17 | 2.09 | 143 | 3429 | 1260 | 141.0411 | 20.6184 | 13.2131 | 1234.284 | 20.7916 | -131.8743 | -9.8595 | 0 | 120.9445 | 300.9445 | 111.3214 | 0 | 0 | 3.5593 | 3.5593 | -32.3692 | 0% | 1.6095 | 0 | 0 | -5.3994 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3430 | 22 | 16.8 | 0 | 0 | 0 | 0 | 0 | 143 | 3430 | 1320 | 141.0411 | 20.6184 | 13.2131 | 1294.284 | 21.7916 | -146.8743 | -16.2709 | 0 | 120.9445 | 300.9445 | 111.3214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1569 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3431 | 23 | 15.3 | 0 | 0 | 0 | 0 | 0 | 143 | 3431 | 1380 | 141.0411 | 20.6184 | 13.2131 | 1354.284 | 22.7916 | -161.8743 | -20.6431 | 0 | 120.9445 | 300.9445 | 111.3214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7831 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
5 | 143 | 23 | 3432 | 24 | 14.5 | 0 | 0 | 0 | 0 | 0 | 143 | 3432 | 1440 | 141.0411 | 20.6184 | 13.2131 | 1414.284 | 23.7916 | -176.8743 | -22.5444 | 0 | 120.9445 | 300.9445 | 111.3214 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3425 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3433 | 1 | 13.9 | 0 | 0 | 0 | 0 | 0 | 144 | 3433 | 60 | 142.0274 | 20.8036 | 12.9357 | 34.284 | 0.787 | 168.1951 | -21.5817 | 0 | 121.2398 | 58.7602 | 111.5135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.001 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3434 | 2 | 13.1 | 0 | 0 | 0 | 0 | 0 | 144 | 3434 | 120 | 142.0274 | 20.8036 | 12.9357 | 94.284 | 1.787 | 153.1951 | -18.2147 | 0 | 121.2398 | 58.7602 | 111.5135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.581 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3435 | 3 | 12.6 | 0 | 0 | 0 | 0 | 0 | 144 | 3435 | 180 | 142.0274 | 20.8036 | 12.9357 | 154.284 | 2.787 | 138.1951 | -12.6145 | 0 | 121.2398 | 58.7602 | 111.5135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7038 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3436 | 4 | 12.1 | 0 | 0 | 0 | 0 | 0 | 144 | 3436 | 240 | 142.0274 | 20.8036 | 12.9357 | 214.284 | 3.787 | 123.1951 | -5.2603 | 0 | 121.2398 | 58.7602 | 111.5135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4658 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3437 | 5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 144 | 3437 | 300 | 142.0274 | 20.8036 | 12.9357 | 274.284 | 4.787 | 108.1951 | 3.3774 | 3.3774 | 117.176 | 62.824 | 106.3041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.1576 | 1.1576 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3438 | 6 | 11.3 | 3.81 | 11.31 | 15.12 | 11.31 | 5.66 | 144 | 3438 | 360 | 142.0274 | 20.8036 | 12.9357 | 334.284 | 5.787 | 93.1951 | 12.893 | 12.893 | 106.7662 | 73.2338 | 92.3531 | -0.70106 | 0 | 9.6537 | 9.6537 | -13.1195 | 0% | 4.3654 | 0 | 0 | 14.1144 | 14.1144 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3439 | 7 | 12.4 | 47.78 | 47.69 | 95.47 | 47.69 | 23.85 | 144 | 3439 | 420 | 142.0274 | 20.8036 | 12.9357 | 394.284 | 6.787 | 78.1951 | 22.9408 | 22.9408 | 96.4761 | 83.5239 | 78.3361 | 24.7825 | 24.7825 | 40.706 | 65.4884 | -1.2097 | 0% | 29.6139 | 0 | 0 | 186.9605 | 186.9605 | 0% | 11.66% | 11.66% | 80% | 9.327% | 2.7622 | 6.6439 | 6 | 16.5729 | 6.1082 | 8.864% | 8.864%
5 | 144 | 24 | 3440 | 8 | 15 | 151.47 | 101.86 | 253.33 | 101.86 | 50.93 | 144 | 3440 | 480 | 142.0274 | 20.8036 | 12.9357 | 454.284 | 7.787 | 63.1951 | 33.1958 | 33.1958 | 85.6163 | 94.3837 | 64.3819 | 119.618 | 119.618 | 86.9429 | 206.561 | 0.19435 | 19.43% | 93.4069 | 18.1536 | 12.7075 | 165.7271 | 165.7271 | 7.668% | 11.52% | 11.52% | 80% | 9.212% | 8.6048 | 6.0165 | 6 | 51.6287 | 19.0287 | 31.15% | 31.15%
5 | 144 | 24 | 3441 | 9 | 17.4 | 235.28 | 153.14 | 388.42 | 153.14 | 76.57 | 144 | 3441 | 540 | 142.0274 | 20.8036 | 12.9357 | 514.284 | 8.787 | 48.1951 | 43.279 | 43.279 | 73.1643 | 106.8357 | 50.6648 | 217.5382 | 217.5382 | 130.7132 | 348.2514 | 0.45791 | 45.79% | 157.4793 | 72.1118 | 50.4782 | 175.9092 | 175.9092 | 28.7% | 11.42% | 11.42% | 85% | 9.704% | 15.282 | 5.4794 | 5.4794 | 83.7357 | 33.7947 | 47.6% | 47.6%
5 | 144 | 24 | 3442 | 10 | 17.8 | 211.86 | 222.14 | 434 | 222.14 | 111.07 | 144 | 3442 | 600 | 142.0274 | 20.8036 | 12.9357 | 574.284 | 9.787 | 33.1951 | 52.6099 | 52.6099 | 57.4399 | 122.5601 | 37.5429 | 211.4273 | 211.4273 | 189.6084 | 401.0357 | 0.50569 | 50.57% | 181.3483 | 91.7064 | 64.1945 | 174.3855 | 174.3855 | 36.81% | 11.4% | 11.4% | 85% | 9.69% | 17.5731 | 5.3938 | 5.3938 | 94.7853 | 38.8613 | 54.35% | 54.35%
5 | 144 | 24 | 3443 | 11 | 21.1 | 292.31 | 236.31 | 528.62 | 236.31 | 118.16 | 144 | 3443 | 660 | 142.0274 | 20.8036 | 12.9357 | 634.284 | 10.787 | 18.1951 | 60.1096 | 60.1096 | 35.8547 | 144.1453 | 26.0182 | 302.9893 | 302.9893 | 201.7032 | 504.6925 | 0.5814 | 58.14% | 228.2219 | 132.6883 | 92.8818 | 173.8699 | 173.8699 | 53.42% | 11.33% | 11.33% | 90% | 10.2% | 23.2803 | 4.7303 | 4.7303 | 110.1231 | 51.4823 | 63.34% | 63.34%
5 | 144 | 24 | 3444 | 12 | 19 | 318.14 | 280.92 | 599.06 | 280.92 | 140.46 | 144 | 3444 | 720 | 142.0274 | 20.8036 | 12.9357 | 694.284 | 11.787 | 3.1951 | 63.8957 | 63.8957 | 6.8004 | 173.1996 | 19.2792 | 334.4106 | 334.4106 | 239.7802 | 574.1909 | 0.6003 | 60.03% | 259.6491 | 155.8662 | 109.1064 | 159.8958 | 159.8958 | 68.24% | 11.36% | 11.36% | 90% | 10.23% | 26.5569 | 5.1437 | 5.1437 | 136.6005 | 58.7281 | 85.43% | 85.43%
5 | 144 | 24 | 3445 | 13 | 24.1 | 307.97 | 304.17 | 612.14 | 304.17 | 152.09 | 144 | 3445 | 780 | 142.0274 | 20.8036 | 12.9357 | 754.284 | 12.787 | -11.8049 | 62.3069 | 62.3069 | 24.2996 | 204.2996 | 22.2393 | 321.9387 | 321.9387 | 259.6253 | 581.564 | 0.622 | 62.2% | 262.9832 | 163.575 | 114.5025 | 270.1392 | 270.1392 | 42.39% | 11.3% | 11.3% | 90% | 10.17% | 26.7519 | 4.1933 | 4.1933 | 112.1791 | 59.1594 | 41.53% | 41.53%
5 | 144 | 24 | 3446 | 14 | 25.1 | 339.53 | 286.19 | 625.72 | 286.19 | 143.1 | 144 | 3446 | 840 | 142.0274 | 20.8036 | 12.9357 | 814.284 | 13.787 | -26.8049 | 56.1193 | 56.1193 | 49.1302 | 229.1302 | 32.3308 | 345.5719 | 345.5719 | 244.2784 | 589.8504 | 0.62818 | 62.82% | 266.7303 | 167.555 | 117.2885 | 288.8163 | 288.8163 | 40.61% | 11.29% | 11.29% | 90% | 10.16% | 27.1098 | 4.0283 | 4.0283 | 109.2068 | 59.9509 | 37.81% | 37.81%
5 | 144 | 24 | 3447 | 15 | 26 | 244.17 | 228.89 | 473.06 | 228.89 | 114.45 | 144 | 3447 | 900 | 142.0274 | 20.8036 | 12.9357 | 874.284 | 14.787 | -41.8049 | 47.3928 | 47.3928 | 66.9966 | 246.9966 | 44.9678 | 234.7125 | 234.7125 | 195.3698 | 430.0824 | 0.56732 | 56.73% | 194.4833 | 110.3339 | 77.2337 | 298.4379 | 298.4379 | 25.88% | 11.23% | 11.23% | 85% | 9.545% | 18.5643 | 3.8858 | 3.8858 | 72.1371 | 41.0532 | 24.17% | 24.17%
5 | 144 | 24 | 3448 | 16 | 25.2 | 283.81 | 266.75 | 550.56 | 266.75 | 133.38 | 144 | 3448 | 960 | 142.0274 | 20.8036 | 12.9357 | 934.284 | 15.787 | -56.8049 | 37.5391 | 37.5391 | 80.5842 | 260.5842 | 58.4952 | 243.4101 | 243.4101 | 227.6854 | 471.0955 | 0.58431 | 58.43% | 213.0294 | 124.4759 | 87.1331 | 278.7756 | 278.7756 | 31.26% | 11.26% | 11.26% | 85% | 9.569% | 20.3853 | 4.0122 | 4.0122 | 81.7899 | 45.0803 | 29.34% | 29.34%
5 | 144 | 24 | 3449 | 17 | 25 | 249.81 | 194.72 | 444.53 | 194.72 | 97.36 | 144 | 3449 | 1020 | 142.0274 | 20.8036 | 12.9357 | 994.284 | 16.787 | -71.8049 | 27.3038 | 27.3038 | 91.9684 | 271.9684 | 72.3757 | 164.8891 | 164.8891 | 166.2039 | 331.093 | 0.49013 | 49.01% | 149.7203 | 73.3825 | 51.3677 | 277.5091 | 277.5091 | 18.51% | 11.22% | 11.22% | 85% | 9.54% | 14.2827 | 4.0445 | 4.0445 | 57.7664 | 31.5849 | 20.82% | 20.82%
5 | 144 | 24 | 3450 | 18 | 25.1 | 158.06 | 158.33 | 316.39 | 158.33 | 79.17 | 144 | 3450 | 1080 | 142.0274 | 20.8036 | 12.9357 | 1054.284 | 17.787 | -86.8049 | 17.1271 | 17.1271 | 102.4029 | 282.4029 | 86.3824 | 33.8652 | 33.8652 | 135.1431 | 169.0083 | 0.19038 | 19.04% | 76.4255 | 14.55 | 10.185 | 267.5045 | 267.5045 | 3.807% | 11.18% | 11.18% | 80% | 8.94% | 6.8324 | 4.0283 | 4.0283 | 27.5233 | 15.1094 | 10.29% | 10.29%
5 | 144 | 24 | 3451 | 19 | 24.5 | 86.03 | 121.67 | 207.7 | 121.67 | 60.84 | 144 | 3451 | 1140 | 142.0274 | 20.8036 | 12.9357 | 1114.284 | 18.787 | -101.8049 | 7.345 | 7.345 | 112.6904 | 292.6904 | 100.3774 | 0 | 0 | 103.8518 | 103.8518 | -0.20695 | 0% | 46.9618 | 0 | 0 | 249.9394 | 249.9394 | 0% | 11.18% | 0% | 80% | 0% | 0 | 4.1265 | 4.1265 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3452 | 20 | 22.9 | 25.75 | 53.53 | 79.28 | 53.53 | 26.77 | 144 | 3452 | 1200 | 142.0274 | 20.8036 | 12.9357 | 1174.284 | 19.787 | -116.8049 | -1.7123 | 0 | 121.2398 | 301.2398 | 111.5135 | 0 | 0 | 45.6907 | 45.6907 | -1.5692 | 0% | 20.6613 | 0 | 0 | 153.5329 | 153.5329 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.4006 | 4.4006 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3453 | 21 | 20.7 | 0 | 5 | 5 | 5 | 2.5 | 144 | 3453 | 1260 | 142.0274 | 20.8036 | 12.9357 | 1234.284 | 20.787 | -131.8049 | -9.6675 | 0 | 121.2398 | 301.2398 | 111.5135 | 0 | 0 | 4.2678 | 4.2678 | -25.7251 | 0% | 1.9299 | 0 | 0 | -2.5196 | 0 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.8067 | 4.8067 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3454 | 22 | 18 | 0 | 0 | 0 | 0 | 0 | 144 | 3454 | 1320 | 142.0274 | 20.8036 | 12.9357 | 1294.284 | 21.787 | -146.8049 | -16.0751 | 0 | 121.2398 | 301.2398 | 111.5135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6702 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3455 | 23 | 16.7 | 0 | 0 | 0 | 0 | 0 | 144 | 3455 | 1380 | 142.0274 | 20.8036 | 12.9357 | 1354.284 | 22.787 | -161.8049 | -20.448 | 0 | 121.2398 | 301.2398 | 111.5135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0122 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
5 | 144 | 24 | 3456 | 24 | 15.8 | 0 | 0 | 0 | 0 | 0 | 144 | 3456 | 1440 | 142.0274 | 20.8036 | 12.9357 | 1414.284 | 23.787 | -176.8049 | -22.3568 | 0 | 121.2398 | 301.2398 | 111.5135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7446 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3457 | 1 | 15.2 | 0 | 0 | 0 | 0 | 0 | 145 | 3457 | 60 | 143.0137 | 20.9824 | 12.6479 | 34.284 | 0.7822 | 168.267 | -21.415 | 0 | 121.5255 | 58.4745 | 111.699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3241 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3458 | 2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 145 | 3458 | 120 | 143.0137 | 20.9824 | 12.6479 | 94.284 | 1.7822 | 153.267 | -18.0674 | 0 | 121.5255 | 58.4745 | 111.699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5927 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3459 | 3 | 14.2 | 0 | 0 | 0 | 0 | 0 | 145 | 3459 | 180 | 143.0137 | 20.9824 | 12.6479 | 154.284 | 2.7822 | 138.267 | -12.4878 | 0 | 121.5255 | 58.4745 | 111.699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8612 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3460 | 4 | 14.2 | 0 | 0 | 0 | 0 | 0 | 145 | 3460 | 240 | 143.0137 | 20.9824 | 12.6479 | 214.284 | 3.7822 | 123.267 | -5.1527 | 0 | 121.5255 | 58.4745 | 111.699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8612 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3461 | 5 | 13.7 | 0 | 0 | 0 | 0 | 0 | 145 | 3461 | 300 | 143.0137 | 20.9824 | 12.6479 | 274.284 | 4.7822 | 108.267 | 3.4693 | 3.4693 | 117.3438 | 62.6562 | 106.3444 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.25714 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3462 | 6 | 13.4 | 3.06 | 12.42 | 15.48 | 12.42 | 6.21 | 145 | 3462 | 360 | 143.0137 | 20.9824 | 12.6479 | 334.284 | 5.7822 | 93.267 | 12.9732 | 12.9732 | 106.944 | 73.056 | 92.4114 | -0.5735 | 0 | 10.6011 | 10.6011 | -11.4188 | 0% | 4.7938 | 0 | 0 | 10.2622 | 10.2622 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3463 | 7 | 14.7 | 45.75 | 50.83 | 96.58 | 50.83 | 25.42 | 145 | 3463 | 420 | 143.0137 | 20.9824 | 12.6479 | 394.284 | 6.7822 | 78.267 | 23.0143 | 23.0143 | 96.6675 | 83.3325 | 78.4113 | 23.5075 | 23.5075 | 43.3861 | 66.8936 | -1.0887 | 0% | 30.2493 | 0 | 0 | 179.4268 | 179.4268 | 0% | 11.57% | 11.57% | 80% | 9.253% | 2.7988 | 6.0865 | 6 | 16.793 | 6.1894 | 9.359% | 9.359%
5 | 145 | 25 | 3464 | 8 | 18.2 | 122.97 | 128.42 | 251.39 | 128.42 | 64.21 | 145 | 3464 | 480 | 143.0137 | 20.9824 | 12.6479 | 454.284 | 7.7822 | 63.267 | 33.2687 | 33.2687 | 85.8274 | 94.1726 | 64.4745 | 96.5961 | 96.5961 | 109.6133 | 206.2094 | 0.22817 | 22.82% | 93.2479 | 21.2766 | 14.8936 | 157.7993 | 157.7993 | 9.438% | 11.41% | 11.41% | 80% | 9.129% | 8.5123 | 5.3093 | 5.3093 | 45.1941 | 18.8241 | 28.64% | 28.64%
5 | 145 | 25 | 3465 | 9 | 21.2 | 145.83 | 177.22 | 323.05 | 177.22 | 88.61 | 145 | 3465 | 540 | 143.0137 | 20.9824 | 12.6479 | 514.284 | 8.7822 | 48.267 | 43.3592 | 43.3592 | 73.4026 | 106.5974 | 50.7777 | 134.3096 | 134.3096 | 151.2667 | 285.5763 | 0.41137 | 41.14% | 129.1376 | 53.1233 | 37.1863 | 166.0565 | 166.0565 | 22.39% | 11.32% | 11.32% | 80% | 9.054% | 11.6927 | 4.7114 | 4.7114 | 55.0889 | 25.8573 | 33.17% | 33.17%
5 | 145 | 25 | 3466 | 10 | 23.3 | 110 | 200.92 | 310.92 | 200.92 | 100.46 | 145 | 3466 | 600 | 143.0137 | 20.9824 | 12.6479 | 574.284 | 9.7822 | 33.267 | 52.7088 | 52.7088 | 57.7093 | 122.2907 | 37.6821 | 109.4259 | 109.4259 | 171.4959 | 280.9219 | 0.42109 | 42.11% | 127.0329 | 53.4926 | 37.4448 | 171.3581 | 171.3581 | 21.85% | 11.26% | 11.26% | 80% | 9.006% | 11.4409 | 4.3304 | 4.3304 | 49.543 | 25.3005 | 28.91% | 28.91%
5 | 145 | 25 | 3467 | 11 | 25.5 | 357.22 | 199.25 | 556.47 | 199.25 | 99.63 | 145 | 3467 | 660 | 143.0137 | 20.9824 | 12.6479 | 634.284 | 10.7822 | 18.267 | 60.242 | 60.242 | 36.1316 | 143.8684 | 26.1918 | 369.2321 | 369.2321 | 170.0705 | 539.3026 | 0.61328 | 61.33% | 243.8726 | 149.5627 | 104.6939 | 289.9084 | 289.9084 | 36.11% | 11.27% | 11.27% | 90% | 10.15% | 24.7429 | 3.9643 | 3.9643 | 98.0876 | 54.7167 | 33.83% | 33.83%
5 | 145 | 25 | 3468 | 12 | 26.8 | 241.67 | 182.78 | 424.45 | 182.78 | 91.39 | 145 | 3468 | 720 | 143.0137 | 20.9824 | 12.6479 | 694.284 | 11.7822 | 3.267 | 64.0679 | 64.0679 | 6.989 | 173.011 | 19.4668 | 253.3655 | 253.3655 | 156.0125 | 409.378 | 0.55948 | 55.95% | 185.1207 | 103.5716 | 72.5001 | 280.9478 | 280.9478 | 25.81% | 11.21% | 11.21% | 85% | 9.525% | 17.6328 | 3.7639 | 3.7639 | 66.3677 | 38.9933 | 23.62% | 23.62%
5 | 145 | 25 | 3469 | 13 | 27.3 | 142.08 | 234.72 | 376.8 | 234.72 | 117.36 | 145 | 3469 | 780 | 143.0137 | 20.9824 | 12.6479 | 754.284 | 12.7822 | -11.733 | 62.4977 | 62.4977 | 24.2776 | 204.2776 | 22.3539 | 148.1445 | 148.1445 | 200.3461 | 348.4905 | 0.51978 | 51.98% | 157.5874 | 81.9111 | 57.3378 | 281.9729 | 281.9729 | 20.33% | 11.17% | 11.17% | 85% | 9.495% | 14.9631 | 3.69 | 3.69 | 55.2132 | 33.0896 | 19.58% | 19.58%
5 | 145 | 25 | 3470 | 14 | 28.1 | 534.25 | 228.33 | 762.58 | 228.33 | 114.17 | 145 | 3470 | 840 | 143.0137 | 20.9824 | 12.6479 | 814.284 | 13.7822 | -26.733 | 56.3054 | 56.3054 | 49.2079 | 229.2079 | 32.3709 | 542.3363 | 542.3363 | 194.8918 | 737.2282 | 0.67193 | 67.19% | 333.3746 | 224.0029 | 156.802 | 312.739 | 312.739 | 50.14% | 11.32% | 11.32% | 90% | 10.19% | 33.9763 | 3.5753 | 3.5753 | 121.476 | 75.1356 | 38.84% | 38.84%
5 | 145 | 25 | 3471 | 15 | 28.3 | 372.31 | 177.97 | 550.28 | 177.97 | 88.99 | 145 | 3471 | 900 | 143.0137 | 20.9824 | 12.6479 | 874.284 | 14.7822 | -41.733 | 47.5701 | 47.5701 | 67.1018 | 247.1018 | 44.9644 | 356.8965 | 356.8965 | 151.9069 | 508.8034 | 0.61345 | 61.35% | 230.0809 | 141.1439 | 98.8007 | 308.4456 | 308.4456 | 32.03% | 11.22% | 11.22% | 90% | 10.1% | 23.2316 | 3.5474 | 3.5474 | 82.4109 | 51.3747 | 26.72% | 26.72%
5 | 145 | 25 | 3472 | 16 | 27.3 | 356.75 | 140.56 | 497.31 | 140.56 | 70.28 | 145 | 3472 | 960 | 143.0137 | 20.9824 | 12.6479 | 934.284 | 15.7822 | -56.733 | 37.7112 | 37.7112 | 80.6889 | 260.6889 | 58.4642 | 305.0467 | 305.0467 | 119.9755 | 425.0222 | 0.57096 | 57.1% | 192.195 | 109.7356 | 76.8149 | 293.8854 | 293.8854 | 26.14% | 11.2% | 11.2% | 85% | 9.521% | 18.2993 | 3.69 | 3.69 | 67.5237 | 40.4673 | 22.98% | 22.98%
5 | 145 | 25 | 3473 | 17 | 24.2 | 252.14 | 196.03 | 448.17 | 196.03 | 98.02 | 145 | 3473 | 1020 | 143.0137 | 20.9824 | 12.6479 | 994.284 | 16.7822 | -71.733 | 27.4748 | 27.4748 | 92.0643 | 272.0643 | 72.3242 | 165.9394 | 165.9394 | 167.3221 | 333.2615 | 0.48704 | 48.7% | 150.7009 | 73.3969 | 51.3778 | 165.9664 | 165.9664 | 30.96% | 11.24% | 11.24% | 85% | 9.558% | 14.4033 | 4.1765 | 4.1765 | 60.1555 | 31.8517 | 36.25% | 36.25%
5 | 145 | 25 | 3474 | 18 | 20.8 | 116.31 | 128.25 | 244.56 | 128.25 | 64.13 | 145 | 3474 | 1080 | 143.0137 | 20.9824 | 12.6479 | 1054.284 | 17.7822 | -86.733 | 17.3 | 17.3 | 102.4877 | 282.4877 | 86.3136 | 25.1472 | 25.1472 | 109.4682 | 134.6155 | -0.035435 | 0% | 60.8731 | 0 | 0 | 126.5285 | 126.5285 | 0% | 11.32% | 11.32% | 80% | 9.058% | 5.514 | 4.7875 | 4.7875 | 26.3981 | 12.1937 | 20.86% | 20.86%
5 | 145 | 25 | 3475 | 19 | 20.3 | 72.78 | 74.64 | 147.42 | 74.64 | 37.32 | 145 | 3475 | 1140 | 143.0137 | 20.9824 | 12.6479 | 1114.284 | 18.7822 | -101.733 | 7.5222 | 7.5222 | 112.7624 | 292.7624 | 100.292 | 0 | 0 | 63.7092 | 63.7092 | -0.98691 | 0% | 28.8093 | 0 | 0 | 158.6769 | 158.6769 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.8842 | 4.8842 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3476 | 20 | 19.7 | 24.17 | 40.19 | 64.36 | 40.19 | 20.1 | 145 | 3476 | 1200 | 143.0137 | 20.9824 | 12.6479 | 1174.284 | 19.7822 | -116.733 | -1.5297 | 0 | 121.5255 | 301.5255 | 111.699 | 0 | 0 | 34.3043 | 34.3043 | -2.5605 | 0% | 15.5124 | 0 | 0 | 146.5334 | 146.5334 | 0% | 11.36% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3477 | 21 | 18.7 | 0 | 5.28 | 5.28 | 5.28 | 2.64 | 145 | 3477 | 1260 | 143.0137 | 20.9824 | 12.6479 | 1234.284 | 20.7822 | -131.733 | -9.4797 | 0 | 121.5255 | 301.5255 | 111.699 | 0 | 0 | 4.5068 | 4.5068 | -25.2968 | 0% | 2.038 | 0 | 0 | -6.6398 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2053 | 5.2053 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3478 | 22 | 17.5 | 0 | 0 | 0 | 0 | 0 | 145 | 3478 | 1320 | 143.0137 | 20.9824 | 12.6479 | 1294.284 | 21.7822 | -146.733 | -15.8843 | 0 | 121.5255 | 301.5255 | 111.699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2992 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3479 | 23 | 17.1 | 0 | 0 | 0 | 0 | 0 | 145 | 3479 | 1380 | 143.0137 | 20.9824 | 12.6479 | 1354.284 | 22.7822 | -161.733 | -20.2586 | 0 | 121.5255 | 301.5255 | 111.699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4153 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
5 | 145 | 25 | 3480 | 24 | 16.5 | 0 | 0 | 0 | 0 | 0 | 145 | 3480 | 1440 | 143.0137 | 20.9824 | 12.6479 | 1414.284 | 23.7822 | -176.733 | -22.1753 | 0 | 121.5255 | 301.5255 | 111.699 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8363 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3481 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 146 | 3481 | 60 | 144 | 21.1548 | 12.3498 | 34.284 | 0.77723 | 168.3415 | -21.2549 | 0 | 121.8015 | 58.1985 | 111.8779 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4343 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3482 | 2 | 15.8 | 0 | 0 | 0 | 0 | 0 | 146 | 3482 | 120 | 144 | 21.1548 | 12.3498 | 94.284 | 1.7772 | 153.3415 | -17.9268 | 0 | 121.8015 | 58.1985 | 111.8779 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0824 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3483 | 3 | 13.7 | 0 | 0 | 0 | 0 | 0 | 146 | 3483 | 180 | 144 | 21.1548 | 12.3498 | 154.284 | 2.7772 | 138.3415 | -12.3678 | 0 | 121.8015 | 58.1985 | 111.8779 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6261 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3484 | 4 | 13 | 0 | 0 | 0 | 0 | 0 | 146 | 3484 | 240 | 144 | 21.1548 | 12.3498 | 214.284 | 3.7772 | 123.3415 | -5.0516 | 0 | 121.8015 | 58.1985 | 111.8779 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6929 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3485 | 5 | 15.3 | 0 | 0 | 0 | 0 | 0 | 146 | 3485 | 300 | 144 | 21.1548 | 12.3498 | 274.284 | 4.7772 | 108.3415 | 3.5548 | 3.5548 | 117.5092 | 62.4908 | 106.3877 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.5599 | 5.5599 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3486 | 6 | 15.1 | 3.97 | 17.22 | 21.19 | 17.22 | 8.61 | 146 | 3486 | 360 | 144 | 21.1548 | 12.3498 | 334.284 | 5.7772 | 93.3415 | 13.0473 | 13.0473 | 107.119 | 72.881 | 92.4723 | -0.75857 | 0 | 14.6982 | 14.6982 | -7.7483 | 0% | 6.6465 | 0 | 0 | 19.6881 | 19.6881 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3487 | 7 | 16.3 | 71.47 | 60.08 | 131.55 | 60.08 | 30.04 | 146 | 3487 | 420 | 144 | 21.1548 | 12.3498 | 394.284 | 6.7772 | 78.3415 | 23.0817 | 23.0817 | 96.8558 | 83.1442 | 78.4884 | 36.381 | 36.381 | 51.2815 | 87.6625 | -0.59903 | 0% | 39.641 | 0 | 0 | 196.325 | 196.325 | 0% | 11.5% | 11.5% | 80% | 9.198% | 3.646 | 5.7206 | 5.7206 | 20.8572 | 8.0628 | 10.62% | 10.62%
5 | 146 | 26 | 3488 | 8 | 18.9 | 183.14 | 96.19 | 279.33 | 96.19 | 48.1 | 146 | 3488 | 480 | 144 | 21.1548 | 12.3498 | 454.284 | 7.7772 | 63.3415 | 33.3353 | 33.3353 | 86.0351 | 93.9649 | 64.5686 | 143.113 | 143.113 | 82.1033 | 225.2163 | 0.28367 | 28.37% | 101.8428 | 28.8898 | 20.2229 | 175.1382 | 175.1382 | 11.55% | 11.39% | 11.39% | 80% | 9.109% | 9.2773 | 5.1642 | 5.1642 | 47.9094 | 20.5159 | 27.36% | 27.36%
5 | 146 | 26 | 3489 | 9 | 20.6 | 286.67 | 118.81 | 405.48 | 118.81 | 59.41 | 146 | 3489 | 540 | 144 | 21.1548 | 12.3498 | 514.284 | 8.7772 | 48.3415 | 43.4327 | 43.4327 | 73.6376 | 106.3624 | 50.8913 | 263.024 | 263.024 | 101.4107 | 364.4347 | 0.49273 | 49.27% | 164.7974 | 81.1998 | 56.8399 | 183.9067 | 183.9067 | 30.91% | 11.34% | 11.34% | 85% | 9.637% | 15.8815 | 4.8259 | 4.8259 | 76.6431 | 35.1205 | 41.68% | 41.68%
5 | 146 | 26 | 3490 | 10 | 23.4 | 363.06 | 177.03 | 540.09 | 177.03 | 88.52 | 146 | 3490 | 600 | 144 | 21.1548 | 12.3498 | 574.284 | 9.7772 | 33.3415 | 52.8007 | 52.8007 | 57.9763 | 122.0237 | 37.8208 | 360.0494 | 360.0494 | 151.1046 | 511.154 | 0.59398 | 59.4% | 231.1438 | 137.2953 | 96.1067 | 197.08 | 197.08 | 48.77% | 11.3% | 11.3% | 90% | 10.17% | 23.5031 | 4.313 | 4.313 | 101.3686 | 51.9751 | 51.44% | 51.44%
5 | 146 | 26 | 3491 | 11 | 25.2 | 563.53 | 157.58 | 721.11 | 157.58 | 78.79 | 146 | 3491 | 660 | 144 | 21.1548 | 12.3498 | 634.284 | 10.7772 | 18.3415 | 60.3671 | 60.3671 | 36.4091 | 143.5909 | 26.3627 | 580.8986 | 580.8986 | 134.5029 | 715.4016 | 0.65934 | 65.93% | 323.5046 | 213.2979 | 149.3086 | 227.9721 | 227.9721 | 65.49% | 11.33% | 11.33% | 90% | 10.2% | 32.9814 | 4.0122 | 4.0122 | 132.3279 | 72.9354 | 58.05% | 58.05%
5 | 146 | 26 | 3492 | 12 | 27 | 540.56 | 214.03 | 754.59 | 214.03 | 107.02 | 146 | 3492 | 720 | 144 | 21.1548 | 12.3498 | 694.284 | 11.7772 | 3.3415 | 64.2333 | 64.2333 | 7.1836 | 172.8164 | 19.6486 | 565.2904 | 565.2904 | 182.686 | 747.9765 | 0.67074 | 67.07% | 338.235 | 226.8662 | 158.8063 | 300.2858 | 300.2858 | 52.89% | 11.33% | 11.33% | 90% | 10.2% | 34.4958 | 3.7341 | 3.7341 | 128.8108 | 76.2844 | 42.9% | 42.9%
5 | 146 | 26 | 3493 | 13 | 28.3 | 637.92 | 222.5 | 860.42 | 222.5 | 111.25 | 146 | 3493 | 780 | 144 | 21.1548 | 12.3498 | 754.284 | 12.7772 | -11.6585 | 62.683 | 62.683 | 24.2465 | 204.2465 | 22.463 | 663.5128 | 663.5128 | 189.9156 | 853.4284 | 0.6904 | 69.04% | 385.9203 | 266.4388 | 186.5072 | 333.9163 | 333.9163 | 55.85% | 11.38% | 11.38% | 95% | 10.81% | 41.7086 | 3.5474 | 3.5474 | 147.9553 | 92.2349 | 44.31% | 44.31%
5 | 146 | 26 | 3494 | 14 | 28.5 | 650.97 | 199.17 | 850.14 | 199.17 | 99.59 | 146 | 3494 | 840 | 144 | 21.1548 | 12.3498 | 814.284 | 13.7772 | -26.6585 | 56.4874 | 56.4874 | 49.2766 | 229.2766 | 32.4066 | 659.1692 | 659.1692 | 170.0022 | 829.1714 | 0.68758 | 68.76% | 374.9513 | 257.8086 | 180.466 | 336.435 | 336.435 | 53.64% | 11.37% | 11.37% | 95% | 10.8% | 40.4848 | 3.5197 | 3.5197 | 142.4934 | 89.5286 | 42.35% | 42.35%
5 | 146 | 26 | 3495 | 15 | 29 | 483.47 | 209.44 | 692.91 | 209.44 | 104.72 | 146 | 3495 | 900 | 144 | 21.1548 | 12.3498 | 874.284 | 14.7772 | -41.6585 | 47.7441 | 47.7441 | 67.1988 | 247.1988 | 44.9574 | 462.2301 | 462.2301 | 178.7682 | 640.9983 | 0.65503 | 65.5% | 289.8594 | 189.8659 | 132.9061 | 346.501 | 346.501 | 38.36% | 11.27% | 11.27% | 90% | 10.15% | 29.409 | 3.4517 | 3.4517 | 101.5112 | 65.0355 | 29.3% | 29.3%
5 | 146 | 26 | 3496 | 16 | 29.9 | 593.69 | 140.92 | 734.61 | 140.92 | 70.46 | 146 | 3496 | 960 | 144 | 21.1548 | 12.3498 | 934.284 | 15.7772 | -56.6585 | 37.8805 | 37.8805 | 80.7863 | 260.7863 | 58.43 | 506.2081 | 506.2081 | 120.2827 | 626.4908 | 0.65456 | 65.46% | 283.2992 | 185.4356 | 129.8049 | 359.6283 | 359.6283 | 36.09% | 11.26% | 11.26% | 90% | 10.13% | 28.7032 | 3.3338 | 3.3338 | 95.6895 | 63.4746 | 26.61% | 26.61%
5 | 146 | 26 | 3497 | 17 | 27.2 | 368.25 | 167.14 | 535.39 | 167.14 | 83.57 | 146 | 3497 | 1020 | 144 | 21.1548 | 12.3498 | 994.284 | 16.7772 | -71.6585 | 27.643 | 27.643 | 92.1537 | 272.1537 | 72.2701 | 241.7085 | 241.7085 | 142.6629 | 384.3714 | 0.54577 | 54.58% | 173.8127 | 94.8611 | 66.4028 | 279.9062 | 279.9062 | 23.72% | 11.19% | 11.19% | 85% | 9.509% | 16.5284 | 3.7046 | 3.7046 | 61.231 | 36.551 | 21.88% | 21.88%
5 | 146 | 26 | 3498 | 18 | 25 | 180.64 | 135.56 | 316.2 | 135.56 | 67.78 | 146 | 3498 | 1080 | 144 | 21.1548 | 12.3498 | 1054.284 | 17.7772 | -86.6585 | 17.4701 | 17.4701 | 102.5663 | 282.5663 | 86.2427 | 39.4309 | 39.4309 | 115.7077 | 155.1386 | 0.13415 | 13.41% | 70.1537 | 9.4109 | 6.5877 | 242.0548 | 242.0548 | 2.722% | 11.17% | 11.17% | 80% | 8.94% | 6.2716 | 4.0445 | 4.0445 | 25.3653 | 13.869 | 10.48% | 10.48%
5 | 146 | 26 | 3499 | 19 | 23.5 | 91.75 | 95.08 | 186.83 | 95.08 | 47.54 | 146 | 3499 | 1140 | 144 | 21.1548 | 12.3498 | 1114.284 | 18.7772 | -101.6585 | 7.6962 | 7.6962 | 112.8284 | 292.8284 | 100.205 | 0 | 0 | 81.1559 | 81.1559 | -0.51613 | 0% | 36.6987 | 0 | 0 | 133.7071 | 133.7071 | 0% | 11.21% | 0% | 80% | 0% | 0 | 4.2957 | 4.2957 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3500 | 20 | 23 | 23.06 | 43.97 | 67.03 | 43.97 | 21.99 | 146 | 3500 | 1200 | 144 | 21.1548 | 12.3498 | 1174.284 | 19.7772 | -116.6585 | -1.3508 | 0 | 121.8015 | 301.8015 | 111.8779 | 0 | 0 | 37.5307 | 37.5307 | -2.0794 | 0% | 16.9714 | 0 | 0 | 150.8086 | 150.8086 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.3829 | 4.3829 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3501 | 21 | 21.5 | 0 | 5.75 | 5.75 | 5.75 | 2.88 | 146 | 3501 | 1260 | 144 | 21.1548 | 12.3498 | 1234.284 | 20.7772 | -131.6585 | -9.2962 | 0 | 121.8015 | 301.8015 | 111.8779 | 0 | 0 | 4.9079 | 4.9079 | -21.9084 | 0% | 2.2194 | 0 | 0 | -3.6874 | 0 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6551 | 4.6551 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3502 | 22 | 20.9 | 0 | 0 | 0 | 0 | 0 | 146 | 3502 | 1320 | 144 | 21.1548 | 12.3498 | 1294.284 | 21.7772 | -146.6585 | -15.6984 | 0 | 121.8015 | 301.8015 | 111.8779 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9367 | 0 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7684 | 4.7684 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3503 | 23 | 17.4 | 0 | 0 | 0 | 0 | 0 | 146 | 3503 | 1380 | 144 | 21.1548 | 12.3498 | 1354.284 | 22.7772 | -161.6585 | -20.0749 | 0 | 121.8015 | 301.8015 | 111.8779 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.614 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
5 | 146 | 26 | 3504 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 146 | 3504 | 1440 | 144 | 21.1548 | 12.3498 | 1414.284 | 23.7772 | -176.6585 | -22.0001 | 0 | 121.8015 | 301.8015 | 111.8779 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.567 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3505 | 1 | 16.1 | 0 | 0 | 0 | 0 | 0 | 147 | 3505 | 60 | 144.9863 | 21.3208 | 12.0418 | 34.284 | 0.7721 | 168.4185 | -21.1014 | 0 | 122.0677 | 57.9323 | 112.0501 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8271 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3506 | 2 | 15.4 | 0 | 0 | 0 | 0 | 0 | 147 | 3506 | 120 | 144.9863 | 21.3208 | 12.0418 | 94.284 | 1.7721 | 153.4185 | -17.7928 | 0 | 122.0677 | 57.9323 | 112.0501 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.055 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3507 | 3 | 14.8 | 0 | 0 | 0 | 0 | 0 | 147 | 3507 | 180 | 144.9863 | 21.3208 | 12.0418 | 154.284 | 2.7721 | 138.4185 | -12.2543 | 0 | 122.0677 | 57.9323 | 112.0501 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1306 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3508 | 4 | 14.1 | 0 | 0 | 0 | 0 | 0 | 147 | 3508 | 240 | 144.9863 | 21.3208 | 12.0418 | 214.284 | 3.7721 | 123.4185 | -4.9569 | 0 | 122.0677 | 57.9323 | 112.0501 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1974 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3509 | 5 | 13.6 | 0 | 0 | 0 | 0 | 0 | 147 | 3509 | 300 | 144.9863 | 21.3208 | 12.0418 | 274.284 | 4.7721 | 108.4185 | 3.634 | 3.634 | 117.6721 | 62.3279 | 106.4339 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.6018 | 7.6018 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3510 | 6 | 13.6 | 3.89 | 16.58 | 20.47 | 16.58 | 8.29 | 147 | 3510 | 360 | 144.9863 | 21.3208 | 12.0418 | 334.284 | 5.7721 | 93.4185 | 13.1151 | 13.1151 | 107.2911 | 72.7089 | 92.5356 | -0.75844 | 0 | 14.1519 | 14.1519 | -8.3197 | 0% | 6.3995 | 0 | 0 | 22.8998 | 22.8998 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3511 | 7 | 14.8 | 29.17 | 61.31 | 90.48 | 61.31 | 30.66 | 147 | 3511 | 420 | 144.9863 | 21.3208 | 12.0418 | 394.284 | 6.7721 | 78.4185 | 23.1429 | 23.1429 | 97.0408 | 82.9592 | 78.5676 | 14.7111 | 14.7111 | 52.3314 | 67.0424 | -1.0811 | 0% | 30.3166 | 0 | 0 | 199.6163 | 199.6163 | 0% | 11.56% | 11.56% | 80% | 9.249% | 2.8041 | 6.0631 | 6 | 16.8244 | 6.201 | 8.428% | 8.428%
5 | 147 | 27 | 3512 | 8 | 17.7 | 142.03 | 99.44 | 241.47 | 99.44 | 49.72 | 147 | 3512 | 480 | 144.9863 | 21.3208 | 12.0418 | 454.284 | 7.7721 | 63.4185 | 33.3955 | 33.3955 | 86.2392 | 93.7608 | 64.664 | 110.4224 | 110.4224 | 84.8773 | 195.2997 | 0.1903 | 19.03% | 88.3145 | 16.8063 | 11.7644 | 180.3354 | 180.3354 | 6.524% | 11.43% | 11.43% | 80% | 9.143% | 8.0744 | 5.4151 | 5.4151 | 43.7236 | 17.8559 | 24.25% | 24.25%
5 | 147 | 27 | 3513 | 9 | 20.6 | 324.17 | 128.61 | 452.78 | 128.61 | 64.31 | 147 | 3513 | 540 | 144.9863 | 21.3208 | 12.0418 | 514.284 | 8.7721 | 48.4185 | 43.4997 | 43.4997 | 73.869 | 106.131 | 51.0056 | 296.3346 | 296.3346 | 109.7755 | 406.1101 | 0.52467 | 52.47% | 183.643 | 96.3517 | 67.4462 | 195.1655 | 195.1655 | 34.56% | 11.34% | 11.34% | 85% | 9.638% | 17.6998 | 4.8259 | 4.8259 | 85.4181 | 39.1415 | 43.77% | 43.77%
5 | 147 | 27 | 3514 | 10 | 22.5 | 476.86 | 134.92 | 611.78 | 134.92 | 67.46 | 147 | 3514 | 600 | 144.9863 | 21.3208 | 12.0418 | 574.284 | 9.7721 | 33.4185 | 52.8856 | 52.8856 | 58.2406 | 121.7594 | 37.959 | 471.4892 | 471.4892 | 115.1614 | 586.6506 | 0.61769 | 61.77% | 265.2834 | 163.8638 | 114.7047 | 199.8537 | 199.8537 | 57.39% | 11.32% | 11.32% | 90% | 10.19% | 27.0334 | 4.4719 | 4.4719 | 120.8901 | 59.782 | 60.49% | 60.49%
5 | 147 | 27 | 3515 | 11 | 23.8 | 598.53 | 141.47 | 740 | 141.47 | 70.74 | 147 | 3515 | 660 | 144.9863 | 21.3208 | 12.0418 | 634.284 | 10.7721 | 18.4185 | 60.4849 | 60.4849 | 36.687 | 143.313 | 26.5307 | 615.3592 | 615.3592 | 120.7522 | 736.1114 | 0.65933 | 65.93% | 332.8696 | 219.4722 | 153.6305 | 307.7067 | 307.7067 | 49.93% | 11.34% | 11.34% | 90% | 10.2% | 33.9686 | 4.2442 | 4.2442 | 144.1689 | 75.1186 | 46.85% | 46.85%
5 | 147 | 27 | 3516 | 12 | 25.5 | 667.42 | 164.36 | 831.78 | 164.36 | 82.18 | 147 | 3516 | 720 | 144.9863 | 21.3208 | 12.0418 | 694.284 | 11.7721 | 3.4185 | 64.3919 | 64.3919 | 7.3841 | 172.6159 | 19.8246 | 696.2582 | 696.2582 | 140.29 | 836.5482 | 0.68105 | 68.1% | 378.2871 | 257.632 | 180.3424 | 315.285 | 315.285 | 57.2% | 11.36% | 11.36% | 95% | 10.79% | 40.8357 | 3.9643 | 3.9643 | 161.8841 | 90.3046 | 51.35% | 51.35%
5 | 147 | 27 | 3517 | 13 | 25.6 | 342.36 | 160 | 502.36 | 160 | 80 | 147 | 3517 | 780 | 144.9863 | 21.3208 | 12.0418 | 754.284 | 12.7721 | -11.5815 | 62.8629 | 62.8629 | 24.2064 | 204.2064 | 22.5665 | 355.2544 | 355.2544 | 136.5685 | 491.823 | 0.5953 | 59.53% | 222.4023 | 132.3968 | 92.6777 | 287.7668 | 287.7668 | 32.21% | 11.26% | 11.26% | 85% | 9.569% | 21.2806 | 3.9484 | 3.9484 | 84.0252 | 47.0602 | 29.2% | 29.2%
5 | 147 | 27 | 3518 | 14 | 26.4 | 240.36 | 216.75 | 457.11 | 216.75 | 108.38 | 147 | 3518 | 840 | 144.9863 | 21.3208 | 12.0418 | 814.284 | 13.7721 | -26.5815 | 56.6652 | 56.6652 | 49.3363 | 229.3363 | 32.438 | 242.8052 | 242.8052 | 185.0077 | 427.8128 | 0.56804 | 56.8% | 193.457 | 109.8918 | 76.9243 | 301.9153 | 301.9153 | 25.48% | 11.22% | 11.22% | 85% | 9.538% | 18.4516 | 3.8243 | 3.8243 | 70.5642 | 40.8041 | 23.37% | 23.37%
5 | 147 | 27 | 3519 | 15 | 26.7 | 289.72 | 259.53 | 549.25 | 259.53 | 129.77 | 147 | 3519 | 900 | 144.9863 | 21.3208 | 12.0418 | 874.284 | 14.7721 | -41.5815 | 47.9148 | 47.9148 | 67.2877 | 247.2877 | 44.9467 | 276.2967 | 276.2967 | 221.5227 | 497.8194 | 0.6025 | 60.25% | 225.1139 | 135.6307 | 94.9415 | 310.9771 | 310.9771 | 30.53% | 11.24% | 11.24% | 85% | 9.555% | 21.5086 | 3.7789 | 3.7789 | 81.2784 | 47.5644 | 26.14% | 26.14%
5 | 147 | 27 | 3520 | 16 | 26.5 | 166.58 | 196.11 | 362.69 | 196.11 | 98.06 | 147 | 3520 | 960 | 144.9863 | 21.3208 | 12.0418 | 934.284 | 15.7721 | -56.5815 | 38.0468 | 38.0468 | 80.8763 | 260.8763 | 58.3929 | 141.6558 | 141.6558 | 167.3904 | 309.0462 | 0.47805 | 47.8% | 139.7507 | 66.8076 | 46.7653 | 298.1819 | 298.1819 | 15.68% | 11.18% | 11.18% | 85% | 9.5% | 13.2763 | 3.8091 | 3.8091 | 50.5705 | 29.3594 | 16.96% | 16.96%
5 | 147 | 27 | 3521 | 17 | 24.7 | 115.83 | 166.03 | 281.86 | 166.03 | 83.02 | 147 | 3521 | 1020 | 144.9863 | 21.3208 | 12.0418 | 994.284 | 16.7721 | -71.5815 | 27.8084 | 27.8084 | 92.2363 | 272.2363 | 72.2135 | 75.8447 | 75.8447 | 141.7155 | 217.5602 | 0.32339 | 32.34% | 98.3807 | 31.8157 | 22.271 | 246.3362 | 246.3362 | 9.041% | 11.2% | 11.2% | 80% | 8.961% | 8.816 | 4.0935 | 4.0935 | 36.0883 | 19.4959 | 14.65% | 14.65%
5 | 147 | 27 | 3522 | 18 | 24.5 | 96.75 | 111.39 | 208.14 | 111.39 | 55.7 | 147 | 3522 | 1080 | 144.9863 | 21.3208 | 12.0418 | 1054.284 | 17.7721 | -86.5815 | 17.6373 | 17.6373 | 102.6387 | 282.6387 | 86.1696 | 21.3312 | 21.3312 | 95.0773 | 116.4086 | -0.097898 | 0% | 52.6399 | 0 | 0 | 228.5749 | 228.5749 | 0% | 11.18% | 11.18% | 80% | 8.946% | 4.7093 | 4.1265 | 4.1265 | 19.4328 | 10.4142 | 8.502% | 8.502%
5 | 147 | 27 | 3523 | 19 | 23 | 52.78 | 76.86 | 129.64 | 76.86 | 38.43 | 147 | 3523 | 1140 | 144.9863 | 21.3208 | 12.0418 | 1114.284 | 18.7721 | -101.5815 | 7.8669 | 7.8669 | 112.8885 | 292.8885 | 100.1165 | 0 | 0 | 65.6041 | 65.6041 | -0.84551 | 0% | 29.6662 | 0 | 0 | 162.8723 | 162.8723 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.3829 | 4.3829 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3524 | 20 | 21.4 | 12.14 | 39.53 | 51.67 | 39.53 | 19.77 | 147 | 3524 | 1200 | 144.9863 | 21.3208 | 12.0418 | 1174.284 | 19.7721 | -116.5815 | -1.1756 | 0 | 122.0677 | 302.0677 | 112.0501 | 0 | 0 | 33.741 | 33.741 | -2.5062 | 0% | 15.2577 | 0 | 0 | 148.3315 | 148.3315 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6738 | 4.6738 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3525 | 21 | 20.7 | 0 | 7.64 | 7.64 | 7.64 | 3.82 | 147 | 3525 | 1260 | 144.9863 | 21.3208 | 12.0418 | 1234.284 | 20.7721 | -131.5815 | -9.1171 | 0 | 122.0677 | 302.0677 | 112.0501 | 0 | 0 | 6.5211 | 6.5211 | -16.558 | 0% | 2.9489 | 0 | 0 | -3.2231 | 0 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.8067 | 4.8067 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3526 | 22 | 19.6 | 0 | 0 | 0 | 0 | 0 | 147 | 3526 | 1320 | 144.9863 | 21.3208 | 12.0418 | 1294.284 | 21.7721 | -146.5815 | -15.5176 | 0 | 122.0677 | 302.0677 | 112.0501 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.0096 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0224 | 5.0224 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3527 | 23 | 18.6 | 0 | 0 | 0 | 0 | 0 | 147 | 3527 | 1380 | 144.9863 | 21.3208 | 12.0418 | 1354.284 | 22.7721 | -161.5815 | -19.8968 | 0 | 122.0677 | 302.0677 | 112.0501 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.6948 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
5 | 147 | 27 | 3528 | 24 | 17.9 | 0 | 0 | 0 | 0 | 0 | 147 | 3528 | 1440 | 144.9863 | 21.3208 | 12.0418 | 1414.284 | 23.7721 | -176.5815 | -21.8312 | 0 | 122.0677 | 302.0677 | 112.0501 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9227 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3529 | 1 | 16.9 | 0 | 0 | 0 | 0 | 0 | 148 | 3529 | 60 | 145.9726 | 21.4803 | 11.7242 | 34.284 | 0.7668 | 168.4979 | -20.9545 | 0 | 122.3239 | 57.6761 | 112.2157 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3078 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3530 | 2 | 16.2 | 0 | 0 | 0 | 0 | 0 | 148 | 3530 | 120 | 145.9726 | 21.4803 | 11.7242 | 94.284 | 1.7668 | 153.4979 | -17.6655 | 0 | 122.3239 | 57.6761 | 112.2157 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8812 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3531 | 3 | 15.7 | 0 | 0 | 0 | 0 | 0 | 148 | 3531 | 180 | 145.9726 | 21.4803 | 11.7242 | 154.284 | 2.7668 | 138.4979 | -12.1474 | 0 | 122.3239 | 57.6761 | 112.2157 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1498 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3532 | 4 | 15.5 | 0 | 0 | 0 | 0 | 0 | 148 | 3532 | 240 | 145.9726 | 21.4803 | 11.7242 | 214.284 | 3.7668 | 123.4979 | -4.8686 | 0 | 122.3239 | 57.6761 | 112.2157 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4546 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3533 | 5 | 15.5 | 0 | 0 | 0 | 0 | 0 | 148 | 3533 | 300 | 145.9726 | 21.4803 | 11.7242 | 274.284 | 4.7668 | 108.4979 | 3.707 | 3.707 | 117.8324 | 62.1676 | 106.483 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.0607 | 4.0607 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3534 | 6 | 15.2 | 1.19 | 9.64 | 10.83 | 9.64 | 4.82 | 148 | 3534 | 360 | 145.9726 | 21.4803 | 11.7242 | 334.284 | 5.7668 | 93.4979 | 13.1768 | 13.1768 | 107.4602 | 72.5398 | 92.6013 | -0.23693 | 0 | 8.2283 | 8.2283 | -14.4455 | 0% | 3.7208 | 0 | 0 | 14.1593 | 14.1593 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3535 | 7 | 15.7 | 19.92 | 54.72 | 74.64 | 54.72 | 27.36 | 148 | 3535 | 420 | 145.9726 | 21.4803 | 11.7242 | 394.284 | 6.7668 | 78.4979 | 23.198 | 23.198 | 97.2224 | 82.7776 | 78.6486 | 9.9535 | 9.9535 | 46.7064 | 56.6599 | -1.3906 | 0% | 25.6216 | 0 | 0 | 181.1737 | 181.1737 | 0% | 11.53% | 11.53% | 80% | 9.222% | 2.3629 | 5.8557 | 5.8557 | 13.8363 | 5.2253 | 7.637% | 7.637%
5 | 148 | 28 | 3536 | 8 | 17.4 | 63.61 | 102.97 | 166.58 | 102.97 | 51.49 | 148 | 3536 | 480 | 145.9726 | 21.4803 | 11.7242 | 454.284 | 7.7668 | 63.4979 | 33.4496 | 33.4496 | 86.4396 | 93.5604 | 64.7608 | 49.2072 | 49.2072 | 87.8904 | 137.0976 | -0.075121 | 0% | 61.9955 | 0 | 0 | 153.9807 | 153.9807 | 0% | 11.45% | 11.45% | 80% | 9.157% | 5.6772 | 5.4794 | 5.4794 | 31.1075 | 12.5546 | 20.2% | 20.2%
5 | 148 | 28 | 3537 | 9 | 17.7 | 130.28 | 103.89 | 234.17 | 103.89 | 51.95 | 148 | 3537 | 540 | 145.9726 | 21.4803 | 11.7242 | 514.284 | 8.7668 | 48.4979 | 43.5603 | 43.5603 | 74.0966 | 105.9034 | 51.1204 | 118.6663 | 118.6663 | 88.6757 | 207.342 | 0.22594 | 22.59% | 93.76 | 21.1845 | 14.8292 | 158.3627 | 158.3627 | 9.364% | 11.43% | 11.43% | 80% | 9.142% | 8.5711 | 5.4151 | 5.4151 | 46.4134 | 18.9543 | 29.31% | 29.31%
5 | 148 | 28 | 3538 | 10 | 20.5 | 285.19 | 138.81 | 424 | 138.81 | 69.41 | 148 | 3538 | 600 | 145.9726 | 21.4803 | 11.7242 | 574.284 | 9.7668 | 33.4979 | 52.9637 | 52.9637 | 58.5019 | 121.4981 | 38.0964 | 281.1599 | 281.1599 | 118.4817 | 399.6417 | 0.5196 | 51.96% | 180.718 | 93.9008 | 65.7305 | 168.6327 | 168.6327 | 38.98% | 11.34% | 11.34% | 85% | 9.64% | 17.4209 | 4.8453 | 4.8453 | 84.4092 | 38.5248 | 50.06% | 50.06%
5 | 148 | 28 | 3539 | 11 | 21.2 | 358.25 | 144.72 | 502.97 | 144.72 | 72.36 | 148 | 3539 | 660 | 145.9726 | 21.4803 | 11.7242 | 634.284 | 10.7668 | 18.4979 | 60.5955 | 60.5955 | 36.9649 | 143.0351 | 26.6959 | 367.391 | 367.391 | 123.5262 | 490.9172 | 0.5756 | 57.56% | 221.9928 | 127.7788 | 89.4452 | 165.3402 | 165.3402 | 54.1% | 11.33% | 11.33% | 85% | 9.632% | 21.382 | 4.7114 | 4.7114 | 100.7393 | 47.2845 | 60.93% | 60.93%
5 | 148 | 28 | 3540 | 12 | 23.2 | 455.08 | 145.75 | 600.83 | 145.75 | 72.88 | 148 | 3540 | 720 | 145.9726 | 21.4803 | 11.7242 | 694.284 | 11.7668 | 3.4979 | 64.5435 | 64.5435 | 7.5903 | 172.4097 | 19.9947 | 473.6339 | 473.6339 | 124.4054 | 598.0393 | 0.62377 | 62.38% | 270.4334 | 168.689 | 118.0823 | 257.6101 | 257.6101 | 45.84% | 11.32% | 11.32% | 90% | 10.18% | 27.5431 | 4.3478 | 4.3478 | 119.752 | 60.9092 | 46.49% | 46.49%
5 | 148 | 28 | 3541 | 13 | 23 | 465 | 210.19 | 675.19 | 210.19 | 105.1 | 148 | 3541 | 780 | 145.9726 | 21.4803 | 11.7242 | 754.284 | 12.7668 | -11.5021 | 63.0373 | 63.0373 | 24.157 | 204.157 | 22.6643 | 481.4218 | 481.4218 | 179.4084 | 660.8302 | 0.64024 | 64.02% | 298.8274 | 191.3225 | 133.9258 | 161.8658 | 161.8658 | 82.74% | 11.33% | 11.33% | 90% | 10.2% | 30.4688 | 4.3829 | 4.3829 | 133.5419 | 67.3791 | 82.5% | 82.5%
5 | 148 | 28 | 3542 | 14 | 24.8 | 355.64 | 259.81 | 615.45 | 259.81 | 129.91 | 148 | 3542 | 840 | 145.9726 | 21.4803 | 11.7242 | 814.284 | 13.7668 | -26.5021 | 56.8388 | 56.8388 | 49.3868 | 229.3868 | 32.4648 | 358.4381 | 358.4381 | 221.7617 | 580.1998 | 0.62415 | 62.42% | 262.3663 | 163.7568 | 114.6298 | 274.7103 | 274.7103 | 41.73% | 11.29% | 11.29% | 90% | 10.16% | 26.6684 | 4.0771 | 4.0771 | 108.7293 | 58.9748 | 39.58% | 39.58%
5 | 148 | 28 | 3543 | 15 | 23.6 | 242.5 | 256.75 | 499.25 | 256.75 | 128.38 | 148 | 3543 | 900 | 145.9726 | 21.4803 | 11.7242 | 874.284 | 14.7668 | -41.5021 | 48.0821 | 48.0821 | 67.3683 | 247.3683 | 44.9325 | 230.7145 | 230.7145 | 219.1498 | 449.8643 | 0.56633 | 56.63% | 203.4286 | 115.2071 | 80.6449 | 250.2109 | 250.2109 | 32.23% | 11.28% | 11.28% | 85% | 9.59% | 19.5094 | 4.2784 | 4.2784 | 83.4696 | 43.1432 | 33.36% | 33.36%
5 | 148 | 28 | 3544 | 16 | 20 | 296.31 | 162.22 | 458.53 | 162.22 | 81.11 | 148 | 3544 | 960 | 145.9726 | 21.4803 | 11.7242 | 934.284 | 15.7668 | -56.5021 | 38.2101 | 38.2101 | 80.959 | 260.959 | 58.3528 | 251.3475 | 251.3475 | 138.4634 | 389.8109 | 0.50961 | 50.96% | 176.2725 | 89.8298 | 62.8808 | 143.5982 | 143.5982 | 43.79% | 11.35% | 11.35% | 85% | 9.649% | 17.0089 | 4.943 | 4.943 | 84.0749 | 37.6136 | 58.55% | 58.55%
5 | 148 | 28 | 3545 | 17 | 18 | 272.69 | 140.64 | 413.33 | 140.64 | 70.32 | 148 | 3545 | 1020 | 145.9726 | 21.4803 | 11.7242 | 994.284 | 16.7668 | -71.5021 | 27.9709 | 27.9709 | 92.3122 | 272.3122 | 72.1544 | 178.1724 | 178.1724 | 120.0437 | 298.2161 | 0.40434 | 40.43% | 134.8533 | 54.526 | 38.1682 | 136.213 | 136.213 | 28.02% | 11.41% | 11.41% | 80% | 9.126% | 12.3064 | 5.3514 | 5.3514 | 65.8564 | 27.2145 | 48.35% | 48.35%
5 | 148 | 28 | 3546 | 18 | 15.4 | 168.89 | 106.03 | 274.92 | 106.03 | 53.02 | 148 | 3546 | 1080 | 145.9726 | 21.4803 | 11.7242 | 1054.284 | 17.7668 | -86.5021 | 17.8014 | 17.8014 | 102.7048 | 282.7048 | 86.0946 | 37.6259 | 37.6259 | 90.5023 | 128.1282 | -0.17177 | 0% | 57.9396 | 0 | 0 | 121.7834 | 121.7834 | 0% | 11.52% | 11.52% | 80% | 9.218% | 5.3406 | 5.9242 | 5.9242 | 31.6388 | 11.8103 | 25.98% | 25.98%
5 | 148 | 28 | 3547 | 19 | 15.8 | 81.86 | 99.25 | 181.11 | 99.25 | 49.63 | 148 | 3547 | 1140 | 145.9726 | 21.4803 | 11.7242 | 1114.284 | 18.7668 | -101.5021 | 8.0343 | 8.0343 | 112.9427 | 292.9427 | 100.0264 | 0 | 0 | 84.7152 | 84.7152 | -0.66114 | 0% | 38.3082 | 0 | 0 | 113.1248 | 113.1248 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3548 | 20 | 15.2 | 21.94 | 44.81 | 66.75 | 44.81 | 22.41 | 148 | 3548 | 1200 | 145.9726 | 21.4803 | 11.7242 | 1174.284 | 19.7668 | -116.5021 | -1.0043 | 0 | 122.3239 | 302.3239 | 112.2157 | 0 | 0 | 38.2477 | 38.2477 | -2.4766 | 0% | 17.2956 | 0 | 0 | 141.1105 | 141.1105 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3549 | 21 | 15.6 | 0 | 5.92 | 5.92 | 5.92 | 2.96 | 148 | 3549 | 1260 | 145.9726 | 21.4803 | 11.7242 | 1234.284 | 20.7668 | -131.5021 | -8.9424 | 0 | 122.3239 | 302.3239 | 112.2157 | 0 | 0 | 5.053 | 5.053 | -23.8488 | 0% | 2.285 | 0 | 0 | -9.8818 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3550 | 22 | 14.8 | 0 | 0 | 0 | 0 | 0 | 148 | 3550 | 1320 | 145.9726 | 21.4803 | 11.7242 | 1294.284 | 21.7668 | -146.5021 | -15.3419 | 0 | 122.3239 | 302.3239 | 112.2157 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9883 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3551 | 23 | 14.5 | 0 | 0 | 0 | 0 | 0 | 148 | 3551 | 1380 | 145.9726 | 21.4803 | 11.7242 | 1354.284 | 22.7668 | -161.5021 | -19.7246 | 0 | 122.3239 | 302.3239 | 112.2157 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9521 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
5 | 148 | 28 | 3552 | 24 | 14.1 | 0 | 0 | 0 | 0 | 0 | 148 | 3552 | 1440 | 145.9726 | 21.4803 | 11.7242 | 1414.284 | 23.7668 | -176.5021 | -21.6685 | 0 | 122.3239 | 302.3239 | 112.2157 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0683 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3553 | 1 | 14.2 | 0 | 0 | 0 | 0 | 0 | 149 | 3553 | 60 | 146.9589 | 21.6333 | 11.3973 | 34.284 | 0.76135 | 168.5797 | -20.8142 | 0 | 122.5702 | 57.4298 | 112.3745 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5029 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3554 | 2 | 14.2 | 0 | 0 | 0 | 0 | 0 | 149 | 3554 | 120 | 146.9589 | 21.6333 | 11.3973 | 94.284 | 1.7614 | 153.5797 | -17.5449 | 0 | 122.5702 | 57.4298 | 112.3745 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.9374 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3555 | 3 | 13.9 | 0 | 0 | 0 | 0 | 0 | 149 | 3555 | 180 | 146.9589 | 21.6333 | 11.3973 | 154.284 | 2.7614 | 138.5797 | -12.0471 | 0 | 122.5702 | 57.4298 | 112.3745 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8291 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3556 | 4 | 13.7 | 0 | 0 | 0 | 0 | 0 | 149 | 3556 | 240 | 146.9589 | 21.6333 | 11.3973 | 214.284 | 3.7614 | 123.5797 | -4.7868 | 0 | 122.5702 | 57.4298 | 112.3745 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1339 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3557 | 5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 149 | 3557 | 300 | 146.9589 | 21.6333 | 11.3973 | 274.284 | 4.7614 | 108.5797 | 3.7737 | 3.7737 | 117.99 | 62.01 | 106.5349 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.8126 | 5.8126 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3558 | 6 | 13.5 | 3.81 | 20 | 23.81 | 20 | 10 | 149 | 3558 | 360 | 146.9589 | 21.6333 | 11.3973 | 334.284 | 5.7614 | 93.5797 | 13.2324 | 13.2324 | 107.6261 | 72.3739 | 92.6694 | -0.77518 | 0 | 17.0711 | 17.0711 | -6.773 | 0% | 7.7195 | 0 | 0 | 18.5384 | 18.5384 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3559 | 7 | 14 | 33.97 | 65.28 | 99.25 | 65.28 | 32.64 | 149 | 3559 | 420 | 146.9589 | 21.6333 | 11.3973 | 394.284 | 6.7614 | 78.5797 | 23.247 | 23.247 | 97.4005 | 82.5995 | 78.7314 | 16.818 | 16.818 | 55.72 | 72.538 | -0.96341 | 0% | 32.8017 | 0 | 0 | 188.1895 | 188.1895 | 0% | 11.59% | 11.59% | 80% | 9.274% | 3.0419 | 6.2522 | 6 | 18.2515 | 6.7269 | 9.698% | 9.698%
5 | 149 | 29 | 3560 | 8 | 14.6 | 119.44 | 117.97 | 237.41 | 117.97 | 58.99 | 149 | 3560 | 480 | 146.9589 | 21.6333 | 11.3973 | 454.284 | 7.7614 | 63.5797 | 33.4975 | 33.4975 | 86.6362 | 93.3638 | 64.8588 | 91.9445 | 91.9445 | 100.6937 | 192.6382 | 0.14557 | 14.56% | 87.111 | 12.681 | 8.8767 | 162.3061 | 162.3061 | 5.469% | 11.53% | 11.53% | 80% | 9.226% | 8.0368 | 6.1099 | 6 | 48.2207 | 17.7726 | 29.71% | 29.71%
5 | 149 | 29 | 3561 | 9 | 15.2 | 237.42 | 96.03 | 333.45 | 96.03 | 48.02 | 149 | 3561 | 540 | 146.9589 | 21.6333 | 11.3973 | 514.284 | 8.7614 | 48.5797 | 43.6144 | 43.6144 | 74.3204 | 105.6796 | 51.2355 | 215.502 | 215.502 | 81.9667 | 297.4687 | 0.38219 | 38.22% | 134.5153 | 51.4098 | 35.9868 | 168.0721 | 168.0721 | 21.41% | 11.48% | 11.48% | 80% | 9.188% | 12.3589 | 5.9702 | 5.9702 | 73.7852 | 27.3306 | 43.9% | 43.9%
5 | 149 | 29 | 3562 | 10 | 16.1 | 342.42 | 90.75 | 433.17 | 90.75 | 45.38 | 149 | 3562 | 600 | 146.9589 | 21.6333 | 11.3973 | 574.284 | 9.7614 | 33.5797 | 53.0349 | 53.0349 | 58.76 | 121.24 | 38.233 | 336.634 | 336.634 | 77.46 | 414.0939 | 0.5059 | 50.59% | 187.2533 | 94.7306 | 66.3114 | 169.8263 | 169.8263 | 39.05% | 11.43% | 11.43% | 85% | 9.72% | 18.2002 | 5.7653 | 5.7653 | 104.9299 | 40.2481 | 61.79% | 61.79%
5 | 149 | 29 | 3563 | 11 | 16.1 | 300.64 | 130.28 | 430.92 | 130.28 | 65.14 | 149 | 3563 | 660 | 146.9589 | 21.6333 | 11.3973 | 634.284 | 10.7614 | 18.5797 | 60.6988 | 60.6988 | 37.2425 | 142.7575 | 26.8579 | 307.5592 | 307.5592 | 111.2009 | 418.7601 | 0.50922 | 50.92% | 189.3633 | 96.4271 | 67.4989 | 160.6401 | 160.6401 | 42.02% | 11.43% | 11.43% | 85% | 9.719% | 18.4037 | 5.7653 | 5.7653 | 106.103 | 40.6981 | 66.05% | 66.05%
5 | 149 | 29 | 3564 | 12 | 16.4 | 296.03 | 148.25 | 444.28 | 148.25 | 74.13 | 149 | 3564 | 720 | 146.9589 | 21.6333 | 11.3973 | 694.284 | 11.7614 | 3.5797 | 64.6883 | 64.6883 | 7.802 | 172.198 | 20.1588 | 307.4081 | 307.4081 | 126.5393 | 433.9474 | 0.52109 | 52.11% | 196.231 | 102.2541 | 71.5778 | 148.9026 | 148.9026 | 48.07% | 11.42% | 11.42% | 85% | 9.711% | 19.0556 | 5.6983 | 5.6983 | 108.5842 | 42.1398 | 72.92% | 72.92%
5 | 149 | 29 | 3565 | 13 | 15.1 | 295.19 | 123.89 | 419.08 | 123.89 | 61.95 | 149 | 3565 | 780 | 146.9589 | 21.6333 | 11.3973 | 754.284 | 12.7614 | -11.4203 | 63.2061 | 63.2061 | 24.0985 | 204.0985 | 22.7564 | 304.9537 | 304.9537 | 105.7467 | 410.7004 | 0.49793 | 49.79% | 185.7187 | 92.4748 | 64.7324 | 143.4345 | 143.4345 | 45.13% | 11.46% | 11.46% | 85% | 9.738% | 18.086 | 5.9933 | 5.9933 | 108.395 | 39.9956 | 75.57% | 75.57%
5 | 149 | 29 | 3566 | 14 | 16.1 | 304.64 | 231.31 | 535.95 | 231.31 | 115.66 | 149 | 3566 | 840 | 146.9589 | 21.6333 | 11.3973 | 814.284 | 13.7614 | -26.4203 | 57.0082 | 57.0082 | 49.428 | 229.428 | 32.4872 | 306.37 | 306.37 | 197.4354 | 503.8055 | 0.55898 | 55.9% | 227.8208 | 127.3469 | 89.1428 | 149.4438 | 149.4438 | 59.65% | 11.42% | 11.42% | 90% | 10.27% | 23.4063 | 5.7653 | 5.7653 | 134.9445 | 51.7609 | 90.3% | 90.3%
5 | 149 | 29 | 3567 | 15 | 16 | 287.14 | 205.92 | 493.06 | 205.92 | 102.96 | 149 | 3567 | 900 | 146.9589 | 21.6333 | 11.3973 | 874.284 | 14.7614 | -41.4203 | 48.246 | 48.246 | 67.4407 | 247.4407 | 44.9146 | 272.5711 | 272.5711 | 175.7637 | 448.3348 | 0.52816 | 52.82% | 202.737 | 107.0776 | 74.9543 | 145.3598 | 145.3598 | 51.56% | 11.43% | 11.43% | 85% | 9.715% | 19.6958 | 5.7878 | 5.7878 | 113.9955 | 43.5556 | 78.42% | 78.42%
5 | 149 | 29 | 3568 | 16 | 15.3 | 238.42 | 156.86 | 395.28 | 156.86 | 78.43 | 149 | 3568 | 960 | 146.9589 | 21.6333 | 11.3973 | 934.284 | 15.7614 | -56.4203 | 38.3704 | 38.3704 | 81.0343 | 261.0343 | 58.3096 | 201.7724 | 201.7724 | 133.8884 | 335.6608 | 0.43085 | 43.09% | 151.7858 | 65.3977 | 45.7784 | 138.034 | 138.034 | 33.16% | 11.47% | 11.47% | 85% | 9.751% | 14.801 | 5.9472 | 5.9472 | 88.0237 | 32.731 | 63.77% | 63.77%
5 | 149 | 29 | 3569 | 17 | 14.6 | 215.47 | 158.25 | 373.72 | 158.25 | 79.13 | 149 | 3569 | 1020 | 146.9589 | 21.6333 | 11.3973 | 994.284 | 16.7614 | -71.4203 | 28.1304 | 28.1304 | 92.3814 | 272.3814 | 72.0928 | 140.519 | 140.519 | 135.0748 | 275.5938 | 0.34376 | 34.38% | 124.6235 | 42.8411 | 29.9887 | 133.573 | 133.573 | 22.45% | 11.51% | 11.51% | 80% | 9.206% | 11.4731 | 6.1099 | 6 | 68.8385 | 25.3717 | 51.54% | 51.54%
5 | 149 | 29 | 3570 | 18 | 13.9 | 145.83 | 85.64 | 231.47 | 85.64 | 42.82 | 149 | 3570 | 1080 | 146.9589 | 21.6333 | 11.3973 | 1054.284 | 17.7614 | -86.4203 | 17.9625 | 17.9625 | 102.7647 | 282.7647 | 86.0176 | 32.8404 | 32.8404 | 73.0983 | 105.9387 | -0.40833 | 0% | 47.9055 | 0 | 0 | 121.5328 | 121.5328 | 0% | 11.58% | 11.58% | 80% | 9.268% | 4.4398 | 6.2762 | 6 | 26.639 | 9.8183 | 21.92% | 21.92%
5 | 149 | 29 | 3571 | 19 | 14.6 | 137.22 | 62.5 | 199.72 | 62.5 | 31.25 | 149 | 3571 | 1140 | 146.9589 | 21.6333 | 11.3973 | 1114.284 | 18.7614 | -101.4203 | 8.1983 | 8.1983 | 112.991 | 292.991 | 99.935 | 0 | 0 | 53.3471 | 53.3471 | -1.5736 | 0% | 24.1236 | 0 | 0 | 116.8429 | 116.8429 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3572 | 20 | 14.6 | 45.92 | 38.42 | 84.34 | 38.42 | 19.21 | 149 | 3572 | 1200 | 146.9589 | 21.6333 | 11.3973 | 1174.284 | 19.7614 | -116.4203 | -0.83681 | 0 | 122.5702 | 302.5702 | 112.3745 | 0 | 0 | 32.7935 | 32.7935 | -3.0638 | 0% | 14.8292 | 0 | 0 | 145.0639 | 145.0639 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3573 | 21 | 14.3 | 0 | 5.64 | 5.64 | 5.64 | 2.82 | 149 | 3573 | 1260 | 146.9589 | 21.6333 | 11.3973 | 1234.284 | 20.7614 | -131.4203 | -8.7722 | 0 | 122.5702 | 302.5702 | 112.3745 | 0 | 0 | 4.814 | 4.814 | -25.6854 | 0% | 2.1769 | 0 | 0 | -9.0266 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3574 | 22 | 14.4 | 0 | 0 | 0 | 0 | 0 | 149 | 3574 | 1320 | 146.9589 | 21.6333 | 11.3973 | 1294.284 | 21.7614 | -146.4203 | -15.1713 | 0 | 122.5702 | 302.5702 | 112.3745 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8945 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3575 | 23 | 13.9 | 0 | 0 | 0 | 0 | 0 | 149 | 3575 | 1380 | 146.9589 | 21.6333 | 11.3973 | 1354.284 | 22.7614 | -161.4203 | -19.5582 | 0 | 122.5702 | 302.5702 | 112.3745 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.091 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
5 | 149 | 29 | 3576 | 24 | 14.1 | 0 | 0 | 0 | 0 | 0 | 149 | 3576 | 1440 | 146.9589 | 21.6333 | 11.3973 | 1414.284 | 23.7614 | -176.4203 | -21.5122 | 0 | 122.5702 | 302.5702 | 112.3745 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2208 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3577 | 1 | 14.4 | 0 | 0 | 0 | 0 | 0 | 150 | 3577 | 60 | 147.9452 | 21.7797 | 11.0612 | 34.284 | 0.75575 | 168.6637 | -20.6805 | 0 | 122.8063 | 57.1937 | 112.5265 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6007 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3578 | 2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 150 | 3578 | 120 | 147.9452 | 21.7797 | 11.0612 | 94.284 | 1.7558 | 153.6637 | -17.431 | 0 | 122.8063 | 57.1937 | 112.5265 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6173 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3579 | 3 | 14.4 | 0 | 0 | 0 | 0 | 0 | 150 | 3579 | 180 | 147.9452 | 21.7797 | 11.0612 | 154.284 | 2.7558 | 138.6637 | -11.9534 | 0 | 122.8063 | 57.1937 | 112.5265 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5484 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3580 | 4 | 14.2 | 0 | 0 | 0 | 0 | 0 | 150 | 3580 | 240 | 147.9452 | 21.7797 | 11.0612 | 214.284 | 3.7558 | 123.6637 | -4.7113 | 0 | 122.8063 | 57.1937 | 112.5265 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8532 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3581 | 5 | 14 | 0 | 0 | 0 | 0 | 0 | 150 | 3581 | 300 | 147.9452 | 21.7797 | 11.0612 | 274.284 | 4.7558 | 108.6637 | 3.8342 | 3.8342 | 118.1449 | 61.8551 | 106.5896 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.2153 | 4.2153 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3582 | 6 | 13.8 | 4.53 | 18.25 | 22.78 | 18.25 | 9.13 | 150 | 3582 | 360 | 147.9452 | 21.7797 | 11.0612 | 334.284 | 5.7558 | 93.6637 | 13.2819 | 13.2819 | 107.7888 | 72.2112 | 92.7397 | -0.94247 | 0 | 15.5773 | 15.5773 | -7.4555 | 0% | 7.0441 | 0 | 0 | 15.2928 | 15.2928 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3583 | 7 | 13.7 | 34.08 | 61.31 | 95.39 | 61.31 | 30.66 | 150 | 3583 | 420 | 147.9452 | 21.7797 | 11.0612 | 394.284 | 6.7558 | 78.6637 | 23.2899 | 23.2899 | 97.575 | 82.425 | 78.816 | 16.7184 | 16.7184 | 52.3314 | 69.0497 | -1.0626 | 0% | 31.2243 | 0 | 0 | 181.5512 | 181.5512 | 0% | 11.61% | 11.61% | 80% | 9.284% | 2.8989 | 6.3243 | 6 | 17.3936 | 6.4107 | 9.581% | 9.581%
5 | 150 | 30 | 3584 | 8 | 13.7 | 93.14 | 107.5 | 200.64 | 107.5 | 53.75 | 150 | 3584 | 480 | 147.9452 | 21.7797 | 11.0612 | 454.284 | 7.7558 | 63.6637 | 33.5392 | 33.5392 | 86.8289 | 93.1711 | 64.9578 | 71.3561 | 71.3561 | 91.757 | 163.1131 | 0.013814 | 1.381% | 73.7597 | 1.0189 | 0.71323 | 152.1144 | 152.1144 | 0.4689% | 11.57% | 11.57% | 80% | 9.258% | 6.8288 | 6.3243 | 6 | 40.9727 | 15.1012 | 26.94% | 26.94%
5 | 150 | 30 | 3585 | 9 | 13.6 | 193.53 | 192.97 | 386.5 | 192.97 | 96.49 | 150 | 3585 | 540 | 147.9452 | 21.7797 | 11.0612 | 514.284 | 8.7558 | 48.6637 | 43.6621 | 43.6621 | 74.54 | 105.46 | 51.351 | 175.0696 | 175.0696 | 164.7102 | 339.7798 | 0.42399 | 42.4% | 153.6484 | 65.146 | 45.6022 | 161.1935 | 161.1935 | 28.29% | 11.51% | 11.51% | 85% | 9.787% | 15.0374 | 6.3484 | 6 | 90.2245 | 33.2539 | 55.97% | 55.97%
5 | 150 | 30 | 3586 | 10 | 13.5 | 254.36 | 253.42 | 507.78 | 253.42 | 126.71 | 150 | 3586 | 600 | 147.9452 | 21.7797 | 11.0612 | 574.284 | 9.7558 | 33.6637 | 53.0992 | 53.0992 | 59.0146 | 120.9854 | 38.3686 | 249.3843 | 249.3843 | 216.3075 | 465.6918 | 0.52625 | 52.62% | 210.5858 | 110.8202 | 77.5742 | 163.5032 | 163.5032 | 47.45% | 11.47% | 11.47% | 85% | 9.751% | 20.5338 | 6.3727 | 6 | 123.2027 | 45.4086 | 75.35% | 75.35%
5 | 150 | 30 | 3587 | 11 | 13.5 | 378.33 | 238.97 | 617.3 | 238.97 | 119.49 | 150 | 3587 | 660 | 147.9452 | 21.7797 | 11.0612 | 634.284 | 10.7558 | 18.6637 | 60.7949 | 60.7949 | 37.5195 | 142.4805 | 27.0169 | 386.1293 | 386.1293 | 203.9737 | 590.103 | 0.58481 | 58.48% | 266.8446 | 156.0523 | 109.2366 | 160.2888 | 160.2888 | 68.15% | 11.43% | 11.43% | 90% | 10.28% | 27.4432 | 6.3727 | 6 | 164.6591 | 60.6882 | 102.7% | 102.7%
5 | 150 | 30 | 3588 | 12 | 13.4 | 444.36 | 171.58 | 615.94 | 171.58 | 85.79 | 150 | 3588 | 720 | 147.9452 | 21.7797 | 11.0612 | 694.284 | 11.7558 | 3.6637 | 64.8261 | 64.8261 | 8.0189 | 171.9811 | 20.3171 | 460.4472 | 460.4472 | 146.4527 | 606.8999 | 0.5905 | 59.05% | 274.4402 | 162.0556 | 113.4389 | 148.2038 | 148.2038 | 76.54% | 11.42% | 11.42% | 90% | 10.28% | 28.2121 | 6.397 | 6 | 169.2728 | 62.3886 | 114.2% | 114.2%
5 | 150 | 30 | 3589 | 13 | 13.4 | 150.42 | 200.28 | 350.7 | 200.28 | 100.14 | 150 | 3589 | 780 | 147.9452 | 21.7797 | 11.0612 | 754.284 | 12.7558 | -11.3363 | 63.3692 | 63.3692 | 24.0309 | 204.0309 | 22.8427 | 155.0745 | 155.0745 | 170.9497 | 326.0242 | 0.40656 | 40.66% | 147.4281 | 59.938 | 41.9566 | 135.1695 | 135.1695 | 31.04% | 11.52% | 11.52% | 85% | 9.795% | 14.4412 | 6.397 | 6 | 86.6474 | 31.9355 | 64.1% | 64.1%
5 | 150 | 30 | 3590 | 14 | 13.4 | 378.69 | 176.67 | 555.36 | 176.67 | 88.34 | 150 | 3590 | 840 | 147.9452 | 21.7797 | 11.0612 | 814.284 | 13.7558 | -26.3363 | 57.1732 | 57.1732 | 49.46 | 229.46 | 32.5051 | 380.0556 | 380.0556 | 150.7973 | 530.8528 | 0.55991 | 55.99% | 240.0517 | 134.4073 | 94.0851 | 141.5526 | 141.5526 | 66.47% | 11.45% | 11.45% | 90% | 10.3% | 24.7367 | 6.397 | 6 | 148.4201 | 54.703 | 104.9% | 104.9%
5 | 150 | 30 | 3591 | 15 | 12.5 | 265.92 | 159.08 | 425 | 159.08 | 79.54 | 150 | 3591 | 900 | 147.9452 | 21.7797 | 11.0612 | 874.284 | 14.7558 | -41.3363 | 48.4064 | 48.4064 | 67.5047 | 247.5047 | 44.8931 | 251.8935 | 251.8935 | 135.7833 | 387.6768 | 0.46443 | 46.44% | 175.3075 | 81.4187 | 56.9931 | 132.2577 | 132.2577 | 43.09% | 11.52% | 11.52% | 85% | 9.794% | 17.1692 | 6.6189 | 6 | 103.0153 | 37.9682 | 77.89% | 77.89%
5 | 150 | 30 | 3592 | 16 | 13.2 | 255.83 | 140.56 | 396.39 | 140.56 | 70.28 | 150 | 3592 | 960 | 147.9452 | 21.7797 | 11.0612 | 934.284 | 15.7558 | -56.3363 | 38.5276 | 38.5276 | 81.1021 | 261.1021 | 58.2636 | 216.0404 | 216.0404 | 119.9755 | 336.0159 | 0.41701 | 41.7% | 151.9464 | 63.3635 | 44.3544 | 130.1132 | 130.1132 | 34.09% | 11.53% | 11.53% | 85% | 9.797% | 14.8857 | 6.4458 | 6 | 89.3144 | 32.9185 | 68.64% | 68.64%
5 | 150 | 30 | 3593 | 17 | 13.7 | 172.42 | 95.36 | 267.78 | 95.36 | 47.68 | 150 | 3593 | 1020 | 147.9452 | 21.7797 | 11.0612 | 994.284 | 16.7558 | -71.3363 | 28.287 | 28.287 | 92.4439 | 272.4439 | 72.0288 | 112.259 | 112.259 | 81.3949 | 193.6539 | 0.13843 | 13.84% | 87.5703 | 12.1226 | 8.4858 | 122.5557 | 122.5557 | 6.924% | 11.56% | 11.56% | 80% | 9.25% | 8.1 | 6.3243 | 6 | 48.5998 | 17.9124 | 39.66% | 39.66%
5 | 150 | 30 | 3594 | 18 | 15.7 | 115.19 | 107.03 | 222.22 | 107.03 | 53.52 | 150 | 3594 | 1080 | 147.9452 | 21.7797 | 11.0612 | 1054.284 | 17.7558 | -86.3363 | 18.1204 | 18.1204 | 102.8183 | 282.8183 | 85.9388 | 26.2303 | 26.2303 | 91.3558 | 117.5861 | -0.25349 | 0% | 53.1724 | 0 | 0 | 119.8632 | 119.8632 | 0% | 11.51% | 11.51% | 80% | 9.211% | 4.8976 | 5.8557 | 5.8557 | 28.6785 | 10.8305 | 23.93% | 23.93%
5 | 150 | 30 | 3595 | 19 | 15.7 | 64.92 | 45.56 | 110.48 | 45.56 | 22.78 | 150 | 3595 | 1140 | 147.9452 | 21.7797 | 11.0612 | 1114.284 | 18.7558 | -101.3363 | 8.3589 | 8.3589 | 113.0335 | 293.0335 | 99.8422 | 0 | 0 | 38.8879 | 38.8879 | -2.3935 | 0% | 17.5851 | 0 | 0 | 152.6028 | 152.6028 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3596 | 20 | 15.7 | 20.75 | 33.81 | 54.56 | 33.81 | 16.91 | 150 | 3596 | 1200 | 147.9452 | 21.7797 | 11.0612 | 1174.284 | 19.7558 | -116.3363 | -0.67327 | 0 | 122.8063 | 302.8063 | 112.5265 | 0 | 0 | 28.8586 | 28.8586 | -3.5048 | 0% | 13.0499 | 0 | 0 | 143.2406 | 143.2406 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3597 | 21 | 14.6 | 0 | 4.17 | 4.17 | 4.17 | 2.09 | 150 | 3597 | 1260 | 147.9452 | 21.7797 | 11.0612 | 1234.284 | 20.7558 | -131.3363 | -8.6065 | 0 | 122.8063 | 302.8063 | 112.5265 | 0 | 0 | 3.5593 | 3.5593 | -34.8316 | 0% | 1.6095 | 0 | 0 | -9.2484 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3598 | 22 | 14.3 | 0 | 0 | 0 | 0 | 0 | 150 | 3598 | 1320 | 147.9452 | 21.7797 | 11.0612 | 1294.284 | 21.7558 | -146.3363 | -15.006 | 0 | 122.8063 | 302.8063 | 112.5265 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3315 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3599 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 150 | 3599 | 1380 | 147.9452 | 21.7797 | 11.0612 | 1354.284 | 22.7558 | -161.3363 | -19.3976 | 0 | 122.8063 | 302.8063 | 112.5265 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2626 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
5 | 150 | 30 | 3600 | 24 | 13.6 | 0 | 0 | 0 | 0 | 0 | 150 | 3600 | 1440 | 147.9452 | 21.7797 | 11.0612 | 1414.284 | 23.7558 | -176.3363 | -21.3623 | 0 | 122.8063 | 302.8063 | 112.5265 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.346 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3601 | 1 | 12.3 | 0 | 0 | 0 | 0 | 0 | 151 | 3601 | 60 | 148.9315 | 21.9196 | 10.7165 | 34.284 | 0.75001 | 168.7499 | -20.5535 | 0 | 123.0321 | 56.9679 | 112.6717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3154 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3602 | 2 | 11.5 | 0 | 0 | 0 | 0 | 0 | 151 | 3602 | 120 | 148.9315 | 21.9196 | 10.7165 | 94.284 | 1.75 | 153.7499 | -17.3238 | 0 | 123.0321 | 56.9679 | 112.6717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0171 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3603 | 3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 151 | 3603 | 180 | 148.9315 | 21.9196 | 10.7165 | 154.284 | 2.75 | 138.7499 | -11.8663 | 0 | 123.0321 | 56.9679 | 112.6717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3472 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3604 | 4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 151 | 3604 | 240 | 148.9315 | 21.9196 | 10.7165 | 214.284 | 3.75 | 123.7499 | -4.6422 | 0 | 123.0321 | 56.9679 | 112.6717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8044 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3605 | 5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 151 | 3605 | 300 | 148.9315 | 21.9196 | 10.7165 | 274.284 | 4.75 | 108.7499 | 3.8884 | 3.8884 | 118.2969 | 61.7031 | 106.647 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.96427 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3606 | 6 | 11.5 | 1.75 | 12.42 | 14.17 | 12.42 | 6.21 | 151 | 3606 | 360 | 148.9315 | 21.9196 | 10.7165 | 334.284 | 5.75 | 93.7499 | 13.3253 | 13.3253 | 107.9483 | 72.0517 | 92.8121 | -0.37252 | 0 | 10.6011 | 10.6011 | -11.8314 | 0% | 4.7938 | 0 | 0 | 9.8361 | 9.8361 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3607 | 7 | 12.5 | 15.92 | 64.36 | 80.28 | 64.36 | 32.18 | 151 | 3607 | 420 | 148.9315 | 21.9196 | 10.7165 | 394.284 | 6.75 | 78.7499 | 23.3268 | 23.3268 | 97.7458 | 82.2542 | 78.9022 | 7.7387 | 7.7387 | 54.9347 | 62.6734 | -1.2964 | 0% | 28.3409 | 0 | 0 | 177.4562 | 177.4562 | 0% | 11.66% | 11.66% | 80% | 9.325% | 2.6428 | 6.6189 | 6 | 15.8566 | 5.8442 | 8.936% | 8.936%
5 | 151 | 31 | 3608 | 8 | 13.6 | 70.92 | 101.47 | 172.39 | 101.47 | 50.74 | 151 | 3608 | 480 | 148.9315 | 21.9196 | 10.7165 | 454.284 | 7.75 | 63.7499 | 33.5748 | 33.5748 | 87.0175 | 92.9825 | 65.0579 | 54.079 | 54.079 | 86.6101 | 140.6891 | -0.11376 | 0% | 63.6196 | 0 | 0 | 149.4027 | 149.4027 | 0% | 11.58% | 11.58% | 80% | 9.267% | 5.8958 | 6.3484 | 6 | 35.3748 | 13.038 | 23.68% | 23.68%
5 | 151 | 31 | 3609 | 9 | 15.2 | 185.47 | 125.64 | 311.11 | 125.64 | 62.82 | 151 | 3609 | 540 | 148.9315 | 21.9196 | 10.7165 | 514.284 | 8.75 | 48.7499 | 43.7035 | 43.7035 | 74.7554 | 105.2446 | 51.4666 | 167.2281 | 167.2281 | 107.2404 | 274.4686 | 0.34684 | 34.68% | 124.1147 | 43.0477 | 30.1334 | 159.0022 | 159.0022 | 18.95% | 11.49% | 11.49% | 80% | 9.193% | 11.4094 | 5.9702 | 5.9702 | 68.1161 | 25.2308 | 42.84% | 42.84%
5 | 151 | 31 | 3610 | 10 | 18.5 | 245.28 | 188.33 | 433.61 | 188.33 | 94.17 | 151 | 3610 | 600 | 148.9315 | 21.9196 | 10.7165 | 574.284 | 9.75 | 33.7499 | 53.1568 | 53.1568 | 59.2654 | 120.7346 | 38.5032 | 239.8533 | 239.8533 | 160.7497 | 400.603 | 0.50926 | 50.93% | 181.1527 | 92.2536 | 64.5776 | 166.4428 | 166.4428 | 38.8% | 11.38% | 11.38% | 85% | 9.677% | 17.5305 | 5.2467 | 5.2467 | 91.9769 | 38.7672 | 55.26% | 55.26%
5 | 151 | 31 | 3611 | 11 | 18 | 295.75 | 262.22 | 557.97 | 262.22 | 131.11 | 151 | 3611 | 660 | 148.9315 | 21.9196 | 10.7165 | 634.284 | 10.75 | 18.7499 | 60.8837 | 60.8837 | 37.7954 | 142.2046 | 27.1725 | 301.167 | 301.167 | 223.8188 | 524.9858 | 0.57697 | 57.7% | 237.3986 | 136.9724 | 95.8807 | 163.4008 | 163.4008 | 58.68% | 11.38% | 11.38% | 90% | 10.24% | 24.3192 | 5.3514 | 5.3514 | 130.1416 | 53.7797 | 79.65% | 79.65%
5 | 151 | 31 | 3612 | 12 | 19.4 | 296.58 | 289.36 | 585.94 | 289.36 | 144.68 | 151 | 3612 | 720 | 148.9315 | 21.9196 | 10.7165 | 694.284 | 11.75 | 3.7499 | 64.9569 | 64.9569 | 8.2408 | 171.7592 | 20.4694 | 306.6854 | 306.6854 | 246.9842 | 553.6696 | 0.59434 | 59.43% | 250.3694 | 148.8054 | 104.1638 | 155.4602 | 155.4602 | 67% | 11.36% | 11.36% | 90% | 10.22% | 25.5981 | 5.0626 | 5.0626 | 129.5922 | 56.6078 | 83.36% | 83.36%
5 | 151 | 31 | 3613 | 13 | 20.2 | 311.11 | 263.97 | 575.08 | 263.97 | 131.99 | 151 | 3613 | 780 | 148.9315 | 21.9196 | 10.7165 | 754.284 | 12.75 | -11.2501 | 63.5267 | 63.5267 | 23.954 | 203.954 | 22.9233 | 320.1065 | 320.1065 | 225.3125 | 545.419 | 0.5944 | 59.44% | 246.6385 | 146.6029 | 102.622 | 153.6373 | 153.6373 | 66.8% | 11.35% | 11.35% | 90% | 10.21% | 25.1923 | 4.9037 | 4.9037 | 123.5357 | 55.7106 | 80.41% | 80.41%
5 | 151 | 31 | 3614 | 14 | 20.4 | 325.19 | 215.56 | 540.75 | 215.56 | 107.78 | 151 | 3614 | 840 | 148.9315 | 21.9196 | 10.7165 | 814.284 | 13.75 | -26.2501 | 57.3339 | 57.3339 | 49.4826 | 229.4826 | 32.5185 | 325.7259 | 325.7259 | 183.992 | 509.7179 | 0.58059 | 58.06% | 230.4944 | 133.8218 | 93.6753 | 151.0176 | 151.0176 | 62.03% | 11.35% | 11.35% | 90% | 10.21% | 23.5359 | 4.8647 | 4.8647 | 114.4947 | 52.0476 | 75.82% | 75.82%
5 | 151 | 31 | 3615 | 15 | 20.8 | 328.06 | 237.22 | 565.28 | 237.22 | 118.61 | 151 | 3615 | 900 | 148.9315 | 21.9196 | 10.7165 | 874.284 | 14.75 | -41.2501 | 48.5633 | 48.5633 | 67.5603 | 247.5603 | 44.868 | 310.1387 | 310.1387 | 202.4799 | 512.6187 | 0.58356 | 58.36% | 231.8062 | 135.2731 | 94.6912 | 150.5861 | 150.5861 | 62.88% | 11.34% | 11.34% | 90% | 10.21% | 23.6568 | 4.7875 | 4.7875 | 113.2564 | 52.3149 | 75.21% | 75.21%
5 | 151 | 31 | 3616 | 16 | 19.4 | 291.75 | 198.61 | 490.36 | 198.61 | 99.31 | 151 | 3616 | 960 | 148.9315 | 21.9196 | 10.7165 | 934.284 | 15.75 | -56.2501 | 38.6817 | 38.6817 | 81.1626 | 261.1626 | 58.2145 | 245.8848 | 245.8848 | 169.5242 | 415.4091 | 0.52456 | 52.46% | 187.848 | 98.5382 | 68.9767 | 143.4045 | 143.4045 | 48.1% | 11.36% | 11.36% | 85% | 9.66% | 18.1461 | 5.0626 | 5.0626 | 91.866 | 40.1285 | 64.06% | 64.06%
5 | 151 | 31 | 3617 | 17 | 20.04 | 203.14 | 174.53 | 377.67 | 174.53 | 87.27 | 151 | 3617 | 1020 | 148.9315 | 21.9196 | 10.7165 | 994.284 | 16.75 | -71.2501 | 28.4405 | 28.4405 | 92.4996 | 272.4996 | 71.9625 | 132.075 | 132.075 | 148.9707 | 281.0457 | 0.39599 | 39.6% | 127.0889 | 50.3259 | 35.2281 | 136.9695 | 136.9695 | 25.72% | 11.35% | 11.35% | 80% | 9.081% | 11.5405 | 4.9351 | 4.9351 | 56.9539 | 25.5209 | 41.58% | 41.58%
5 | 151 | 31 | 3618 | 18 | 19.96 | 112.5 | 125.08 | 237.58 | 125.08 | 62.54 | 151 | 3618 | 1080 | 148.9315 | 21.9196 | 10.7165 | 1054.284 | 17.75 | -86.2501 | 18.2751 | 18.2751 | 102.8658 | 282.8658 | 85.8581 | 25.9119 | 25.9119 | 106.7625 | 132.6744 | -0.06162 | 0% | 59.9954 | 0 | 0 | 126.445 | 126.445 | 0% | 11.35% | 11.35% | 80% | 9.083% | 5.4492 | 4.9509 | 4.9509 | 26.9786 | 12.0505 | 21.34% | 21.34%
5 | 151 | 31 | 3619 | 19 | 18.81 | 65.56 | 115.19 | 180.75 | 115.19 | 57.6 | 151 | 3619 | 1140 | 148.9315 | 21.9196 | 10.7165 | 1114.284 | 18.75 | -101.2501 | 8.5159 | 8.5159 | 113.0701 | 293.0701 | 99.7482 | 0 | 0 | 98.3208 | 98.3208 | -0.38991 | 0% | 44.4607 | 0 | 0 | 117.7039 | 117.7039 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1826 | 5.1826 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3620 | 20 | 17.41 | 22.42 | 63.14 | 85.56 | 63.14 | 31.57 | 151 | 3620 | 1200 | 148.9315 | 21.9196 | 10.7165 | 1174.284 | 19.75 | -116.2501 | -0.51373 | 0 | 123.0321 | 303.0321 | 112.6717 | 0 | 0 | 53.8934 | 53.8934 | -1.432 | 0% | 24.3706 | 0 | 0 | 146.0457 | 146.0457 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4772 | 5.4772 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3621 | 21 | 16.36 | 0 | 6.94 | 6.94 | 6.94 | 3.47 | 151 | 3621 | 1260 | 148.9315 | 21.9196 | 10.7165 | 1234.284 | 20.75 | -131.2501 | -8.4454 | 0 | 123.0321 | 303.0321 | 112.6717 | 0 | 0 | 5.9237 | 5.9237 | -19.9362 | 0% | 2.6787 | 0 | 0 | -7.8468 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7072 | 5.7072 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3622 | 22 | 15.63 | 0 | 0 | 0 | 0 | 0 | 151 | 3622 | 1320 | 148.9315 | 21.9196 | 10.7165 | 1294.284 | 21.75 | -146.2501 | -14.8459 | 0 | 123.0321 | 303.0321 | 112.6717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.793 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8716 | 5.8716 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3623 | 23 | 14.69 | 0 | 0 | 0 | 0 | 0 | 151 | 3623 | 1380 | 148.9315 | 21.9196 | 10.7165 | 1354.284 | 22.75 | -161.2501 | -19.2429 | 0 | 123.0321 | 303.0321 | 112.6717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7081 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0888 | 6 | 0 | 0 | 0% | 0%
5 | 151 | 31 | 3624 | 24 | 12.52 | 0 | 0 | 0 | 0 | 0 | 151 | 3624 | 1440 | 148.9315 | 21.9196 | 10.7165 | 1414.284 | 23.75 | -176.2501 | -21.2188 | 0 | 123.0321 | 303.0321 | 112.6717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4976 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6139 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3625 | 1 | 10.05 | 0 | 0 | 0 | 0 | 0 | 152 | 3625 | 60 | 149.9178 | 22.0529 | 10.3633 | 34.284 | 0.74412 | 168.8382 | -20.4332 | 0 | 123.2477 | 56.7523 | 112.8101 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6014 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2516 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3626 | 2 | 8.38 | 0 | 0 | 0 | 0 | 0 | 152 | 3626 | 120 | 149.9178 | 22.0529 | 10.3633 | 94.284 | 1.7441 | 153.8382 | -17.2233 | 0 | 123.2477 | 56.7523 | 112.8101 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8145 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.707 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3627 | 3 | 8.34 | 0 | 0 | 0 | 0 | 0 | 152 | 3627 | 180 | 149.9178 | 22.0529 | 10.3633 | 154.284 | 2.7441 | 138.8382 | -11.7857 | 0 | 123.2477 | 56.7523 | 112.8101 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5436 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7182 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3628 | 4 | 8.67 | 0 | 0 | 0 | 0 | 0 | 152 | 3628 | 240 | 149.9178 | 22.0529 | 10.3633 | 214.284 | 3.7441 | 123.8382 | -4.5796 | 0 | 123.2477 | 56.7523 | 112.8101 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0406 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6266 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3629 | 5 | 8.93 | 0 | 0 | 0 | 0 | 0 | 152 | 3629 | 300 | 149.9178 | 22.0529 | 10.3633 | 274.284 | 4.7441 | 108.8382 | 3.9366 | 3.9366 | 118.4461 | 61.5539 | 106.7071 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.5694 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5549 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3630 | 6 | 9.23 | 1.94 | 11.86 | 13.8 | 11.86 | 5.93 | 152 | 3630 | 360 | 149.9178 | 22.0529 | 10.3633 | 334.284 | 5.7441 | 93.8382 | 13.3627 | 13.3627 | 108.1044 | 71.8956 | 92.8868 | -0.42275 | 0 | 10.1231 | 10.1231 | -12.9506 | 0% | 4.5777 | 0 | 0 | 3.3772 | 3.3772 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4728 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3631 | 7 | 9 | 21.31 | 39.81 | 61.12 | 39.81 | 19.91 | 152 | 3631 | 420 | 149.9178 | 22.0529 | 10.3633 | 394.284 | 6.7441 | 78.8382 | 23.3578 | 23.3578 | 97.9128 | 82.0872 | 78.99 | 10.265 | 10.265 | 33.98 | 44.245 | -2.3552 | 0% | 20.0076 | 0 | 0 | 163.6718 | 163.6718 | 0% | 11.81% | 11.81% | 80% | 9.447% | 1.8902 | 7.5357 | 6 | 11.3412 | 4.18 | 6.929% | 6.929%
6 | 152 | 1 | 3632 | 8 | 8 | 61.19 | 48.69 | 109.88 | 48.69 | 24.35 | 152 | 3632 | 480 | 149.9178 | 22.0529 | 10.3633 | 454.284 | 7.7441 | 63.8382 | 33.6044 | 33.6044 | 87.2019 | 92.7981 | 65.1589 | 46.4465 | 46.4465 | 41.5595 | 88.006 | -0.81105 | 0% | 39.7963 | 0 | 0 | 170.583 | 170.583 | 0% | 11.82% | 11.82% | 80% | 9.458% | 3.7637 | 7.8134 | 6 | 22.5825 | 8.3232 | 13.24% | 13.24%
6 | 152 | 1 | 3633 | 9 | 9.1 | 118.89 | 73.69 | 192.58 | 73.69 | 36.85 | 152 | 3633 | 540 | 149.9178 | 22.0529 | 10.3633 | 514.284 | 8.7441 | 48.8382 | 43.7386 | 43.7386 | 74.9663 | 105.0337 | 51.5824 | 106.856 | 106.856 | 62.8983 | 169.7544 | -0.018037 | 0% | 76.7629 | 0 | 0 | 155.7928 | 155.7928 | 0% | 11.73% | 11.73% | 80% | 9.384% | 7.2033 | 7.5083 | 6 | 43.22 | 15.9295 | 27.74% | 27.74%
6 | 152 | 1 | 3634 | 10 | 10.2 | 176.67 | 129.08 | 305.75 | 129.08 | 64.54 | 152 | 3634 | 600 | 149.9178 | 22.0529 | 10.3633 | 574.284 | 9.7441 | 33.8382 | 53.2077 | 53.2077 | 59.5123 | 120.4877 | 38.6365 | 172.3264 | 172.3264 | 110.1767 | 282.503 | 0.31915 | 31.92% | 127.7479 | 40.7711 | 28.5398 | 140.12 | 140.12 | 20.37% | 11.63% | 11.63% | 80% | 9.305% | 11.8866 | 7.2117 | 6 | 71.3197 | 26.2862 | 50.9% | 50.9%
6 | 152 | 1 | 3635 | 11 | 10.7 | 192.86 | 156.67 | 349.53 | 156.67 | 78.34 | 152 | 3635 | 660 | 149.9178 | 22.0529 | 10.3633 | 634.284 | 10.7441 | 18.8382 | 60.9653 | 60.9653 | 38.0701 | 141.9299 | 27.3249 | 195.9685 | 195.9685 | 133.7262 | 329.6947 | 0.39208 | 39.21% | 149.0879 | 58.4551 | 40.9186 | 137.5732 | 137.5732 | 29.74% | 11.59% | 11.59% | 85% | 9.854% | 14.6906 | 7.0797 | 6 | 88.1439 | 32.4871 | 64.07% | 64.07%
6 | 152 | 1 | 3636 | 12 | 9.9 | 224.25 | 256.94 | 481.19 | 256.94 | 128.47 | 152 | 3636 | 720 | 149.9178 | 22.0529 | 10.3633 | 694.284 | 11.7441 | 3.8382 | 65.0806 | 65.0806 | 8.4674 | 171.5326 | 20.6157 | 231.4361 | 231.4361 | 219.312 | 450.7481 | 0.49857 | 49.86% | 203.8283 | 101.6231 | 71.1362 | 134.496 | 134.496 | 52.89% | 11.55% | 11.55% | 85% | 9.814% | 20.0039 | 7.2918 | 6 | 120.0236 | 44.2369 | 89.24% | 89.24%
6 | 152 | 1 | 3637 | 13 | 12.1 | 273.69 | 250 | 523.69 | 250 | 125 | 152 | 3637 | 780 | 149.9178 | 22.0529 | 10.3633 | 754.284 | 12.7441 | -11.1618 | 63.6783 | 63.6783 | 23.868 | 203.868 | 22.9981 | 281.079 | 281.079 | 213.3883 | 494.4674 | 0.53591 | 53.59% | 223.5981 | 119.8277 | 83.8794 | 138.4313 | 138.4313 | 60.59% | 11.48% | 11.48% | 85% | 9.762% | 21.8277 | 6.7193 | 6 | 130.9665 | 48.2701 | 94.61% | 94.61%
6 | 152 | 1 | 3638 | 14 | 12.8 | 380.92 | 212.14 | 593.06 | 212.14 | 106.07 | 152 | 3638 | 840 | 149.9178 | 22.0529 | 10.3633 | 814.284 | 13.7441 | -26.1618 | 57.4902 | 57.4902 | 49.4957 | 229.4957 | 32.5274 | 380.8455 | 380.8455 | 181.0728 | 561.9183 | 0.57096 | 57.1% | 254.0995 | 145.0795 | 101.5556 | 141.6235 | 141.6235 | 71.71% | 11.45% | 11.45% | 90% | 10.3% | 26.1764 | 6.5443 | 6 | 157.0587 | 57.8869 | 110.9% | 110.9%
6 | 152 | 1 | 3639 | 15 | 13.3 | 258.53 | 187.03 | 445.56 | 187.03 | 93.52 | 152 | 3639 | 900 | 149.9178 | 22.0529 | 10.3633 | 874.284 | 14.7441 | -41.1618 | 48.7166 | 48.7166 | 67.6075 | 247.6075 | 44.8394 | 243.9534 | 243.9534 | 159.6401 | 403.5935 | 0.48238 | 48.24% | 182.505 | 88.0362 | 61.6253 | 134.8144 | 134.8144 | 45.71% | 11.5% | 11.5% | 85% | 9.773% | 17.8369 | 6.4214 | 6 | 107.0213 | 39.4447 | 79.38% | 79.38%
6 | 152 | 1 | 3640 | 16 | 14.7 | 334.64 | 138.69 | 473.33 | 138.69 | 69.35 | 152 | 3640 | 960 | 149.9178 | 22.0529 | 10.3633 | 934.284 | 15.7441 | -56.1618 | 38.8326 | 38.8326 | 81.2155 | 261.2155 | 58.1626 | 281.5194 | 281.5194 | 118.3793 | 399.8987 | 0.48739 | 48.74% | 180.8342 | 88.1372 | 61.696 | 137.077 | 137.077 | 45.01% | 11.47% | 11.47% | 85% | 9.748% | 17.6283 | 6.0865 | 6 | 105.7699 | 38.9835 | 77.16% | 77.16%
6 | 152 | 1 | 3641 | 17 | 13.4 | 162.22 | 103.06 | 265.28 | 103.06 | 51.53 | 152 | 3641 | 1020 | 149.9178 | 22.0529 | 10.3633 | 994.284 | 16.7441 | -71.1618 | 28.5909 | 28.5909 | 92.5487 | 272.5487 | 71.8939 | 105.3479 | 105.3479 | 87.9672 | 193.3151 | 0.13372 | 13.37% | 87.4171 | 11.6891 | 8.1824 | 123.7057 | 123.7057 | 6.614% | 11.57% | 11.57% | 80% | 9.258% | 8.0929 | 6.397 | 6 | 48.5573 | 17.8967 | 39.25% | 39.25%
6 | 152 | 1 | 3642 | 18 | 13.9 | 172.58 | 97.86 | 270.44 | 97.86 | 48.93 | 152 | 3642 | 1080 | 149.9178 | 22.0529 | 10.3633 | 1054.284 | 17.7441 | -86.1618 | 18.4266 | 18.4266 | 102.907 | 282.907 | 85.7757 | 40.2178 | 40.2178 | 83.5287 | 123.7465 | -0.23387 | 0% | 55.9582 | 0 | 0 | 121.7706 | 121.7706 | 0% | 11.58% | 11.58% | 80% | 9.263% | 5.1835 | 6.2762 | 6 | 31.1008 | 11.4628 | 25.54% | 25.54%
6 | 152 | 1 | 3643 | 19 | 14.3 | 82.5 | 84.81 | 167.31 | 84.81 | 42.41 | 152 | 3643 | 1140 | 149.9178 | 22.0529 | 10.3633 | 1114.284 | 18.7441 | -101.1618 | 8.6693 | 8.6693 | 113.101 | 293.101 | 99.6531 | 0 | 0 | 72.3899 | 72.3899 | -0.95758 | 0% | 32.7347 | 0 | 0 | 113.2238 | 113.2238 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3644 | 20 | 13.7 | 19.92 | 39.08 | 59 | 39.08 | 19.54 | 152 | 3644 | 1200 | 149.9178 | 22.0529 | 10.3633 | 1174.284 | 19.7441 | -116.1618 | -0.35826 | 0 | 123.2477 | 303.2477 | 112.8101 | 0 | 0 | 33.3569 | 33.3569 | -3.06 | 0% | 15.084 | 0 | 0 | 142.4759 | 142.4759 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3645 | 21 | 12 | 0 | 5.14 | 5.14 | 5.14 | 2.57 | 152 | 3645 | 1260 | 149.9178 | 22.0529 | 10.3633 | 1234.284 | 20.7441 | -131.1618 | -8.289 | 0 | 123.2477 | 303.2477 | 112.8101 | 0 | 0 | 4.3873 | 4.3873 | -29.4641 | 0% | 1.9839 | 0 | 0 | -11.0037 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3646 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 152 | 3646 | 1320 | 149.9178 | 22.0529 | 10.3633 | 1294.284 | 21.7441 | -146.1618 | -14.6911 | 0 | 123.2477 | 303.2477 | 112.8101 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1494 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3647 | 23 | 10.2 | 0 | 0 | 0 | 0 | 0 | 152 | 3647 | 1380 | 149.9178 | 22.0529 | 10.3633 | 1354.284 | 22.7441 | -161.1618 | -19.0942 | 0 | 123.2477 | 303.2477 | 112.8101 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0366 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
6 | 152 | 1 | 3648 | 24 | 9.4 | 0 | 0 | 0 | 0 | 0 | 152 | 3648 | 1440 | 149.9178 | 22.0529 | 10.3633 | 1414.284 | 23.7441 | -176.1618 | -21.0816 | 0 | 123.2477 | 303.2477 | 112.8101 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9239 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3649 | 1 | 8.2 | 0 | 0 | 0 | 0 | 0 | 153 | 3649 | 60 | 150.9041 | 22.1796 | 10.0019 | 34.284 | 0.7381 | 168.9285 | -20.3196 | 0 | 123.4528 | 56.5472 | 112.9416 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6023 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3650 | 2 | 6.2 | 0 | 0 | 0 | 0 | 0 | 153 | 3650 | 120 | 150.9041 | 22.1796 | 10.0019 | 94.284 | 1.7381 | 153.9285 | -17.1295 | 0 | 123.4528 | 56.5472 | 112.9416 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.1676 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3651 | 3 | 5.8 | 0 | 0 | 0 | 0 | 0 | 153 | 3651 | 180 | 150.9041 | 22.1796 | 10.0019 | 154.284 | 2.7381 | 138.9285 | -11.7117 | 0 | 123.4528 | 56.5472 | 112.9416 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2944 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3652 | 4 | 5.1 | 0 | 0 | 0 | 0 | 0 | 153 | 3652 | 240 | 150.9041 | 22.1796 | 10.0019 | 214.284 | 3.7381 | 123.9285 | -4.5232 | 0 | 123.4528 | 56.5472 | 112.9416 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3612 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3653 | 5 | 4.5 | 0 | 0 | 0 | 0 | 0 | 153 | 3653 | 300 | 150.9041 | 22.1796 | 10.0019 | 274.284 | 4.7381 | 108.9285 | 3.9785 | 3.9785 | 118.5924 | 61.4076 | 106.7698 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5449 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3654 | 6 | 4.4 | 2.42 | 9.17 | 11.59 | 9.17 | 4.59 | 153 | 3654 | 360 | 150.9041 | 22.1796 | 10.0019 | 334.284 | 5.7381 | 93.9285 | 13.3941 | 13.3941 | 108.2571 | 71.7429 | 92.9634 | -0.54009 | 0 | 7.8271 | 7.8271 | -18.4527 | 0% | 3.5394 | 0 | 0 | 0.36113 | 0.36113 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3655 | 7 | 5.7 | 32.78 | 25.36 | 58.14 | 25.36 | 12.68 | 153 | 3655 | 420 | 150.9041 | 22.1796 | 10.0019 | 394.284 | 6.7381 | 78.9285 | 23.3828 | 23.3828 | 98.076 | 81.924 | 79.0792 | 15.6479 | 15.6479 | 21.6461 | 37.294 | -3.1538 | 0% | 16.8643 | 0 | 0 | 167.0611 | 167.0611 | 0% | 11.95% | 11.95% | 80% | 9.561% | 1.6125 | 8.4787 | 6 | 9.6749 | 3.5659 | 5.791% | 5.791%
6 | 153 | 2 | 3656 | 8 | 8.8 | 98.69 | 85.92 | 184.61 | 85.92 | 42.96 | 153 | 3656 | 480 | 150.9041 | 22.1796 | 10.0019 | 454.284 | 7.7381 | 63.9285 | 33.6281 | 33.6281 | 87.382 | 92.618 | 65.2608 | 74.5769 | 74.5769 | 73.3373 | 147.9143 | -0.14418 | 0% | 66.8868 | 0 | 0 | 142.9067 | 142.9067 | 0% | 11.75% | 11.75% | 80% | 9.403% | 6.2893 | 7.5907 | 6 | 37.736 | 13.9083 | 26.41% | 26.41%
6 | 153 | 2 | 3657 | 9 | 10.9 | 203.89 | 129.53 | 333.42 | 129.53 | 64.77 | 153 | 3657 | 540 | 150.9041 | 22.1796 | 10.0019 | 514.284 | 8.7381 | 48.9285 | 43.7675 | 43.7675 | 75.1726 | 104.8274 | 51.6981 | 182.6892 | 182.6892 | 110.5608 | 293.25 | 0.34248 | 34.25% | 132.6076 | 45.4151 | 31.7906 | 153.4415 | 153.4415 | 20.72% | 11.61% | 11.61% | 80% | 9.285% | 12.312 | 7.0274 | 6 | 73.8718 | 27.2268 | 48.14% | 48.14%
6 | 153 | 2 | 3658 | 10 | 13.5 | 210.47 | 158.69 | 369.16 | 158.69 | 79.35 | 153 | 3658 | 600 | 150.9041 | 22.1796 | 10.0019 | 574.284 | 9.7381 | 33.9285 | 53.2519 | 53.2519 | 59.7549 | 120.2451 | 38.7686 | 204.7985 | 204.7985 | 135.4504 | 340.2489 | 0.42385 | 42.38% | 153.8606 | 65.2132 | 45.6492 | 155.7971 | 155.7971 | 29.3% | 11.52% | 11.52% | 85% | 9.789% | 15.0613 | 6.3727 | 6 | 90.3676 | 33.3067 | 58% | 58%
6 | 153 | 2 | 3659 | 11 | 15.2 | 334.72 | 183.81 | 518.53 | 183.81 | 91.91 | 153 | 3659 | 660 | 150.9041 | 22.1796 | 10.0019 | 634.284 | 10.7381 | 18.9285 | 61.0397 | 61.0397 | 38.3431 | 141.6569 | 27.4738 | 339.4127 | 339.4127 | 156.8916 | 496.3044 | 0.55118 | 55.12% | 224.4288 | 123.7002 | 86.5902 | 157.3867 | 157.3867 | 55.02% | 11.43% | 11.43% | 85% | 9.717% | 21.8085 | 5.9702 | 5.9702 | 130.2013 | 48.2276 | 82.73% | 82.73%
6 | 153 | 2 | 3660 | 12 | 15.3 | 381.03 | 186.11 | 567.14 | 186.11 | 93.06 | 153 | 3660 | 720 | 150.9041 | 22.1796 | 10.0019 | 694.284 | 11.7381 | 3.9285 | 65.1973 | 65.1973 | 8.6985 | 171.3015 | 20.7561 | 392.506 | 392.506 | 158.8548 | 551.3608 | 0.57683 | 57.68% | 249.3253 | 143.8194 | 100.6736 | 148.6252 | 148.6252 | 67.74% | 11.42% | 11.42% | 90% | 10.27% | 25.6173 | 5.9472 | 5.9472 | 152.35 | 56.6504 | 102.5% | 102.5%
6 | 153 | 2 | 3661 | 13 | 15.4 | 257.03 | 116.31 | 373.34 | 116.31 | 58.16 | 153 | 3661 | 780 | 150.9041 | 22.1796 | 10.0019 | 754.284 | 12.7381 | -11.0715 | 63.8242 | 63.8242 | 23.773 | 203.773 | 23.0672 | 263.503 | 263.503 | 99.2768 | 362.7798 | 0.45937 | 45.94% | 164.049 | 75.3596 | 52.7517 | 138.3025 | 138.3025 | 38.14% | 11.46% | 11.46% | 85% | 9.743% | 15.9837 | 5.9242 | 5.9242 | 94.6901 | 35.3465 | 68.47% | 68.47%
6 | 153 | 2 | 3662 | 14 | 16.2 | 274.81 | 146.03 | 420.84 | 146.03 | 73.02 | 153 | 3662 | 840 | 150.9041 | 22.1796 | 10.0019 | 814.284 | 13.7381 | -26.0715 | 57.642 | 57.642 | 49.4994 | 229.4994 | 32.5318 | 274.2807 | 274.2807 | 124.6444 | 398.9251 | 0.49512 | 49.51% | 180.394 | 89.3175 | 62.5223 | 140.6105 | 140.6105 | 44.46% | 11.44% | 11.44% | 85% | 9.72% | 17.5351 | 5.7429 | 5.7429 | 100.7024 | 38.7773 | 71.62% | 71.62%
6 | 153 | 2 | 3663 | 15 | 15.8 | 335.36 | 165.64 | 501 | 165.64 | 82.82 | 153 | 3663 | 900 | 150.9041 | 22.1796 | 10.0019 | 874.284 | 14.7381 | -41.0715 | 48.8663 | 48.8663 | 67.6462 | 247.6462 | 44.8071 | 315.9052 | 315.9052 | 141.3826 | 457.2878 | 0.53257 | 53.26% | 206.7855 | 110.1286 | 77.09 | 141.5413 | 141.5413 | 54.46% | 11.43% | 11.43% | 85% | 9.716% | 20.0923 | 5.833 | 5.833 | 117.198 | 44.4323 | 82.8% | 82.8%
6 | 153 | 2 | 3664 | 16 | 16.2 | 350.64 | 132.97 | 483.61 | 132.97 | 66.49 | 153 | 3664 | 960 | 150.9041 | 22.1796 | 10.0019 | 934.284 | 15.7381 | -56.0715 | 38.9802 | 38.9802 | 81.261 | 261.261 | 58.1079 | 294.4917 | 294.4917 | 113.497 | 407.9887 | 0.50199 | 50.2% | 184.4925 | 92.6128 | 64.8289 | 139.9563 | 139.9563 | 46.32% | 11.43% | 11.43% | 85% | 9.719% | 17.9305 | 5.7429 | 5.7429 | 102.9733 | 39.6518 | 73.58% | 73.58%
6 | 153 | 2 | 3665 | 17 | 16 | 250.83 | 141.75 | 392.58 | 141.75 | 70.88 | 153 | 3665 | 1020 | 150.9041 | 22.1796 | 10.0019 | 994.284 | 16.7381 | -71.0715 | 28.7381 | 28.7381 | 92.591 | 272.591 | 71.823 | 162.7419 | 162.7419 | 120.9912 | 283.7331 | 0.36814 | 36.81% | 128.3041 | 47.2335 | 33.0635 | 133.6598 | 133.6598 | 24.74% | 11.47% | 11.47% | 80% | 9.172% | 11.7686 | 5.7878 | 5.7878 | 68.1146 | 26.0253 | 50.96% | 50.96%
6 | 153 | 2 | 3666 | 18 | 15.5 | 128.89 | 116.31 | 245.2 | 116.31 | 58.16 | 153 | 3666 | 1080 | 150.9041 | 22.1796 | 10.0019 | 1054.284 | 17.7381 | -86.0715 | 18.5747 | 18.5747 | 102.942 | 282.942 | 85.6916 | 30.3974 | 30.3974 | 99.2768 | 129.6742 | -0.15839 | 0% | 58.6387 | 0 | 0 | 122.3487 | 122.3487 | 0% | 11.52% | 11.52% | 80% | 9.214% | 5.4032 | 5.9013 | 5.9013 | 31.8855 | 11.9486 | 26.06% | 26.06%
6 | 153 | 2 | 3667 | 19 | 15.3 | 81.94 | 70.47 | 152.41 | 70.47 | 35.24 | 153 | 3667 | 1140 | 150.9041 | 22.1796 | 10.0019 | 1114.284 | 18.7381 | -101.0715 | 8.8191 | 8.8191 | 113.126 | 293.126 | 99.5568 | 0 | 0 | 60.1499 | 60.1499 | -1.2783 | 0% | 27.1998 | 0 | 0 | 113.728 | 113.728 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3668 | 20 | 14.8 | 31.67 | 39.72 | 71.39 | 39.72 | 19.86 | 153 | 3668 | 1200 | 150.9041 | 22.1796 | 10.0019 | 1174.284 | 19.7381 | -116.0715 | -0.2069 | 0 | 123.4528 | 303.4528 | 112.9416 | 0 | 0 | 33.9031 | 33.9031 | -2.9238 | 0% | 15.331 | 0 | 0 | 144.631 | 144.631 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3669 | 21 | 14.3 | 0 | 8.06 | 8.06 | 8.06 | 4.03 | 153 | 3669 | 1260 | 150.9041 | 22.1796 | 10.0019 | 1234.284 | 20.7381 | -131.0715 | -8.1372 | 0 | 123.4528 | 303.4528 | 112.9416 | 0 | 0 | 6.8796 | 6.8796 | -17.732 | 0% | 3.111 | 0 | 0 | -7.9556 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3670 | 22 | 13 | 0 | 0 | 0 | 0 | 0 | 153 | 3670 | 1320 | 150.9041 | 22.1796 | 10.0019 | 1294.284 | 21.7381 | -146.0715 | -14.5417 | 0 | 123.4528 | 303.4528 | 112.9416 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7354 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3671 | 23 | 12.4 | 0 | 0 | 0 | 0 | 0 | 153 | 3671 | 1380 | 150.9041 | 22.1796 | 10.0019 | 1354.284 | 22.7381 | -161.0715 | -18.9514 | 0 | 123.4528 | 303.4528 | 112.9416 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.167 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
6 | 153 | 2 | 3672 | 24 | 11.8 | 0 | 0 | 0 | 0 | 0 | 153 | 3672 | 1440 | 150.9041 | 22.1796 | 10.0019 | 1414.284 | 23.7381 | -176.0715 | -20.951 | 0 | 123.4528 | 303.4528 | 112.9416 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5987 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3673 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 154 | 3673 | 60 | 151.8904 | 22.2996 | 9.6328 | 34.284 | 0.73195 | 169.0208 | -20.2127 | 0 | 123.6475 | 56.3525 | 113.0662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9129 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3674 | 2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 154 | 3674 | 120 | 151.8904 | 22.2996 | 9.6328 | 94.284 | 1.7319 | 154.0208 | -17.0424 | 0 | 123.6475 | 56.3525 | 113.0662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0341 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3675 | 3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 154 | 3675 | 180 | 151.8904 | 22.2996 | 9.6328 | 154.284 | 2.7319 | 139.0208 | -11.6443 | 0 | 123.6475 | 56.3525 | 113.0662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0884 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3676 | 4 | 10.2 | 0 | 0 | 0 | 0 | 0 | 154 | 3676 | 240 | 151.8904 | 22.2996 | 9.6328 | 214.284 | 3.7319 | 124.0208 | -4.4733 | 0 | 123.6475 | 56.3525 | 113.0662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5456 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3677 | 5 | 9.7 | 0 | 0 | 0 | 0 | 0 | 154 | 3677 | 300 | 151.8904 | 22.2996 | 9.6328 | 274.284 | 4.7319 | 109.0208 | 4.0144 | 4.0144 | 118.7356 | 61.2644 | 106.8351 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.315 | 6.315 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3678 | 6 | 9.6 | 3.89 | 17.78 | 21.67 | 17.78 | 8.89 | 154 | 3678 | 360 | 151.8904 | 22.2996 | 9.6328 | 334.284 | 5.7319 | 94.0208 | 13.4195 | 13.4195 | 108.4063 | 71.5937 | 93.0421 | -0.88953 | 0 | 15.1762 | 15.1762 | -8.3137 | 0% | 6.8627 | 0 | 0 | 22.2878 | 22.2878 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3679 | 7 | 9.7 | 53.81 | 63.14 | 116.95 | 63.14 | 31.57 | 154 | 3679 | 420 | 151.8904 | 22.2996 | 9.6328 | 394.284 | 6.7319 | 79.0208 | 23.402 | 23.402 | 98.2351 | 81.7649 | 79.1699 | 25.4564 | 25.4564 | 53.8934 | 79.3497 | -0.93688 | 0% | 35.882 | 0 | 0 | 200.4052 | 200.4052 | 0% | 11.76% | 11.76% | 80% | 9.408% | 3.3758 | 7.3455 | 6 | 20.2551 | 7.4654 | 10.11% | 10.11%
6 | 154 | 3 | 3680 | 8 | 10.6 | 226.94 | 81.03 | 307.97 | 81.03 | 40.52 | 154 | 3680 | 480 | 151.8904 | 22.2996 | 9.6328 | 454.284 | 7.7319 | 64.0208 | 33.6458 | 33.6458 | 87.5576 | 92.4424 | 65.3633 | 170.7456 | 170.7456 | 69.1634 | 239.909 | 0.23696 | 23.7% | 108.4869 | 25.7066 | 17.9946 | 180.6412 | 180.6412 | 9.962% | 11.64% | 11.64% | 80% | 9.313% | 10.1037 | 7.1059 | 6 | 60.6219 | 22.3433 | 33.56% | 33.56%
6 | 154 | 3 | 3681 | 9 | 9.7 | 371.19 | 99.08 | 470.27 | 99.08 | 49.54 | 154 | 3681 | 540 | 151.8904 | 22.2996 | 9.6328 | 514.284 | 8.7319 | 49.0208 | 43.7902 | 43.7902 | 75.3742 | 104.6258 | 51.8136 | 331.6057 | 331.6057 | 84.5701 | 416.1758 | 0.47208 | 47.21% | 188.1947 | 88.8423 | 62.1896 | 186.8968 | 186.8968 | 33.27% | 11.57% | 11.57% | 85% | 9.834% | 18.5071 | 7.3455 | 6 | 111.0426 | 40.9268 | 59.41% | 59.41%
6 | 154 | 3 | 3682 | 10 | 10.7 | 516.94 | 119.72 | 636.66 | 119.72 | 59.86 | 154 | 3682 | 600 | 151.8904 | 22.2996 | 9.6328 | 574.284 | 9.7319 | 34.0208 | 53.2894 | 53.2894 | 59.9931 | 120.0069 | 38.8992 | 501.8422 | 501.8422 | 102.1874 | 604.0296 | 0.57917 | 57.92% | 273.1422 | 158.1947 | 110.7363 | 190.4125 | 190.4125 | 58.16% | 11.45% | 11.45% | 90% | 10.31% | 28.1528 | 7.0797 | 6 | 168.9168 | 62.2574 | 88.71% | 88.71%
6 | 154 | 3 | 3683 | 11 | 11.9 | 635.64 | 125.28 | 760.92 | 125.28 | 62.64 | 154 | 3683 | 660 | 151.8904 | 22.2996 | 9.6328 | 634.284 | 10.7319 | 19.0208 | 61.1069 | 61.1069 | 38.6141 | 141.3859 | 27.6192 | 643.2815 | 643.2815 | 106.9332 | 750.2147 | 0.62668 | 62.67% | 339.2471 | 212.6007 | 148.8205 | 184.8102 | 184.8102 | 80.53% | 11.37% | 11.37% | 90% | 10.24% | 34.7279 | 6.77 | 6 | 208.3675 | 76.7977 | 112.7% | 112.7%
6 | 154 | 3 | 3684 | 12 | 12.2 | 732.5 | 115.97 | 848.47 | 115.97 | 57.99 | 154 | 3684 | 720 | 151.8904 | 22.2996 | 9.6328 | 694.284 | 11.7319 | 4.0208 | 65.3068 | 65.3068 | 8.9337 | 171.0663 | 20.8905 | 753.2246 | 753.2246 | 98.9866 | 852.2111 | 0.64872 | 64.87% | 385.3699 | 249.9964 | 174.9975 | 170.6702 | 170.6702 | 102.5% | 11.33% | 11.33% | 95% | 10.76% | 41.4778 | 6.6941 | 6 | 248.867 | 91.7245 | 145.8% | 145.8%
6 | 154 | 3 | 3685 | 13 | 13.2 | 629.72 | 159.64 | 789.36 | 159.64 | 79.82 | 154 | 3685 | 780 | 151.8904 | 22.2996 | 9.6328 | 754.284 | 12.7319 | -10.9792 | 63.9642 | 63.9642 | 23.6688 | 203.6688 | 23.1304 | 644.503 | 644.503 | 136.2613 | 780.7642 | 0.63745 | 63.75% | 353.0616 | 225.0601 | 157.5421 | 166.119 | 166.119 | 94.84% | 11.36% | 11.36% | 90% | 10.22% | 36.0945 | 6.4458 | 6 | 216.5667 | 79.8197 | 130.4% | 130.4%
6 | 154 | 3 | 3686 | 14 | 14.4 | 721.25 | 167.64 | 888.89 | 167.64 | 83.82 | 154 | 3686 | 840 | 151.8904 | 22.2996 | 9.6328 | 814.284 | 13.7319 | -25.9792 | 57.7893 | 57.7893 | 49.4937 | 229.4937 | 32.5316 | 718.6943 | 718.6943 | 143.0897 | 861.784 | 0.65629 | 65.63% | 389.6987 | 255.7558 | 179.029 | 170.38 | 170.38 | 105.1% | 11.33% | 11.33% | 95% | 10.77% | 41.9562 | 6.1571 | 6 | 251.7373 | 92.7824 | 147.8% | 147.8%
6 | 154 | 3 | 3687 | 15 | 14.7 | 666.67 | 189.31 | 855.98 | 189.31 | 94.66 | 154 | 3687 | 900 | 151.8904 | 22.2996 | 9.6328 | 874.284 | 14.7319 | -40.9792 | 49.0123 | 49.0123 | 67.6764 | 247.6764 | 44.7713 | 626.992 | 626.992 | 161.5862 | 788.5782 | 0.64344 | 64.34% | 356.595 | 229.4489 | 160.6142 | 167.0793 | 167.0793 | 96.13% | 11.36% | 11.36% | 90% | 10.22% | 36.4433 | 6.0865 | 6 | 218.6597 | 80.5911 | 130.9% | 130.9%
6 | 154 | 3 | 3688 | 16 | 14.9 | 373.33 | 176.31 | 549.64 | 176.31 | 88.16 | 154 | 3688 | 960 | 151.8904 | 22.2996 | 9.6328 | 934.284 | 15.7319 | -55.9792 | 39.1246 | 39.1246 | 81.299 | 261.299 | 58.0503 | 313.081 | 313.081 | 150.49 | 463.571 | 0.53186 | 53.19% | 209.6268 | 111.4918 | 78.0443 | 151.7966 | 151.7966 | 51.41% | 11.45% | 11.45% | 85% | 9.729% | 20.3955 | 6.0398 | 6 | 122.3727 | 45.1027 | 80.62% | 80.62%
6 | 154 | 3 | 3689 | 17 | 15.3 | 448.25 | 160.47 | 608.72 | 160.47 | 80.24 | 154 | 3689 | 1020 | 151.8904 | 22.2996 | 9.6328 | 994.284 | 16.7319 | -70.9792 | 28.882 | 28.882 | 92.6265 | 272.6265 | 71.7499 | 290.6292 | 290.6292 | 136.9697 | 427.599 | 0.51108 | 51.11% | 193.3602 | 98.8235 | 69.1764 | 151.9675 | 151.9675 | 45.52% | 11.45% | 11.45% | 85% | 9.731% | 18.8159 | 5.9472 | 5.9472 | 111.9013 | 41.6098 | 73.64% | 73.64%
6 | 154 | 3 | 3690 | 18 | 15 | 236.47 | 110.19 | 346.66 | 110.19 | 55.1 | 154 | 3690 | 1080 | 151.8904 | 22.2996 | 9.6328 | 1054.284 | 17.7319 | -85.9792 | 18.7195 | 18.7195 | 102.9709 | 282.9709 | 85.6059 | 56.4522 | 56.4522 | 94.053 | 150.5052 | -0.032715 | 0% | 68.0585 | 0 | 0 | 133.3149 | 133.3149 | 0% | 11.53% | 11.53% | 80% | 9.224% | 6.278 | 6.0165 | 6 | 37.6683 | 13.8833 | 28.26% | 28.26%
6 | 154 | 3 | 3691 | 19 | 14.7 | 145.36 | 82.69 | 228.05 | 82.69 | 41.35 | 154 | 3691 | 1140 | 151.8904 | 22.2996 | 9.6328 | 1114.284 | 18.7319 | -100.9792 | 8.9652 | 8.9652 | 113.1453 | 293.1453 | 99.4595 | 0 | 0 | 70.5803 | 70.5803 | -0.98986 | 0% | 31.9164 | 0 | 0 | 121.1575 | 121.1575 | 0% | 11.56% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3692 | 20 | 14 | 28.61 | 36.47 | 65.08 | 36.47 | 18.24 | 154 | 3692 | 1200 | 151.8904 | 22.2996 | 9.6328 | 1174.284 | 19.7319 | -115.9792 | -0.059729 | 0 | 123.6475 | 303.6475 | 113.0662 | 0 | 0 | 31.1291 | 31.1291 | -3.3145 | 0% | 14.0766 | 0 | 0 | 143.1325 | 143.1325 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3693 | 21 | 13.6 | 0 | 7.03 | 7.03 | 7.03 | 3.52 | 154 | 3693 | 1260 | 151.8904 | 22.2996 | 9.6328 | 1234.284 | 20.7319 | -130.9792 | -7.9903 | 0 | 123.6475 | 303.6475 | 113.0662 | 0 | 0 | 6.0005 | 6.0005 | -20.714 | 0% | 2.7134 | 0 | 0 | -9.7798 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3694 | 22 | 13.5 | 0 | 0 | 0 | 0 | 0 | 154 | 3694 | 1320 | 151.8904 | 22.2996 | 9.6328 | 1294.284 | 21.7319 | -145.9792 | -14.3977 | 0 | 123.6475 | 303.6475 | 113.0662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4828 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3695 | 23 | 13.6 | 0 | 0 | 0 | 0 | 0 | 154 | 3695 | 1380 | 151.8904 | 22.2996 | 9.6328 | 1354.284 | 22.7319 | -160.9792 | -18.8147 | 0 | 123.6475 | 303.6475 | 113.0662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5371 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
6 | 154 | 3 | 3696 | 24 | 13.3 | 0 | 0 | 0 | 0 | 0 | 154 | 3696 | 1440 | 151.8904 | 22.2996 | 9.6328 | 1414.284 | 23.7319 | -175.9792 | -20.8268 | 0 | 123.6475 | 303.6475 | 113.0662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.201 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3697 | 1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 155 | 3697 | 60 | 152.8767 | 22.413 | 9.2563 | 34.284 | 0.72567 | 169.1149 | -20.1124 | 0 | 123.8316 | 56.1684 | 113.1839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7355 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3698 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 155 | 3698 | 120 | 152.8767 | 22.413 | 9.2563 | 94.284 | 1.7257 | 154.1149 | -16.962 | 0 | 123.8316 | 56.1684 | 113.1839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7774 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3699 | 3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 155 | 3699 | 180 | 152.8767 | 22.413 | 9.2563 | 154.284 | 2.7257 | 139.1149 | -11.5834 | 0 | 123.8316 | 56.1684 | 113.1839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.143 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3700 | 4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 155 | 3700 | 240 | 152.8767 | 22.413 | 9.2563 | 214.284 | 3.7257 | 124.1149 | -4.4296 | 0 | 123.8316 | 56.1684 | 113.1839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2953 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3701 | 5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 155 | 3701 | 300 | 152.8767 | 22.413 | 9.2563 | 274.284 | 4.7257 | 109.1149 | 4.0441 | 4.0441 | 118.8758 | 61.1242 | 106.903 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.661 | 5.661 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3702 | 6 | 10.1 | 4.72 | 18.53 | 23.25 | 18.53 | 9.27 | 155 | 3702 | 360 | 152.8767 | 22.413 | 9.2563 | 334.284 | 5.7257 | 94.1149 | 13.4391 | 13.4391 | 108.5519 | 71.4481 | 93.1227 | -1.1063 | 0 | 15.8163 | 15.8163 | -7.8708 | 0% | 7.1522 | 0 | 0 | 20.2644 | 20.2644 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3703 | 7 | 10.4 | 65.47 | 71.86 | 137.33 | 71.86 | 35.93 | 155 | 3703 | 420 | 152.8767 | 22.413 | 9.2563 | 394.284 | 6.7257 | 79.1149 | 23.4154 | 23.4154 | 98.3902 | 81.6098 | 79.2619 | 30.696 | 30.696 | 61.3363 | 92.0323 | -0.67922 | 0% | 41.617 | 0 | 0 | 197.731 | 197.731 | 0% | 11.73% | 11.73% | 80% | 9.381% | 3.9039 | 7.1587 | 6 | 23.4237 | 8.6332 | 11.85% | 11.85%
6 | 155 | 4 | 3704 | 8 | 11.8 | 170.28 | 114.44 | 284.72 | 114.44 | 57.22 | 155 | 3704 | 480 | 152.8767 | 22.413 | 9.2563 | 454.284 | 7.7257 | 64.1149 | 33.6576 | 33.6576 | 87.7288 | 92.2712 | 65.4665 | 127.5725 | 127.5725 | 97.6807 | 225.2532 | 0.21242 | 21.24% | 101.8595 | 21.6366 | 15.1456 | 175.3746 | 175.3746 | 8.636% | 11.61% | 11.61% | 80% | 9.289% | 9.4617 | 6.7954 | 6 | 56.7702 | 20.9237 | 32.37% | 32.37%
6 | 155 | 4 | 3705 | 9 | 13.8 | 324.72 | 136.58 | 461.3 | 136.58 | 68.29 | 155 | 3705 | 540 | 152.8767 | 22.413 | 9.2563 | 514.284 | 8.7257 | 49.1149 | 43.8068 | 43.8068 | 75.5709 | 104.4291 | 51.929 | 289.2607 | 289.2607 | 116.5783 | 405.839 | 0.48697 | 48.7% | 183.5204 | 89.3698 | 62.5588 | 186.939 | 186.939 | 33.46% | 11.49% | 11.49% | 85% | 9.763% | 17.9179 | 6.3002 | 6 | 107.5075 | 39.6239 | 57.51% | 57.51%
6 | 155 | 4 | 3706 | 10 | 15.5 | 429.08 | 156.86 | 585.94 | 156.86 | 78.43 | 155 | 3706 | 600 | 152.8767 | 22.413 | 9.2563 | 574.284 | 9.7257 | 34.1149 | 53.3205 | 53.3205 | 60.2266 | 119.7734 | 39.0283 | 415.6219 | 415.6219 | 133.8884 | 549.5103 | 0.57689 | 57.69% | 248.4886 | 143.3513 | 100.3459 | 189.6923 | 189.6923 | 52.9% | 11.41% | 11.41% | 90% | 10.27% | 25.5262 | 5.9013 | 5.9013 | 150.6373 | 56.449 | 79.41% | 79.41%
6 | 155 | 4 | 3707 | 11 | 16.5 | 556.31 | 159.81 | 716.12 | 159.81 | 79.91 | 155 | 3707 | 660 | 152.8767 | 22.413 | 9.2563 | 634.284 | 10.7257 | 19.1149 | 61.167 | 61.167 | 38.8828 | 141.1172 | 27.7611 | 561.9419 | 561.9419 | 136.4064 | 698.3482 | 0.62852 | 62.85% | 315.7931 | 198.4836 | 138.9386 | 184.7154 | 184.7154 | 75.22% | 11.37% | 11.37% | 90% | 10.23% | 32.3196 | 5.6761 | 5.6761 | 183.4483 | 71.4718 | 99.31% | 99.31%
6 | 155 | 4 | 3708 | 12 | 17.3 | 499.31 | 187.92 | 687.23 | 187.92 | 93.96 | 155 | 3708 | 720 | 152.8767 | 22.413 | 9.2563 | 694.284 | 11.7257 | 4.1149 | 65.4093 | 65.4093 | 9.1728 | 170.8272 | 21.0188 | 512.5759 | 512.5759 | 160.3998 | 672.9757 | 0.62457 | 62.46% | 304.3196 | 190.0702 | 133.0492 | 167.8004 | 167.8004 | 79.29% | 11.37% | 11.37% | 90% | 10.23% | 31.1434 | 5.501 | 5.501 | 171.3184 | 68.8708 | 102.1% | 102.1%
6 | 155 | 4 | 3709 | 13 | 18.1 | 495.19 | 220.75 | 715.94 | 220.75 | 110.38 | 155 | 3709 | 780 | 152.8767 | 22.413 | 9.2563 | 754.284 | 12.7257 | -10.8851 | 64.0983 | 64.0983 | 23.5557 | 203.5557 | 23.1877 | 506.0207 | 506.0207 | 188.4219 | 694.4426 | 0.63269 | 63.27% | 314.0269 | 198.6823 | 139.0776 | 166.2138 | 166.2138 | 83.67% | 11.36% | 11.36% | 90% | 10.23% | 32.1147 | 5.3303 | 5.3303 | 171.1814 | 71.0188 | 103% | 103%
6 | 155 | 4 | 3710 | 14 | 19.2 | 471.86 | 236.39 | 708.25 | 236.39 | 118.2 | 155 | 3710 | 840 | 152.8767 | 22.413 | 9.2563 | 814.284 | 13.7257 | -25.8851 | 57.932 | 57.932 | 49.4784 | 229.4784 | 32.5268 | 469.4776 | 469.4776 | 201.7715 | 671.249 | 0.63041 | 63.04% | 303.5388 | 191.3537 | 133.9476 | 165.6063 | 165.6063 | 80.88% | 11.36% | 11.36% | 90% | 10.22% | 31.0274 | 5.103 | 5.103 | 158.333 | 68.6144 | 95.61% | 95.61%
6 | 155 | 4 | 3711 | 15 | 19 | 343.25 | 261.39 | 604.64 | 261.39 | 130.7 | 155 | 3711 | 900 | 152.8767 | 22.413 | 9.2563 | 874.284 | 14.7257 | -40.8851 | 49.1545 | 49.1545 | 67.6982 | 247.6982 | 44.7319 | 322.3465 | 322.3465 | 223.1103 | 545.4568 | 0.58956 | 58.96% | 246.6556 | 145.4194 | 101.7936 | 157.9307 | 157.9307 | 64.45% | 11.37% | 11.37% | 90% | 10.23% | 25.2314 | 5.1437 | 5.1437 | 129.7827 | 55.797 | 82.18% | 82.18%
6 | 155 | 4 | 3712 | 16 | 18.2 | 356.67 | 250.47 | 607.14 | 250.47 | 125.24 | 155 | 3712 | 960 | 152.8767 | 22.413 | 9.2563 | 934.284 | 15.7257 | -55.8851 | 39.2655 | 39.2655 | 81.3296 | 261.3296 | 57.9899 | 298.712 | 298.712 | 213.7895 | 512.5015 | 0.57231 | 57.23% | 231.7532 | 132.6349 | 92.8444 | 154.0466 | 154.0466 | 60.27% | 11.38% | 11.38% | 90% | 10.24% | 23.7371 | 5.3093 | 5.3093 | 126.0275 | 52.4925 | 81.81% | 81.81%
6 | 155 | 4 | 3713 | 17 | 18.3 | 243.81 | 194.64 | 438.45 | 194.64 | 97.32 | 155 | 3713 | 1020 | 152.8767 | 22.413 | 9.2563 | 994.284 | 16.7257 | -70.8851 | 29.0227 | 29.0227 | 92.6554 | 272.6554 | 71.6747 | 158.004 | 158.004 | 166.1356 | 324.1397 | 0.43836 | 43.84% | 146.5759 | 64.253 | 44.9771 | 143.2625 | 143.2625 | 31.39% | 11.4% | 11.4% | 85% | 9.687% | 14.1988 | 5.2884 | 5.2884 | 75.0885 | 31.3995 | 52.41% | 52.41%
6 | 155 | 4 | 3714 | 18 | 17.9 | 183.06 | 177.03 | 360.09 | 177.03 | 88.52 | 155 | 3714 | 1080 | 152.8767 | 22.413 | 9.2563 | 1054.284 | 17.7257 | -85.8851 | 18.8608 | 18.8608 | 102.9937 | 282.9937 | 85.5186 | 44.2459 | 44.2459 | 151.1046 | 195.3505 | 0.19274 | 19.27% | 88.3375 | 17.0265 | 11.9186 | 134.0956 | 134.0956 | 8.888% | 11.42% | 11.42% | 80% | 9.137% | 8.0718 | 5.3726 | 5.3726 | 43.3662 | 17.8501 | 32.34% | 32.34%
6 | 155 | 4 | 3715 | 19 | 17.2 | 102.69 | 110.83 | 213.52 | 110.83 | 55.42 | 155 | 3715 | 1140 | 152.8767 | 22.413 | 9.2563 | 1114.284 | 18.7257 | -100.8851 | 9.1075 | 9.1075 | 113.1589 | 293.1589 | 99.3614 | 0 | 0 | 94.5993 | 94.5993 | -0.47479 | 0% | 42.7778 | 0 | 0 | 120.7791 | 120.7791 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3716 | 20 | 16.6 | 14.36 | 54.81 | 69.17 | 54.81 | 27.41 | 155 | 3716 | 1200 | 152.8767 | 22.413 | 9.2563 | 1174.284 | 19.7257 | -115.8851 | 0.083211 | 0.083211 | 123.7251 | 303.7251 | 113.0519 | 0 | 0 | 46.7833 | 46.7833 | -1.8106 | 0% | 21.1554 | 0 | 0 | 144.9878 | 144.9878 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3717 | 21 | 15.1 | 0 | 6.39 | 6.39 | 6.39 | 3.2 | 155 | 3717 | 1260 | 152.8767 | 22.413 | 9.2563 | 1234.284 | 20.7257 | -130.8851 | -7.8481 | 0 | 123.8316 | 303.8316 | 113.1839 | 0 | 0 | 5.4542 | 5.4542 | -22.243 | 0% | 2.4664 | 0 | 0 | -8.9432 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3718 | 22 | 14.1 | 0 | 0 | 0 | 0 | 0 | 155 | 3718 | 1320 | 152.8767 | 22.413 | 9.2563 | 1294.284 | 21.7257 | -145.8851 | -14.2591 | 0 | 123.8316 | 303.8316 | 113.1839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7244 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3719 | 23 | 13.2 | 0 | 0 | 0 | 0 | 0 | 155 | 3719 | 1380 | 152.8767 | 22.413 | 9.2563 | 1354.284 | 22.7257 | -160.8851 | -18.6839 | 0 | 123.8316 | 303.8316 | 113.1839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3092 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
6 | 155 | 4 | 3720 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 155 | 3720 | 1440 | 152.8767 | 22.413 | 9.2563 | 1414.284 | 23.7257 | -175.8851 | -20.709 | 0 | 123.8316 | 303.8316 | 113.1839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8271 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3721 | 1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 156 | 3721 | 60 | 153.863 | 22.5197 | 8.8726 | 34.284 | 0.71928 | 169.2109 | -20.0189 | 0 | 124.0051 | 55.9949 | 113.2947 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8819 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3722 | 2 | 12.3 | 0 | 0 | 0 | 0 | 0 | 156 | 3722 | 120 | 153.863 | 22.5197 | 8.8726 | 94.284 | 1.7193 | 154.2109 | -16.8882 | 0 | 124.0051 | 55.9949 | 113.2947 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6578 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3723 | 3 | 12.4 | 0 | 0 | 0 | 0 | 0 | 156 | 3723 | 180 | 153.863 | 22.5197 | 8.8726 | 154.284 | 2.7193 | 139.2109 | -11.529 | 0 | 124.0051 | 55.9949 | 113.2947 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8242 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3724 | 4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 156 | 3724 | 240 | 153.863 | 22.5197 | 8.8726 | 214.284 | 3.7193 | 124.2109 | -4.3922 | 0 | 124.0051 | 55.9949 | 113.2947 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7385 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3725 | 5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 156 | 3725 | 300 | 153.863 | 22.5197 | 8.8726 | 274.284 | 4.7193 | 109.2109 | 4.0679 | 4.0679 | 119.0128 | 60.9872 | 106.9733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.505 | 3.505 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3726 | 6 | 11 | 4.64 | 14.81 | 19.45 | 14.81 | 7.41 | 156 | 3726 | 360 | 153.863 | 22.5197 | 8.8726 | 334.284 | 5.7193 | 94.2109 | 13.4528 | 13.4528 | 108.6938 | 71.3062 | 93.2052 | -1.1151 | 0 | 12.6411 | 12.6411 | -9.8841 | 0% | 5.7163 | 0 | 0 | 16.1403 | 16.1403 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3727 | 7 | 11.2 | 40.47 | 42.22 | 82.69 | 42.22 | 21.11 | 156 | 3727 | 420 | 153.863 | 22.5197 | 8.8726 | 394.284 | 6.7193 | 79.2109 | 23.423 | 23.423 | 98.5411 | 81.4589 | 79.3551 | 18.806 | 18.806 | 36.037 | 54.843 | -1.6511 | 0% | 24.8 | 0 | 0 | 186.394 | 186.394 | 0% | 11.71% | 11.71% | 80% | 9.37% | 2.3238 | 6.9494 | 6 | 13.9427 | 5.1389 | 7.48% | 7.48%
6 | 156 | 5 | 3728 | 8 | 12.3 | 130.64 | 74.92 | 205.56 | 74.92 | 37.46 | 156 | 3728 | 480 | 153.863 | 22.5197 | 8.8726 | 454.284 | 7.7193 | 64.2109 | 33.6637 | 33.6637 | 87.8953 | 92.1047 | 65.5703 | 97.4705 | 97.4705 | 63.9482 | 161.4187 | -0.014384 | 0% | 72.9935 | 0 | 0 | 161.3498 | 161.3498 | 0% | 11.62% | 11.62% | 80% | 9.298% | 6.7869 | 6.669 | 6 | 40.7214 | 15.0086 | 25.24% | 25.24%
6 | 156 | 5 | 3729 | 9 | 14.2 | 234.72 | 126.39 | 361.11 | 126.39 | 63.2 | 156 | 3729 | 540 | 153.863 | 22.5197 | 8.8726 | 514.284 | 8.7193 | 49.2109 | 43.8174 | 43.8174 | 75.7626 | 104.2374 | 52.044 | 208.5121 | 208.5121 | 107.8806 | 316.3927 | 0.40023 | 40.02% | 143.0728 | 57.2626 | 40.0838 | 171.9163 | 171.9163 | 23.32% | 11.51% | 11.51% | 85% | 9.78% | 13.993 | 6.2045 | 6 | 83.9579 | 30.9443 | 48.84% | 48.84%
6 | 156 | 5 | 3730 | 10 | 16.1 | 262.08 | 195.69 | 457.77 | 195.69 | 97.85 | 156 | 3730 | 600 | 153.863 | 22.5197 | 8.8726 | 574.284 | 9.7193 | 34.2109 | 53.345 | 53.345 | 60.4552 | 119.5448 | 39.1559 | 253.3205 | 253.3205 | 167.0319 | 420.3523 | 0.51033 | 51.03% | 190.0833 | 97.0059 | 67.9041 | 175.1283 | 175.1283 | 38.77% | 11.43% | 11.43% | 85% | 9.718% | 18.4731 | 5.7653 | 5.7653 | 106.5032 | 40.8516 | 60.81% | 60.81%
6 | 156 | 5 | 3731 | 11 | 17.9 | 401.86 | 246.11 | 647.97 | 246.11 | 123.06 | 156 | 3731 | 660 | 153.863 | 22.5197 | 8.8726 | 634.284 | 10.7193 | 19.2109 | 61.22 | 61.22 | 39.1488 | 140.8512 | 27.8993 | 405.2055 | 405.2055 | 210.068 | 615.2735 | 0.60993 | 60.99% | 278.2267 | 169.6974 | 118.7882 | 176.4375 | 176.4375 | 67.33% | 11.37% | 11.37% | 90% | 10.24% | 28.4793 | 5.3726 | 5.3726 | 153.0066 | 62.9794 | 86.72% | 86.72%
6 | 156 | 5 | 3732 | 12 | 19.1 | 448.14 | 237.86 | 686 | 237.86 | 118.93 | 156 | 3732 | 720 | 153.863 | 22.5197 | 8.8726 | 694.284 | 11.7193 | 4.2109 | 65.5046 | 65.5046 | 9.4154 | 170.5846 | 21.1412 | 459.3188 | 459.3188 | 203.0262 | 662.345 | 0.62774 | 62.77% | 299.5124 | 188.0164 | 131.6115 | 165.5396 | 165.5396 | 79.5% | 11.36% | 11.36% | 90% | 10.22% | 30.619 | 5.1233 | 5.1233 | 156.8705 | 67.7111 | 94.76% | 94.76%
6 | 156 | 5 | 3733 | 13 | 19.2 | 408.53 | 308.33 | 716.86 | 308.33 | 154.17 | 156 | 3733 | 780 | 153.863 | 22.5197 | 8.8726 | 754.284 | 12.7193 | -10.7891 | 64.2264 | 64.2264 | 23.4338 | 203.4338 | 23.2393 | 416.8527 | 416.8527 | 263.1761 | 680.0288 | 0.63265 | 63.27% | 307.509 | 194.5457 | 136.182 | 163.5698 | 163.5698 | 83.26% | 11.36% | 11.36% | 90% | 10.22% | 31.4322 | 5.103 | 5.103 | 160.3985 | 69.5095 | 98.06% | 98.06%
6 | 156 | 5 | 3734 | 14 | 19.3 | 294.81 | 345.56 | 640.37 | 345.56 | 172.78 | 156 | 3734 | 840 | 153.863 | 22.5197 | 8.8726 | 814.284 | 13.7193 | -25.7891 | 58.0701 | 58.0701 | 49.4535 | 229.4535 | 32.5175 | 292.9104 | 292.9104 | 294.9539 | 587.8643 | 0.60616 | 60.62% | 265.8322 | 161.1376 | 112.7963 | 158.7883 | 158.7883 | 71.04% | 11.36% | 11.36% | 90% | 10.22% | 27.1791 | 5.0828 | 5.0828 | 138.1446 | 60.1041 | 87% | 87%
6 | 156 | 5 | 3735 | 15 | 16.9 | 320.75 | 254.25 | 575 | 254.25 | 127.13 | 156 | 3735 | 900 | 153.863 | 22.5197 | 8.8726 | 874.284 | 14.7193 | -40.7891 | 49.2929 | 49.2929 | 67.7114 | 247.7114 | 44.6891 | 300.8124 | 300.8124 | 217.0159 | 517.8283 | 0.56909 | 56.91% | 234.162 | 133.2584 | 93.2809 | 148.4371 | 148.4371 | 62.84% | 11.4% | 11.4% | 90% | 10.26% | 24.0253 | 5.588 | 5.588 | 134.252 | 53.1297 | 90.44% | 90.44%
6 | 156 | 5 | 3736 | 16 | 18.9 | 176.86 | 233.69 | 410.55 | 233.69 | 116.85 | 156 | 3736 | 960 | 153.863 | 22.5197 | 8.8726 | 934.284 | 15.7193 | -55.7891 | 39.4031 | 39.4031 | 81.3526 | 261.3526 | 57.9268 | 147.9475 | 147.9475 | 199.4669 | 347.4144 | 0.46669 | 46.67% | 157.1008 | 73.3172 | 51.322 | 141.5605 | 141.5605 | 36.25% | 11.38% | 11.38% | 85% | 9.672% | 15.1955 | 5.1642 | 5.1642 | 78.4721 | 33.6036 | 55.43% | 55.43%
6 | 156 | 5 | 3737 | 17 | 19.8 | 56.58 | 174.72 | 231.3 | 174.72 | 87.36 | 156 | 3737 | 1020 | 153.863 | 22.5197 | 8.8726 | 994.284 | 16.7193 | -70.7891 | 29.1601 | 29.1601 | 92.6776 | 272.6776 | 71.5974 | 36.6584 | 36.6584 | 149.1328 | 185.7913 | 0.18396 | 18.4% | 84.0148 | 15.4554 | 10.8188 | 131.3767 | 131.3767 | 8.235% | 11.36% | 11.36% | 80% | 9.087% | 7.6344 | 4.9826 | 4.9826 | 38.0392 | 16.8829 | 28.95% | 28.95%
6 | 156 | 5 | 3738 | 18 | 20.5 | 16.86 | 92.58 | 109.44 | 92.58 | 46.29 | 156 | 3738 | 1080 | 153.863 | 22.5197 | 8.8726 | 1054.284 | 17.7193 | -85.7891 | 18.9986 | 18.9986 | 103.0103 | 283.0103 | 85.4299 | 4.1266 | 4.1266 | 79.022 | 83.1485 | -0.56294 | 0% | 37.5998 | 0 | 0 | 164.1419 | 164.1419 | 0% | 11.33% | 11.33% | 80% | 9.066% | 3.4087 | 4.8453 | 4.8453 | 16.5162 | 7.5381 | 10.06% | 10.06%
6 | 156 | 5 | 3739 | 19 | 19.9 | 23.14 | 76.11 | 99.25 | 76.11 | 38.06 | 156 | 3739 | 1140 | 153.863 | 22.5197 | 8.8726 | 1114.284 | 18.7193 | -100.7891 | 9.246 | 9.246 | 113.1668 | 293.1668 | 99.2623 | 0 | 0 | 64.9639 | 64.9639 | -0.96587 | 0% | 29.3767 | 0 | 0 | 158.2316 | 158.2316 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3740 | 20 | 18.9 | 3.81 | 38.53 | 42.34 | 38.53 | 19.27 | 156 | 3740 | 1200 | 153.863 | 22.5197 | 8.8726 | 1174.284 | 19.7193 | -115.7891 | 0.22186 | 0.22186 | 123.7211 | 303.7211 | 112.9426 | 0 | 0 | 32.8874 | 32.8874 | -2.7593 | 0% | 14.8717 | 0 | 0 | 146.2243 | 146.2243 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3741 | 21 | 17.9 | 0 | 7.97 | 7.97 | 7.97 | 3.99 | 156 | 3741 | 1260 | 153.863 | 22.5197 | 8.8726 | 1234.284 | 20.7193 | -130.7891 | -7.7108 | 0 | 124.0051 | 304.0051 | 113.2947 | 0 | 0 | 6.8028 | 6.8028 | -16.7489 | 0% | 3.0762 | 0 | 0 | -4.8339 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3742 | 22 | 16.4 | 0 | 0 | 0 | 0 | 0 | 156 | 3742 | 1320 | 153.863 | 22.5197 | 8.8726 | 1294.284 | 21.7193 | -145.7891 | -14.126 | 0 | 124.0051 | 304.0051 | 113.2947 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1346 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3743 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 156 | 3743 | 1380 | 153.863 | 22.5197 | 8.8726 | 1354.284 | 22.7193 | -160.7891 | -18.5593 | 0 | 124.0051 | 304.0051 | 113.2947 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5869 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
6 | 156 | 5 | 3744 | 24 | 13.5 | 0 | 0 | 0 | 0 | 0 | 156 | 3744 | 1440 | 153.863 | 22.5197 | 8.8726 | 1414.284 | 23.7193 | -175.7891 | -20.5978 | 0 | 124.0051 | 304.0051 | 113.2947 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1916 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3745 | 1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 157 | 3745 | 60 | 154.8493 | 22.6197 | 8.4821 | 34.284 | 0.71277 | 169.3085 | -19.9321 | 0 | 124.1679 | 55.8321 | 113.3986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6028 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3746 | 2 | 11.5 | 0 | 0 | 0 | 0 | 0 | 157 | 3746 | 120 | 154.8493 | 22.6197 | 8.4821 | 94.284 | 1.7128 | 154.3085 | -16.8212 | 0 | 124.1679 | 55.8321 | 113.3986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.876 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3747 | 3 | 10.8 | 0 | 0 | 0 | 0 | 0 | 157 | 3747 | 180 | 154.8493 | 22.6197 | 8.4821 | 154.284 | 2.7128 | 139.3085 | -11.4811 | 0 | 124.1679 | 55.8321 | 113.3986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5397 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3748 | 4 | 11.7 | 0 | 0 | 0 | 0 | 0 | 157 | 3748 | 240 | 154.8493 | 22.6197 | 8.4821 | 214.284 | 3.7128 | 124.3085 | -4.361 | 0 | 124.1679 | 55.8321 | 113.3986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1681 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3749 | 5 | 12.1 | 0 | 0 | 0 | 0 | 0 | 157 | 3749 | 300 | 154.8493 | 22.6197 | 8.4821 | 274.284 | 4.7128 | 109.3085 | 4.0856 | 4.0856 | 119.1466 | 60.8534 | 107.046 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.0699 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3750 | 6 | 12.2 | 4.64 | 12.69 | 17.33 | 12.69 | 6.35 | 157 | 3750 | 360 | 154.8493 | 22.6197 | 8.4821 | 334.284 | 5.7128 | 94.3085 | 13.4607 | 13.4607 | 108.832 | 71.168 | 93.2895 | -1.1438 | 0 | 10.8316 | 10.8316 | -11.4133 | 0% | 4.898 | 0 | 0 | 6.271 | 6.271 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3751 | 7 | 12.8 | 31.58 | 33.81 | 65.39 | 33.81 | 16.91 | 157 | 3751 | 420 | 154.8493 | 22.6197 | 8.4821 | 394.284 | 6.7128 | 79.3085 | 23.4249 | 23.4249 | 98.6878 | 81.3122 | 79.4495 | 14.5451 | 14.5451 | 28.8586 | 43.4037 | -2.2131 | 0% | 19.6272 | 0 | 0 | 168.3454 | 168.3454 | 0% | 11.65% | 11.65% | 80% | 9.321% | 1.8295 | 6.5443 | 6 | 10.977 | 4.0458 | 6.521% | 6.521%
6 | 157 | 6 | 3752 | 8 | 14.6 | 76.94 | 53.33 | 130.27 | 53.33 | 26.67 | 157 | 3752 | 480 | 154.8493 | 22.6197 | 8.4821 | 454.284 | 7.7128 | 64.3085 | 33.664 | 33.664 | 88.057 | 91.943 | 65.6746 | 57.1744 | 57.1744 | 45.52 | 102.6944 | -0.4311 | 0% | 46.4384 | 0 | 0 | 180.2238 | 180.2238 | 0% | 11.56% | 11.56% | 80% | 9.247% | 4.2943 | 6.1099 | 6 | 25.7657 | 9.4964 | 14.3% | 14.3%
6 | 157 | 6 | 3753 | 9 | 16.2 | 131.86 | 78.25 | 210.11 | 78.25 | 39.13 | 157 | 3753 | 540 | 154.8493 | 22.6197 | 8.4821 | 514.284 | 8.7128 | 49.3085 | 43.8221 | 43.8221 | 75.9491 | 104.0509 | 52.1586 | 116.8265 | 116.8265 | 66.7906 | 183.6171 | 0.13294 | 13.29% | 83.0316 | 11.0382 | 7.7268 | 144.8062 | 144.8062 | 5.336% | 11.48% | 11.48% | 80% | 9.185% | 7.6262 | 5.7429 | 5.7429 | 43.7963 | 16.8646 | 30.24% | 30.24%
6 | 157 | 6 | 3754 | 10 | 16.9 | 162.22 | 131.58 | 293.8 | 131.58 | 65.79 | 157 | 3754 | 600 | 154.8493 | 22.6197 | 8.4821 | 574.284 | 9.7128 | 34.3085 | 53.3631 | 53.3631 | 60.6787 | 119.3213 | 39.2817 | 156.4805 | 156.4805 | 112.3106 | 268.791 | 0.35144 | 35.14% | 121.5473 | 42.7162 | 29.9013 | 147.5591 | 147.5591 | 20.26% | 11.44% | 11.44% | 80% | 9.154% | 11.1265 | 5.588 | 5.588 | 62.1744 | 24.6053 | 42.14% | 42.14%
6 | 157 | 6 | 3755 | 11 | 17.5 | 236.47 | 227.22 | 463.69 | 227.22 | 113.61 | 157 | 3755 | 660 | 154.8493 | 22.6197 | 8.4821 | 634.284 | 10.7128 | 19.3085 | 61.266 | 61.266 | 39.4118 | 140.5882 | 28.0338 | 238.0368 | 238.0368 | 193.9444 | 431.9812 | 0.52551 | 52.55% | 195.3419 | 102.6544 | 71.8581 | 150.2871 | 150.2871 | 47.81% | 11.4% | 11.4% | 85% | 9.692% | 18.933 | 5.4579 | 5.4579 | 103.3337 | 41.8685 | 68.76% | 68.76%
6 | 157 | 6 | 3756 | 12 | 18.4 | 321.75 | 255.08 | 576.83 | 255.08 | 127.54 | 157 | 3756 | 720 | 154.8493 | 22.6197 | 8.4821 | 694.284 | 11.7128 | 4.3085 | 65.5928 | 65.5928 | 9.6612 | 170.3388 | 21.2576 | 329.2858 | 329.2858 | 217.7244 | 547.0102 | 0.58774 | 58.77% | 247.358 | 145.3823 | 101.7676 | 147.7958 | 147.7958 | 68.86% | 11.37% | 11.37% | 90% | 10.24% | 25.3216 | 5.2675 | 5.2675 | 133.3812 | 55.9965 | 90.25% | 90.25%
6 | 157 | 6 | 3757 | 13 | 18.7 | 307.31 | 251.75 | 559.06 | 251.75 | 125.88 | 157 | 3757 | 780 | 154.8493 | 22.6197 | 8.4821 | 754.284 | 12.7128 | -10.6915 | 64.3485 | 64.3485 | 23.303 | 203.303 | 23.2849 | 313.1417 | 313.1417 | 214.8821 | 528.0238 | 0.58123 | 58.12% | 238.7724 | 138.7806 | 97.1464 | 145.4041 | 145.4041 | 66.81% | 11.37% | 11.37% | 90% | 10.23% | 24.4367 | 5.2053 | 5.2053 | 127.1997 | 54.0395 | 87.48% | 87.48%
6 | 157 | 6 | 3758 | 14 | 19.3 | 158.33 | 247.31 | 405.64 | 247.31 | 123.66 | 157 | 3758 | 840 | 154.8493 | 22.6197 | 8.4821 | 814.284 | 13.7128 | -25.6915 | 58.2035 | 58.2035 | 49.4192 | 229.4192 | 32.5037 | 157.1065 | 157.1065 | 211.0923 | 368.1988 | 0.48813 | 48.81% | 166.4995 | 81.2741 | 56.8918 | 139.1258 | 139.1258 | 40.89% | 11.37% | 11.37% | 85% | 9.663% | 16.0894 | 5.0828 | 5.0828 | 81.7785 | 35.5803 | 58.78% | 58.78%
6 | 157 | 6 | 3759 | 15 | 19 | 232.86 | 259.72 | 492.58 | 259.72 | 129.86 | 157 | 3759 | 900 | 154.8493 | 22.6197 | 8.4821 | 874.284 | 14.7128 | -40.6915 | 49.4275 | 49.4275 | 67.7161 | 247.7161 | 44.6427 | 218.1201 | 218.1201 | 221.6849 | 439.805 | 0.53805 | 53.81% | 198.8798 | 107.0077 | 74.9054 | 140.1552 | 140.1552 | 53.44% | 11.37% | 11.37% | 85% | 9.666% | 19.2238 | 5.1437 | 5.1437 | 98.8815 | 42.5117 | 70.55% | 70.55%
6 | 157 | 6 | 3760 | 16 | 19.6 | 103.81 | 165.75 | 269.56 | 165.75 | 82.88 | 157 | 3760 | 960 | 154.8493 | 22.6197 | 8.4821 | 934.284 | 15.7128 | -55.6915 | 39.5372 | 39.5372 | 81.3682 | 261.3682 | 57.8611 | 86.7516 | 86.7516 | 141.4765 | 228.2281 | 0.29732 | 29.73% | 103.2048 | 30.6847 | 21.4793 | 129.4243 | 129.4243 | 16.6% | 11.36% | 11.36% | 80% | 9.092% | 9.383 | 5.0224 | 5.0224 | 47.1257 | 20.7497 | 36.41% | 36.41%
6 | 157 | 6 | 3761 | 17 | 18.6 | 88.33 | 188.89 | 277.22 | 188.89 | 94.45 | 157 | 3761 | 1020 | 154.8493 | 22.6197 | 8.4821 | 994.284 | 16.7128 | -70.6915 | 29.294 | 29.294 | 92.6931 | 272.6931 | 71.518 | 57.2279 | 57.2279 | 161.2277 | 218.4556 | 0.26452 | 26.45% | 98.7856 | 26.1309 | 18.2917 | 126.1907 | 126.1907 | 14.5% | 11.4% | 11.4% | 80% | 9.117% | 9.0067 | 5.2259 | 5.2259 | 47.0685 | 19.9175 | 37.3% | 37.3%
6 | 157 | 6 | 3762 | 18 | 17.8 | 71.58 | 170.83 | 242.41 | 170.83 | 85.42 | 157 | 3762 | 1080 | 154.8493 | 22.6197 | 8.4821 | 1054.284 | 17.7128 | -85.6915 | 19.1329 | 19.1329 | 103.0208 | 283.0208 | 85.3397 | 17.7437 | 17.7437 | 145.8125 | 163.5562 | 0.072557 | 7.256% | 73.9601 | 5.3663 | 3.7564 | 120.4605 | 120.4605 | 3.118% | 11.43% | 11.43% | 80% | 9.143% | 6.7623 | 5.3938 | 5.3938 | 36.4745 | 14.9543 | 30.28% | 30.28%
6 | 157 | 6 | 3763 | 19 | 16.7 | 53.42 | 116.47 | 169.89 | 116.47 | 58.24 | 157 | 3763 | 1140 | 154.8493 | 22.6197 | 8.4821 | 1114.284 | 18.7128 | -100.6915 | 9.3806 | 9.3806 | 113.1691 | 293.1691 | 99.1625 | 0 | 0 | 99.4134 | 99.4134 | -0.42414 | 0% | 44.9547 | 0 | 0 | 112.1515 | 112.1515 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3764 | 20 | 15.7 | 23.97 | 54.08 | 78.05 | 54.08 | 27.04 | 157 | 3764 | 1200 | 154.8493 | 22.6197 | 8.4821 | 1174.284 | 19.7128 | -115.6915 | 0.35617 | 0.35617 | 123.7118 | 303.7118 | 112.8334 | 0 | 0 | 46.1602 | 46.1602 | -1.8898 | 0% | 20.8736 | 0 | 0 | 142.9834 | 142.9834 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3765 | 21 | 15 | 0 | 7.69 | 7.69 | 7.69 | 3.85 | 157 | 3765 | 1260 | 154.8493 | 22.6197 | 8.4821 | 1234.284 | 20.7128 | -130.6915 | -7.5784 | 0 | 124.1679 | 304.1679 | 113.3986 | 0 | 0 | 6.5638 | 6.5638 | -18.3815 | 0% | 2.9682 | 0 | 0 | -9.6094 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3766 | 22 | 14.9 | 0 | 0 | 0 | 0 | 0 | 157 | 3766 | 1320 | 154.8493 | 22.6197 | 8.4821 | 1294.284 | 21.7128 | -145.6915 | -13.9984 | 0 | 124.1679 | 304.1679 | 113.3986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.307 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3767 | 23 | 14.2 | 0 | 0 | 0 | 0 | 0 | 157 | 3767 | 1380 | 154.8493 | 22.6197 | 8.4821 | 1354.284 | 22.7128 | -160.6915 | -18.4407 | 0 | 124.1679 | 304.1679 | 113.3986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9707 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
6 | 157 | 6 | 3768 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 157 | 3768 | 1440 | 154.8493 | 22.6197 | 8.4821 | 1414.284 | 23.7128 | -175.6915 | -20.493 | 0 | 124.1679 | 304.1679 | 113.3986 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8723 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3769 | 1 | 13.5 | 0 | 0 | 0 | 0 | 0 | 158 | 3769 | 60 | 155.8356 | 22.713 | 8.0852 | 34.284 | 0.70615 | 169.4077 | -19.8519 | 0 | 124.32 | 55.68 | 113.4955 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.618 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3770 | 2 | 13.3 | 0 | 0 | 0 | 0 | 0 | 158 | 3770 | 120 | 155.8356 | 22.713 | 8.0852 | 94.284 | 1.7062 | 154.4077 | -16.7608 | 0 | 124.32 | 55.68 | 113.4955 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2825 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3771 | 3 | 13.3 | 0 | 0 | 0 | 0 | 0 | 158 | 3771 | 180 | 155.8356 | 22.713 | 8.0852 | 154.284 | 2.7062 | 139.4077 | -11.4397 | 0 | 124.32 | 55.68 | 113.4955 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6422 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3772 | 4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 158 | 3772 | 240 | 155.8356 | 22.713 | 8.0852 | 214.284 | 3.7062 | 124.4077 | -4.3361 | 0 | 124.32 | 55.68 | 113.4955 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7946 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3773 | 5 | 13.1 | 0 | 0 | 0 | 0 | 0 | 158 | 3773 | 300 | 155.8356 | 22.713 | 8.0852 | 274.284 | 4.7062 | 109.4077 | 4.0974 | 4.0974 | 119.2771 | 60.7229 | 107.1211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.2279 | 6.2279 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3774 | 6 | 13.1 | 7.58 | 21.58 | 29.16 | 21.58 | 10.79 | 158 | 3774 | 360 | 155.8356 | 22.713 | 8.0852 | 334.284 | 5.7062 | 94.4077 | 13.4628 | 13.4628 | 108.9664 | 71.0336 | 93.3755 | -1.917 | 0 | 18.4197 | 18.4197 | -6.268 | 0% | 8.3294 | 0 | 0 | 21.1225 | 21.1225 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3775 | 7 | 13 | 73.97 | 85.36 | 159.33 | 85.36 | 42.68 | 158 | 3775 | 420 | 155.8356 | 22.713 | 8.0852 | 394.284 | 6.7062 | 79.4077 | 23.4211 | 23.4211 | 98.8302 | 81.1698 | 79.545 | 33.7692 | 33.7692 | 72.8593 | 106.6285 | -0.41981 | 0% | 48.2174 | 0 | 0 | 153.1235 | 153.1235 | 0% | 11.62% | 11.62% | 80% | 9.295% | 4.4819 | 6.4949 | 6 | 26.8913 | 9.9113 | 17.56% | 17.56%
6 | 158 | 7 | 3776 | 8 | 13 | 161.67 | 127.14 | 288.81 | 127.14 | 63.57 | 158 | 3776 | 480 | 155.8356 | 22.713 | 8.0852 | 454.284 | 7.7062 | 64.4077 | 33.6587 | 33.6587 | 88.2139 | 91.7861 | 65.7792 | 119.6689 | 119.6689 | 108.5208 | 228.1896 | 0.23214 | 23.21% | 103.1874 | 23.9538 | 16.7677 | 168.7002 | 168.7002 | 9.939% | 11.57% | 11.57% | 80% | 9.258% | 9.5528 | 6.4949 | 6 | 57.3168 | 21.1252 | 33.98% | 33.98%
6 | 158 | 7 | 3777 | 9 | 13 | 266.67 | 127.58 | 394.25 | 127.58 | 63.79 | 158 | 3777 | 540 | 155.8356 | 22.713 | 8.0852 | 514.284 | 8.7062 | 49.4077 | 43.8209 | 43.8209 | 76.1302 | 103.8698 | 52.2727 | 235.6658 | 235.6658 | 108.8963 | 344.5621 | 0.42528 | 42.53% | 155.811 | 66.2632 | 46.3842 | 173.9885 | 173.9885 | 26.66% | 11.53% | 11.53% | 85% | 9.798% | 15.2667 | 6.4949 | 6 | 91.6004 | 33.761 | 52.65% | 52.65%
6 | 158 | 7 | 3778 | 10 | 14 | 354.92 | 135.83 | 490.75 | 135.83 | 67.92 | 158 | 3778 | 600 | 155.8356 | 22.713 | 8.0852 | 574.284 | 9.7062 | 34.4077 | 53.3749 | 53.3749 | 60.8969 | 119.1031 | 39.4057 | 341.7033 | 341.7033 | 115.9382 | 457.6414 | 0.52386 | 52.39% | 206.9455 | 108.41 | 75.887 | 175.8556 | 175.8556 | 43.15% | 11.46% | 11.46% | 85% | 9.745% | 20.1673 | 6.2522 | 6 | 121.0039 | 44.5982 | 68.81% | 68.81%
6 | 158 | 7 | 3779 | 11 | 14.1 | 402.14 | 156.67 | 558.81 | 156.67 | 78.34 | 158 | 3779 | 660 | 155.8356 | 22.713 | 8.0852 | 634.284 | 10.7062 | 19.4077 | 61.305 | 61.305 | 39.6715 | 140.3285 | 28.1645 | 404.1611 | 404.1611 | 133.7262 | 537.8873 | 0.56608 | 56.61% | 243.2326 | 137.688 | 96.3816 | 169.0129 | 169.0129 | 57.03% | 11.44% | 11.44% | 90% | 10.29% | 25.0368 | 6.2283 | 6 | 150.2207 | 55.3666 | 88.88% | 88.88%
6 | 158 | 7 | 3780 | 12 | 14.1 | 498.47 | 264.72 | 763.19 | 264.72 | 132.36 | 158 | 3780 | 720 | 155.8356 | 22.713 | 8.0852 | 694.284 | 11.7062 | 4.4077 | 65.6738 | 65.6738 | 9.9099 | 170.0901 | 21.368 | 509.4353 | 509.4353 | 225.9527 | 735.3879 | 0.62997 | 63% | 332.5424 | 209.4931 | 146.6452 | 163.6988 | 163.6988 | 89.58% | 11.37% | 11.37% | 90% | 10.24% | 34.0379 | 6.2283 | 6 | 204.2277 | 75.2719 | 124.8% | 124.8%
6 | 158 | 7 | 3781 | 13 | 14.3 | 447.92 | 269.86 | 717.78 | 269.86 | 134.93 | 158 | 3781 | 780 | 155.8356 | 22.713 | 8.0852 | 754.284 | 12.7062 | -10.5923 | 64.4646 | 64.4646 | 23.1636 | 203.1636 | 23.3247 | 455.8411 | 455.8411 | 230.3399 | 686.181 | 0.61816 | 61.82% | 310.2911 | 191.8091 | 134.2664 | 159.2483 | 159.2483 | 84.31% | 11.39% | 11.39% | 90% | 10.25% | 31.8015 | 6.1808 | 6 | 190.8088 | 70.3261 | 119.8% | 119.8%
6 | 158 | 7 | 3782 | 14 | 14.9 | 539.72 | 273.33 | 813.05 | 273.33 | 136.67 | 158 | 3782 | 840 | 155.8356 | 22.713 | 8.0852 | 814.284 | 13.7062 | -25.5923 | 58.3321 | 58.3321 | 49.3753 | 229.3753 | 32.4853 | 534.9154 | 534.9154 | 233.3017 | 768.2171 | 0.63978 | 63.98% | 347.3878 | 222.2516 | 155.5761 | 162.6212 | 162.6212 | 95.67% | 11.36% | 11.36% | 90% | 10.22% | 35.5198 | 6.0398 | 6 | 213.1187 | 78.5488 | 131.1% | 131.1%
6 | 158 | 7 | 3783 | 15 | 15.1 | 611.94 | 240.83 | 852.77 | 240.83 | 120.42 | 158 | 3783 | 900 | 155.8356 | 22.713 | 8.0852 | 874.284 | 14.7062 | -40.5923 | 49.5582 | 49.5582 | 67.7123 | 247.7123 | 44.5928 | 572.5799 | 572.5799 | 205.5613 | 778.1412 | 0.64246 | 64.25% | 351.8754 | 226.0648 | 158.2454 | 162.0297 | 162.0297 | 97.66% | 11.36% | 11.36% | 90% | 10.22% | 35.9691 | 5.9933 | 5.9933 | 215.5739 | 79.5424 | 133% | 133%
6 | 158 | 7 | 3784 | 16 | 15 | 500 | 195.28 | 695.28 | 195.28 | 97.64 | 158 | 3784 | 960 | 155.8356 | 22.713 | 8.0852 | 934.284 | 15.7062 | -55.5923 | 39.6677 | 39.6677 | 81.3763 | 261.3763 | 57.7926 | 417.4812 | 417.4812 | 166.6819 | 584.1631 | 0.58843 | 58.84% | 264.1586 | 155.4379 | 108.8066 | 153.2631 | 153.2631 | 70.99% | 11.41% | 11.41% | 90% | 10.27% | 27.1297 | 6.0165 | 6 | 162.778 | 59.9948 | 106.2% | 106.2%
6 | 158 | 7 | 3785 | 17 | 14.9 | 345.08 | 191.47 | 536.55 | 191.47 | 95.74 | 158 | 3785 | 1020 | 155.8356 | 22.713 | 8.0852 | 994.284 | 16.7062 | -70.5923 | 29.4245 | 29.4245 | 92.702 | 272.702 | 71.4367 | 223.6148 | 223.6148 | 163.4299 | 387.0447 | 0.47805 | 47.81% | 175.0216 | 83.6692 | 58.5685 | 143.2968 | 143.2968 | 40.87% | 11.47% | 11.47% | 85% | 9.748% | 17.0605 | 6.0398 | 6 | 102.363 | 37.7278 | 71.43% | 71.43%
6 | 158 | 7 | 3786 | 18 | 14.5 | 169.44 | 168.42 | 337.86 | 168.42 | 84.21 | 158 | 3786 | 1080 | 155.8356 | 22.713 | 8.0852 | 1054.284 | 17.7062 | -85.5923 | 19.2635 | 19.2635 | 103.0253 | 283.0253 | 85.2482 | 42.5451 | 42.5451 | 143.7555 | 186.3006 | 0.12195 | 12.2% | 84.2451 | 10.274 | 7.1918 | 128.4255 | 128.4255 | 5.6% | 11.54% | 11.54% | 80% | 9.23% | 7.7759 | 6.1335 | 6 | 46.6555 | 17.1958 | 36.33% | 36.33%
6 | 158 | 7 | 3787 | 19 | 14.6 | 96.19 | 98.14 | 194.33 | 98.14 | 49.07 | 158 | 3787 | 1140 | 155.8356 | 22.713 | 8.0852 | 1114.284 | 18.7062 | -100.5923 | 9.5113 | 9.5113 | 113.1657 | 293.1657 | 99.062 | 0 | 0 | 83.7677 | 83.7677 | -0.71017 | 0% | 37.8798 | 0 | 0 | 116.0332 | 116.0332 | 0% | 11.56% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3788 | 20 | 14.8 | 27.42 | 47.58 | 75 | 47.58 | 23.79 | 158 | 3788 | 1200 | 155.8356 | 22.713 | 8.0852 | 1174.284 | 19.7062 | -115.5923 | 0.48609 | 0.48609 | 123.6974 | 303.6974 | 112.7241 | 0 | 0 | 40.6121 | 40.6121 | -2.308 | 0% | 18.3648 | 0 | 0 | 143.1863 | 143.1863 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3789 | 21 | 14.3 | 0 | 8.61 | 8.61 | 8.61 | 4.31 | 158 | 3789 | 1260 | 155.8356 | 22.713 | 8.0852 | 1234.284 | 20.7062 | -130.5923 | -7.451 | 0 | 124.32 | 304.32 | 113.4955 | 0 | 0 | 7.3491 | 7.3491 | -16.5479 | 0% | 3.3233 | 0 | 0 | -9.9244 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3790 | 22 | 14.1 | 0 | 0 | 0 | 0 | 0 | 158 | 3790 | 1320 | 155.8356 | 22.713 | 8.0852 | 1294.284 | 21.7062 | -145.5923 | -13.8764 | 0 | 124.32 | 304.32 | 113.4955 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6245 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3791 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 158 | 3791 | 1380 | 155.8356 | 22.713 | 8.0852 | 1354.284 | 22.7062 | -160.5923 | -18.3282 | 0 | 124.32 | 304.32 | 113.4955 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1366 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
6 | 158 | 7 | 3792 | 24 | 13.5 | 0 | 0 | 0 | 0 | 0 | 158 | 3792 | 1440 | 155.8356 | 22.713 | 8.0852 | 1414.284 | 23.7062 | -175.5923 | -20.3948 | 0 | 124.32 | 304.32 | 113.4955 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2583 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3793 | 1 | 13.3 | 0 | 0 | 0 | 0 | 0 | 159 | 3793 | 60 | 156.8219 | 22.7996 | 7.6823 | 34.284 | 0.69944 | 169.5084 | -19.7785 | 0 | 124.4613 | 55.5387 | 113.5854 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7981 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3794 | 2 | 13.2 | 0 | 0 | 0 | 0 | 0 | 159 | 3794 | 120 | 156.8219 | 22.7996 | 7.6823 | 94.284 | 1.6994 | 154.5084 | -16.7071 | 0 | 124.4613 | 55.5387 | 113.5854 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5015 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3795 | 3 | 13.3 | 0 | 0 | 0 | 0 | 0 | 159 | 3795 | 180 | 156.8219 | 22.7996 | 7.6823 | 154.284 | 2.6994 | 139.5084 | -11.4048 | 0 | 124.4613 | 55.5387 | 113.5854 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9001 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3796 | 4 | 13.4 | 0 | 0 | 0 | 0 | 0 | 159 | 3796 | 240 | 156.8219 | 22.7996 | 7.6823 | 214.284 | 3.6994 | 124.5084 | -4.3173 | 0 | 124.4613 | 55.5387 | 113.5854 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7477 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3797 | 5 | 13.8 | 0 | 0 | 0 | 0 | 0 | 159 | 3797 | 300 | 156.8219 | 22.7996 | 7.6823 | 274.284 | 4.6994 | 109.5084 | 4.1032 | 4.1032 | 119.4043 | 60.5957 | 107.1984 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.44138 | 0.44138 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3798 | 6 | 14 | 4.44 | 24.36 | 28.8 | 24.36 | 12.18 | 159 | 3798 | 360 | 156.8219 | 22.7996 | 7.6823 | 334.284 | 5.6994 | 94.5084 | 13.4593 | 13.4593 | 109.0969 | 70.9031 | 93.4631 | -1.1523 | 0 | 20.7926 | 20.7926 | -5.3619 | 0% | 9.4024 | 0 | 0 | 12.7131 | 12.7131 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3799 | 7 | 14 | 36.31 | 85.19 | 121.5 | 85.19 | 42.6 | 159 | 3799 | 420 | 156.8219 | 22.7996 | 7.6823 | 394.284 | 6.6994 | 79.5084 | 23.4118 | 23.4118 | 98.9682 | 81.0318 | 79.6415 | 16.4313 | 16.4313 | 72.7142 | 89.1455 | -0.63415 | 0% | 40.3116 | 0 | 0 | 180.0543 | 180.0543 | 0% | 11.59% | 11.59% | 80% | 9.269% | 3.7366 | 6.2522 | 6 | 22.4195 | 8.2631 | 12.45% | 12.45%
6 | 159 | 8 | 3800 | 8 | 14 | 130.75 | 136.19 | 266.94 | 136.19 | 68.1 | 159 | 3800 | 480 | 156.8219 | 22.7996 | 7.6823 | 454.284 | 7.6994 | 64.5084 | 33.6478 | 33.6478 | 88.3659 | 91.6341 | 65.8841 | 96.4152 | 96.4152 | 116.2454 | 212.6607 | 0.20114 | 20.11% | 96.1651 | 19.3426 | 13.5398 | 153.1538 | 153.1538 | 8.841% | 11.55% | 11.55% | 80% | 9.237% | 8.8824 | 6.2522 | 6 | 53.2947 | 19.6427 | 34.8% | 34.8%
6 | 159 | 8 | 3801 | 9 | 14.7 | 191.19 | 163.61 | 354.8 | 163.61 | 81.81 | 159 | 3801 | 540 | 156.8219 | 22.7996 | 7.6823 | 514.284 | 8.6994 | 49.5084 | 43.8139 | 43.8139 | 76.306 | 103.694 | 52.3862 | 168.55 | 168.55 | 139.6499 | 308.1999 | 0.39319 | 39.32% | 139.368 | 54.7984 | 38.3588 | 158.7633 | 158.7633 | 24.16% | 11.5% | 11.5% | 85% | 9.771% | 13.6177 | 6.0865 | 6 | 81.7063 | 30.1144 | 51.46% | 51.46%
6 | 159 | 8 | 3802 | 10 | 16 | 288.06 | 204.81 | 492.87 | 204.81 | 102.41 | 159 | 3802 | 600 | 156.8219 | 22.7996 | 7.6823 | 574.284 | 9.6994 | 34.5084 | 53.3804 | 53.3804 | 61.1096 | 118.8904 | 39.5279 | 276.8268 | 276.8268 | 174.8163 | 451.6431 | 0.53018 | 53.02% | 204.233 | 108.2803 | 75.7962 | 164.5025 | 164.5025 | 46.08% | 11.43% | 11.43% | 85% | 9.714% | 19.8399 | 5.7878 | 5.7878 | 114.8293 | 43.8742 | 69.8% | 69.8%
6 | 159 | 8 | 3803 | 11 | 18.6 | 467.03 | 193.14 | 660.17 | 193.14 | 96.57 | 159 | 3803 | 660 | 156.8219 | 22.7996 | 7.6823 | 634.284 | 10.6994 | 19.5084 | 61.337 | 61.337 | 39.9276 | 140.0724 | 28.2914 | 468.6762 | 468.6762 | 164.8553 | 633.5315 | 0.61798 | 61.8% | 286.483 | 177.0396 | 123.9277 | 168.0748 | 168.0748 | 73.73% | 11.36% | 11.36% | 90% | 10.23% | 29.3024 | 5.2259 | 5.2259 | 153.1328 | 64.7997 | 91.11% | 91.11%
6 | 159 | 8 | 3804 | 12 | 19.8 | 572.42 | 204.25 | 776.67 | 204.25 | 102.13 | 159 | 3804 | 720 | 156.8219 | 22.7996 | 7.6823 | 694.284 | 11.6994 | 4.5084 | 65.7476 | 65.7476 | 10.1611 | 169.8389 | 21.4723 | 584.2542 | 584.2542 | 174.3383 | 758.5925 | 0.65214 | 65.21% | 343.0355 | 223.708 | 156.5956 | 163.516 | 163.516 | 95.77% | 11.35% | 11.35% | 90% | 10.22% | 35.0487 | 4.9826 | 4.9826 | 174.6328 | 77.507 | 106.8% | 106.8%
6 | 159 | 8 | 3805 | 13 | 21.1 | 556.58 | 222.14 | 778.72 | 222.14 | 111.07 | 159 | 3805 | 780 | 156.8219 | 22.7996 | 7.6823 | 754.284 | 12.6994 | -10.4916 | 64.5744 | 64.5744 | 23.0156 | 203.0156 | 23.3587 | 565.7606 | 565.7606 | 189.6084 | 755.3689 | 0.65527 | 65.53% | 341.5778 | 223.8264 | 156.6785 | 163.9085 | 163.9085 | 95.59% | 11.35% | 11.35% | 90% | 10.21% | 34.89 | 4.7303 | 4.7303 | 165.0408 | 77.1562 | 100.7% | 100.7%
6 | 159 | 8 | 3806 | 14 | 22 | 377.78 | 220.19 | 597.97 | 220.19 | 110.1 | 159 | 3806 | 840 | 156.8219 | 22.7996 | 7.6823 | 814.284 | 13.6994 | -25.4916 | 58.456 | 58.456 | 49.322 | 229.322 | 32.4624 | 374.0144 | 374.0144 | 187.9439 | 561.9583 | 0.60758 | 60.76% | 254.1175 | 154.3956 | 108.0769 | 157.8668 | 157.8668 | 68.46% | 11.33% | 11.33% | 90% | 10.19% | 25.9028 | 4.5626 | 4.5626 | 118.1841 | 57.2817 | 74.86% | 74.86%
6 | 159 | 8 | 3807 | 15 | 22.2 | 431.67 | 165.83 | 597.5 | 165.83 | 82.92 | 159 | 3807 | 900 | 156.8219 | 22.7996 | 7.6823 | 874.284 | 14.6994 | -40.4916 | 49.685 | 49.685 | 67.6999 | 247.6999 | 44.5396 | 403.5153 | 403.5153 | 141.5448 | 545.06 | 0.60228 | 60.23% | 246.4761 | 148.4485 | 103.9139 | 156.1874 | 156.1874 | 66.53% | 11.32% | 11.32% | 90% | 10.19% | 25.1135 | 4.5261 | 4.5261 | 113.6664 | 55.5364 | 72.78% | 72.78%
6 | 159 | 8 | 3808 | 16 | 22.1 | 525.19 | 179.25 | 704.44 | 179.25 | 89.63 | 159 | 3808 | 960 | 156.8219 | 22.7996 | 7.6823 | 934.284 | 15.6994 | -55.4916 | 39.7947 | 39.7947 | 81.377 | 261.377 | 57.7216 | 438.2067 | 438.2067 | 152.9994 | 591.2062 | 0.61766 | 61.77% | 267.3434 | 165.1275 | 115.5893 | 159.8191 | 159.8191 | 72.33% | 11.33% | 11.33% | 90% | 10.2% | 27.2559 | 4.5443 | 4.5443 | 123.8595 | 60.274 | 77.5% | 77.5%
6 | 159 | 8 | 3809 | 17 | 22.1 | 401.11 | 144.81 | 545.92 | 144.81 | 72.41 | 159 | 3809 | 1020 | 156.8219 | 22.7996 | 7.6823 | 994.284 | 16.6994 | -70.4916 | 29.5515 | 29.5515 | 92.7042 | 272.7042 | 71.3535 | 260.0256 | 260.0256 | 123.6031 | 383.6287 | 0.51683 | 51.68% | 173.4769 | 89.6588 | 62.7612 | 150.6923 | 150.6923 | 41.65% | 11.3% | 11.3% | 85% | 9.608% | 16.6682 | 4.5443 | 4.5443 | 75.7456 | 36.8603 | 50.27% | 50.27%
6 | 159 | 8 | 3810 | 18 | 21.8 | 284.72 | 111.47 | 396.19 | 111.47 | 55.74 | 159 | 3810 | 1080 | 156.8219 | 22.7996 | 7.6823 | 1054.284 | 17.6994 | -85.4916 | 19.3905 | 19.3905 | 103.0237 | 283.0237 | 85.1555 | 72.4244 | 72.4244 | 95.1456 | 167.57 | 0.14268 | 14.27% | 75.7751 | 10.8116 | 7.5681 | 139.2948 | 139.2948 | 5.433% | 11.29% | 11.29% | 80% | 9.032% | 6.8436 | 4.5994 | 4.5994 | 31.4765 | 15.1341 | 22.6% | 22.6%
6 | 159 | 8 | 3811 | 19 | 20.9 | 155 | 87.78 | 242.78 | 87.78 | 43.89 | 159 | 3811 | 1140 | 156.8219 | 22.7996 | 7.6823 | 1114.284 | 18.6994 | -100.4916 | 9.638 | 9.638 | 113.1569 | 293.1569 | 98.9608 | 0 | 0 | 74.9249 | 74.9249 | -0.70127 | 0% | 33.881 | 0 | 0 | 125.3132 | 125.3132 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.7684 | 4.7684 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3812 | 20 | 20 | 48.25 | 49.36 | 97.61 | 49.36 | 24.68 | 159 | 3812 | 1200 | 156.8219 | 22.7996 | 7.6823 | 1174.284 | 19.6994 | -115.4916 | 0.61157 | 0.61157 | 123.6778 | 303.6778 | 112.615 | 0 | 0 | 42.1314 | 42.1314 | -1.9198 | 0% | 19.0518 | 0 | 0 | 150.3276 | 150.3276 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3813 | 21 | 18.2 | 0 | 11.39 | 11.39 | 11.39 | 5.7 | 159 | 3813 | 1260 | 156.8219 | 22.7996 | 7.6823 | 1234.284 | 20.6994 | -130.4916 | -7.3285 | 0 | 124.4613 | 304.4613 | 113.5854 | 0 | 0 | 9.722 | 9.722 | -11.4097 | 0% | 4.3963 | 0 | 0 | -6.3134 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3093 | 5.3093 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3814 | 22 | 15.7 | 0 | 0 | 0 | 0 | 0 | 159 | 3814 | 1320 | 156.8219 | 22.7996 | 7.6823 | 1294.284 | 21.6994 | -145.4916 | -13.7599 | 0 | 124.4613 | 304.4613 | 113.5854 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4877 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3815 | 23 | 14.4 | 0 | 0 | 0 | 0 | 0 | 159 | 3815 | 1380 | 156.8219 | 22.7996 | 7.6823 | 1354.284 | 22.6994 | -160.4916 | -18.2218 | 0 | 124.4613 | 304.4613 | 113.5854 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0198 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
6 | 159 | 8 | 3816 | 24 | 13.5 | 0 | 0 | 0 | 0 | 0 | 159 | 3816 | 1440 | 156.8219 | 22.7996 | 7.6823 | 1414.284 | 23.6994 | -175.4916 | -20.3031 | 0 | 124.4613 | 304.4613 | 113.5854 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9424 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3817 | 1 | 12.9 | 0 | 0 | 0 | 0 | 0 | 160 | 3817 | 60 | 157.8082 | 22.8794 | 7.2737 | 34.284 | 0.69263 | 169.6106 | -19.7117 | 0 | 124.5917 | 55.4083 | 113.6684 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4912 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3818 | 2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 160 | 3818 | 120 | 157.8082 | 22.8794 | 7.2737 | 94.284 | 1.6926 | 154.6106 | -16.66 | 0 | 124.5917 | 55.4083 | 113.6684 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4363 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3819 | 3 | 11.8 | 0 | 0 | 0 | 0 | 0 | 160 | 3819 | 180 | 157.8082 | 22.8794 | 7.2737 | 154.284 | 2.6926 | 139.6106 | -11.3762 | 0 | 124.5917 | 55.4083 | 113.6684 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5339 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3820 | 4 | 11.7 | 0 | 0 | 0 | 0 | 0 | 160 | 3820 | 240 | 157.8082 | 22.8794 | 7.2737 | 214.284 | 3.6926 | 124.6106 | -4.3047 | 0 | 124.5917 | 55.4083 | 113.6684 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6863 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3821 | 5 | 11.2 | 0 | 0 | 0 | 0 | 0 | 160 | 3821 | 300 | 157.8082 | 22.8794 | 7.2737 | 274.284 | 4.6926 | 109.6106 | 4.1032 | 4.1032 | 119.5281 | 60.4719 | 107.278 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.5149 | 5.5149 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3822 | 6 | 11.1 | 10.08 | 19.64 | 29.72 | 19.64 | 9.82 | 160 | 3822 | 360 | 157.8082 | 22.8794 | 7.2737 | 334.284 | 5.6926 | 94.6106 | 13.4501 | 13.4501 | 109.2235 | 70.7765 | 93.5523 | -2.6851 | 0 | 16.7638 | 16.7638 | -7.2417 | 0% | 7.5806 | 0 | 0 | 22.8902 | 22.8902 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3823 | 7 | 12.9 | 88.81 | 54.92 | 143.73 | 54.92 | 27.46 | 160 | 3823 | 420 | 157.8082 | 22.8794 | 7.2737 | 394.284 | 6.6926 | 79.6106 | 23.397 | 23.397 | 99.1018 | 80.8982 | 79.739 | 39.8388 | 39.8388 | 46.8772 | 86.7159 | -0.70348 | 0% | 39.2129 | 0 | 0 | 204.7255 | 204.7255 | 0% | 11.63% | 11.63% | 80% | 9.304% | 3.6485 | 6.5196 | 6 | 21.8912 | 8.0684 | 10.69% | 10.69%
6 | 160 | 9 | 3824 | 8 | 15 | 236.94 | 75.56 | 312.5 | 75.56 | 37.78 | 160 | 3824 | 480 | 157.8082 | 22.8794 | 7.2737 | 454.284 | 7.6926 | 64.6106 | 33.6313 | 33.6313 | 88.5129 | 91.4871 | 65.9893 | 174.0785 | 174.0785 | 64.4945 | 238.573 | 0.27615 | 27.62% | 107.8827 | 29.7921 | 20.8545 | 185.2696 | 185.2696 | 11.26% | 11.51% | 11.51% | 80% | 9.205% | 9.9307 | 6.0165 | 6 | 59.5844 | 21.9609 | 32.16% | 32.16%
6 | 160 | 9 | 3825 | 9 | 17.1 | 392.58 | 88.25 | 480.83 | 88.25 | 44.13 | 160 | 3825 | 540 | 157.8082 | 22.8794 | 7.2737 | 514.284 | 8.6926 | 49.6106 | 43.8011 | 43.8011 | 76.4761 | 103.5239 | 52.499 | 345.2871 | 345.2871 | 75.3261 | 420.6132 | 0.51586 | 51.59% | 190.2013 | 98.1167 | 68.6817 | 196.3327 | 196.3327 | 34.98% | 11.41% | 11.41% | 85% | 9.701% | 18.4507 | 5.5443 | 5.5443 | 102.2967 | 40.8022 | 52.1% | 52.1%
6 | 160 | 9 | 3826 | 10 | 19.2 | 529.17 | 98.42 | 627.59 | 98.42 | 49.21 | 160 | 3826 | 600 | 157.8082 | 22.8794 | 7.2737 | 574.284 | 9.6926 | 34.6106 | 53.3797 | 53.3797 | 61.3166 | 118.6834 | 39.6481 | 507.6575 | 507.6575 | 84.0067 | 591.6642 | 0.60706 | 60.71% | 267.5506 | 162.4191 | 113.6934 | 200.4354 | 200.4354 | 56.72% | 11.36% | 11.36% | 90% | 10.23% | 27.3572 | 5.103 | 5.103 | 139.6037 | 60.498 | 69.65% | 69.65%
6 | 160 | 9 | 3827 | 11 | 20.6 | 658.42 | 103.33 | 761.75 | 103.33 | 51.67 | 160 | 3827 | 660 | 157.8082 | 22.8794 | 7.2737 | 634.284 | 10.6926 | 19.6106 | 61.3621 | 61.3621 | 40.1797 | 139.8203 | 28.4144 | 659.8176 | 659.8176 | 88.1977 | 748.0153 | 0.65235 | 65.23% | 338.2525 | 220.6578 | 154.4604 | 195.3461 | 195.3461 | 79.07% | 11.35% | 11.35% | 90% | 10.22% | 34.5534 | 4.8259 | 4.8259 | 166.7524 | 76.4117 | 85.36% | 85.36%
6 | 160 | 9 | 3828 | 12 | 21.7 | 740.14 | 109.31 | 849.45 | 109.31 | 54.66 | 160 | 3828 | 720 | 157.8082 | 22.8794 | 7.2737 | 694.284 | 11.6926 | 4.6106 | 65.8143 | 65.8143 | 10.4144 | 169.5856 | 21.5707 | 754.5353 | 754.5353 | 93.3019 | 847.8373 | 0.67304 | 67.3% | 383.392 | 258.0371 | 180.626 | 182.2282 | 182.2282 | 99.12% | 11.36% | 11.36% | 95% | 10.79% | 41.3628 | 4.6179 | 4.6179 | 191.0083 | 91.4702 | 104.8% | 104.8%
6 | 160 | 9 | 3829 | 13 | 22.2 | 776.81 | 118.33 | 895.14 | 118.33 | 59.17 | 160 | 3829 | 780 | 157.8082 | 22.8794 | 7.2737 | 754.284 | 12.6926 | -10.3894 | 64.6782 | 64.6782 | 22.8593 | 202.8593 | 23.3867 | 788.7785 | 788.7785 | 101.001 | 889.7795 | 0.68043 | 68.04% | 402.3583 | 273.7777 | 191.6444 | 180.4778 | 180.4778 | 106.2% | 11.36% | 11.36% | 95% | 10.79% | 43.4335 | 4.5261 | 4.5261 | 196.5841 | 96.0492 | 108.9% | 108.9%
6 | 160 | 9 | 3830 | 14 | 23.5 | 649.36 | 152.03 | 801.39 | 152.03 | 76.02 | 160 | 3830 | 840 | 157.8082 | 22.8794 | 7.2737 | 814.284 | 13.6926 | -25.3894 | 58.575 | 58.575 | 49.2592 | 229.2592 | 32.435 | 642.2655 | 642.2655 | 129.7657 | 772.0312 | 0.66523 | 66.52% | 349.1125 | 232.2395 | 162.5677 | 185.8188 | 185.8188 | 87.49% | 11.35% | 11.35% | 90% | 10.21% | 35.6512 | 4.2957 | 4.2957 | 153.146 | 78.8395 | 82.42% | 82.42%
6 | 160 | 9 | 3831 | 15 | 23.6 | 565.19 | 147.69 | 712.88 | 147.69 | 73.85 | 160 | 3831 | 900 | 157.8082 | 22.8794 | 7.2737 | 874.284 | 14.6926 | -40.3894 | 49.8077 | 49.8077 | 67.6791 | 247.6791 | 44.4829 | 527.8826 | 527.8826 | 126.0613 | 653.9439 | 0.6405 | 64.05% | 295.7134 | 189.4041 | 132.5828 | 181.0799 | 181.0799 | 73.22% | 11.32% | 11.32% | 90% | 10.19% | 30.1355 | 4.2784 | 4.2784 | 128.9329 | 66.6419 | 71.2% | 71.2%
6 | 160 | 9 | 3832 | 16 | 23.1 | 573.33 | 130.64 | 703.97 | 130.64 | 65.32 | 160 | 3832 | 960 | 157.8082 | 22.8794 | 7.2737 | 934.284 | 15.6926 | -55.3894 | 39.9181 | 39.9181 | 81.3702 | 261.3702 | 57.648 | 478.1116 | 478.1116 | 111.5082 | 589.6198 | 0.62083 | 62.08% | 266.6261 | 165.5303 | 115.8712 | 169.0351 | 169.0351 | 68.55% | 11.32% | 11.32% | 90% | 10.18% | 27.1546 | 4.3653 | 4.3653 | 118.5383 | 60.0499 | 70.13% | 70.13%
6 | 160 | 9 | 3833 | 17 | 23.8 | 445 | 153.33 | 598.33 | 153.33 | 76.67 | 160 | 3833 | 1020 | 157.8082 | 22.8794 | 7.2737 | 994.284 | 16.6926 | -70.3894 | 29.6749 | 29.6749 | 92.6998 | 272.6998 | 71.2685 | 288.651 | 288.651 | 130.8753 | 419.5264 | 0.55017 | 55.02% | 189.7098 | 104.3717 | 73.0602 | 174.3209 | 174.3209 | 41.91% | 11.27% | 11.27% | 85% | 9.582% | 18.1773 | 4.2442 | 4.2442 | 77.1475 | 40.1974 | 44.26% | 44.26%
6 | 160 | 9 | 3834 | 18 | 23.8 | 204.53 | 113.42 | 317.95 | 113.42 | 56.71 | 160 | 3834 | 1080 | 157.8082 | 22.8794 | 7.2737 | 1054.284 | 17.6926 | -85.3894 | 19.5138 | 19.5138 | 103.0161 | 283.0161 | 85.0615 | 52.711 | 52.711 | 96.81 | 149.521 | 0.09179 | 9.179% | 67.6134 | 6.2062 | 4.3443 | 155.2395 | 155.2395 | 2.798% | 11.22% | 11.22% | 80% | 8.973% | 6.0668 | 4.2442 | 4.2442 | 25.7488 | 13.4163 | 16.59% | 16.59%
6 | 160 | 9 | 3835 | 19 | 22.6 | 117.97 | 94.44 | 212.41 | 94.44 | 47.22 | 160 | 3835 | 1140 | 157.8082 | 22.8794 | 7.2737 | 1114.284 | 18.6926 | -100.3894 | 9.7606 | 9.7606 | 113.1425 | 293.1425 | 98.8592 | 0 | 0 | 80.6096 | 80.6096 | -0.54919 | 0% | 36.4517 | 0 | 0 | 128.4513 | 128.4513 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.4539 | 4.4539 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3836 | 20 | 21.7 | 30.75 | 44.64 | 75.39 | 44.64 | 22.32 | 160 | 3836 | 1200 | 157.8082 | 22.8794 | 7.2737 | 1174.284 | 19.6926 | -115.3894 | 0.73256 | 0.73256 | 123.6533 | 303.6533 | 112.5061 | 0 | 0 | 38.1026 | 38.1026 | -2.1101 | 0% | 17.23 | 0 | 0 | 151.8057 | 151.8057 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.6179 | 4.6179 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3837 | 21 | 19.2 | 0 | 8.69 | 8.69 | 8.69 | 4.35 | 160 | 3837 | 1260 | 157.8082 | 22.8794 | 7.2737 | 1234.284 | 20.6926 | -130.3894 | -7.2111 | 0 | 124.5917 | 304.5917 | 113.6684 | 0 | 0 | 7.4174 | 7.4174 | -14.9054 | 0% | 3.3541 | 0 | 0 | -4.708 | 0 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3838 | 22 | 17.7 | 0 | 0 | 0 | 0 | 0 | 160 | 3838 | 1320 | 157.8082 | 22.8794 | 7.2737 | 1294.284 | 21.6926 | -145.3894 | -13.6491 | 0 | 124.5917 | 304.5917 | 113.6684 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6265 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3839 | 23 | 16.9 | 0 | 0 | 0 | 0 | 0 | 160 | 3839 | 1380 | 157.8082 | 22.8794 | 7.2737 | 1354.284 | 22.6926 | -160.3894 | -18.1216 | 0 | 124.5917 | 304.5917 | 113.6684 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0289 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
6 | 160 | 9 | 3840 | 24 | 15.4 | 0 | 0 | 0 | 0 | 0 | 160 | 3840 | 1440 | 157.8082 | 22.8794 | 7.2737 | 1414.284 | 23.6926 | -175.3894 | -20.2179 | 0 | 124.5917 | 304.5917 | 113.6684 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.498 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3841 | 1 | 14.6 | 0 | 0 | 0 | 0 | 0 | 161 | 3841 | 60 | 158.7945 | 22.9526 | 6.8597 | 34.284 | 0.68573 | 169.7141 | -19.6516 | 0 | 124.7113 | 55.2887 | 113.7443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0672 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3842 | 2 | 14.5 | 0 | 0 | 0 | 0 | 0 | 161 | 3842 | 120 | 158.7945 | 22.9526 | 6.8597 | 94.284 | 1.6857 | 154.7141 | -16.6195 | 0 | 124.7113 | 55.2887 | 113.7443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3293 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3843 | 3 | 13.9 | 0 | 0 | 0 | 0 | 0 | 161 | 3843 | 180 | 158.7945 | 22.9526 | 6.8597 | 154.284 | 2.6857 | 139.7141 | -11.3541 | 0 | 124.7113 | 55.2887 | 113.7443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3533 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3844 | 4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 161 | 3844 | 240 | 158.7945 | 22.9526 | 6.8597 | 214.284 | 3.6857 | 124.7141 | -4.2982 | 0 | 124.7113 | 55.2887 | 113.7443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5057 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3845 | 5 | 13.3 | 0 | 0 | 0 | 0 | 0 | 161 | 3845 | 300 | 158.7945 | 22.9526 | 6.8597 | 274.284 | 4.6857 | 109.7141 | 4.0974 | 4.0974 | 119.6484 | 60.3516 | 107.3598 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.6309 | 10.6309 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3846 | 6 | 13.2 | 11.19 | 19.72 | 30.91 | 19.72 | 9.86 | 161 | 3846 | 360 | 158.7945 | 22.9526 | 6.8597 | 334.284 | 5.6857 | 94.7141 | 13.4353 | 13.4353 | 109.3461 | 70.6539 | 93.6431 | -3.0602 | 0 | 16.8321 | 16.8321 | -6.9214 | 0% | 7.6115 | 0 | 0 | 28.9296 | 28.9296 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3847 | 7 | 14.8 | 100.75 | 52.86 | 153.61 | 52.86 | 26.43 | 161 | 3847 | 420 | 158.7945 | 22.9526 | 6.8597 | 394.284 | 6.6857 | 79.7141 | 23.3767 | 23.3767 | 99.2308 | 80.7692 | 79.8373 | 44.8031 | 44.8031 | 45.1188 | 89.9219 | -0.60148 | 0% | 40.6627 | 0 | 0 | 169.9275 | 169.9275 | 0% | 11.56% | 11.56% | 80% | 9.244% | 3.7589 | 6.0631 | 6 | 22.5533 | 8.3124 | 13.27% | 13.27%
6 | 161 | 10 | 3848 | 8 | 17 | 251.86 | 69.81 | 321.67 | 69.81 | 34.91 | 161 | 3848 | 480 | 158.7945 | 22.9526 | 6.8597 | 454.284 | 7.6857 | 64.7141 | 33.6094 | 33.6094 | 88.6548 | 91.3452 | 66.0945 | 184.3826 | 184.3826 | 59.5866 | 243.9691 | 0.30631 | 30.63% | 110.3228 | 33.7931 | 23.6552 | 192.8811 | 192.8811 | 12.26% | 11.44% | 11.44% | 80% | 9.155% | 10.1001 | 5.5661 | 5.5661 | 56.2179 | 22.3354 | 29.15% | 29.15%
6 | 161 | 10 | 3849 | 9 | 19.3 | 399.92 | 82.5 | 482.42 | 82.5 | 41.25 | 161 | 3849 | 540 | 158.7945 | 22.9526 | 6.8597 | 514.284 | 8.6857 | 49.7141 | 43.7827 | 43.7827 | 76.6406 | 103.3594 | 52.6111 | 350.9633 | 350.9633 | 70.4182 | 421.3815 | 0.528 | 52.8% | 190.5487 | 100.6096 | 70.4267 | 203.7105 | 203.7105 | 34.57% | 11.37% | 11.37% | 85% | 9.662% | 18.41 | 5.0828 | 5.0828 | 93.5737 | 40.7122 | 45.93% | 45.93%
6 | 161 | 10 | 3850 | 10 | 20.5 | 531.75 | 94.81 | 626.56 | 94.81 | 47.41 | 161 | 3850 | 600 | 158.7945 | 22.9526 | 6.8597 | 574.284 | 9.6857 | 34.7141 | 53.3729 | 53.3729 | 61.5177 | 118.4823 | 39.7663 | 509.3045 | 509.3045 | 80.9254 | 590.2299 | 0.61143 | 61.14% | 266.902 | 163.1927 | 114.2349 | 205.6715 | 205.6715 | 55.54% | 11.35% | 11.35% | 90% | 10.21% | 27.255 | 4.8453 | 4.8453 | 132.0579 | 60.272 | 64.21% | 64.21%
6 | 161 | 10 | 3851 | 11 | 21.3 | 634.92 | 112.14 | 747.06 | 112.14 | 56.07 | 161 | 3851 | 660 | 158.7945 | 22.9526 | 6.8597 | 634.284 | 10.6857 | 19.7141 | 61.3804 | 61.3804 | 40.4275 | 139.5725 | 28.5335 | 635.4401 | 635.4401 | 95.7175 | 731.1576 | 0.65094 | 65.09% | 330.6295 | 215.2215 | 150.6551 | 198.3539 | 198.3539 | 75.95% | 11.35% | 11.35% | 90% | 10.21% | 33.7651 | 4.6926 | 4.6926 | 158.4446 | 74.6685 | 79.88% | 79.88%
6 | 161 | 10 | 3852 | 12 | 21.9 | 696.67 | 135.69 | 832.36 | 135.69 | 67.85 | 161 | 3852 | 720 | 158.7945 | 22.9526 | 6.8597 | 694.284 | 11.6857 | 4.7141 | 65.8738 | 65.8738 | 10.6694 | 169.3306 | 21.6631 | 709.4357 | 709.4357 | 115.8187 | 825.2544 | 0.66998 | 67% | 373.18 | 250.0235 | 175.0165 | 183.5597 | 183.5597 | 95.35% | 11.35% | 11.35% | 95% | 10.79% | 40.2546 | 4.581 | 4.581 | 184.4044 | 89.0194 | 100.5% | 100.5%
6 | 161 | 10 | 3853 | 13 | 23.6 | 480.92 | 197.03 | 677.95 | 197.03 | 98.52 | 161 | 3853 | 780 | 158.7945 | 22.9526 | 6.8597 | 754.284 | 12.6857 | -10.2859 | 64.7757 | 64.7757 | 22.6948 | 202.6948 | 23.409 | 487.8557 | 487.8557 | 168.1756 | 656.0313 | 0.64102 | 64.1% | 296.6574 | 190.163 | 133.1141 | 279.2148 | 279.2148 | 47.67% | 11.32% | 11.32% | 90% | 10.19% | 30.2328 | 4.2784 | 4.2784 | 129.3491 | 66.8571 | 46.33% | 46.33%
6 | 161 | 10 | 3854 | 14 | 24.1 | 450.56 | 159.64 | 610.2 | 159.64 | 79.82 | 161 | 3854 | 840 | 158.7945 | 22.9526 | 6.8597 | 814.284 | 13.6857 | -25.2859 | 58.6892 | 58.6892 | 49.187 | 229.187 | 32.403 | 445.2543 | 445.2543 | 136.2613 | 581.5156 | 0.62198 | 62.2% | 262.9614 | 163.5574 | 114.4901 | 189.7456 | 189.7456 | 60.34% | 11.3% | 11.3% | 90% | 10.17% | 26.7496 | 4.1933 | 4.1933 | 112.1696 | 59.1544 | 59.12% | 59.12%
6 | 161 | 10 | 3855 | 15 | 24.2 | 500.08 | 190.47 | 690.55 | 190.47 | 95.24 | 161 | 3855 | 900 | 158.7945 | 22.9526 | 6.8597 | 874.284 | 14.6857 | -40.2859 | 49.9263 | 49.9263 | 67.6498 | 247.6498 | 44.4228 | 466.7354 | 466.7354 | 162.5763 | 629.3117 | 0.63615 | 63.61% | 284.5747 | 181.0315 | 126.7221 | 191.4307 | 191.4307 | 66.2% | 11.31% | 11.31% | 90% | 10.18% | 28.9734 | 4.1765 | 4.1765 | 121.0076 | 64.0722 | 63.21% | 63.21%
6 | 161 | 10 | 3856 | 16 | 23.8 | 442.22 | 146.94 | 589.16 | 146.94 | 73.47 | 161 | 3856 | 960 | 158.7945 | 22.9526 | 6.8597 | 934.284 | 15.6857 | -55.2859 | 40.0378 | 40.0378 | 81.3561 | 261.3561 | 57.5719 | 368.6298 | 368.6298 | 125.4211 | 494.051 | 0.58845 | 58.85% | 223.4098 | 131.4665 | 92.0266 | 176.5272 | 176.5272 | 52.13% | 11.29% | 11.29% | 85% | 9.595% | 21.4358 | 4.2442 | 4.2442 | 90.9775 | 47.4034 | 51.54% | 51.54%
6 | 161 | 10 | 3857 | 17 | 23.6 | 304.17 | 143.69 | 447.86 | 143.69 | 71.85 | 161 | 3857 | 1020 | 158.7945 | 22.9526 | 6.8597 | 994.284 | 16.6857 | -70.2859 | 29.7947 | 29.7947 | 92.6889 | 272.6889 | 71.1816 | 197.4588 | 197.4588 | 122.6471 | 320.1059 | 0.46998 | 47% | 144.7519 | 68.031 | 47.6217 | 162.9538 | 162.9538 | 29.22% | 11.26% | 11.26% | 85% | 9.568% | 13.8505 | 4.2784 | 4.2784 | 59.2585 | 30.6291 | 36.37% | 36.37%
6 | 161 | 10 | 3858 | 18 | 21.4 | 231.03 | 150.47 | 381.5 | 150.47 | 75.24 | 161 | 3858 | 1080 | 158.7945 | 22.9526 | 6.8597 | 1054.284 | 17.6857 | -85.2859 | 19.6333 | 19.6333 | 103.0026 | 283.0026 | 84.9664 | 60.3293 | 60.3293 | 128.4342 | 188.7634 | 0.21231 | 21.23% | 85.3588 | 18.1226 | 12.6858 | 140.9071 | 140.9071 | 9.003% | 11.3% | 11.3% | 80% | 9.044% | 7.7198 | 4.6738 | 4.6738 | 36.0807 | 17.0717 | 25.61% | 25.61%
6 | 161 | 10 | 3859 | 19 | 16.4 | 123.42 | 104.92 | 228.34 | 104.92 | 52.46 | 161 | 3859 | 1140 | 158.7945 | 22.9526 | 6.8597 | 1114.284 | 18.6857 | -100.2859 | 9.8792 | 9.8792 | 113.1227 | 293.1227 | 98.757 | 0 | 0 | 89.5548 | 89.5548 | -0.56687 | 0% | 40.4967 | 0 | 0 | 120.1477 | 120.1477 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3860 | 20 | 15.2 | 34.81 | 56.94 | 91.75 | 56.94 | 28.47 | 161 | 3860 | 1200 | 158.7945 | 22.9526 | 6.8597 | 1174.284 | 19.6857 | -115.2859 | 0.84902 | 0.84902 | 123.6237 | 303.6237 | 112.3975 | 0 | 0 | 48.6013 | 48.6013 | -1.7778 | 0% | 21.9775 | 0 | 0 | 143.2935 | 143.2935 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3861 | 21 | 15.1 | 0 | 9.92 | 9.92 | 9.92 | 4.96 | 161 | 3861 | 1260 | 158.7945 | 22.9526 | 6.8597 | 1234.284 | 20.6857 | -130.2859 | -7.0987 | 0 | 124.7113 | 304.7113 | 113.7443 | 0 | 0 | 8.4672 | 8.4672 | -14.0418 | 0% | 3.8289 | 0 | 0 | -10.3394 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3862 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 161 | 3862 | 1320 | 158.7945 | 22.9526 | 6.8597 | 1294.284 | 21.6857 | -145.2859 | -13.5438 | 0 | 124.7113 | 304.7113 | 113.7443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1287 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3863 | 23 | 14.7 | 0 | 0 | 0 | 0 | 0 | 161 | 3863 | 1380 | 158.7945 | 22.9526 | 6.8597 | 1354.284 | 22.6857 | -160.2859 | -18.0275 | 0 | 124.7113 | 304.7113 | 113.7443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6955 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
6 | 161 | 10 | 3864 | 24 | 13.8 | 0 | 0 | 0 | 0 | 0 | 161 | 3864 | 1440 | 158.7945 | 22.9526 | 6.8597 | 1414.284 | 23.6857 | -175.2859 | -20.1392 | 0 | 124.7113 | 304.7113 | 113.7443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1768 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3865 | 1 | 13.3 | 0 | 0 | 0 | 0 | 0 | 162 | 3865 | 60 | 159.7808 | 23.019 | 6.4408 | 34.284 | 0.67875 | 169.8188 | -19.5982 | 0 | 124.82 | 55.18 | 113.8133 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.303 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3866 | 2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 162 | 3866 | 120 | 159.7808 | 23.019 | 6.4408 | 94.284 | 1.6787 | 154.8188 | -16.5856 | 0 | 124.82 | 55.18 | 113.8133 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1417 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3867 | 3 | 12.3 | 0 | 0 | 0 | 0 | 0 | 162 | 3867 | 180 | 159.7808 | 23.019 | 6.4408 | 154.284 | 2.6787 | 139.8188 | -11.3383 | 0 | 124.82 | 55.18 | 113.8133 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7612 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3868 | 4 | 11.9 | 0 | 0 | 0 | 0 | 0 | 162 | 3868 | 240 | 159.7808 | 23.019 | 6.4408 | 214.284 | 3.6787 | 124.8188 | -4.2977 | 0 | 124.82 | 55.18 | 113.8133 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3708 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3869 | 5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 162 | 3869 | 300 | 159.7808 | 23.019 | 6.4408 | 274.284 | 4.6787 | 109.8188 | 4.0858 | 4.0858 | 119.7652 | 60.2348 | 107.4436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.5961 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3870 | 6 | 11.5 | 3.81 | 15.92 | 19.73 | 15.92 | 7.96 | 162 | 3870 | 360 | 159.7808 | 23.019 | 6.4408 | 334.284 | 5.6787 | 94.8188 | 13.415 | 13.415 | 109.4646 | 70.5354 | 93.7352 | -1.0698 | 0 | 13.5886 | 13.5886 | -9.0536 | 0% | 6.1448 | 0 | 0 | 9.5241 | 9.5241 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3871 | 7 | 12.3 | 40.56 | 56.67 | 97.23 | 56.67 | 28.34 | 162 | 3871 | 420 | 159.7808 | 23.019 | 6.4408 | 394.284 | 6.6787 | 79.8188 | 23.351 | 23.351 | 99.3553 | 80.6447 | 79.9364 | 17.8814 | 17.8814 | 48.3709 | 66.2522 | -1.1899 | 0% | 29.9593 | 0 | 0 | 177.5704 | 177.5704 | 0% | 11.66% | 11.66% | 80% | 9.33% | 2.7953 | 6.669 | 6 | 16.7715 | 6.1815 | 9.445% | 9.445%
6 | 162 | 11 | 3872 | 8 | 13.4 | 78.69 | 73.06 | 151.75 | 73.06 | 36.53 | 162 | 3872 | 480 | 159.7808 | 23.019 | 6.4408 | 454.284 | 7.6787 | 64.8188 | 33.5821 | 33.5821 | 88.7915 | 91.2085 | 66.1999 | 57.4098 | 57.4098 | 62.3606 | 119.7704 | -0.27787 | 0% | 54.1602 | 0 | 0 | 147.0615 | 147.0615 | 0% | 11.6% | 11.6% | 80% | 9.279% | 5.0256 | 6.397 | 6 | 30.1536 | 11.1137 | 20.5% | 20.5%
6 | 162 | 11 | 3873 | 9 | 15.3 | 155.92 | 140.36 | 296.28 | 140.36 | 70.18 | 162 | 3873 | 540 | 159.7808 | 23.019 | 6.4408 | 514.284 | 8.6787 | 49.8188 | 43.7587 | 43.7587 | 76.7993 | 103.2007 | 52.7223 | 136.5448 | 136.5448 | 119.8048 | 256.3495 | 0.31541 | 31.54% | 115.9212 | 36.5625 | 25.5938 | 157.1972 | 157.1972 | 16.28% | 11.49% | 11.49% | 80% | 9.194% | 10.6578 | 5.9472 | 5.9472 | 63.3838 | 23.5688 | 40.32% | 40.32%
6 | 162 | 11 | 3874 | 10 | 18.3 | 302.31 | 176.86 | 479.17 | 176.86 | 88.43 | 162 | 3874 | 600 | 159.7808 | 23.019 | 6.4408 | 574.284 | 9.6787 | 34.8188 | 53.36 | 53.36 | 61.7127 | 118.2873 | 39.8824 | 289.1087 | 289.1087 | 150.9595 | 440.0682 | 0.53468 | 53.47% | 198.9988 | 106.401 | 74.4807 | 166.7606 | 166.7606 | 44.66% | 11.39% | 11.39% | 85% | 9.678% | 19.2587 | 5.2884 | 5.2884 | 101.8469 | 42.5889 | 61.07% | 61.07%
6 | 162 | 11 | 3875 | 11 | 20.4 | 445.08 | 114.36 | 559.44 | 114.36 | 57.18 | 162 | 3875 | 660 | 159.7808 | 23.019 | 6.4408 | 634.284 | 10.6787 | 19.8188 | 61.3919 | 61.3919 | 40.6708 | 139.3292 | 28.6486 | 444.9082 | 444.9082 | 97.6124 | 542.5206 | 0.59409 | 59.41% | 245.3278 | 145.7479 | 102.0235 | 164.9887 | 164.9887 | 61.84% | 11.35% | 11.35% | 90% | 10.21% | 25.0521 | 4.8647 | 4.8647 | 121.8707 | 55.4006 | 73.87% | 73.87%
6 | 162 | 11 | 3876 | 12 | 21.1 | 147.5 | 144.58 | 292.08 | 144.58 | 72.29 | 162 | 3876 | 720 | 159.7808 | 23.019 | 6.4408 | 694.284 | 11.6787 | 4.8188 | 65.9262 | 65.9262 | 10.9259 | 169.0741 | 21.7495 | 150.0513 | 150.0513 | 123.4067 | 273.4581 | 0.39317 | 39.32% | 123.6577 | 48.6186 | 34.033 | 143.6255 | 143.6255 | 23.7% | 11.32% | 11.32% | 80% | 9.056% | 11.1986 | 4.7303 | 4.7303 | 52.9728 | 24.7647 | 36.88% | 36.88%
6 | 162 | 11 | 3877 | 13 | 21.8 | 292.78 | 227.5 | 520.28 | 227.5 | 113.75 | 162 | 3877 | 780 | 159.7808 | 23.019 | 6.4408 | 754.284 | 12.6787 | -10.1812 | 64.8669 | 64.8669 | 22.5223 | 202.5223 | 23.4253 | 296.7435 | 296.7435 | 194.1834 | 490.9269 | 0.57827 | 57.83% | 221.9971 | 128.3741 | 89.8618 | 151.8285 | 151.8285 | 59.19% | 11.32% | 11.32% | 85% | 9.623% | 21.3632 | 4.5994 | 4.5994 | 98.2575 | 47.2428 | 64.72% | 64.72%
6 | 162 | 11 | 3878 | 14 | 23.2 | 155 | 238.06 | 393.06 | 238.06 | 119.03 | 162 | 3878 | 840 | 159.7808 | 23.019 | 6.4408 | 814.284 | 13.6787 | -25.1812 | 58.7983 | 58.7983 | 49.1054 | 229.1054 | 32.3666 | 153.0595 | 153.0595 | 203.1969 | 356.2564 | 0.50146 | 50.15% | 161.0991 | 80.7843 | 56.549 | 150.9465 | 150.9465 | 37.46% | 11.27% | 11.27% | 85% | 9.583% | 15.4378 | 4.3478 | 4.3478 | 67.1206 | 34.1394 | 44.47% | 44.47%
6 | 162 | 11 | 3879 | 15 | 23.8 | 196.03 | 196.67 | 392.7 | 196.67 | 98.34 | 162 | 3879 | 900 | 159.7808 | 23.019 | 6.4408 | 874.284 | 14.6787 | -40.1812 | 50.0409 | 50.0409 | 67.612 | 247.612 | 44.3594 | 182.8501 | 182.8501 | 167.8683 | 350.7185 | 0.50036 | 50.04% | 158.5949 | 79.3553 | 55.5487 | 159.2155 | 159.2155 | 34.89% | 11.26% | 11.26% | 85% | 9.569% | 15.1766 | 4.2442 | 4.2442 | 64.412 | 33.5616 | 40.46% | 40.46%
6 | 162 | 11 | 3880 | 16 | 23.8 | 222.22 | 166.58 | 388.8 | 166.58 | 83.29 | 162 | 3880 | 960 | 159.7808 | 23.019 | 6.4408 | 934.284 | 15.6787 | -55.1812 | 40.1537 | 40.1537 | 81.3345 | 261.3345 | 57.4933 | 185.1942 | 185.1942 | 142.1849 | 327.3791 | 0.47872 | 47.87% | 148.0409 | 70.8699 | 49.6089 | 156.9233 | 156.9233 | 31.61% | 11.25% | 11.25% | 85% | 9.565% | 14.1605 | 4.2442 | 4.2442 | 60.0995 | 31.3146 | 38.3% | 38.3%
6 | 162 | 11 | 3881 | 17 | 23.6 | 57.14 | 192.69 | 249.83 | 192.69 | 96.35 | 162 | 3881 | 1020 | 159.7808 | 23.019 | 6.4408 | 994.284 | 16.6787 | -70.1812 | 29.9108 | 29.9108 | 92.6714 | 272.6714 | 71.093 | 37.1306 | 37.1306 | 164.4712 | 201.6018 | 0.27364 | 27.36% | 91.1643 | 24.9466 | 17.4626 | 144.3843 | 144.3843 | 12.09% | 11.23% | 11.23% | 80% | 8.987% | 8.1928 | 4.2784 | 4.2784 | 35.0523 | 18.1176 | 24.28% | 24.28%
6 | 162 | 11 | 3882 | 18 | 23.3 | 97.31 | 148.33 | 245.64 | 148.33 | 74.17 | 162 | 3882 | 1080 | 159.7808 | 23.019 | 6.4408 | 1054.284 | 17.6787 | -85.1812 | 19.7489 | 19.7489 | 102.9833 | 282.9833 | 84.8703 | 25.7492 | 25.7492 | 126.6076 | 152.3568 | 0.097978 | 9.798% | 68.8957 | 6.7503 | 4.7252 | 228.7739 | 228.7739 | 2.065% | 11.23% | 11.23% | 80% | 8.988% | 6.192 | 4.3304 | 4.3304 | 26.8138 | 13.6932 | 11.72% | 11.72%
6 | 162 | 11 | 3883 | 19 | 23.1 | 76.58 | 130 | 206.58 | 130 | 65 | 162 | 3883 | 1140 | 159.7808 | 23.019 | 6.4408 | 1114.284 | 18.6787 | -100.1812 | 9.9936 | 9.9936 | 113.0974 | 293.0974 | 98.6545 | 0 | 0 | 110.9619 | 110.9619 | -0.1693 | 0% | 50.177 | 0 | 0 | 125.9381 | 125.9381 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.3653 | 4.3653 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3884 | 20 | 22.6 | 30.56 | 48.25 | 78.81 | 48.25 | 24.13 | 162 | 3884 | 1200 | 159.7808 | 23.019 | 6.4408 | 1174.284 | 19.6787 | -115.1812 | 0.9609 | 0.9609 | 123.5892 | 303.5892 | 112.2892 | 0 | 0 | 41.184 | 41.184 | -1.8446 | 0% | 18.6234 | 0 | 0 | 153.0013 | 153.0013 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4539 | 4.4539 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3885 | 21 | 20.6 | 0 | 10.08 | 10.08 | 10.08 | 5.04 | 162 | 3885 | 1260 | 159.7808 | 23.019 | 6.4408 | 1234.284 | 20.6787 | -130.1812 | -6.9915 | 0 | 124.82 | 304.82 | 113.8133 | 0 | 0 | 8.6038 | 8.6038 | -12.3808 | 0% | 3.8906 | 0 | 0 | -1.9076 | 0 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8259 | 4.8259 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3886 | 22 | 18.5 | 0 | 0 | 0 | 0 | 0 | 162 | 3886 | 1320 | 159.7808 | 23.019 | 6.4408 | 1294.284 | 21.6787 | -145.1812 | -13.4443 | 0 | 124.82 | 304.82 | 113.8133 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9769 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3887 | 23 | 16.5 | 0 | 0 | 0 | 0 | 0 | 162 | 3887 | 1380 | 159.7808 | 23.019 | 6.4408 | 1354.284 | 22.6787 | -160.1812 | -17.9396 | 0 | 124.82 | 304.82 | 113.8133 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.492 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
6 | 162 | 11 | 3888 | 24 | 15.4 | 0 | 0 | 0 | 0 | 0 | 162 | 3888 | 1440 | 159.7808 | 23.019 | 6.4408 | 1414.284 | 23.6787 | -175.1812 | -20.067 | 0 | 124.82 | 304.82 | 113.8133 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6355 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3889 | 1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 163 | 3889 | 60 | 160.7671 | 23.0787 | 6.0173 | 34.284 | 0.67169 | 169.9247 | -19.5514 | 0 | 124.9178 | 55.0822 | 113.8754 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3414 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3890 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 163 | 3890 | 120 | 160.7671 | 23.0787 | 6.0173 | 94.284 | 1.6717 | 154.9247 | -16.5583 | 0 | 124.9178 | 55.0822 | 113.8754 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3654 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3891 | 3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 163 | 3891 | 180 | 160.7671 | 23.0787 | 6.0173 | 154.284 | 2.6717 | 139.9247 | -11.3288 | 0 | 124.9178 | 55.0822 | 113.8754 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6942 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3892 | 4 | 12.6 | 0 | 0 | 0 | 0 | 0 | 163 | 3892 | 240 | 160.7671 | 23.0787 | 6.0173 | 214.284 | 3.6717 | 124.9247 | -4.3032 | 0 | 124.9178 | 55.0822 | 113.8754 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1514 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3893 | 5 | 12.4 | 0 | 0 | 0 | 0 | 0 | 163 | 3893 | 300 | 160.7671 | 23.0787 | 6.0173 | 274.284 | 4.6717 | 109.9247 | 4.0685 | 4.0685 | 119.8784 | 60.1216 | 107.5295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.1896 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3894 | 6 | 12.4 | 7.5 | 16.58 | 24.08 | 16.58 | 8.29 | 163 | 3894 | 360 | 160.7671 | 23.0787 | 6.0173 | 334.284 | 5.6717 | 94.9247 | 13.3892 | 13.3892 | 109.5791 | 70.4209 | 93.8288 | -2.1627 | 0 | 14.1519 | 14.1519 | -8.5143 | 0% | 6.3995 | 0 | 0 | 5.3545 | 5.3545 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3895 | 7 | 13.2 | 46.86 | 50 | 96.86 | 50 | 25 | 163 | 3895 | 420 | 160.7671 | 23.0787 | 6.0173 | 394.284 | 6.6717 | 79.9247 | 23.32 | 23.32 | 99.4751 | 80.5249 | 80.0362 | 20.4817 | 20.4817 | 42.6777 | 63.1594 | -1.2548 | 0% | 28.5607 | 0 | 0 | 169.6823 | 169.6823 | 0% | 11.63% | 11.63% | 80% | 9.302% | 2.6567 | 6.4458 | 6 | 15.9404 | 5.8751 | 9.394% | 9.394%
6 | 163 | 12 | 3896 | 8 | 16 | 86.03 | 112.14 | 198.17 | 112.14 | 56.07 | 163 | 3896 | 480 | 160.7671 | 23.0787 | 6.0173 | 454.284 | 7.6717 | 64.9247 | 33.5495 | 33.5495 | 88.9229 | 91.0771 | 66.3051 | 62.5568 | 62.5568 | 95.7175 | 158.2743 | 0.022643 | 2.264% | 71.5716 | 1.6206 | 1.1344 | 143.3169 | 143.3169 | 0.7916% | 11.49% | 11.49% | 80% | 9.195% | 6.5807 | 5.7878 | 5.7878 | 38.0877 | 14.5526 | 26.58% | 26.58%
6 | 163 | 12 | 3897 | 9 | 18.5 | 131.03 | 136.86 | 267.89 | 136.86 | 68.43 | 163 | 3897 | 540 | 160.7671 | 23.0787 | 6.0173 | 514.284 | 8.6717 | 49.9247 | 43.7293 | 43.7293 | 76.9521 | 103.0479 | 52.8325 | 114.5189 | 114.5189 | 116.8173 | 231.3362 | 0.2936 | 29.36% | 104.6102 | 30.7135 | 21.4995 | 151.0587 | 151.0587 | 14.23% | 11.4% | 11.4% | 80% | 9.119% | 9.5395 | 5.2467 | 5.2467 | 50.0509 | 21.0959 | 33.13% | 33.13%
6 | 163 | 12 | 3898 | 10 | 21 | 149.25 | 251.19 | 400.44 | 251.19 | 125.6 | 163 | 3898 | 600 | 160.7671 | 23.0787 | 6.0173 | 574.284 | 9.6717 | 34.9247 | 53.3412 | 53.3412 | 61.9015 | 118.0985 | 39.9964 | 142.53 | 142.53 | 214.4041 | 356.934 | 0.48864 | 48.86% | 161.4056 | 78.869 | 55.2083 | 159.5549 | 159.5549 | 34.6% | 11.33% | 11.33% | 85% | 9.628% | 15.5409 | 4.7493 | 4.7493 | 73.8085 | 34.3673 | 46.26% | 46.26%
6 | 163 | 12 | 3899 | 11 | 22.6 | 328.69 | 232.86 | 561.55 | 232.86 | 116.43 | 163 | 3899 | 660 | 160.7671 | 23.0787 | 6.0173 | 634.284 | 10.6717 | 19.9247 | 61.3967 | 61.3967 | 40.9093 | 139.0907 | 28.7597 | 328.1993 | 328.1993 | 198.7584 | 526.9578 | 0.597 | 59.7% | 238.2903 | 142.2593 | 99.5815 | 163.1693 | 163.1693 | 61.03% | 11.31% | 11.31% | 90% | 10.18% | 24.2619 | 4.4539 | 4.4539 | 108.0611 | 53.653 | 66.23% | 66.23%
6 | 163 | 12 | 3900 | 12 | 23 | 441.03 | 201.94 | 642.97 | 201.94 | 100.97 | 163 | 3900 | 720 | 160.7671 | 23.0787 | 6.0173 | 694.284 | 11.6717 | 4.9247 | 65.9714 | 65.9714 | 11.1834 | 168.8166 | 21.8299 | 448.249 | 448.249 | 172.3666 | 620.6156 | 0.62963 | 62.96% | 280.6424 | 176.7017 | 123.6912 | 158.0745 | 158.0745 | 78.25% | 11.32% | 11.32% | 90% | 10.19% | 28.5979 | 4.3829 | 4.3829 | 125.3418 | 63.2417 | 79.29% | 79.29%
6 | 163 | 12 | 3901 | 13 | 23.3 | 525.92 | 242.31 | 768.23 | 242.31 | 121.16 | 163 | 3901 | 780 | 160.7671 | 23.0787 | 6.0173 | 754.284 | 12.6717 | -10.0753 | 64.9518 | 64.9518 | 22.342 | 202.342 | 23.4358 | 532.6274 | 532.6274 | 206.8245 | 739.4519 | 0.65853 | 65.85% | 334.3802 | 220.1998 | 154.1398 | 276.3051 | 276.3051 | 55.79% | 11.34% | 11.34% | 90% | 10.21% | 34.1299 | 4.3304 | 4.3304 | 147.7945 | 75.4752 | 53.49% | 53.49%
6 | 163 | 12 | 3902 | 14 | 24 | 315 | 203.89 | 518.89 | 203.89 | 101.95 | 163 | 3902 | 840 | 160.7671 | 23.0787 | 6.0173 | 814.284 | 13.6717 | -25.0753 | 58.9025 | 58.9025 | 49.0145 | 229.0145 | 32.3256 | 310.8554 | 310.8554 | 174.031 | 484.8864 | 0.58527 | 58.53% | 219.2656 | 128.3289 | 89.8302 | 271.2473 | 271.2473 | 33.12% | 11.28% | 11.28% | 85% | 9.59% | 21.0282 | 4.2102 | 4.2102 | 88.5328 | 46.5019 | 32.64% | 32.64%
6 | 163 | 12 | 3903 | 15 | 24.1 | 336.75 | 205.83 | 542.58 | 205.83 | 102.92 | 163 | 3903 | 900 | 160.7671 | 23.0787 | 6.0173 | 874.284 | 14.6717 | -40.0753 | 50.1513 | 50.1513 | 67.5659 | 247.5659 | 44.2928 | 313.9601 | 313.9601 | 175.6869 | 489.647 | 0.58783 | 58.78% | 221.4184 | 130.1568 | 91.1098 | 273.4392 | 273.4392 | 33.32% | 11.28% | 11.28% | 85% | 9.59% | 21.2334 | 4.1933 | 4.1933 | 89.0383 | 46.9557 | 32.56% | 32.56%
6 | 163 | 12 | 3904 | 16 | 24.2 | 472.78 | 195.36 | 668.14 | 195.36 | 97.68 | 163 | 3904 | 960 | 160.7671 | 23.0787 | 6.0173 | 934.284 | 15.6717 | -55.0753 | 40.2658 | 40.2658 | 81.3057 | 261.3057 | 57.4124 | 393.9666 | 393.9666 | 166.7502 | 560.7168 | 0.61561 | 61.56% | 253.5561 | 156.0926 | 109.2648 | 276.2343 | 276.2343 | 39.56% | 11.3% | 11.3% | 90% | 10.17% | 25.7792 | 4.1765 | 4.1765 | 107.6668 | 57.0084 | 38.98% | 38.98%
6 | 163 | 12 | 3905 | 17 | 24.3 | 376.03 | 151.67 | 527.7 | 151.67 | 75.84 | 163 | 3905 | 1020 | 160.7671 | 23.0787 | 6.0173 | 994.284 | 16.6717 | -70.0753 | 30.0232 | 30.0232 | 92.6474 | 272.6474 | 71.0028 | 244.6408 | 244.6408 | 129.4584 | 374.0992 | 0.52221 | 52.22% | 169.1677 | 88.3412 | 61.8388 | 266.3165 | 266.3165 | 23.22% | 11.25% | 11.25% | 85% | 9.564% | 16.1785 | 4.1598 | 4.1598 | 67.2986 | 35.7773 | 25.27% | 25.27%
6 | 163 | 12 | 3906 | 18 | 24.4 | 245.92 | 141.39 | 387.31 | 141.39 | 70.7 | 163 | 3906 | 1080 | 160.7671 | 23.0787 | 6.0173 | 1054.284 | 17.6717 | -85.0753 | 19.8607 | 19.8607 | 102.958 | 282.958 | 84.7731 | 65.9436 | 65.9436 | 120.6839 | 186.6275 | 0.2403 | 24.03% | 84.3929 | 20.2792 | 14.1954 | 252.1572 | 252.1572 | 5.63% | 11.2% | 11.2% | 80% | 8.963% | 7.564 | 4.1431 | 4.1431 | 31.3383 | 16.7271 | 12.43% | 12.43%
6 | 163 | 12 | 3907 | 19 | 23.6 | 112.97 | 69.53 | 182.5 | 69.53 | 34.77 | 163 | 3907 | 1140 | 160.7671 | 23.0787 | 6.0173 | 1114.284 | 18.6717 | -100.0753 | 10.1038 | 10.1038 | 113.0668 | 293.0668 | 98.5517 | -95.7568 | 0 | 59.3476 | 59.3476 | -0.9976 | 0% | 26.837 | 0 | 0 | 229.7669 | 229.7669 | 0% | 11.21% | 0% | 80% | 0% | 0 | 4.2784 | 4.2784 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3908 | 20 | 22.5 | 15.08 | 32.42 | 47.5 | 32.42 | 16.21 | 163 | 3908 | 1200 | 160.7671 | 23.0787 | 6.0173 | 1174.284 | 19.6717 | -115.0753 | 1.0682 | 1.0682 | 123.5498 | 303.5498 | 112.1814 | 0 | 0 | 27.6722 | 27.6722 | -3.1457 | 0% | 12.5134 | 0 | 0 | 149.4632 | 149.4632 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.4719 | 4.4719 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3909 | 21 | 20.4 | 0 | 9.92 | 9.92 | 9.92 | 4.96 | 163 | 3909 | 1260 | 160.7671 | 23.0787 | 6.0173 | 1234.284 | 20.6717 | -130.0753 | -6.8894 | 0 | 124.9178 | 304.9178 | 113.8754 | 0 | 0 | 8.4672 | 8.4672 | -12.6453 | 0% | 3.8289 | 0 | 0 | -3.8852 | 0 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8647 | 4.8647 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3910 | 22 | 18.2 | 0 | 0 | 0 | 0 | 0 | 163 | 3910 | 1320 | 160.7671 | 23.0787 | 6.0173 | 1294.284 | 21.6717 | -145.0753 | -13.3504 | 0 | 124.9178 | 304.9178 | 113.8754 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3549 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3093 | 5.3093 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3911 | 23 | 16.2 | 0 | 0 | 0 | 0 | 0 | 163 | 3911 | 1380 | 160.7671 | 23.0787 | 6.0173 | 1354.284 | 22.6717 | -160.0753 | -17.8579 | 0 | 124.9178 | 304.9178 | 113.8754 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0553 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
6 | 163 | 12 | 3912 | 24 | 15.5 | 0 | 0 | 0 | 0 | 0 | 163 | 3912 | 1440 | 160.7671 | 23.0787 | 6.0173 | 1414.284 | 23.6717 | -175.0753 | -20.0014 | 0 | 124.9178 | 304.9178 | 113.8754 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7746 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3913 | 1 | 14.7 | 0 | 0 | 0 | 0 | 0 | 164 | 3913 | 60 | 161.7534 | 23.1317 | 5.5896 | 34.284 | 0.66456 | 170.0316 | -19.5113 | 0 | 125.0047 | 54.9953 | 113.9304 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.095 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3914 | 2 | 13.9 | 0 | 0 | 0 | 0 | 0 | 164 | 3914 | 120 | 161.7534 | 23.1317 | 5.5896 | 94.284 | 1.6646 | 155.0316 | -16.5375 | 0 | 125.0047 | 54.9953 | 113.9304 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6582 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3915 | 3 | 13.9 | 0 | 0 | 0 | 0 | 0 | 164 | 3915 | 180 | 161.7534 | 23.1317 | 5.5896 | 154.284 | 2.6646 | 140.0316 | -11.3256 | 0 | 125.0047 | 54.9953 | 113.9304 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0022 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3916 | 4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 164 | 3916 | 240 | 161.7534 | 23.1317 | 5.5896 | 214.284 | 3.6646 | 125.0316 | -4.3148 | 0 | 125.0047 | 54.9953 | 113.9304 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1546 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3917 | 5 | 13.7 | 0 | 0 | 0 | 0 | 0 | 164 | 3917 | 300 | 161.7534 | 23.1317 | 5.5896 | 274.284 | 4.6646 | 110.0316 | 4.0455 | 4.0455 | 119.988 | 60.012 | 107.6174 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.2743 | 6.2743 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3918 | 6 | 13.3 | 3.89 | 18.25 | 22.14 | 18.25 | 9.13 | 164 | 3918 | 360 | 161.7534 | 23.1317 | 5.5896 | 334.284 | 5.6646 | 95.0316 | 13.3581 | 13.3581 | 109.6893 | 70.3107 | 93.9236 | -1.1521 | 0 | 15.5773 | 15.5773 | -7.5289 | 0% | 7.0441 | 0 | 0 | 19.9298 | 19.9298 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3919 | 7 | 14.5 | 44.08 | 51.11 | 95.19 | 51.11 | 25.56 | 164 | 3919 | 420 | 161.7534 | 23.1317 | 5.5896 | 394.284 | 6.6646 | 80.0316 | 23.2838 | 23.2838 | 99.5901 | 80.4099 | 80.1366 | 19.1024 | 19.1024 | 43.6251 | 62.7275 | -1.2217 | 0% | 28.3654 | 0 | 0 | 193.8205 | 193.8205 | 0% | 11.58% | 11.58% | 80% | 9.26% | 2.6266 | 6.1335 | 6 | 15.7598 | 5.8086 | 8.131% | 8.131%
6 | 164 | 13 | 3920 | 8 | 16.7 | 157.31 | 73.89 | 231.2 | 73.89 | 36.95 | 164 | 3920 | 480 | 161.7534 | 23.1317 | 5.5896 | 454.284 | 7.6646 | 65.0316 | 33.5117 | 33.5117 | 89.049 | 90.951 | 66.4103 | 114.023 | 114.023 | 63.0691 | 177.0921 | 0.11456 | 11.46% | 80.0811 | 9.1744 | 6.4221 | 171.7222 | 171.7222 | 3.74% | 11.47% | 11.47% | 80% | 9.172% | 7.3451 | 5.6319 | 5.6319 | 41.3665 | 16.243 | 24.09% | 24.09%
6 | 164 | 13 | 3921 | 9 | 19.6 | 270 | 82.97 | 352.97 | 82.97 | 41.49 | 164 | 3921 | 540 | 161.7534 | 23.1317 | 5.5896 | 514.284 | 8.6646 | 50.0316 | 43.6944 | 43.6944 | 77.099 | 102.901 | 52.9418 | 235.5331 | 235.5331 | 70.8193 | 306.3525 | 0.42653 | 42.65% | 138.5326 | 59.0883 | 41.3618 | 182.1747 | 182.1747 | 22.7% | 11.36% | 11.36% | 85% | 9.658% | 13.3801 | 5.0224 | 5.0224 | 67.2006 | 29.5888 | 36.89% | 36.89%
6 | 164 | 13 | 3922 | 10 | 21.2 | 365.83 | 132.58 | 498.41 | 132.58 | 66.29 | 164 | 3922 | 600 | 161.7534 | 23.1317 | 5.5896 | 574.284 | 9.6646 | 35.0316 | 53.3165 | 53.3165 | 62.0839 | 117.9161 | 40.108 | 348.8983 | 348.8983 | 113.1641 | 462.0624 | 0.56134 | 56.13% | 208.9446 | 117.2881 | 82.1017 | 186.8944 | 186.8944 | 43.93% | 11.33% | 11.33% | 85% | 9.63% | 20.1219 | 4.7114 | 4.7114 | 94.8022 | 44.4977 | 50.73% | 50.73%
6 | 164 | 13 | 3923 | 11 | 22.8 | 485.64 | 191.39 | 677.03 | 191.39 | 95.7 | 164 | 3923 | 660 | 161.7534 | 23.1317 | 5.5896 | 634.284 | 10.6646 | 20.0316 | 61.3949 | 61.3949 | 41.1426 | 138.8574 | 28.8668 | 484.4252 | 484.4252 | 163.3616 | 647.7868 | 0.63628 | 63.63% | 292.9292 | 186.3848 | 130.4693 | 186.7866 | 186.7866 | 69.85% | 11.33% | 11.33% | 90% | 10.2% | 29.8662 | 4.4183 | 4.4183 | 131.9572 | 66.0464 | 70.65% | 70.65%
6 | 164 | 13 | 3924 | 12 | 24.1 | 516.67 | 203.89 | 720.56 | 203.89 | 101.95 | 164 | 3924 | 720 | 161.7534 | 23.1317 | 5.5896 | 694.284 | 11.6646 | 5.0316 | 66.0094 | 66.0094 | 11.4416 | 168.5584 | 21.9043 | 524.698 | 524.698 | 174.031 | 698.729 | 0.65252 | 65.25% | 315.9653 | 206.1725 | 144.3208 | 194.4431 | 194.4431 | 74.22% | 11.33% | 11.33% | 90% | 10.2% | 32.2166 | 4.1933 | 4.1933 | 135.0944 | 71.2441 | 69.48% | 69.48%
6 | 164 | 13 | 3925 | 13 | 25.1 | 206.53 | 220.14 | 426.67 | 220.14 | 110.07 | 164 | 3925 | 780 | 161.7534 | 23.1317 | 5.5896 | 754.284 | 12.6646 | -9.9684 | 65.0304 | 65.0304 | 22.1542 | 202.1542 | 23.4405 | 209.0229 | 209.0229 | 187.9012 | 396.9241 | 0.54272 | 54.27% | 179.4891 | 97.4131 | 68.1891 | 198.7152 | 198.7152 | 34.32% | 11.24% | 11.24% | 85% | 9.553% | 17.1468 | 4.0283 | 4.0283 | 69.0726 | 37.9185 | 34.76% | 34.76%
6 | 164 | 13 | 3926 | 14 | 23 | 153.06 | 257.92 | 410.98 | 257.92 | 128.96 | 164 | 3926 | 840 | 161.7534 | 23.1317 | 5.5896 | 814.284 | 13.6646 | -24.9684 | 59.0016 | 59.0016 | 48.9145 | 228.9145 | 32.2803 | 150.9645 | 150.9645 | 220.1485 | 371.113 | 0.5124 | 51.24% | 167.8173 | 85.9904 | 60.1933 | 157.8227 | 157.8227 | 38.14% | 11.28% | 11.28% | 85% | 9.589% | 16.0921 | 4.3829 | 4.3829 | 70.53 | 35.5862 | 44.69% | 44.69%
6 | 164 | 13 | 3927 | 15 | 18.2 | 171.94 | 303.75 | 475.69 | 303.75 | 151.88 | 164 | 3927 | 900 | 161.7534 | 23.1317 | 5.5896 | 874.284 | 14.6646 | -39.9684 | 50.2574 | 50.2574 | 67.5114 | 247.5114 | 44.2228 | 160.2471 | 160.2471 | 259.2668 | 419.5139 | 0.52096 | 52.1% | 189.7042 | 98.8275 | 69.1792 | 150.2977 | 150.2977 | 46.03% | 11.39% | 11.39% | 85% | 9.681% | 18.3657 | 5.3093 | 5.3093 | 97.5089 | 40.6141 | 64.88% | 64.88%
6 | 164 | 13 | 3928 | 16 | 18.2 | 307.78 | 184.92 | 492.7 | 184.92 | 92.46 | 164 | 3928 | 960 | 161.7534 | 23.1317 | 5.5896 | 934.284 | 15.6646 | -54.9684 | 40.3741 | 40.3741 | 81.2695 | 261.2695 | 57.3291 | 256.4837 | 256.4837 | 157.8391 | 414.3227 | 0.51741 | 51.74% | 187.3567 | 96.9401 | 67.8581 | 148.1455 | 148.1455 | 45.81% | 11.39% | 11.39% | 85% | 9.682% | 18.1392 | 5.3093 | 5.3093 | 96.3066 | 40.1133 | 65.01% | 65.01%
6 | 164 | 13 | 3929 | 17 | 19 | 257.31 | 222.97 | 480.28 | 222.97 | 111.49 | 164 | 3929 | 1020 | 161.7534 | 23.1317 | 5.5896 | 994.284 | 16.6646 | -69.9684 | 30.1317 | 30.1317 | 92.617 | 272.617 | 70.911 | 167.6325 | 167.6325 | 190.3168 | 357.9493 | 0.47724 | 47.72% | 161.8647 | 77.2475 | 54.0733 | 145.8835 | 145.8835 | 37.07% | 11.38% | 11.38% | 85% | 9.67% | 15.6521 | 5.1437 | 5.1437 | 80.5097 | 34.6132 | 55.19% | 55.19%
6 | 164 | 13 | 3930 | 18 | 20.5 | 247.03 | 157.03 | 404.06 | 157.03 | 78.52 | 164 | 3930 | 1080 | 161.7534 | 23.1317 | 5.5896 | 1054.284 | 17.6646 | -84.9684 | 19.9685 | 19.9685 | 102.9269 | 282.9269 | 84.6751 | 67.1306 | 67.1306 | 134.0335 | 201.1641 | 0.239 | 23.9% | 90.9664 | 21.7405 | 15.2184 | 139.9269 | 139.9269 | 10.88% | 11.34% | 11.34% | 80% | 9.068% | 8.2492 | 4.8453 | 4.8453 | 39.9697 | 18.2424 | 28.56% | 28.56%
6 | 164 | 13 | 3931 | 19 | 20.6 | 81.11 | 89.64 | 170.75 | 89.64 | 44.82 | 164 | 3931 | 1140 | 161.7534 | 23.1317 | 5.5896 | 1114.284 | 18.6646 | -99.9684 | 10.2098 | 10.2098 | 113.0309 | 293.0309 | 98.4486 | -67.231 | 0 | 76.5125 | 76.5125 | -0.67862 | 0% | 34.599 | 0 | 0 | 122.5693 | 122.5693 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8259 | 4.8259 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3932 | 20 | 19.8 | 30.75 | 42.5 | 73.25 | 42.5 | 21.25 | 164 | 3932 | 1200 | 161.7534 | 23.1317 | 5.5896 | 1174.284 | 19.6646 | -114.9684 | 1.1708 | 1.1708 | 123.5055 | 303.5055 | 112.0741 | 0 | 0 | 36.276 | 36.276 | -2.3716 | 0% | 16.404 | 0 | 0 | 149.466 | 149.466 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9826 | 4.9826 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3933 | 21 | 19.5 | 0 | 9.08 | 9.08 | 9.08 | 4.54 | 164 | 3933 | 1260 | 161.7534 | 23.1317 | 5.5896 | 1234.284 | 20.6646 | -129.9684 | -6.7924 | 0 | 125.0047 | 305.0047 | 113.9304 | 0 | 0 | 7.7503 | 7.7503 | -14.1451 | 0% | 3.5047 | 0 | 0 | -3.3117 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0425 | 5.0425 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3934 | 22 | 19.2 | 0 | 0 | 0 | 0 | 0 | 164 | 3934 | 1320 | 161.7534 | 23.1317 | 5.5896 | 1294.284 | 21.6646 | -144.9684 | -13.2622 | 0 | 125.0047 | 305.0047 | 113.9304 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.205 | 0 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3935 | 23 | 18.3 | 0 | 0 | 0 | 0 | 0 | 164 | 3935 | 1380 | 161.7534 | 23.1317 | 5.5896 | 1354.284 | 22.6646 | -159.9684 | -17.7823 | 0 | 125.0047 | 305.0047 | 113.9304 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9206 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
6 | 164 | 13 | 3936 | 24 | 17.9 | 0 | 0 | 0 | 0 | 0 | 164 | 3936 | 1440 | 161.7534 | 23.1317 | 5.5896 | 1414.284 | 23.6646 | -174.9684 | -19.9423 | 0 | 125.0047 | 305.0047 | 113.9304 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.8742 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3937 | 1 | 17.5 | 0 | 0 | 0 | 0 | 0 | 165 | 3937 | 60 | 162.7397 | 23.178 | 5.1582 | 34.284 | 0.65737 | 170.1395 | -19.4778 | 0 | 125.0806 | 54.9194 | 113.9785 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.52 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3938 | 2 | 16.8 | 0 | 0 | 0 | 0 | 0 | 165 | 3938 | 120 | 162.7397 | 23.178 | 5.1582 | 94.284 | 1.6574 | 155.1395 | -16.5232 | 0 | 125.0806 | 54.9194 | 113.9785 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7974 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3939 | 3 | 16.5 | 0 | 0 | 0 | 0 | 0 | 165 | 3939 | 180 | 162.7397 | 23.178 | 5.1582 | 154.284 | 2.6574 | 140.1395 | -11.3287 | 0 | 125.0806 | 54.9194 | 113.9785 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4651 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3940 | 4 | 16.1 | 0 | 0 | 0 | 0 | 0 | 165 | 3940 | 240 | 162.7397 | 23.178 | 5.1582 | 214.284 | 3.6574 | 125.1395 | -4.3322 | 0 | 125.0806 | 54.9194 | 113.9785 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0747 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3941 | 5 | 15.9 | 0 | 0 | 0 | 0 | 0 | 165 | 3941 | 300 | 162.7397 | 23.178 | 5.1582 | 274.284 | 4.6574 | 110.1395 | 4.017 | 4.017 | 120.094 | 59.906 | 107.7071 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.5235 | 10.5235 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3942 | 6 | 15.2 | 6.94 | 16.19 | 23.13 | 16.19 | 8.1 | 165 | 3942 | 360 | 162.7397 | 23.178 | 5.1582 | 334.284 | 5.6574 | 95.1395 | 13.3215 | 13.3215 | 109.7954 | 70.2046 | 94.0196 | -2.1113 | 0 | 13.819 | 13.819 | -8.276 | 0% | 6.249 | 0 | 0 | 25.6784 | 25.6784 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3943 | 7 | 14.8 | 68.97 | 60.19 | 129.16 | 60.19 | 30.1 | 165 | 3943 | 420 | 162.7397 | 23.178 | 5.1582 | 394.284 | 6.6574 | 80.1395 | 23.2424 | 23.2424 | 99.7004 | 80.2996 | 80.2375 | 29.6356 | 29.6356 | 51.3754 | 81.011 | -0.75608 | 0% | 36.6332 | 0 | 0 | 202.0637 | 202.0637 | 0% | 11.56% | 11.56% | 80% | 9.246% | 3.3871 | 6.0631 | 6 | 20.3228 | 7.4904 | 10.06% | 10.06%
6 | 165 | 14 | 3944 | 8 | 16.8 | 180.36 | 100.75 | 281.11 | 100.75 | 50.38 | 165 | 3944 | 480 | 162.7397 | 23.178 | 5.1582 | 454.284 | 7.6574 | 65.1395 | 33.4687 | 33.4687 | 89.1697 | 90.8303 | 66.5153 | 130.3292 | 130.3292 | 85.9955 | 216.3247 | 0.24064 | 24.06% | 97.822 | 23.5396 | 16.4777 | 181.2687 | 181.2687 | 9.09% | 11.45% | 11.45% | 80% | 9.164% | 8.9642 | 5.6099 | 5.6099 | 50.2881 | 19.8235 | 27.74% | 27.74%
6 | 165 | 14 | 3945 | 9 | 19.6 | 341.47 | 136.03 | 477.5 | 136.03 | 68.02 | 165 | 3945 | 540 | 162.7397 | 23.178 | 5.1582 | 514.284 | 8.6574 | 50.1395 | 43.6542 | 43.6542 | 77.2397 | 102.7603 | 53.05 | 297.3527 | 297.3527 | 116.1089 | 413.4616 | 0.52432 | 52.43% | 186.9673 | 98.0298 | 68.6209 | 195.0931 | 195.0931 | 35.17% | 11.36% | 11.36% | 85% | 9.656% | 18.0544 | 5.0224 | 5.0224 | 90.677 | 39.9256 | 46.48% | 46.48%
6 | 165 | 14 | 3946 | 10 | 21.2 | 357.86 | 132.58 | 490.44 | 132.58 | 66.29 | 165 | 3946 | 600 | 162.7397 | 23.178 | 5.1582 | 574.284 | 9.6574 | 35.1395 | 53.286 | 53.286 | 62.2598 | 117.7402 | 40.2174 | 340.8829 | 340.8829 | 113.1641 | 454.047 | 0.55705 | 55.71% | 205.3201 | 114.374 | 80.0618 | 192.9477 | 192.9477 | 41.49% | 11.33% | 11.33% | 85% | 9.63% | 19.7719 | 4.7114 | 4.7114 | 93.1533 | 43.7238 | 48.28% | 48.28%
6 | 165 | 14 | 3947 | 11 | 23.7 | 486.86 | 185 | 671.86 | 185 | 92.5 | 165 | 3947 | 660 | 162.7397 | 23.178 | 5.1582 | 634.284 | 10.6574 | 20.1395 | 61.3865 | 61.3865 | 41.3705 | 138.6295 | 28.9698 | 485.1987 | 485.1987 | 157.9074 | 643.1061 | 0.63808 | 63.81% | 290.8126 | 185.5611 | 129.8928 | 204.8636 | 204.8636 | 63.4% | 11.32% | 11.32% | 90% | 10.19% | 29.6282 | 4.2613 | 4.2613 | 126.2538 | 65.5201 | 61.63% | 61.63%
6 | 165 | 14 | 3948 | 12 | 24.6 | 552.22 | 222.22 | 774.44 | 222.22 | 111.11 | 165 | 3948 | 720 | 162.7397 | 23.178 | 5.1582 | 694.284 | 11.6574 | 5.1395 | 66.0404 | 66.0404 | 11.6999 | 168.3001 | 21.9728 | 560.3958 | 560.3958 | 189.6766 | 750.0724 | 0.66431 | 66.43% | 339.1827 | 225.3238 | 157.7267 | 208.9517 | 208.9517 | 75.48% | 11.34% | 11.34% | 90% | 10.21% | 34.6151 | 4.1099 | 4.1099 | 142.2658 | 76.5481 | 68.09% | 68.09%
6 | 165 | 14 | 3949 | 13 | 25.1 | 464.86 | 242.78 | 707.64 | 242.78 | 121.39 | 165 | 3949 | 780 | 162.7397 | 23.178 | 5.1582 | 754.284 | 12.6574 | -9.8605 | 65.1026 | 65.1026 | 21.959 | 201.959 | 23.4393 | 470.1996 | 470.1996 | 207.2257 | 677.4253 | 0.65091 | 65.09% | 306.3317 | 199.3946 | 139.5762 | 211.6852 | 211.6852 | 65.94% | 11.32% | 11.32% | 90% | 10.19% | 31.2025 | 4.0283 | 4.0283 | 125.6935 | 69.0016 | 59.38% | 59.38%
6 | 165 | 14 | 3950 | 14 | 24.7 | 724.86 | 170.28 | 895.14 | 170.28 | 85.14 | 165 | 3950 | 840 | 162.7397 | 23.178 | 5.1582 | 814.284 | 13.6574 | -24.8605 | 59.0955 | 59.0955 | 48.8053 | 228.8053 | 32.2305 | 714.6253 | 714.6253 | 145.3431 | 859.9683 | 0.68241 | 68.24% | 388.8777 | 265.3753 | 185.7627 | 208.9073 | 208.9073 | 88.92% | 11.37% | 11.37% | 95% | 10.8% | 41.9954 | 4.0935 | 4.0935 | 171.9071 | 92.8691 | 82.29% | 82.29%
6 | 165 | 14 | 3951 | 15 | 22.4 | 478.89 | 223.06 | 701.95 | 223.06 | 111.53 | 165 | 3951 | 900 | 162.7397 | 23.178 | 5.1582 | 874.284 | 14.6574 | -39.8605 | 50.3592 | 50.3592 | 67.4485 | 247.4485 | 44.1497 | 446.218 | 446.218 | 190.3936 | 636.6116 | 0.63197 | 63.2% | 287.8758 | 181.93 | 127.351 | 165.5994 | 165.5994 | 76.9% | 11.33% | 11.33% | 90% | 10.2% | 29.3558 | 4.4899 | 4.4899 | 131.8041 | 64.9178 | 79.59% | 79.59%
6 | 165 | 14 | 3952 | 16 | 21.6 | 483.89 | 194.92 | 678.81 | 194.92 | 97.46 | 165 | 3952 | 960 | 162.7397 | 23.178 | 5.1582 | 934.284 | 15.6574 | -54.8605 | 40.4784 | 40.4784 | 81.2261 | 261.2261 | 57.2435 | 403.3175 | 403.3175 | 166.3746 | 569.6921 | 0.60871 | 60.87% | 257.6148 | 156.8136 | 109.7695 | 160.7462 | 160.7462 | 68.29% | 11.33% | 11.33% | 90% | 10.2% | 26.273 | 4.6364 | 4.6364 | 121.8132 | 58.1004 | 75.78% | 75.78%
6 | 165 | 14 | 3953 | 17 | 21.2 | 331.75 | 137.22 | 468.97 | 137.22 | 68.61 | 165 | 3953 | 1020 | 162.7397 | 23.178 | 5.1582 | 994.284 | 16.6574 | -69.8605 | 30.2365 | 30.2365 | 92.5802 | 272.5802 | 70.8177 | 216.4645 | 216.4645 | 117.1246 | 333.5891 | 0.46788 | 46.79% | 150.849 | 70.5792 | 49.4055 | 147.3105 | 147.3105 | 33.54% | 11.32% | 11.32% | 85% | 9.623% | 14.5162 | 4.7114 | 4.7114 | 68.3919 | 32.1014 | 46.43% | 46.43%
6 | 165 | 14 | 3954 | 18 | 21.1 | 211.58 | 108.42 | 320 | 108.42 | 54.21 | 165 | 3954 | 1080 | 162.7397 | 23.178 | 5.1582 | 1054.284 | 17.6574 | -84.8605 | 20.0723 | 20.0723 | 102.8901 | 282.8901 | 84.5762 | 58.2711 | 58.2711 | 92.5423 | 150.8133 | 0.059076 | 5.908% | 68.1978 | 4.0288 | 2.8202 | 134.9364 | 134.9364 | 2.09% | 11.31% | 11.31% | 80% | 9.05% | 6.172 | 4.7303 | 4.7303 | 29.1956 | 13.6489 | 21.64% | 21.64%
6 | 165 | 14 | 3955 | 19 | 21.4 | 140.19 | 79.36 | 219.55 | 79.36 | 39.68 | 165 | 3955 | 1140 | 162.7397 | 23.178 | 5.1582 | 1114.284 | 18.6574 | -99.8605 | 10.3115 | 10.3115 | 112.9898 | 292.9898 | 98.3454 | -113.672 | 0 | 67.738 | 67.738 | -0.84484 | 0% | 30.6311 | 0 | 0 | 125.2335 | 125.2335 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.6738 | 4.6738 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3956 | 20 | 21.8 | 46.47 | 71.94 | 118.41 | 71.94 | 35.97 | 165 | 3956 | 1200 | 162.7397 | 23.178 | 5.1582 | 1174.284 | 19.6574 | -114.8605 | 1.2687 | 1.2687 | 123.4566 | 303.4566 | 111.9675 | 0 | 0 | 61.4046 | 61.4046 | -1.0007 | 0% | 27.7672 | 0 | 0 | 153.2064 | 153.2064 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.5994 | 4.5994 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3957 | 21 | 21 | 0 | 14.17 | 14.17 | 14.17 | 7.09 | 165 | 3957 | 1260 | 162.7397 | 23.178 | 5.1582 | 1234.284 | 20.6574 | -129.8605 | -6.7007 | 0 | 125.0806 | 305.0806 | 113.9785 | 0 | 0 | 12.0949 | 12.0949 | -8.5027 | 0% | 5.4693 | 0 | 0 | -2.8142 | 0 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7493 | 4.7493 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3958 | 22 | 19.9 | 0 | 0 | 0 | 0 | 0 | 165 | 3958 | 1320 | 162.7397 | 23.178 | 5.1582 | 1294.284 | 21.6574 | -144.8605 | -13.1798 | 0 | 125.0806 | 305.0806 | 113.9785 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2307 | 0 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3959 | 23 | 18.6 | 0 | 0 | 0 | 0 | 0 | 165 | 3959 | 1380 | 162.7397 | 23.178 | 5.1582 | 1354.284 | 22.6574 | -159.8605 | -17.713 | 0 | 125.0806 | 305.0806 | 113.9785 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4224 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
6 | 165 | 14 | 3960 | 24 | 18.4 | 0 | 0 | 0 | 0 | 0 | 165 | 3960 | 1440 | 162.7397 | 23.178 | 5.1582 | 1414.284 | 23.6574 | -174.8605 | -19.8897 | 0 | 125.0806 | 305.0806 | 113.9785 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9378 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3961 | 1 | 17.6 | 0 | 0 | 0 | 0 | 0 | 166 | 3961 | 60 | 163.726 | 23.2176 | 4.7232 | 34.284 | 0.65012 | 170.2482 | -19.4508 | 0 | 125.1456 | 54.8544 | 114.0197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.5037 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3962 | 2 | 17.3 | 0 | 0 | 0 | 0 | 0 | 166 | 3962 | 120 | 163.726 | 23.2176 | 4.7232 | 94.284 | 1.6501 | 155.2482 | -16.5153 | 0 | 125.1456 | 54.8544 | 114.0197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.3356 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3963 | 3 | 17.3 | 0 | 0 | 0 | 0 | 0 | 166 | 3963 | 180 | 163.726 | 23.2176 | 4.7232 | 154.284 | 2.6501 | 140.2482 | -11.338 | 0 | 125.1456 | 54.8544 | 114.0197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.7103 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3964 | 4 | 17.3 | 0 | 0 | 0 | 0 | 0 | 166 | 3964 | 240 | 163.726 | 23.2176 | 4.7232 | 214.284 | 3.6501 | 125.2482 | -4.3555 | 0 | 125.1456 | 54.8544 | 114.0197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.7103 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3965 | 5 | 17.3 | 0 | 0 | 0 | 0 | 0 | 166 | 3965 | 300 | 163.726 | 23.2176 | 4.7232 | 274.284 | 4.6501 | 110.2482 | 3.9829 | 3.9829 | 120.1962 | 59.8038 | 107.7987 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.4141 | 9.4141 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3966 | 6 | 17.3 | 4.17 | 16.19 | 20.36 | 16.19 | 8.1 | 166 | 3966 | 360 | 163.726 | 23.2176 | 4.7232 | 334.284 | 5.6501 | 95.2482 | 13.2797 | 13.2797 | 109.8972 | 70.1028 | 94.1168 | -1.3033 | 0 | 13.819 | 13.819 | -7.9339 | 0% | 6.249 | 0 | 0 | 21.81 | 21.81 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3967 | 7 | 16.8 | 50.08 | 46.39 | 96.47 | 46.39 | 23.2 | 166 | 3967 | 420 | 163.726 | 23.2176 | 4.7232 | 394.284 | 6.6501 | 80.2482 | 23.1959 | 23.1959 | 99.8059 | 80.1941 | 80.3389 | 21.3377 | 21.3377 | 39.5963 | 60.934 | -1.196 | 0% | 27.5544 | 0 | 0 | 190.2308 | 190.2308 | 0% | 11.48% | 11.48% | 80% | 9.186% | 2.5311 | 5.6099 | 5.6099 | 14.1989 | 5.5972 | 7.464% | 7.464%
6 | 166 | 15 | 3968 | 8 | 16.6 | 154.64 | 70.92 | 225.56 | 70.92 | 35.46 | 166 | 3968 | 480 | 163.726 | 23.2176 | 4.7232 | 454.284 | 7.6501 | 65.2482 | 33.4207 | 33.4207 | 89.285 | 90.715 | 66.62 | 111.4149 | 111.4149 | 60.534 | 171.9489 | 0.092635 | 9.264% | 77.7553 | 7.2029 | 5.042 | 162.4648 | 162.4648 | 3.103% | 11.47% | 11.47% | 80% | 9.176% | 7.1345 | 5.6539 | 5.6539 | 40.3379 | 15.7773 | 24.83% | 24.83%
6 | 166 | 15 | 3969 | 9 | 16.6 | 241.94 | 95.47 | 337.41 | 95.47 | 47.74 | 166 | 3969 | 540 | 163.726 | 23.2176 | 4.7232 | 514.284 | 8.6501 | 50.2482 | 43.6087 | 43.6087 | 77.3743 | 102.6257 | 53.157 | 210.3332 | 210.3332 | 81.4887 | 291.8219 | 0.38485 | 38.48% | 131.9619 | 50.785 | 35.5495 | 167.6935 | 167.6935 | 21.2% | 11.45% | 11.45% | 80% | 9.158% | 12.0846 | 5.6539 | 5.6539 | 68.3254 | 26.724 | 40.74% | 40.74%
6 | 166 | 15 | 3970 | 10 | 16.9 | 295 | 123.06 | 418.06 | 123.06 | 61.53 | 166 | 3970 | 600 | 163.726 | 23.2176 | 4.7232 | 574.284 | 9.6501 | 35.2482 | 53.2498 | 53.2498 | 62.4291 | 117.5709 | 40.3245 | 280.693 | 280.693 | 105.0383 | 385.7312 | 0.48864 | 48.86% | 174.4277 | 85.232 | 59.6624 | 167.5676 | 167.5676 | 35.6% | 11.42% | 11.42% | 85% | 9.709% | 16.9356 | 5.588 | 5.588 | 94.6354 | 37.4516 | 56.48% | 56.48%
6 | 166 | 15 | 3971 | 11 | 17.8 | 265 | 215.08 | 480.08 | 215.08 | 107.54 | 166 | 3971 | 660 | 163.726 | 23.2176 | 4.7232 | 634.284 | 10.6501 | 20.2482 | 61.3717 | 61.3717 | 41.5928 | 138.4072 | 29.0687 | 263.8803 | 263.8803 | 183.5823 | 447.4626 | 0.53664 | 53.66% | 202.3426 | 108.5858 | 76.0101 | 162.6981 | 162.6981 | 46.72% | 11.39% | 11.39% | 85% | 9.685% | 19.5978 | 5.3938 | 5.3938 | 105.7063 | 43.3388 | 64.97% | 64.97%
6 | 166 | 15 | 3972 | 12 | 17.1 | 378.89 | 209.92 | 588.81 | 209.92 | 104.96 | 166 | 3972 | 720 | 163.726 | 23.2176 | 4.7232 | 694.284 | 11.6501 | 5.2482 | 66.0643 | 66.0643 | 11.9582 | 168.0418 | 22.0354 | 384.2588 | 384.2588 | 179.1779 | 563.4367 | 0.5889 | 58.89% | 254.7861 | 150.0429 | 105.03 | 153.0568 | 153.0568 | 68.62% | 11.39% | 11.39% | 90% | 10.25% | 26.1175 | 5.5443 | 5.5443 | 144.8037 | 57.7565 | 94.61% | 94.61%
6 | 166 | 15 | 3973 | 13 | 17.1 | 281.19 | 226.11 | 507.3 | 226.11 | 113.06 | 166 | 3973 | 780 | 163.726 | 23.2176 | 4.7232 | 754.284 | 12.6501 | -9.7518 | 65.1683 | 65.1683 | 21.7568 | 201.7568 | 23.4323 | 284.2837 | 284.2837 | 192.997 | 477.2806 | 0.55007 | 55.01% | 215.8263 | 118.7192 | 83.1034 | 146.5225 | 146.5225 | 56.72% | 11.4% | 11.4% | 85% | 9.693% | 20.9199 | 5.5443 | 5.5443 | 115.9867 | 46.2626 | 79.16% | 79.16%
6 | 166 | 15 | 3974 | 14 | 17.4 | 293.61 | 242.42 | 536.03 | 242.42 | 121.21 | 166 | 3974 | 840 | 163.726 | 23.2176 | 4.7232 | 814.284 | 13.6501 | -24.7518 | 59.1843 | 59.1843 | 48.6872 | 228.6872 | 32.1763 | 289.3688 | 289.3688 | 206.9184 | 496.2872 | 0.56115 | 56.11% | 224.4211 | 125.933 | 88.1531 | 146.2665 | 146.2665 | 60.27% | 11.4% | 11.4% | 85% | 9.686% | 21.7377 | 5.4794 | 5.4794 | 119.109 | 48.071 | 81.43% | 81.43%
6 | 166 | 15 | 3975 | 15 | 18.4 | 247.5 | 162.69 | 410.19 | 162.69 | 81.35 | 166 | 3975 | 900 | 163.726 | 23.2176 | 4.7232 | 874.284 | 14.6501 | -39.7518 | 50.4567 | 50.4567 | 67.3775 | 247.3775 | 44.0734 | 230.5876 | 230.5876 | 138.8646 | 369.4522 | 0.48381 | 48.38% | 167.0663 | 80.8277 | 56.5794 | 139.2853 | 139.2853 | 40.62% | 11.39% | 11.39% | 85% | 9.681% | 16.1744 | 5.2675 | 5.2675 | 85.1981 | 35.7682 | 61.17% | 61.17%
6 | 166 | 15 | 3976 | 16 | 19 | 208.06 | 164.25 | 372.31 | 164.25 | 82.13 | 166 | 3976 | 960 | 163.726 | 23.2176 | 4.7232 | 934.284 | 15.6501 | -54.7518 | 40.5788 | 40.5788 | 81.1755 | 261.1755 | 57.1558 | 173.4728 | 173.4728 | 140.1961 | 313.6689 | 0.43111 | 43.11% | 141.8411 | 61.1486 | 42.804 | 136.1937 | 136.1937 | 31.43% | 11.38% | 11.38% | 85% | 9.672% | 13.7188 | 5.1437 | 5.1437 | 70.5653 | 30.3379 | 51.81% | 51.81%
6 | 166 | 15 | 3977 | 17 | 19.9 | 152.14 | 172.5 | 324.64 | 172.5 | 86.25 | 166 | 3977 | 1020 | 163.726 | 23.2176 | 4.7232 | 994.284 | 16.6501 | -69.7518 | 30.3373 | 30.3373 | 92.5371 | 272.5371 | 70.7229 | 99.4421 | 99.4421 | 147.238 | 246.68 | 0.3379 | 33.79% | 111.5487 | 37.6923 | 26.3846 | 132.8405 | 132.8405 | 19.86% | 11.36% | 11.36% | 80% | 9.084% | 10.1331 | 4.9628 | 4.9628 | 50.2882 | 22.4085 | 37.86% | 37.86%
6 | 166 | 15 | 3978 | 18 | 20.5 | 103.53 | 151.39 | 254.92 | 151.39 | 75.7 | 166 | 3978 | 1080 | 163.726 | 23.2176 | 4.7232 | 1054.284 | 17.6501 | -84.7518 | 20.1722 | 20.1722 | 102.8476 | 282.8476 | 84.4765 | 28.8977 | 28.8977 | 129.2194 | 158.1171 | 0.085174 | 8.517% | 71.5006 | 6.09 | 4.263 | 126.753 | 126.753 | 3.363% | 11.33% | 11.33% | 80% | 9.067% | 6.4833 | 4.8453 | 4.8453 | 31.4134 | 14.3372 | 24.78% | 24.78%
6 | 166 | 15 | 3979 | 19 | 20.1 | 31.86 | 92.42 | 124.28 | 92.42 | 46.21 | 166 | 3979 | 1140 | 163.726 | 23.2176 | 4.7232 | 1114.284 | 18.6501 | -99.7518 | 10.4089 | 10.4089 | 112.9435 | 292.9435 | 98.2421 | -25.2798 | 0 | 78.8854 | 78.8854 | -0.64795 | 0% | 35.672 | 0 | 0 | 157.6246 | 157.6246 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3980 | 20 | 19.6 | 28.81 | 50.83 | 79.64 | 50.83 | 25.42 | 166 | 3980 | 1200 | 163.726 | 23.2176 | 4.7232 | 1174.284 | 19.6501 | -114.7518 | 1.3618 | 1.3618 | 123.4029 | 303.4029 | 111.8615 | 0 | 0 | 43.3861 | 43.3861 | -1.8613 | 0% | 19.6192 | 0 | 0 | 148.4815 | 148.4815 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0224 | 5.0224 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3981 | 21 | 18.5 | 0 | 9.36 | 9.36 | 9.36 | 4.68 | 166 | 3981 | 1260 | 163.726 | 23.2176 | 4.7232 | 1234.284 | 20.6501 | -129.7518 | -6.6141 | 0 | 125.1456 | 305.1456 | 114.0197 | 0 | 0 | 7.9893 | 7.9893 | -13.9751 | 0% | 3.6127 | 0 | 0 | -5.0992 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3982 | 22 | 16.9 | 0 | 0 | 0 | 0 | 0 | 166 | 3982 | 1320 | 163.726 | 23.2176 | 4.7232 | 1294.284 | 21.6501 | -144.7518 | -13.1031 | 0 | 125.1456 | 305.1456 | 114.0197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4463 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3983 | 23 | 16.1 | 0 | 0 | 0 | 0 | 0 | 166 | 3983 | 1380 | 163.726 | 23.2176 | 4.7232 | 1354.284 | 22.6501 | -159.7518 | -17.6498 | 0 | 125.1456 | 305.1456 | 114.0197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0402 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
6 | 166 | 15 | 3984 | 24 | 15.2 | 0 | 0 | 0 | 0 | 0 | 166 | 3984 | 1440 | 163.726 | 23.2176 | 4.7232 | 1414.284 | 23.6501 | -174.7518 | -19.8436 | 0 | 125.1456 | 305.1456 | 114.0197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7865 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 3985 | 1 | 15.1 | 0 | 0 | 0 | 0 | 0 | 167 | 3985 | 60 | 164.7123 | 23.2506 | 4.2853 | 34.284 | 0.64282 | 170.3577 | -19.4305 | 0 | 125.1996 | 54.8004 | 114.0539 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5216 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 3986 | 2 | 15.5 | 0 | 0 | 0 | 0 | 0 | 167 | 3986 | 120 | 164.7123 | 23.2506 | 4.2853 | 94.284 | 1.6428 | 155.3577 | -16.5139 | 0 | 125.1996 | 54.8004 | 114.0539 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2729 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 3987 | 3 | 15.9 | 0 | 0 | 0 | 0 | 0 | 167 | 3987 | 180 | 164.7123 | 23.2506 | 4.2853 | 154.284 | 2.6428 | 140.3577 | -11.3534 | 0 | 125.1996 | 54.8004 | 114.0539 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0241 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 3988 | 4 | 15.5 | 0 | 0 | 0 | 0 | 0 | 167 | 3988 | 240 | 164.7123 | 23.2506 | 4.2853 | 214.284 | 3.6428 | 125.3577 | -4.3847 | 0 | 125.1996 | 54.8004 | 114.0539 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6337 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 3989 | 5 | 15.3 | 0 | 0 | 0 | 0 | 0 | 167 | 3989 | 300 | 164.7123 | 23.2506 | 4.2853 | 274.284 | 4.6428 | 110.3577 | 3.9433 | 3.9433 | 120.2946 | 59.7054 | 107.8921 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.8113 | 7.8113 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 3990 | 6 | 15.5 | 3.25 | 15.28 | 18.53 | 15.28 | 7.64 | 167 | 3990 | 360 | 164.7123 | 23.2506 | 4.2853 | 334.284 | 5.6428 | 95.3577 | 13.2328 | 13.2328 | 109.9946 | 70.0054 | 94.2151 | -1.0436 | 0 | 13.0423 | 13.0423 | -8.7647 | 0% | 5.8977 | 0 | 0 | 21.5946 | 21.5946 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 3991 | 7 | 16 | 38.97 | 71.58 | 110.55 | 71.58 | 35.79 | 167 | 3991 | 420 | 164.7123 | 23.2506 | 4.2853 | 394.284 | 6.6428 | 80.3577 | 23.1444 | 23.1444 | 99.9065 | 80.0935 | 80.4407 | 16.4653 | 16.4653 | 61.0974 | 77.5626 | -0.79044 | 0% | 35.0738 | 0 | 0 | 193.9914 | 193.9914 | 0% | 11.51% | 11.51% | 80% | 9.209% | 3.2299 | 5.7878 | 5.7878 | 18.6938 | 7.1425 | 9.636% | 9.636%
6 | 167 | 16 | 3992 | 8 | 17.8 | 125.75 | 126.67 | 252.42 | 126.67 | 63.34 | 167 | 3992 | 480 | 164.7123 | 23.2506 | 4.2853 | 454.284 | 7.6428 | 65.3577 | 33.3677 | 33.3677 | 89.3947 | 90.6053 | 66.7244 | 90.345 | 90.345 | 108.1196 | 198.4647 | 0.20121 | 20.12% | 89.7457 | 18.0579 | 12.6405 | 170.8604 | 170.8604 | 7.398% | 11.42% | 11.42% | 80% | 9.14% | 8.2026 | 5.3938 | 5.3938 | 44.243 | 18.1393 | 25.89% | 25.89%
6 | 167 | 16 | 3993 | 9 | 18.9 | 239.17 | 162.78 | 401.95 | 162.78 | 81.39 | 167 | 3993 | 540 | 164.7123 | 23.2506 | 4.2853 | 514.284 | 8.6428 | 50.3577 | 43.5581 | 43.5581 | 77.5027 | 102.4973 | 53.2628 | 207.6048 | 207.6048 | 138.9414 | 346.5462 | 0.46584 | 46.58% | 156.7082 | 73.0016 | 51.1011 | 179.9003 | 179.9003 | 28.41% | 11.38% | 11.38% | 85% | 9.673% | 15.1576 | 5.1642 | 5.1642 | 78.2764 | 33.5198 | 43.51% | 43.51%
6 | 167 | 16 | 3994 | 10 | 20.1 | 275.28 | 243.81 | 519.09 | 243.81 | 121.91 | 167 | 3994 | 600 | 164.7123 | 23.2506 | 4.2853 | 574.284 | 9.6428 | 35.3577 | 53.208 | 53.208 | 62.5915 | 117.4085 | 40.4291 | 261.6657 | 261.6657 | 208.1049 | 469.7705 | 0.56018 | 56.02% | 212.4302 | 119.0001 | 83.3 | 182.6149 | 182.6149 | 45.62% | 11.35% | 11.35% | 85% | 9.648% | 20.4945 | 4.9233 | 4.9233 | 100.9011 | 45.3218 | 55.25% | 55.25%
6 | 167 | 16 | 3995 | 11 | 20.8 | 287.58 | 248.89 | 536.47 | 248.89 | 124.45 | 167 | 3995 | 660 | 164.7123 | 23.2506 | 4.2853 | 634.284 | 10.6428 | 20.3577 | 61.3504 | 61.3504 | 41.8091 | 138.1909 | 29.1635 | 286.1592 | 286.1592 | 212.4409 | 498.6001 | 0.57736 | 57.74% | 225.467 | 130.1764 | 91.1235 | 174.4425 | 174.4425 | 52.24% | 11.34% | 11.34% | 85% | 9.638% | 21.7303 | 4.7875 | 4.7875 | 104.0336 | 48.0547 | 59.64% | 59.64%
6 | 167 | 16 | 3996 | 12 | 21.4 | 32.22 | 188.75 | 220.97 | 188.75 | 94.38 | 167 | 3996 | 720 | 164.7123 | 23.2506 | 4.2853 | 694.284 | 11.6428 | 5.3577 | 66.0811 | 66.0811 | 12.2158 | 167.7842 | 22.092 | 32.6592 | 32.6592 | 161.1082 | 193.7674 | 0.22759 | 22.76% | 87.6216 | 19.9419 | 13.9593 | 147.9827 | 147.9827 | 9.433% | 11.31% | 11.31% | 80% | 9.044% | 7.9247 | 4.6738 | 4.6738 | 37.0384 | 17.5248 | 25.03% | 25.03%
6 | 167 | 16 | 3997 | 13 | 21.5 | 230.36 | 301.39 | 531.75 | 301.39 | 150.7 | 167 | 3997 | 780 | 164.7123 | 23.2506 | 4.2853 | 754.284 | 12.6428 | -9.6423 | 65.2277 | 65.2277 | 21.5478 | 201.5478 | 23.4195 | 232.8055 | 232.8055 | 257.2525 | 490.058 | 0.57653 | 57.65% | 221.6042 | 127.7626 | 89.4338 | 158.8942 | 158.8942 | 56.29% | 11.33% | 11.33% | 85% | 9.627% | 21.3349 | 4.6551 | 4.6551 | 99.3154 | 47.1802 | 62.5% | 62.5%
6 | 167 | 16 | 3998 | 14 | 22.5 | 203.61 | 347.86 | 551.47 | 347.86 | 173.93 | 167 | 3998 | 840 | 164.7123 | 23.2506 | 4.2853 | 814.284 | 13.6428 | -24.6423 | 59.2679 | 59.2679 | 48.5602 | 228.5602 | 32.1177 | 200.6235 | 200.6235 | 296.9171 | 497.5406 | 0.58433 | 58.43% | 224.9878 | 131.4662 | 92.0263 | 160.1418 | 160.1418 | 57.47% | 11.31% | 11.31% | 85% | 9.614% | 21.63 | 4.4719 | 4.4719 | 96.7266 | 47.8328 | 60.4% | 60.4%
6 | 167 | 16 | 3999 | 15 | 22.3 | 186.86 | 288.61 | 475.47 | 288.61 | 144.31 | 167 | 3999 | 900 | 164.7123 | 23.2506 | 4.2853 | 874.284 | 14.6428 | -39.6423 | 50.5498 | 50.5498 | 67.2982 | 247.2982 | 43.994 | 174.0914 | 174.0914 | 246.344 | 420.4354 | 0.54301 | 54.3% | 190.1209 | 103.237 | 72.2659 | 153.6615 | 153.6615 | 47.03% | 11.3% | 11.3% | 85% | 9.608% | 18.2676 | 4.508 | 4.508 | 82.3493 | 40.3971 | 53.59% | 53.59%
6 | 167 | 16 | 4000 | 16 | 22.3 | 295.47 | 245 | 540.47 | 245 | 122.5 | 167 | 4000 | 960 | 164.7123 | 23.2506 | 4.2853 | 934.284 | 15.6428 | -54.6423 | 40.6751 | 40.6751 | 81.1177 | 261.1177 | 57.0658 | 246.467 | 246.467 | 209.1206 | 455.5875 | 0.56314 | 56.31% | 206.0167 | 116.0172 | 81.2121 | 154.0299 | 154.0299 | 52.72% | 11.31% | 11.31% | 85% | 9.612% | 19.8027 | 4.508 | 4.508 | 89.2695 | 43.7918 | 57.96% | 57.96%
6 | 167 | 16 | 4001 | 17 | 22.2 | 284.36 | 166.67 | 451.03 | 166.67 | 83.34 | 167 | 4001 | 1020 | 164.7123 | 23.2506 | 4.2853 | 994.284 | 16.6428 | -69.6423 | 30.4342 | 30.4342 | 92.4876 | 272.4876 | 70.6267 | 186.2179 | 186.2179 | 142.2617 | 328.4797 | 0.46928 | 46.93% | 148.5385 | 69.7066 | 48.7946 | 147.1791 | 147.1791 | 33.15% | 11.29% | 11.29% | 85% | 9.601% | 14.2607 | 4.5261 | 4.5261 | 64.5455 | 31.5364 | 43.86% | 43.86%
6 | 167 | 16 | 4002 | 18 | 22.1 | 126.86 | 159.53 | 286.39 | 159.53 | 79.77 | 167 | 4002 | 1080 | 164.7123 | 23.2506 | 4.2853 | 1054.284 | 17.6428 | -84.6423 | 20.2679 | 20.2679 | 102.7994 | 282.7994 | 84.3762 | 35.8877 | 35.8877 | 136.1674 | 172.0551 | 0.16371 | 16.37% | 77.8033 | 12.7373 | 8.9161 | 134.6179 | 134.6179 | 6.623% | 11.28% | 11.28% | 80% | 9.024% | 7.0206 | 4.5443 | 4.5443 | 31.904 | 15.5255 | 23.7% | 23.7%
6 | 167 | 16 | 4003 | 19 | 21.2 | 24.25 | 75.47 | 99.72 | 75.47 | 37.74 | 167 | 4003 | 1140 | 164.7123 | 23.2506 | 4.2853 | 1114.284 | 18.6428 | -99.6423 | 10.5019 | 10.5019 | 112.8921 | 292.8921 | 98.1388 | -18.8356 | 0 | 64.4177 | 64.4177 | -0.93661 | 0% | 29.1297 | 0 | 0 | 160.3593 | 160.3593 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.7114 | 4.7114 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 4004 | 20 | 20.6 | 29.81 | 66.19 | 96 | 66.19 | 33.1 | 167 | 4004 | 1200 | 164.7123 | 23.2506 | 4.2853 | 1174.284 | 19.6428 | -114.6423 | 1.4502 | 1.4502 | 123.3446 | 303.3446 | 111.7562 | 0 | 0 | 56.4967 | 56.4967 | -1.2039 | 0% | 25.5478 | 0 | 0 | 151.3801 | 151.3801 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8259 | 4.8259 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 4005 | 21 | 18.3 | 0 | 13.89 | 13.89 | 13.89 | 6.95 | 167 | 4005 | 1260 | 164.7123 | 23.2506 | 4.2853 | 1234.284 | 20.6428 | -129.6423 | -6.5329 | 0 | 125.1996 | 305.1996 | 114.0539 | 0 | 0 | 11.8559 | 11.8559 | -9.1926 | 0% | 5.3612 | 0 | 0 | -5.0575 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 4006 | 22 | 16.5 | 0 | 0 | 0 | 0 | 0 | 167 | 4006 | 1320 | 164.7123 | 23.2506 | 4.2853 | 1294.284 | 21.6428 | -144.6423 | -13.0321 | 0 | 125.1996 | 305.1996 | 114.0539 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3054 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 4007 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 167 | 4007 | 1380 | 164.7123 | 23.2506 | 4.2853 | 1354.284 | 22.6428 | -159.6423 | -17.5928 | 0 | 125.1996 | 305.1996 | 114.0539 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9523 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
6 | 167 | 16 | 4008 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 167 | 4008 | 1440 | 164.7123 | 23.2506 | 4.2853 | 1414.284 | 23.6428 | -174.6423 | -19.804 | 0 | 125.1996 | 305.1996 | 114.0539 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8371 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4009 | 1 | 13.3 | 0 | 0 | 0 | 0 | 0 | 168 | 4009 | 60 | 165.6986 | 23.2768 | 3.8447 | 34.284 | 0.63548 | 170.4678 | -19.4167 | 0 | 125.2427 | 54.7573 | 114.0811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4741 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4010 | 2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 168 | 4010 | 120 | 165.6986 | 23.2768 | 3.8447 | 94.284 | 1.6355 | 155.4678 | -16.519 | 0 | 125.2427 | 54.7573 | 114.0811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6976 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4011 | 3 | 12.3 | 0 | 0 | 0 | 0 | 0 | 168 | 4011 | 180 | 165.6986 | 23.2768 | 3.8447 | 154.284 | 2.6355 | 140.4678 | -11.3749 | 0 | 125.2427 | 54.7573 | 114.0811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9212 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4012 | 4 | 12.2 | 0 | 0 | 0 | 0 | 0 | 168 | 4012 | 240 | 165.6986 | 23.2768 | 3.8447 | 214.284 | 3.6355 | 125.4678 | -4.4196 | 0 | 125.2427 | 54.7573 | 114.0811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0736 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4013 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 168 | 4013 | 300 | 165.6986 | 23.2768 | 3.8447 | 274.284 | 4.6355 | 110.4678 | 3.8983 | 3.8983 | 120.3892 | 59.6108 | 107.9872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.30448 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4014 | 6 | 12.1 | 4.25 | 15.75 | 20 | 15.75 | 7.88 | 168 | 4014 | 360 | 165.6986 | 23.2768 | 3.8447 | 334.284 | 5.6355 | 95.4678 | 13.1806 | 13.1806 | 110.0877 | 69.9123 | 94.3143 | -1.4021 | 0 | 13.4435 | 13.4435 | -9.0568 | 0% | 6.0791 | 0 | 0 | 13.1829 | 13.1829 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4015 | 7 | 13.3 | 16.47 | 55.75 | 72.22 | 55.75 | 27.88 | 168 | 4015 | 420 | 165.6986 | 23.2768 | 3.8447 | 394.284 | 6.6355 | 80.4678 | 23.0879 | 23.0879 | 100.0021 | 79.9979 | 80.5428 | 6.901 | 6.901 | 47.5856 | 54.4866 | -1.5783 | 0% | 24.6389 | 0 | 0 | 183.1198 | 183.1198 | 0% | 11.63% | 11.63% | 80% | 9.301% | 2.2918 | 6.4214 | 6 | 13.7505 | 5.068 | 7.509% | 7.509%
6 | 168 | 17 | 4016 | 8 | 16.8 | 33.25 | 123.81 | 157.06 | 123.81 | 61.91 | 168 | 4016 | 480 | 165.6986 | 23.2768 | 3.8447 | 454.284 | 7.6355 | 65.4678 | 33.3097 | 33.3097 | 89.4989 | 90.5011 | 66.8284 | 23.8242 | 23.8242 | 105.6784 | 129.5027 | -0.13706 | 0% | 58.5611 | 0 | 0 | 159.7399 | 159.7399 | 0% | 11.47% | 11.47% | 80% | 9.176% | 5.3736 | 5.6099 | 5.6099 | 30.1451 | 11.8832 | 18.87% | 18.87%
6 | 168 | 17 | 4017 | 9 | 18.8 | 192.69 | 172.5 | 365.19 | 172.5 | 86.25 | 168 | 4017 | 540 | 165.6986 | 23.2768 | 3.8447 | 514.284 | 8.6355 | 50.4678 | 43.5025 | 43.5025 | 77.6247 | 102.3753 | 53.3673 | 167.0209 | 167.0209 | 147.238 | 314.2589 | 0.4304 | 43.04% | 142.1079 | 61.1627 | 42.8139 | 173.8499 | 173.8499 | 24.63% | 11.38% | 11.38% | 85% | 9.676% | 13.751 | 5.1847 | 5.1847 | 71.2945 | 30.4091 | 41.01% | 41.01%
6 | 168 | 17 | 4018 | 10 | 20.5 | 360.75 | 190.47 | 551.22 | 190.47 | 95.24 | 168 | 4018 | 600 | 165.6986 | 23.2768 | 3.8447 | 574.284 | 9.6355 | 35.4678 | 53.1606 | 53.1606 | 62.7471 | 117.2529 | 40.5312 | 342.5992 | 342.5992 | 162.5763 | 505.1755 | 0.57901 | 57.9% | 228.4404 | 132.2696 | 92.5887 | 181.5903 | 181.5903 | 50.99% | 11.34% | 11.34% | 90% | 10.21% | 23.3226 | 4.8453 | 4.8453 | 113.0045 | 51.5759 | 62.23% | 62.23%
6 | 168 | 17 | 4019 | 11 | 23 | 565.64 | 160.47 | 726.11 | 160.47 | 80.24 | 168 | 4019 | 660 | 165.6986 | 23.2768 | 3.8447 | 634.284 | 10.6355 | 20.4678 | 61.3227 | 61.3227 | 42.0193 | 137.9807 | 29.2542 | 562.4961 | 562.4961 | 136.9697 | 699.4658 | 0.64929 | 64.93% | 316.2984 | 205.3692 | 143.7584 | 183.6287 | 183.6287 | 78.29% | 11.34% | 11.34% | 90% | 10.2% | 32.2684 | 4.3829 | 4.3829 | 141.429 | 71.3586 | 77.02% | 77.02%
6 | 168 | 17 | 4020 | 12 | 24.3 | 615.42 | 203.89 | 819.31 | 203.89 | 101.95 | 168 | 4020 | 720 | 165.6986 | 23.2768 | 3.8447 | 694.284 | 11.6355 | 5.4678 | 66.0909 | 66.0909 | 12.4726 | 167.5274 | 22.1428 | 623.5374 | 623.5374 | 174.031 | 797.5684 | 0.67183 | 67.18% | 360.6604 | 242.3014 | 169.611 | 272.8912 | 272.8912 | 62.15% | 11.35% | 11.35% | 90% | 10.22% | 36.8461 | 4.1598 | 4.1598 | 153.2707 | 81.4818 | 56.17% | 56.17%
6 | 168 | 17 | 4021 | 13 | 24.7 | 509.72 | 238.75 | 748.47 | 238.75 | 119.38 | 168 | 4021 | 780 | 165.6986 | 23.2768 | 3.8447 | 754.284 | 12.6355 | -9.5322 | 65.2805 | 65.2805 | 21.3323 | 201.3323 | 23.401 | 514.9847 | 514.9847 | 203.7859 | 718.7705 | 0.65853 | 65.85% | 325.028 | 214.0401 | 149.8281 | 201.3759 | 201.3759 | 74.4% | 11.33% | 11.33% | 90% | 10.2% | 33.146 | 4.0935 | 4.0935 | 135.6825 | 73.2995 | 67.38% | 67.38%
6 | 168 | 17 | 4022 | 14 | 25.6 | 239.86 | 247.64 | 487.5 | 247.64 | 123.82 | 168 | 4022 | 840 | 165.6986 | 23.2768 | 3.8447 | 814.284 | 13.6355 | -24.5322 | 59.3461 | 59.3461 | 48.4244 | 228.4244 | 32.0548 | 236.3128 | 236.3128 | 211.374 | 447.6868 | 0.57473 | 57.47% | 202.444 | 116.3502 | 81.4452 | 207.5109 | 207.5109 | 39.25% | 11.24% | 11.24% | 85% | 9.557% | 19.3475 | 3.9484 | 3.9484 | 76.3924 | 42.7853 | 36.81% | 36.81%
6 | 168 | 17 | 4023 | 15 | 26 | 447.69 | 209.17 | 656.86 | 209.17 | 104.59 | 168 | 4023 | 900 | 165.6986 | 23.2768 | 3.8447 | 874.284 | 14.6355 | -39.5322 | 50.6384 | 50.6384 | 67.2109 | 247.2109 | 43.9116 | 417.1468 | 417.1468 | 178.5378 | 595.6845 | 0.63312 | 63.31% | 269.3685 | 170.5417 | 119.3792 | 272.67 | 272.67 | 43.78% | 11.28% | 11.28% | 90% | 10.16% | 27.3574 | 3.8858 | 3.8858 | 106.3053 | 60.4984 | 38.99% | 38.99%
6 | 168 | 17 | 4024 | 16 | 25 | 563.61 | 146.58 | 710.19 | 146.58 | 73.29 | 168 | 4024 | 960 | 165.6986 | 23.2768 | 3.8447 | 934.284 | 15.6355 | -54.5322 | 40.7674 | 40.7674 | 81.0529 | 261.0529 | 56.9738 | 470.4203 | 470.4203 | 125.1139 | 595.5342 | 0.6295 | 62.95% | 269.3006 | 169.525 | 118.6675 | 263.4698 | 263.4698 | 45.04% | 11.3% | 11.3% | 90% | 10.17% | 27.3776 | 4.0445 | 4.0445 | 110.7288 | 60.5432 | 42.03% | 42.03%
6 | 168 | 17 | 4025 | 17 | 24.7 | 507.22 | 115.19 | 622.41 | 115.19 | 57.6 | 168 | 4025 | 1020 | 165.6986 | 23.2768 | 3.8447 | 994.284 | 16.6355 | -69.5322 | 30.5271 | 30.5271 | 92.4319 | 272.4319 | 70.5292 | 332.8501 | 332.8501 | 98.3208 | 431.171 | 0.5615 | 56.15% | 194.9755 | 109.4779 | 76.6345 | 190.1329 | 190.1329 | 40.31% | 11.26% | 11.26% | 85% | 9.568% | 18.6556 | 4.0935 | 4.0935 | 76.3661 | 41.2551 | 40.16% | 40.16%
6 | 168 | 17 | 4026 | 18 | 24.5 | 329.44 | 101.03 | 430.47 | 101.03 | 50.52 | 168 | 4026 | 1080 | 165.6986 | 23.2768 | 3.8447 | 1054.284 | 17.6355 | -84.5322 | 20.3595 | 20.3595 | 102.7457 | 282.7457 | 84.2752 | 94.4547 | 94.4547 | 86.2345 | 180.6892 | 0.22295 | 22.3% | 81.7077 | 18.2171 | 12.752 | 172.83 | 172.83 | 7.378% | 11.2% | 11.2% | 80% | 8.959% | 7.3202 | 4.1265 | 4.1265 | 30.2065 | 16.1879 | 17.48% | 17.48%
6 | 168 | 17 | 4027 | 19 | 23.9 | 190.64 | 75.92 | 266.56 | 75.92 | 37.96 | 168 | 4027 | 1140 | 165.6986 | 23.2768 | 3.8447 | 1114.284 | 18.6355 | -99.5322 | 10.5905 | 10.5905 | 112.8356 | 292.8356 | 98.0356 | -145 | 0 | 64.8018 | 64.8018 | -0.83601 | 0% | 29.3034 | 0 | 0 | 147.8183 | 147.8183 | 0% | 11.19% | 0% | 80% | 0% | 0 | 4.2272 | 4.2272 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4028 | 20 | 22.6 | 62.58 | 52.97 | 115.55 | 52.97 | 26.49 | 168 | 4028 | 1200 | 165.6986 | 23.2768 | 3.8447 | 1174.284 | 19.6355 | -114.5322 | 1.5338 | 1.5338 | 123.2818 | 303.2818 | 111.6518 | 0 | 0 | 45.2127 | 45.2127 | -1.6086 | 0% | 20.4452 | 0 | 0 | 155.1614 | 155.1614 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4539 | 4.4539 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4029 | 21 | 21.3 | 0 | 13.69 | 13.69 | 13.69 | 6.85 | 168 | 4029 | 1260 | 165.6986 | 23.2768 | 3.8447 | 1234.284 | 20.6355 | -129.5322 | -6.4569 | 0 | 125.2427 | 305.2427 | 114.0811 | 0 | 0 | 11.6851 | 11.6851 | -8.7729 | 0% | 5.284 | 0 | 0 | -2.1319 | 0 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.6926 | 4.6926 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4030 | 22 | 20.5 | 0 | 0 | 0 | 0 | 0 | 168 | 4030 | 1320 | 165.6986 | 23.2768 | 3.8447 | 1294.284 | 21.6355 | -144.5322 | -12.9669 | 0 | 125.2427 | 305.2427 | 114.0811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.1167 | 0 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8453 | 4.8453 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4031 | 23 | 19.5 | 0 | 0 | 0 | 0 | 0 | 168 | 4031 | 1380 | 165.6986 | 23.2768 | 3.8447 | 1354.284 | 22.6355 | -159.5322 | -17.5421 | 0 | 125.2427 | 305.2427 | 114.0811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.1022 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0425 | 5.0425 | 0 | 0 | 0% | 0%
6 | 168 | 17 | 4032 | 24 | 18.5 | 0 | 0 | 0 | 0 | 0 | 168 | 4032 | 1440 | 165.6986 | 23.2768 | 3.8447 | 1414.284 | 23.6355 | -174.5322 | -19.7708 | 0 | 125.2427 | 305.2427 | 114.0811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0878 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4033 | 1 | 18.5 | 0 | 0 | 0 | 0 | 0 | 169 | 4033 | 60 | 166.6849 | 23.2964 | 3.4018 | 34.284 | 0.6281 | 170.5785 | -19.4094 | 0 | 125.2749 | 54.7251 | 114.1015 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.0331 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4034 | 2 | 17.5 | 0 | 0 | 0 | 0 | 0 | 169 | 4034 | 120 | 166.6849 | 23.2964 | 3.4018 | 94.284 | 1.6281 | 155.5785 | -16.5303 | 0 | 125.2749 | 54.7251 | 114.1015 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7006 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4035 | 3 | 16.7 | 0 | 0 | 0 | 0 | 0 | 169 | 4035 | 180 | 166.6849 | 23.2964 | 3.4018 | 154.284 | 2.6281 | 140.5785 | -11.4026 | 0 | 125.2749 | 54.7251 | 114.1015 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.0634 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4036 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 169 | 4036 | 240 | 166.6849 | 23.2964 | 3.4018 | 214.284 | 3.6281 | 125.5785 | -4.4602 | 0 | 125.2749 | 54.7251 | 114.1015 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.1302 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4037 | 5 | 15.3 | 0 | 0 | 0 | 0 | 0 | 169 | 4037 | 300 | 166.6849 | 23.2964 | 3.4018 | 274.284 | 4.6281 | 110.5785 | 3.8479 | 3.8479 | 120.4799 | 59.5201 | 108.0838 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 13.3926 | 13.3926 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4038 | 6 | 15.3 | 7.86 | 14.72 | 22.58 | 14.72 | 7.36 | 169 | 4038 | 360 | 166.6849 | 23.2964 | 3.4018 | 334.284 | 5.6281 | 95.5785 | 13.1234 | 13.1234 | 110.1764 | 69.8236 | 94.4145 | -2.6646 | 0 | 12.5643 | 12.5643 | -9.1647 | 0% | 5.6816 | 0 | 0 | 30.2114 | 30.2114 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4039 | 7 | 15.3 | 76.39 | 55 | 131.39 | 55 | 27.5 | 169 | 4039 | 420 | 166.6849 | 23.2964 | 3.4018 | 394.284 | 6.6281 | 80.5785 | 23.0265 | 23.0265 | 100.0928 | 79.9072 | 80.6452 | 31.7443 | 31.7443 | 46.9454 | 78.6898 | -0.7877 | 0% | 35.5835 | 0 | 0 | 207.9972 | 207.9972 | 0% | 11.54% | 11.54% | 80% | 9.231% | 3.2846 | 5.9472 | 5.9472 | 19.5342 | 7.2637 | 9.392% | 9.392%
6 | 169 | 18 | 4040 | 8 | 16.2 | 222.42 | 87.97 | 310.39 | 87.97 | 43.99 | 169 | 4040 | 480 | 166.6849 | 23.2964 | 3.4018 | 454.284 | 7.6281 | 65.5785 | 33.247 | 33.247 | 89.5974 | 90.4026 | 66.9319 | 158.9604 | 158.9604 | 75.0871 | 234.0475 | 0.27753 | 27.75% | 105.8363 | 29.3732 | 20.5612 | 187.0117 | 187.0117 | 10.99% | 11.47% | 11.47% | 80% | 9.176% | 9.7118 | 5.7429 | 5.7429 | 55.7738 | 21.4767 | 29.82% | 29.82%
6 | 169 | 18 | 4041 | 9 | 17.4 | 341.67 | 116.11 | 457.78 | 116.11 | 58.06 | 169 | 4041 | 540 | 166.6849 | 23.2964 | 3.4018 | 514.284 | 8.6281 | 50.5785 | 43.4418 | 43.4418 | 77.7404 | 102.2596 | 53.4704 | 295.7672 | 295.7672 | 99.1061 | 394.8733 | 0.49877 | 49.88% | 178.5617 | 89.062 | 62.3434 | 195.505 | 195.505 | 31.89% | 11.41% | 11.41% | 85% | 9.698% | 17.3177 | 5.4794 | 5.4794 | 94.8903 | 38.2966 | 48.54% | 48.54%
6 | 169 | 18 | 4042 | 10 | 17.8 | 368.53 | 143.33 | 511.86 | 143.33 | 71.67 | 169 | 4042 | 600 | 166.6849 | 23.2964 | 3.4018 | 574.284 | 9.6281 | 35.5785 | 53.1078 | 53.1078 | 62.8956 | 117.1044 | 40.6308 | 349.7084 | 349.7084 | 122.3398 | 472.0482 | 0.55057 | 55.06% | 213.4602 | 117.5244 | 82.2671 | 192.2545 | 192.2545 | 42.79% | 11.39% | 11.39% | 85% | 9.683% | 20.6692 | 5.3938 | 5.3938 | 111.4851 | 45.7081 | 57.99% | 57.99%
6 | 169 | 18 | 4043 | 11 | 19.5 | 440.28 | 122.42 | 562.7 | 122.42 | 61.21 | 169 | 4043 | 660 | 166.6849 | 23.2964 | 3.4018 | 634.284 | 10.6281 | 20.5785 | 61.2889 | 61.2889 | 42.2232 | 137.7768 | 29.3407 | 437.6037 | 437.6037 | 104.492 | 542.0958 | 0.59027 | 59.03% | 245.1357 | 144.6974 | 101.2882 | 184.0671 | 184.0671 | 55.03% | 11.36% | 11.36% | 90% | 10.22% | 25.0607 | 5.0425 | 5.0425 | 126.3678 | 55.4194 | 68.65% | 68.65%
6 | 169 | 18 | 4044 | 12 | 20.7 | 354.86 | 118.61 | 473.47 | 118.61 | 59.31 | 169 | 4044 | 720 | 166.6849 | 23.2964 | 3.4018 | 694.284 | 11.6281 | 5.5785 | 66.0937 | 66.0937 | 12.7281 | 167.2719 | 22.1877 | 359.4181 | 359.4181 | 101.24 | 460.6581 | 0.55822 | 55.82% | 208.3096 | 116.2828 | 81.398 | 164.1977 | 164.1977 | 49.57% | 11.34% | 11.34% | 85% | 9.638% | 20.0771 | 4.8067 | 4.8067 | 96.504 | 44.3987 | 58.77% | 58.77%
6 | 169 | 18 | 4045 | 13 | 19.9 | 181.86 | 196.19 | 378.05 | 196.19 | 98.1 | 169 | 4045 | 780 | 166.6849 | 23.2964 | 3.4018 | 754.284 | 12.6281 | -9.4215 | 65.3268 | 65.3268 | 21.1105 | 201.1105 | 23.3766 | 183.7038 | 183.7038 | 167.4586 | 351.1624 | 0.47658 | 47.66% | 158.7957 | 75.6788 | 52.9752 | 155.4017 | 155.4017 | 34.09% | 11.35% | 11.35% | 85% | 9.651% | 15.3258 | 4.9628 | 4.9628 | 76.0584 | 33.8917 | 48.94% | 48.94%
6 | 169 | 18 | 4046 | 14 | 19.9 | 230.28 | 278.61 | 508.89 | 278.61 | 139.31 | 169 | 4046 | 840 | 166.6849 | 23.2964 | 3.4018 | 814.284 | 13.6281 | -24.4215 | 59.4191 | 59.4191 | 48.28 | 228.28 | 31.9876 | 226.87 | 226.87 | 237.8085 | 464.6785 | 0.55657 | 55.66% | 210.1276 | 116.9497 | 81.8648 | 158.5163 | 158.5163 | 51.64% | 11.35% | 11.35% | 85% | 9.651% | 20.2789 | 4.9628 | 4.9628 | 100.6393 | 44.845 | 63.49% | 63.49%
6 | 169 | 18 | 4047 | 15 | 20.7 | 320 | 296.19 | 616.19 | 296.19 | 148.1 | 169 | 4047 | 900 | 166.6849 | 23.2964 | 3.4018 | 874.284 | 14.6281 | -39.4215 | 50.7225 | 50.7225 | 67.1155 | 247.1155 | 43.8261 | 298.2372 | 298.2372 | 252.814 | 551.0512 | 0.59854 | 59.85% | 249.1853 | 149.1469 | 104.4028 | 160.4693 | 160.4693 | 65.06% | 11.34% | 11.34% | 90% | 10.21% | 25.4373 | 4.8067 | 4.8067 | 122.2687 | 56.2523 | 76.19% | 76.19%
6 | 169 | 18 | 4048 | 16 | 20.9 | 184.36 | 225.83 | 410.19 | 225.83 | 112.92 | 169 | 4048 | 960 | 166.6849 | 23.2964 | 3.4018 | 934.284 | 15.6281 | -54.4215 | 40.8556 | 40.8556 | 80.9811 | 260.9811 | 56.8798 | 153.9908 | 153.9908 | 192.758 | 346.7488 | 0.47874 | 47.87% | 156.7998 | 75.067 | 52.5469 | 148.3342 | 148.3342 | 35.42% | 11.33% | 11.33% | 85% | 9.63% | 15.1 | 4.7684 | 4.7684 | 72.0023 | 33.3924 | 48.54% | 48.54%
6 | 169 | 18 | 4049 | 17 | 20.3 | 208.42 | 168.25 | 376.67 | 168.25 | 84.13 | 169 | 4049 | 1020 | 166.6849 | 23.2964 | 3.4018 | 994.284 | 16.6281 | -69.4215 | 30.6159 | 30.6159 | 92.3701 | 272.3701 | 70.4305 | 137.0764 | 137.0764 | 143.6104 | 280.6867 | 0.3975 | 39.75% | 126.9265 | 50.4539 | 35.3177 | 142.4456 | 142.4456 | 24.79% | 11.34% | 11.34% | 80% | 9.075% | 11.5183 | 4.8842 | 4.8842 | 56.257 | 25.4716 | 39.49% | 39.49%
6 | 169 | 18 | 4050 | 18 | 19.5 | 149.72 | 106.39 | 256.11 | 106.39 | 53.2 | 169 | 4050 | 1080 | 166.6849 | 23.2964 | 3.4018 | 1054.284 | 17.6281 | -84.4215 | 20.4469 | 20.4469 | 102.6864 | 282.6864 | 84.1737 | 43.5064 | 43.5064 | 90.8095 | 134.3159 | -0.058591 | 0% | 60.7377 | 0 | 0 | 130.6846 | 130.6846 | 0% | 11.37% | 11.37% | 80% | 9.096% | 5.5248 | 5.0425 | 5.0425 | 27.8589 | 12.2177 | 21.32% | 21.32%
6 | 169 | 18 | 4051 | 19 | 19 | 58.69 | 104.81 | 163.5 | 104.81 | 52.41 | 169 | 4051 | 1140 | 166.6849 | 23.2964 | 3.4018 | 1114.284 | 18.6281 | -99.4215 | 10.6746 | 10.6746 | 112.7742 | 292.7742 | 97.9325 | -43.727 | 0 | 89.4609 | 89.4609 | -0.50344 | 0% | 40.4542 | 0 | 0 | 119.9272 | 119.9272 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4052 | 20 | 19 | 32.78 | 53.33 | 86.11 | 53.33 | 26.67 | 169 | 4052 | 1200 | 166.6849 | 23.2964 | 3.4018 | 1174.284 | 19.6281 | -114.4215 | 1.6125 | 1.6125 | 123.2145 | 303.2145 | 111.5482 | 0 | 0 | 45.52 | 45.52 | -1.7655 | 0% | 20.5841 | 0 | 0 | 149.4129 | 149.4129 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4053 | 21 | 17.9 | 0 | 9.36 | 9.36 | 9.36 | 4.68 | 169 | 4053 | 1260 | 166.6849 | 23.2964 | 3.4018 | 1234.284 | 20.6281 | -129.4215 | -6.3862 | 0 | 125.2749 | 305.2749 | 114.1015 | 0 | 0 | 7.9893 | 7.9893 | -14.1422 | 0% | 3.6127 | 0 | 0 | -5.1185 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4054 | 22 | 17.6 | 0 | 0 | 0 | 0 | 0 | 169 | 4054 | 1320 | 166.6849 | 23.2964 | 3.4018 | 1294.284 | 21.6281 | -144.4215 | -12.9075 | 0 | 125.2749 | 305.2749 | 114.1015 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9741 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4055 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 169 | 4055 | 1380 | 166.6849 | 23.2964 | 3.4018 | 1354.284 | 22.6281 | -159.4215 | -17.4975 | 0 | 125.2749 | 305.2749 | 114.1015 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.556 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
6 | 169 | 18 | 4056 | 24 | 14.6 | 0 | 0 | 0 | 0 | 0 | 169 | 4056 | 1440 | 166.6849 | 23.2964 | 3.4018 | 1414.284 | 23.6281 | -174.4215 | -19.7442 | 0 | 125.2749 | 305.2749 | 114.1015 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8331 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4057 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 170 | 4057 | 60 | 167.6712 | 23.3094 | 2.9571 | 34.284 | 0.62069 | 170.6897 | -19.4086 | 0 | 125.2962 | 54.7038 | 114.115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6961 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4058 | 2 | 13.5 | 0 | 0 | 0 | 0 | 0 | 170 | 4058 | 120 | 167.6712 | 23.3094 | 2.9571 | 94.284 | 1.6207 | 155.6897 | -16.548 | 0 | 125.2962 | 54.7038 | 114.115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8995 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4059 | 3 | 13.5 | 0 | 0 | 0 | 0 | 0 | 170 | 4059 | 180 | 167.6712 | 23.3094 | 2.9571 | 154.284 | 2.6207 | 140.6897 | -11.4362 | 0 | 125.2962 | 54.7038 | 114.115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.341 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4060 | 4 | 12.6 | 0 | 0 | 0 | 0 | 0 | 170 | 4060 | 240 | 167.6712 | 23.3094 | 2.9571 | 214.284 | 3.6207 | 125.6897 | -4.5064 | 0 | 125.2962 | 54.7038 | 114.115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7126 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4061 | 5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 170 | 4061 | 300 | 167.6712 | 23.3094 | 2.9571 | 274.284 | 4.6207 | 110.6897 | 3.7923 | 3.7923 | 120.5666 | 59.4334 | 108.1821 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.3981 | 1.3981 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4062 | 6 | 12.6 | 4.92 | 16.19 | 21.11 | 16.19 | 8.1 | 170 | 4062 | 360 | 167.6712 | 23.3094 | 2.9571 | 334.284 | 5.6207 | 95.6897 | 13.0612 | 13.0612 | 110.2606 | 69.7394 | 94.5155 | -1.714 | 0 | 13.819 | 13.819 | -8.7055 | 0% | 6.249 | 0 | 0 | 14.896 | 14.896 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4063 | 7 | 13.3 | 49.81 | 50.08 | 99.89 | 50.08 | 25.04 | 170 | 4063 | 420 | 167.6712 | 23.3094 | 2.9571 | 394.284 | 6.6207 | 80.6897 | 22.9604 | 22.9604 | 100.1784 | 79.8216 | 80.7477 | 20.5298 | 20.5298 | 42.746 | 63.2757 | -1.2474 | 0% | 28.6133 | 0 | 0 | 185.4573 | 185.4573 | 0% | 11.62% | 11.62% | 80% | 9.299% | 2.6607 | 6.4214 | 6 | 15.9641 | 5.8839 | 8.608% | 8.608%
6 | 170 | 19 | 4064 | 8 | 15.2 | 149.44 | 60.56 | 210 | 60.56 | 30.28 | 170 | 4064 | 480 | 167.6712 | 23.3094 | 2.9571 | 454.284 | 7.6207 | 65.6897 | 33.1795 | 33.1795 | 89.6903 | 90.3097 | 67.0348 | 106.5436 | 106.5436 | 51.6912 | 158.2348 | 0.011022 | 1.102% | 71.5538 | 0.7887 | 0.55209 | 160.6321 | 160.6321 | 0.3437% | 11.52% | 11.52% | 80% | 9.217% | 6.5952 | 5.9702 | 5.9702 | 39.3747 | 14.5847 | 24.51% | 24.51%
6 | 170 | 19 | 4065 | 9 | 15.9 | 235.47 | 96.19 | 331.66 | 96.19 | 48.1 | 170 | 4065 | 540 | 167.6712 | 23.3094 | 2.9571 | 514.284 | 8.6207 | 50.6897 | 43.3763 | 43.3763 | 77.8497 | 102.1503 | 53.5721 | 203.5923 | 203.5923 | 82.1033 | 285.6956 | 0.37034 | 37.03% | 129.1915 | 47.845 | 33.4915 | 167.7742 | 167.7742 | 19.96% | 11.47% | 11.47% | 80% | 9.174% | 11.8525 | 5.8104 | 5.8104 | 68.8674 | 26.2108 | 41.05% | 41.05%
6 | 170 | 19 | 4066 | 10 | 16.8 | 235.47 | 140.56 | 376.03 | 140.56 | 70.28 | 170 | 4066 | 600 | 167.6712 | 23.3094 | 2.9571 | 574.284 | 9.6207 | 35.6897 | 53.0497 | 53.0497 | 63.037 | 116.963 | 40.7279 | 223.2892 | 223.2892 | 119.9755 | 343.2647 | 0.44897 | 44.9% | 155.2243 | 69.691 | 48.7837 | 167.832 | 167.832 | 29.07% | 11.43% | 11.43% | 85% | 9.718% | 15.084 | 5.6099 | 5.6099 | 84.6192 | 33.3568 | 50.42% | 50.42%
6 | 170 | 19 | 4067 | 11 | 17.6 | 342.78 | 162.69 | 505.47 | 162.69 | 81.35 | 170 | 4067 | 660 | 167.6712 | 23.3094 | 2.9571 | 634.284 | 10.6207 | 20.6897 | 61.2488 | 61.2488 | 42.4204 | 137.5796 | 29.423 | 340.5514 | 340.5514 | 138.8646 | 479.416 | 0.55353 | 55.35% | 216.7919 | 120.0012 | 84.0008 | 165.9889 | 165.9889 | 50.61% | 11.39% | 11.39% | 85% | 9.685% | 20.9967 | 5.4364 | 5.4364 | 114.1471 | 46.4323 | 68.77% | 68.77%
6 | 170 | 19 | 4068 | 12 | 18.1 | 379.58 | 209.31 | 588.89 | 209.31 | 104.66 | 170 | 4068 | 720 | 167.6712 | 23.3094 | 2.9571 | 694.284 | 11.6207 | 5.6897 | 66.0895 | 66.0895 | 12.9818 | 167.0182 | 22.2267 | 384.3612 | 384.3612 | 178.6573 | 563.0184 | 0.5927 | 59.27% | 254.5969 | 150.9006 | 105.6304 | 157.6528 | 157.6528 | 67% | 11.38% | 11.38% | 90% | 10.24% | 26.0684 | 5.3303 | 5.3303 | 138.9528 | 57.648 | 88.14% | 88.14%
6 | 170 | 19 | 4069 | 13 | 18.5 | 316.11 | 245.56 | 561.67 | 245.56 | 122.78 | 170 | 4069 | 780 | 167.6712 | 23.3094 | 2.9571 | 754.284 | 12.6207 | -9.3103 | 65.3666 | 65.3666 | 20.883 | 200.883 | 23.3466 | 319.2856 | 319.2856 | 209.5986 | 528.8842 | 0.58075 | 58.07% | 239.1614 | 138.8927 | 97.2249 | 155.2387 | 155.2387 | 62.63% | 11.37% | 11.37% | 90% | 10.24% | 24.4828 | 5.2467 | 5.2467 | 128.4532 | 54.1415 | 82.75% | 82.75%
6 | 170 | 19 | 4070 | 14 | 20.9 | 563.33 | 265.97 | 829.3 | 265.97 | 132.99 | 170 | 4070 | 840 | 167.6712 | 23.3094 | 2.9571 | 814.284 | 13.6207 | -24.3103 | 59.4866 | 59.4866 | 48.1272 | 228.1272 | 31.9162 | 555.0337 | 555.0337 | 227.0196 | 782.0533 | 0.65979 | 65.98% | 353.6445 | 233.3302 | 163.3311 | 168.5644 | 168.5644 | 96.9% | 11.35% | 11.35% | 90% | 10.22% | 36.1283 | 4.7684 | 4.7684 | 172.2727 | 79.8946 | 102.2% | 102.2%
6 | 170 | 19 | 4071 | 15 | 21.8 | 597.22 | 178.47 | 775.69 | 178.47 | 89.24 | 170 | 4071 | 900 | 167.6712 | 23.3094 | 2.9571 | 874.284 | 14.6207 | -39.3103 | 50.8021 | 50.8021 | 67.0122 | 247.0122 | 43.7378 | 556.7955 | 556.7955 | 152.3337 | 709.1292 | 0.64773 | 64.77% | 320.6682 | 207.7056 | 145.3939 | 165.3332 | 165.3332 | 87.94% | 11.34% | 11.34% | 90% | 10.21% | 32.7361 | 4.5994 | 4.5994 | 150.5656 | 72.3929 | 91.07% | 91.07%
6 | 170 | 19 | 4072 | 16 | 21.7 | 472.03 | 151.58 | 623.61 | 151.58 | 75.79 | 170 | 4072 | 960 | 167.6712 | 23.3094 | 2.9571 | 934.284 | 15.6207 | -54.3103 | 40.9395 | 40.9395 | 80.9023 | 260.9023 | 56.7838 | 394.6172 | 394.6172 | 129.3816 | 523.9988 | 0.5921 | 59.21% | 236.9523 | 140.2995 | 98.2097 | 157.205 | 157.205 | 62.47% | 11.33% | 11.33% | 90% | 10.19% | 24.1539 | 4.6179 | 4.6179 | 111.5397 | 53.4142 | 70.95% | 70.95%
6 | 170 | 19 | 4073 | 17 | 21.8 | 363.06 | 162.42 | 525.48 | 162.42 | 81.21 | 170 | 4073 | 1020 | 167.6712 | 23.3094 | 2.9571 | 994.284 | 16.6207 | -69.3103 | 30.7006 | 30.7006 | 92.3021 | 272.3021 | 70.3306 | 239.3548 | 239.3548 | 138.6341 | 377.9889 | 0.51082 | 51.08% | 170.9266 | 87.3133 | 61.1193 | 150.5906 | 150.5906 | 40.59% | 11.31% | 11.31% | 85% | 9.614% | 16.4323 | 4.5994 | 4.5994 | 75.5786 | 36.3387 | 50.19% | 50.19%
6 | 170 | 19 | 4074 | 18 | 21.3 | 254.17 | 101.31 | 355.48 | 101.31 | 50.66 | 170 | 4074 | 1080 | 167.6712 | 23.3094 | 2.9571 | 1054.284 | 17.6207 | -84.3103 | 20.5301 | 20.5301 | 102.6217 | 282.6217 | 84.0718 | 74.8546 | 74.8546 | 86.4735 | 161.3281 | 0.11034 | 11.03% | 72.9526 | 8.0493 | 5.6345 | 137.5668 | 137.5668 | 4.096% | 11.31% | 11.31% | 80% | 9.045% | 6.5986 | 4.6926 | 4.6926 | 30.9643 | 14.5922 | 22.51% | 22.51%
6 | 170 | 19 | 4075 | 19 | 20.6 | 141.19 | 74.17 | 215.36 | 74.17 | 37.09 | 170 | 4075 | 1140 | 167.6712 | 23.3094 | 2.9571 | 1114.284 | 18.6207 | -99.3103 | 10.7542 | 10.7542 | 112.7078 | 292.7078 | 97.8296 | -103.0782 | 0 | 63.3081 | 63.3081 | -0.98786 | 0% | 28.6279 | 0 | 0 | 124.4398 | 124.4398 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8259 | 4.8259 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4076 | 20 | 20.2 | 51.58 | 53.53 | 105.11 | 53.53 | 26.77 | 170 | 4076 | 1200 | 167.6712 | 23.3094 | 2.9571 | 1174.284 | 19.6207 | -114.3103 | 1.6863 | 1.6863 | 123.1427 | 303.1427 | 111.4456 | 0 | 0 | 45.6907 | 45.6907 | -1.698 | 0% | 20.6613 | 0 | 0 | 151.7788 | 151.7788 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.9037 | 4.9037 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4077 | 21 | 19.5 | 0 | 9.36 | 9.36 | 9.36 | 4.68 | 170 | 4077 | 1260 | 167.6712 | 23.3094 | 2.9571 | 1234.284 | 20.6207 | -129.3103 | -6.3208 | 0 | 125.2962 | 305.2962 | 114.115 | 0 | 0 | 7.9893 | 7.9893 | -13.6979 | 0% | 3.6127 | 0 | 0 | -3.6499 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0425 | 5.0425 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4078 | 22 | 18.8 | 0 | 0 | 0 | 0 | 0 | 170 | 4078 | 1320 | 167.6712 | 23.3094 | 2.9571 | 1294.284 | 21.6207 | -144.3103 | -12.8539 | 0 | 125.2962 | 305.2962 | 114.115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.0564 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4079 | 23 | 18 | 0 | 0 | 0 | 0 | 0 | 170 | 4079 | 1380 | 167.6712 | 23.3094 | 2.9571 | 1354.284 | 22.6207 | -159.3103 | -17.4591 | 0 | 125.2962 | 305.2962 | 114.115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7171 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
6 | 170 | 19 | 4080 | 24 | 17.5 | 0 | 0 | 0 | 0 | 0 | 170 | 4080 | 1440 | 167.6712 | 23.3094 | 2.9571 | 1414.284 | 23.6207 | -174.3103 | -19.7239 | 0 | 125.2962 | 305.2962 | 114.115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9206 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4081 | 1 | 17.1 | 0 | 0 | 0 | 0 | 0 | 171 | 4081 | 60 | 168.6575 | 23.3157 | 2.5109 | 34.284 | 0.61325 | 170.8013 | -19.4142 | 0 | 125.3066 | 54.6934 | 114.1215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7289 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4082 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 171 | 4082 | 120 | 168.6575 | 23.3157 | 2.5109 | 94.284 | 1.6132 | 155.8013 | -16.5721 | 0 | 125.3066 | 54.6934 | 114.1215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7519 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4083 | 3 | 14.8 | 0 | 0 | 0 | 0 | 0 | 171 | 4083 | 180 | 168.6575 | 23.3157 | 2.5109 | 154.284 | 2.6132 | 140.8013 | -11.4758 | 0 | 125.3066 | 54.6934 | 114.1215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9274 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4084 | 4 | 15.5 | 0 | 0 | 0 | 0 | 0 | 171 | 4084 | 240 | 168.6575 | 23.3157 | 2.5109 | 214.284 | 3.6132 | 125.8013 | -4.5583 | 0 | 125.3066 | 54.6934 | 114.1215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8606 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4085 | 5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 171 | 4085 | 300 | 168.6575 | 23.3157 | 2.5109 | 274.284 | 4.6132 | 110.8013 | 3.7314 | 3.7314 | 120.6494 | 59.3506 | 108.2817 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.537 | 8.537 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4086 | 6 | 14.5 | 6.19 | 18.89 | 25.08 | 18.89 | 9.45 | 171 | 4086 | 360 | 168.6575 | 23.3157 | 2.5109 | 334.284 | 5.6132 | 95.8013 | 12.9941 | 12.9941 | 110.3403 | 69.6597 | 94.6172 | -2.2161 | 0 | 16.1236 | 16.1236 | -7.0767 | 0% | 7.2911 | 0 | 0 | 21.7201 | 21.7201 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4087 | 7 | 13.5 | 53.53 | 63.53 | 117.06 | 63.53 | 31.77 | 171 | 4087 | 420 | 168.6575 | 23.3157 | 2.5109 | 394.284 | 6.6132 | 80.8013 | 22.8895 | 22.8895 | 100.259 | 79.741 | 80.8503 | 21.8844 | 21.8844 | 54.2262 | 76.1106 | -0.89546 | 0% | 34.4172 | 0 | 0 | 193.2204 | 193.2204 | 0% | 11.61% | 11.61% | 80% | 9.289% | 3.1969 | 6.3727 | 6 | 19.1813 | 7.0696 | 9.927% | 9.927%
6 | 171 | 20 | 4088 | 8 | 13.5 | 173.42 | 116.19 | 289.61 | 116.19 | 58.1 | 171 | 4088 | 480 | 168.6575 | 23.3157 | 2.5109 | 454.284 | 7.6132 | 65.8013 | 33.1073 | 33.1073 | 89.7774 | 90.2226 | 67.137 | 123.357 | 123.357 | 99.1744 | 222.5313 | 0.22275 | 22.27% | 100.6287 | 22.4147 | 15.6903 | 169.2433 | 169.2433 | 9.271% | 11.56% | 11.56% | 80% | 9.247% | 9.3049 | 6.3727 | 6 | 55.8293 | 20.5769 | 32.99% | 32.99%
6 | 171 | 20 | 4089 | 9 | 15.2 | 247.58 | 142.5 | 390.08 | 142.5 | 71.25 | 171 | 4089 | 540 | 168.6575 | 23.3157 | 2.5109 | 514.284 | 8.6132 | 50.8013 | 43.3059 | 43.3059 | 77.9524 | 102.0476 | 53.6724 | 213.8332 | 213.8332 | 121.6314 | 335.4646 | 0.42996 | 43% | 151.6971 | 65.2239 | 45.6567 | 176.6428 | 176.6428 | 25.85% | 11.47% | 11.47% | 85% | 9.753% | 14.7957 | 5.9702 | 5.9702 | 88.3332 | 32.7193 | 50.01% | 50.01%
6 | 171 | 20 | 4090 | 10 | 15.7 | 454.81 | 151.11 | 605.92 | 151.11 | 75.56 | 171 | 4090 | 600 | 168.6575 | 23.3157 | 2.5109 | 574.284 | 9.6132 | 35.8013 | 52.9863 | 52.9863 | 63.1712 | 116.8288 | 40.8223 | 431.0292 | 431.0292 | 128.9805 | 560.0097 | 0.58196 | 58.2% | 253.2364 | 147.3729 | 103.1611 | 182.5943 | 182.5943 | 56.5% | 11.41% | 11.41% | 90% | 10.27% | 26.002 | 5.8557 | 5.8557 | 152.2593 | 57.5011 | 83.39% | 83.39%
6 | 171 | 20 | 4091 | 11 | 16.5 | 597.97 | 155 | 752.97 | 155 | 77.5 | 171 | 4091 | 660 | 168.6575 | 23.3157 | 2.5109 | 634.284 | 10.6132 | 20.8013 | 61.2026 | 61.2026 | 42.6108 | 137.3892 | 29.5011 | 593.8874 | 593.8874 | 132.3008 | 726.1882 | 0.63525 | 63.53% | 328.3823 | 208.6054 | 146.0238 | 179.3386 | 179.3386 | 81.42% | 11.37% | 11.37% | 90% | 10.23% | 33.5922 | 5.6761 | 5.6761 | 190.6716 | 74.2861 | 106.3% | 106.3%
6 | 171 | 20 | 4092 | 12 | 17.7 | 551.58 | 172.14 | 723.72 | 172.14 | 86.07 | 171 | 4092 | 720 | 168.6575 | 23.3157 | 2.5109 | 694.284 | 11.6132 | 5.8013 | 66.0784 | 66.0784 | 13.2335 | 166.7665 | 22.2599 | 558.4432 | 558.4432 | 146.9307 | 705.3739 | 0.63408 | 63.41% | 318.9701 | 202.2534 | 141.5774 | 164.7527 | 164.7527 | 85.93% | 11.36% | 11.36% | 90% | 10.23% | 32.6229 | 5.4151 | 5.4151 | 176.6554 | 72.1426 | 107.2% | 107.2%
6 | 171 | 20 | 4093 | 13 | 18.3 | 535.56 | 184.64 | 720.2 | 184.64 | 92.32 | 171 | 4093 | 780 | 168.6575 | 23.3157 | 2.5109 | 754.284 | 12.6132 | -9.1987 | 65.3998 | 65.3998 | 20.6498 | 200.6498 | 23.3108 | 540.9423 | 540.9423 | 157.6001 | 698.5424 | 0.63433 | 63.43% | 315.8809 | 200.3741 | 140.2619 | 162.5994 | 162.5994 | 86.26% | 11.36% | 11.36% | 90% | 10.23% | 32.2999 | 5.2884 | 5.2884 | 170.8133 | 71.4283 | 105.1% | 105.1%
6 | 171 | 20 | 4094 | 14 | 19.1 | 517.86 | 155 | 672.86 | 155 | 77.5 | 171 | 4094 | 840 | 168.6575 | 23.3157 | 2.5109 | 814.284 | 13.6132 | -24.1987 | 59.5487 | 59.5487 | 47.966 | 227.966 | 31.8405 | 510.3269 | 510.3269 | 132.3008 | 642.6277 | 0.62233 | 62.23% | 290.5963 | 180.8478 | 126.5935 | 160.5768 | 160.5768 | 78.84% | 11.36% | 11.36% | 90% | 10.22% | 29.71 | 5.1233 | 5.1233 | 152.2137 | 65.701 | 94.79% | 94.79%
6 | 171 | 20 | 4095 | 15 | 18.3 | 450 | 176.58 | 626.58 | 176.58 | 88.29 | 171 | 4095 | 900 | 168.6575 | 23.3157 | 2.5109 | 874.284 | 14.6132 | -39.1987 | 50.877 | 50.877 | 66.9011 | 246.9011 | 43.6465 | 419.7321 | 419.7321 | 150.7205 | 570.4526 | 0.59624 | 59.62% | 257.9587 | 153.8047 | 107.6633 | 155.5093 | 155.5093 | 69.23% | 11.37% | 11.37% | 90% | 10.24% | 26.4049 | 5.2884 | 5.2884 | 139.6387 | 58.3922 | 89.79% | 89.79%
6 | 171 | 20 | 4096 | 16 | 18.1 | 582.14 | 143.42 | 725.56 | 143.42 | 71.71 | 171 | 4096 | 960 | 168.6575 | 23.3157 | 2.5109 | 934.284 | 15.6132 | -54.1987 | 41.0192 | 41.0192 | 80.8167 | 260.8167 | 56.686 | 487.1569 | 487.1569 | 122.4166 | 609.5736 | 0.60884 | 60.88% | 275.6492 | 167.8266 | 117.4786 | 157.7476 | 157.7476 | 74.47% | 11.37% | 11.37% | 90% | 10.23% | 28.2119 | 5.3303 | 5.3303 | 150.3783 | 62.3881 | 95.33% | 95.33%
6 | 171 | 20 | 4097 | 17 | 18.9 | 438.61 | 131.11 | 569.72 | 131.11 | 65.56 | 171 | 4097 | 1020 | 168.6575 | 23.3157 | 2.5109 | 994.284 | 16.6132 | -69.1987 | 30.7811 | 30.7811 | 92.2281 | 272.2281 | 70.2297 | 289.9016 | 289.9016 | 111.9094 | 401.8109 | 0.51235 | 51.24% | 181.6989 | 93.0941 | 65.1659 | 149.6491 | 149.6491 | 43.55% | 11.38% | 11.38% | 85% | 9.67% | 17.5697 | 5.1642 | 5.1642 | 90.7326 | 38.8538 | 60.63% | 60.63%
6 | 171 | 20 | 4098 | 18 | 18.9 | 229.17 | 85.08 | 314.25 | 85.08 | 42.54 | 171 | 4098 | 1080 | 168.6575 | 23.3157 | 2.5109 | 1054.284 | 17.6132 | -84.1987 | 20.609 | 20.609 | 102.5516 | 282.5516 | 83.9694 | 68.4016 | 68.4016 | 72.6203 | 141.0219 | -0.026982 | 0% | 63.7701 | 0 | 0 | 132.7555 | 132.7555 | 0% | 11.39% | 11.39% | 80% | 9.113% | 5.8117 | 5.1642 | 5.1642 | 30.0124 | 12.852 | 22.61% | 22.61%
6 | 171 | 20 | 4099 | 19 | 18.8 | 169.81 | 86.03 | 255.84 | 86.03 | 43.02 | 171 | 4099 | 1140 | 168.6575 | 23.3157 | 2.5109 | 1114.284 | 18.6132 | -99.1987 | 10.8293 | 10.8293 | 112.6366 | 292.6366 | 97.727 | -121.52 | 0 | 73.4312 | 73.4312 | -0.79489 | 0% | 33.2056 | 0 | 0 | 124.6487 | 124.6487 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4100 | 20 | 19.2 | 64.25 | 40.08 | 104.33 | 40.08 | 20.04 | 171 | 4100 | 1200 | 168.6575 | 23.3157 | 2.5109 | 1174.284 | 19.6132 | -114.1987 | 1.7553 | 1.7553 | 123.0667 | 303.0667 | 111.3441 | 0 | 0 | 34.2104 | 34.2104 | -2.6021 | 0% | 15.47 | 0 | 0 | 150.7949 | 150.7949 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4101 | 21 | 17.1 | 0 | 8.53 | 8.53 | 8.53 | 4.27 | 171 | 4101 | 1260 | 168.6575 | 23.3157 | 2.5109 | 1234.284 | 20.6132 | -129.1987 | -6.2608 | 0 | 125.3066 | 305.3066 | 114.1215 | 0 | 0 | 7.2808 | 7.2808 | -15.8421 | 0% | 3.2924 | 0 | 0 | -7.2917 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4102 | 22 | 16.6 | 0 | 0 | 0 | 0 | 0 | 171 | 4102 | 1320 | 168.6575 | 23.3157 | 2.5109 | 1294.284 | 21.6132 | -144.1987 | -12.8061 | 0 | 125.3066 | 305.3066 | 114.1215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.451 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4103 | 23 | 16.1 | 0 | 0 | 0 | 0 | 0 | 171 | 4103 | 1380 | 168.6575 | 23.3157 | 2.5109 | 1354.284 | 22.6132 | -159.1987 | -17.427 | 0 | 125.3066 | 305.3066 | 114.1215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5596 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
6 | 171 | 20 | 4104 | 24 | 14.5 | 0 | 0 | 0 | 0 | 0 | 171 | 4104 | 1440 | 168.6575 | 23.3157 | 2.5109 | 1414.284 | 23.6132 | -174.1987 | -19.7102 | 0 | 125.3066 | 305.3066 | 114.1215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3447 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4105 | 1 | 14.3 | 0 | 0 | 0 | 0 | 0 | 172 | 4105 | 60 | 169.6438 | 23.3154 | 2.0637 | 34.284 | 0.60579 | 170.9131 | -19.4263 | 0 | 125.3062 | 54.6938 | 114.1213 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0192 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4106 | 2 | 14.2 | 0 | 0 | 0 | 0 | 0 | 172 | 4106 | 120 | 169.6438 | 23.3154 | 2.0637 | 94.284 | 1.6058 | 155.9131 | -16.6023 | 0 | 125.3062 | 54.6938 | 114.1213 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3257 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4107 | 3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 172 | 4107 | 180 | 169.6438 | 23.3154 | 2.0637 | 154.284 | 2.6058 | 140.9131 | -11.5213 | 0 | 125.3062 | 54.6938 | 114.1213 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0038 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4108 | 4 | 12.6 | 0 | 0 | 0 | 0 | 0 | 172 | 4108 | 240 | 169.6438 | 23.3154 | 2.0637 | 214.284 | 3.6058 | 125.9131 | -4.6157 | 0 | 125.3062 | 54.6938 | 114.1213 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9182 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4109 | 5 | 12.5 | 0 | 0 | 0 | 0 | 0 | 172 | 4109 | 300 | 169.6438 | 23.3154 | 2.0637 | 274.284 | 4.6058 | 110.9131 | 3.6653 | 3.6653 | 120.7282 | 59.2718 | 108.3828 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.6455 | 8.6455 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4110 | 6 | 11.7 | 6.19 | 18.61 | 24.8 | 18.61 | 9.31 | 172 | 4110 | 360 | 169.6438 | 23.3154 | 2.0637 | 334.284 | 5.6058 | 95.9131 | 12.9222 | 12.9222 | 110.4154 | 69.5846 | 94.7197 | -2.2775 | 0 | 15.8846 | 15.8846 | -7.5996 | 0% | 7.183 | 0 | 0 | 24.201 | 24.201 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4111 | 7 | 11.9 | 62.86 | 63.25 | 126.11 | 63.25 | 31.63 | 172 | 4111 | 420 | 169.6438 | 23.3154 | 2.0637 | 394.284 | 6.6058 | 80.9131 | 22.814 | 22.814 | 100.3346 | 79.6654 | 80.9529 | 25.4925 | 25.4925 | 53.9873 | 79.4798 | -0.8697 | 0% | 35.9408 | 0 | 0 | 202.2125 | 202.2125 | 0% | 11.67% | 11.67% | 80% | 9.338% | 3.3563 | 6.77 | 6 | 20.1377 | 7.4221 | 9.959% | 9.959%
6 | 172 | 21 | 4112 | 8 | 15 | 185.64 | 112.69 | 298.33 | 112.69 | 56.35 | 172 | 4112 | 480 | 169.6438 | 23.3154 | 2.0637 | 454.284 | 7.6058 | 65.9131 | 33.0305 | 33.0305 | 89.8588 | 90.1412 | 67.2386 | 131.7647 | 131.7647 | 96.1869 | 227.9516 | 0.25156 | 25.16% | 103.0797 | 25.9306 | 18.1514 | 184.4549 | 184.4549 | 9.841% | 11.51% | 11.51% | 80% | 9.207% | 9.491 | 6.0165 | 6 | 56.9461 | 20.9885 | 30.87% | 30.87%
6 | 172 | 21 | 4113 | 9 | 16.1 | 351.39 | 121.94 | 473.33 | 121.94 | 60.97 | 172 | 4113 | 540 | 169.6438 | 23.3154 | 2.0637 | 514.284 | 8.6058 | 50.9131 | 43.2309 | 43.2309 | 78.0486 | 101.9514 | 53.771 | 303.2037 | 303.2037 | 104.0823 | 407.286 | 0.50091 | 50.09% | 184.1747 | 92.2554 | 64.5788 | 194.5143 | 194.5143 | 33.2% | 11.44% | 11.44% | 85% | 9.721% | 17.9033 | 5.7653 | 5.7653 | 103.2179 | 39.5915 | 53.06% | 53.06%
6 | 172 | 21 | 4114 | 10 | 17.7 | 478.61 | 147.42 | 626.03 | 147.42 | 73.71 | 172 | 4114 | 600 | 169.6438 | 23.3154 | 2.0637 | 574.284 | 9.6058 | 35.9131 | 52.9177 | 52.9177 | 63.298 | 116.702 | 40.9141 | 453.366 | 453.366 | 125.8308 | 579.1968 | 0.59707 | 59.71% | 261.9128 | 156.3794 | 109.4656 | 197.8822 | 197.8822 | 55.32% | 11.38% | 11.38% | 90% | 10.24% | 26.8249 | 5.4151 | 5.4151 | 145.2591 | 59.321 | 73.41% | 73.41%
6 | 172 | 21 | 4115 | 11 | 18.6 | 598.81 | 160.75 | 759.56 | 160.75 | 80.38 | 172 | 4115 | 660 | 169.6438 | 23.3154 | 2.0637 | 634.284 | 10.6058 | 20.9131 | 61.1505 | 61.1505 | 42.7943 | 137.2057 | 29.5751 | 594.5846 | 594.5846 | 137.2087 | 731.7934 | 0.64295 | 64.3% | 330.917 | 212.7645 | 148.9352 | 192.0527 | 192.0527 | 77.55% | 11.36% | 11.36% | 90% | 10.22% | 33.8248 | 5.2259 | 5.2259 | 176.7662 | 74.8005 | 92.04% | 92.04%
6 | 172 | 21 | 4116 | 12 | 19.2 | 568.61 | 207.14 | 775.75 | 207.14 | 103.57 | 172 | 4116 | 720 | 169.6438 | 23.3154 | 2.0637 | 694.284 | 11.6058 | 5.9131 | 66.0605 | 66.0605 | 13.4828 | 166.5172 | 22.2873 | 575.6524 | 575.6524 | 176.805 | 752.4575 | 0.64914 | 64.91% | 340.2613 | 220.8786 | 154.615 | 175.6276 | 175.6276 | 88.04% | 11.35% | 11.35% | 90% | 10.22% | 34.7702 | 5.103 | 5.103 | 177.4324 | 76.8912 | 101% | 101%
6 | 172 | 21 | 4117 | 13 | 19.6 | 522.42 | 269.36 | 791.78 | 269.36 | 134.68 | 172 | 4117 | 780 | 169.6438 | 23.3154 | 2.0637 | 754.284 | 12.6058 | -9.0869 | 65.4264 | 65.4264 | 20.4115 | 200.4115 | 23.2693 | 527.7225 | 527.7225 | 229.9131 | 757.6357 | 0.65137 | 65.14% | 342.6029 | 223.1607 | 156.2125 | 172.7183 | 172.7183 | 90.44% | 11.35% | 11.35% | 90% | 10.22% | 35.0059 | 5.0224 | 5.0224 | 175.8151 | 77.4125 | 101.8% | 101.8%
6 | 172 | 21 | 4118 | 14 | 20.2 | 427.42 | 233.69 | 661.11 | 233.69 | 116.85 | 172 | 4118 | 840 | 169.6438 | 23.3154 | 2.0637 | 814.284 | 13.6058 | -24.0869 | 59.6053 | 59.6053 | 47.7968 | 227.7968 | 31.7607 | 421.3221 | 421.3221 | 199.4669 | 620.789 | 0.61985 | 61.99% | 280.7208 | 174.0051 | 121.8036 | 165.755 | 165.755 | 73.48% | 11.35% | 11.35% | 90% | 10.22% | 28.6757 | 4.9037 | 4.9037 | 140.617 | 63.4138 | 84.83% | 84.83%
6 | 172 | 21 | 4119 | 15 | 20.2 | 326.39 | 221.19 | 547.58 | 221.19 | 110.6 | 172 | 4119 | 900 | 169.6438 | 23.3154 | 2.0637 | 874.284 | 14.6058 | -39.0869 | 50.9472 | 50.9472 | 66.7823 | 246.7823 | 43.5525 | 304.6092 | 304.6092 | 188.7975 | 493.4067 | 0.57231 | 57.23% | 223.1185 | 127.6929 | 89.385 | 157.3865 | 157.3865 | 56.79% | 11.35% | 11.35% | 85% | 9.646% | 21.5228 | 4.9037 | 4.9037 | 105.5411 | 47.5957 | 67.06% | 67.06%
6 | 172 | 21 | 4120 | 16 | 20.7 | 294.25 | 218.33 | 512.58 | 218.33 | 109.17 | 172 | 4120 | 960 | 169.6438 | 23.3154 | 2.0637 | 934.284 | 15.6058 | -54.0869 | 41.0946 | 41.0946 | 80.7242 | 260.7242 | 56.5863 | 246.5181 | 246.5181 | 186.3563 | 432.8745 | 0.54245 | 54.24% | 195.7458 | 106.1815 | 74.3271 | 153.4981 | 153.4981 | 48.42% | 11.34% | 11.34% | 85% | 9.637% | 18.8644 | 4.8067 | 4.8067 | 90.675 | 41.7169 | 59.07% | 59.07%
6 | 172 | 21 | 4121 | 17 | 20.6 | 228.89 | 190.56 | 419.45 | 190.56 | 95.28 | 172 | 4121 | 1020 | 169.6438 | 23.3154 | 2.0637 | 994.284 | 16.6058 | -69.0869 | 30.8575 | 30.8575 | 92.1482 | 272.1482 | 70.1277 | 151.6957 | 151.6957 | 162.6531 | 314.3489 | 0.44313 | 44.31% | 142.1486 | 62.9902 | 44.0931 | 145.6016 | 145.6016 | 30.28% | 11.34% | 11.34% | 85% | 9.636% | 13.6968 | 4.8259 | 4.8259 | 66.1001 | 30.2893 | 45.4% | 45.4%
6 | 172 | 21 | 4122 | 18 | 20.5 | 191.19 | 157.14 | 348.33 | 157.14 | 78.57 | 172 | 4122 | 1080 | 169.6438 | 23.3154 | 2.0637 | 1054.284 | 17.6058 | -84.0869 | 20.6835 | 20.6835 | 102.4762 | 282.4762 | 83.8667 | 57.8333 | 57.8333 | 134.1274 | 191.9607 | 0.21191 | 21.19% | 86.8046 | 18.3945 | 12.8761 | 137.03 | 137.03 | 9.397% | 11.34% | 11.34% | 80% | 9.068% | 7.8716 | 4.8453 | 4.8453 | 38.1402 | 17.4074 | 27.83% | 27.83%
6 | 172 | 21 | 4123 | 19 | 20.2 | 102.97 | 105.83 | 208.8 | 105.83 | 52.92 | 172 | 4123 | 1140 | 169.6438 | 23.3154 | 2.0637 | 1114.284 | 18.6058 | -99.0869 | 10.8998 | 10.8998 | 112.5605 | 292.5605 | 97.6248 | -72.254 | 0 | 90.3316 | 90.3316 | -0.46153 | 0% | 40.8479 | 0 | 0 | 124.4008 | 124.4008 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.9037 | 4.9037 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4124 | 20 | 20 | 64.58 | 63.47 | 128.05 | 63.47 | 31.74 | 172 | 4124 | 1200 | 169.6438 | 23.3154 | 2.0637 | 1174.284 | 19.6058 | -114.0869 | 1.8193 | 1.8193 | 122.9863 | 302.9863 | 111.2436 | 0 | 0 | 54.175 | 54.175 | -1.3143 | 0% | 24.498 | 0 | 0 | 153.5916 | 153.5916 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4125 | 21 | 17.4 | 0 | 10.92 | 10.92 | 10.92 | 5.46 | 172 | 4125 | 1260 | 169.6438 | 23.3154 | 2.0637 | 1234.284 | 20.6058 | -129.0869 | -6.2062 | 0 | 125.3062 | 305.3062 | 114.1213 | 0 | 0 | 9.3208 | 9.3208 | -12.1268 | 0% | 4.2149 | 0 | 0 | -6.2791 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4126 | 22 | 16.6 | 0 | 0 | 0 | 0 | 0 | 172 | 4126 | 1320 | 169.6438 | 23.3154 | 2.0637 | 1294.284 | 21.6058 | -144.0869 | -12.7641 | 0 | 125.3062 | 305.3062 | 114.1213 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0516 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4127 | 23 | 15.3 | 0 | 0 | 0 | 0 | 0 | 172 | 4127 | 1380 | 169.6438 | 23.3154 | 2.0637 | 1354.284 | 22.6058 | -159.0869 | -17.401 | 0 | 125.3062 | 305.3062 | 114.1213 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1869 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
6 | 172 | 21 | 4128 | 24 | 13.9 | 0 | 0 | 0 | 0 | 0 | 172 | 4128 | 1440 | 169.6438 | 23.3154 | 2.0637 | 1414.284 | 23.6058 | -174.0869 | -19.7028 | 0 | 125.3062 | 305.3062 | 114.1213 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4746 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4129 | 1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 173 | 4129 | 60 | 170.6301 | 23.3086 | 1.6158 | 34.284 | 0.59833 | 171.0251 | -19.4448 | 0 | 125.295 | 54.705 | 114.1142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0328 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4130 | 2 | 11.5 | 0 | 0 | 0 | 0 | 0 | 173 | 4130 | 120 | 170.6301 | 23.3086 | 1.6158 | 94.284 | 1.5983 | 156.0251 | -16.6388 | 0 | 125.295 | 54.705 | 114.1142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.1209 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4131 | 3 | 11.8 | 0 | 0 | 0 | 0 | 0 | 173 | 4131 | 180 | 170.6301 | 23.3086 | 1.6158 | 154.284 | 2.5983 | 141.0251 | -11.5727 | 0 | 125.295 | 54.705 | 114.1142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0753 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4132 | 4 | 12.1 | 0 | 0 | 0 | 0 | 0 | 173 | 4132 | 240 | 170.6301 | 23.3086 | 1.6158 | 214.284 | 3.5983 | 126.0251 | -4.6785 | 0 | 125.295 | 54.705 | 114.1142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6181 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4133 | 5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 173 | 4133 | 300 | 170.6301 | 23.3086 | 1.6158 | 274.284 | 4.5983 | 111.0251 | 3.5942 | 3.5942 | 120.8029 | 59.1971 | 108.4852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.5696 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4134 | 6 | 10.8 | 4.17 | 15.19 | 19.36 | 15.19 | 7.6 | 173 | 4134 | 360 | 170.6301 | 23.3086 | 1.6158 | 334.284 | 5.5983 | 96.0251 | 12.8454 | 12.8454 | 110.486 | 69.514 | 94.8228 | -1.5769 | 0 | 12.9655 | 12.9655 | -9.6525 | 0% | 5.863 | 0 | 0 | 10.4676 | 10.4676 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4135 | 7 | 12.4 | 37.58 | 55.83 | 93.41 | 55.83 | 27.92 | 173 | 4135 | 420 | 170.6301 | 23.3086 | 1.6158 | 394.284 | 6.5983 | 81.0251 | 22.7339 | 22.7339 | 100.4049 | 79.5951 | 81.0554 | 15.1193 | 15.1193 | 47.6539 | 62.7732 | -1.2968 | 0% | 28.386 | 0 | 0 | 182.9853 | 182.9853 | 0% | 11.66% | 11.66% | 80% | 9.328% | 2.6479 | 6.6439 | 6 | 15.8873 | 5.8556 | 8.682% | 8.682%
6 | 173 | 22 | 4136 | 8 | 15.5 | 91.47 | 99.36 | 190.83 | 99.36 | 49.68 | 173 | 4136 | 480 | 170.6301 | 23.3086 | 1.6158 | 454.284 | 7.5983 | 66.0251 | 32.9493 | 32.9493 | 89.9345 | 90.0655 | 67.3394 | 64.7932 | 64.7932 | 84.8091 | 149.6023 | -0.030196 | 0% | 67.6501 | 0 | 0 | 159.3628 | 159.3628 | 0% | 11.51% | 11.51% | 80% | 9.21% | 6.2308 | 5.9013 | 5.9013 | 36.7699 | 13.7789 | 23.07% | 23.07%
6 | 173 | 22 | 4137 | 9 | 17 | 212.78 | 175.83 | 388.61 | 175.83 | 87.92 | 173 | 4137 | 540 | 170.6301 | 23.3086 | 1.6158 | 514.284 | 8.5983 | 51.0251 | 43.1512 | 43.1512 | 78.1382 | 101.8618 | 53.8681 | 183.4483 | 183.4483 | 150.0803 | 333.5286 | 0.43995 | 44% | 150.8216 | 66.3541 | 46.4479 | 171.7308 | 171.7308 | 27.05% | 11.43% | 11.43% | 85% | 9.715% | 14.6518 | 5.5661 | 5.5661 | 81.5531 | 32.401 | 47.49% | 47.49%
6 | 173 | 22 | 4138 | 10 | 19.4 | 407.22 | 155.28 | 562.5 | 155.28 | 77.64 | 173 | 4138 | 600 | 170.6301 | 23.3086 | 1.6158 | 574.284 | 9.5983 | 36.0251 | 52.8441 | 52.8441 | 63.4175 | 116.5825 | 41.0031 | 385.5962 | 385.5962 | 132.5398 | 518.1359 | 0.57997 | 58% | 234.3011 | 135.8865 | 95.1205 | 179.7144 | 179.7144 | 52.93% | 11.36% | 11.36% | 90% | 10.23% | 23.9577 | 5.0626 | 5.0626 | 121.2877 | 52.9803 | 67.49% | 67.49%
6 | 173 | 22 | 4139 | 11 | 22 | 580.75 | 153.97 | 734.72 | 153.97 | 76.99 | 173 | 4139 | 660 | 170.6301 | 23.3086 | 1.6158 | 634.284 | 10.5983 | 21.0251 | 61.0924 | 61.0924 | 42.9706 | 137.0294 | 29.6448 | 576.5755 | 576.5755 | 131.4216 | 707.9972 | 0.64809 | 64.81% | 320.1563 | 207.4908 | 145.2436 | 181.5841 | 181.5841 | 79.99% | 11.34% | 11.34% | 90% | 10.21% | 32.6806 | 4.5626 | 4.5626 | 149.1084 | 72.2702 | 82.12% | 82.12%
6 | 173 | 22 | 4140 | 12 | 22.9 | 650.19 | 164.64 | 814.83 | 164.64 | 82.32 | 173 | 4140 | 720 | 170.6301 | 23.3086 | 1.6158 | 694.284 | 11.5983 | 6.0251 | 66.0357 | 66.0357 | 13.7292 | 166.2708 | 22.3089 | 658.2674 | 658.2674 | 140.529 | 798.7964 | 0.66826 | 66.83% | 361.2158 | 241.385 | 168.9695 | 172.5094 | 172.5094 | 97.95% | 11.35% | 11.35% | 90% | 10.22% | 36.9041 | 4.4006 | 4.4006 | 162.3984 | 81.6101 | 94.14% | 94.14%
6 | 173 | 22 | 4141 | 13 | 23.9 | 701.81 | 158.61 | 860.42 | 158.61 | 79.31 | 173 | 4141 | 780 | 170.6301 | 23.3086 | 1.6158 | 754.284 | 12.5983 | -8.9749 | 65.4464 | 65.4464 | 20.1682 | 200.1682 | 23.2222 | 709.0708 | 709.0708 | 135.3821 | 844.4529 | 0.67815 | 67.81% | 381.8616 | 258.9589 | 181.2713 | 188.2048 | 188.2048 | 96.32% | 11.36% | 11.36% | 95% | 10.79% | 41.2161 | 4.2272 | 4.2272 | 174.2267 | 91.1457 | 92.57% | 92.57%
6 | 173 | 22 | 4142 | 14 | 24.7 | 723.19 | 156.11 | 879.3 | 156.11 | 78.06 | 173 | 4142 | 840 | 170.6301 | 23.3086 | 1.6158 | 814.284 | 13.5983 | -23.9749 | 59.6563 | 59.6563 | 47.6197 | 227.6197 | 31.6767 | 713.1459 | 713.1459 | 133.2482 | 846.3941 | 0.68046 | 68.05% | 382.7394 | 260.4401 | 182.3081 | 202.7494 | 202.7494 | 89.92% | 11.36% | 11.36% | 95% | 10.8% | 41.3198 | 4.0935 | 4.0935 | 169.1414 | 91.375 | 83.42% | 83.42%
6 | 173 | 22 | 4143 | 15 | 25 | 565.97 | 175.97 | 741.94 | 175.97 | 87.99 | 173 | 4143 | 900 | 170.6301 | 23.3086 | 1.6158 | 874.284 | 14.5983 | -38.9749 | 51.0127 | 51.0127 | 66.6559 | 246.6559 | 43.4557 | 528.5594 | 528.5594 | 150.1998 | 678.7592 | 0.6509 | 65.09% | 306.9349 | 199.783 | 139.8481 | 200.9572 | 200.9572 | 69.59% | 11.32% | 11.32% | 90% | 10.19% | 31.2668 | 4.0445 | 4.0445 | 126.4587 | 69.1438 | 62.93% | 62.93%
6 | 173 | 22 | 4144 | 16 | 25.3 | 595 | 138.33 | 733.33 | 138.33 | 69.17 | 173 | 4144 | 960 | 170.6301 | 23.3086 | 1.6158 | 934.284 | 15.5983 | -53.9749 | 41.1657 | 41.1657 | 80.6251 | 260.6251 | 56.485 | 499.109 | 499.109 | 118.072 | 617.181 | 0.63666 | 63.67% | 279.0892 | 177.6844 | 124.379 | 204.7048 | 204.7048 | 60.76% | 11.3% | 11.3% | 90% | 10.17% | 28.3801 | 3.9962 | 3.9962 | 113.4114 | 62.7601 | 55.4% | 55.4%
6 | 173 | 22 | 4145 | 17 | 26.2 | 390.83 | 131.11 | 521.94 | 131.11 | 65.56 | 173 | 4145 | 1020 | 170.6301 | 23.3086 | 1.6158 | 994.284 | 16.5983 | -68.9749 | 30.9296 | 30.9296 | 92.0623 | 272.0623 | 70.0248 | 259.7606 | 259.7606 | 111.9094 | 371.67 | 0.53126 | 53.13% | 168.0692 | 89.2886 | 62.502 | 209.5676 | 209.5676 | 29.82% | 11.21% | 11.21% | 85% | 9.525% | 16.0087 | 3.8549 | 3.8549 | 61.7118 | 35.4017 | 29.45% | 29.45%
6 | 173 | 22 | 4146 | 18 | 26.3 | 276.31 | 116.31 | 392.62 | 116.31 | 58.16 | 173 | 4146 | 1080 | 170.6301 | 23.3086 | 1.6158 | 1054.284 | 17.5983 | -83.9749 | 20.7537 | 20.7537 | 102.3955 | 282.3955 | 83.7638 | 84.7035 | 84.7035 | 99.2768 | 183.9802 | 0.25417 | 25.42% | 83.1959 | 21.1462 | 14.8024 | 201.0087 | 201.0087 | 7.364% | 11.14% | 11.14% | 80% | 8.911% | 7.4135 | 3.8396 | 3.8396 | 28.4643 | 16.3942 | 14.16% | 14.16%
6 | 173 | 22 | 4147 | 19 | 25.2 | 155 | 71.39 | 226.39 | 71.39 | 35.7 | 173 | 4147 | 1140 | 170.6301 | 23.3086 | 1.6158 | 1114.284 | 18.5983 | -98.9749 | 10.9657 | 10.9657 | 112.4798 | 292.4798 | 97.523 | -106.683 | 0 | 60.9352 | 60.9352 | -0.89442 | 0% | 27.5549 | 0 | 0 | 167.3748 | 167.3748 | 0% | 11.14% | 0% | 80% | 0% | 0 | 4.0122 | 4.0122 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4148 | 20 | 24.6 | 58.81 | 37.22 | 96.03 | 37.22 | 18.61 | 173 | 4148 | 1200 | 170.6301 | 23.3086 | 1.6158 | 1174.284 | 19.5983 | -113.9749 | 1.8783 | 1.8783 | 122.9018 | 302.9018 | 111.1443 | 0 | 0 | 31.7693 | 31.7693 | -2.494 | 0% | 14.3661 | 0 | 0 | 183.3372 | 183.3372 | 0% | 11.16% | 0% | 80% | 0% | 0 | 4.1099 | 4.1099 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4149 | 21 | 23.2 | 0 | 11.58 | 11.58 | 11.58 | 5.79 | 173 | 4149 | 1260 | 170.6301 | 23.3086 | 1.6158 | 1234.284 | 20.5983 | -128.9749 | -6.1569 | 0 | 125.295 | 305.295 | 114.1142 | 0 | 0 | 9.8841 | 9.8841 | -10.1006 | 0% | 4.4696 | 0 | 0 | -0.21563 | 0 | 0% | 11.21% | 0% | 80% | 0% | 0 | 4.3478 | 4.3478 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4150 | 22 | 21.7 | 0 | 0 | 0 | 0 | 0 | 173 | 4150 | 1320 | 170.6301 | 23.3086 | 1.6158 | 1294.284 | 21.5983 | -143.9749 | -12.7279 | 0 | 125.295 | 305.295 | 114.1142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.9295 | 0 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.6179 | 4.6179 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4151 | 23 | 18.7 | 0 | 0 | 0 | 0 | 0 | 173 | 4151 | 1380 | 170.6301 | 23.3086 | 1.6158 | 1354.284 | 22.5983 | -158.9749 | -17.3812 | 0 | 125.295 | 305.295 | 114.1142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.9131 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2053 | 5.2053 | 0 | 0 | 0% | 0%
6 | 173 | 22 | 4152 | 24 | 18 | 0 | 0 | 0 | 0 | 0 | 173 | 4152 | 1440 | 170.6301 | 23.3086 | 1.6158 | 1414.284 | 23.5983 | -173.9749 | -19.7018 | 0 | 125.295 | 305.295 | 114.1142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3916 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4153 | 1 | 17.2 | 0 | 0 | 0 | 0 | 0 | 174 | 4153 | 60 | 171.6164 | 23.2952 | 1.1676 | 34.284 | 0.59086 | 171.1371 | -19.4697 | 0 | 125.273 | 54.727 | 114.1003 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4074 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4154 | 2 | 16.1 | 0 | 0 | 0 | 0 | 0 | 174 | 4154 | 120 | 171.6164 | 23.2952 | 1.1676 | 94.284 | 1.5909 | 156.1371 | -16.6814 | 0 | 125.273 | 54.727 | 114.1003 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5284 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4155 | 3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 174 | 4155 | 180 | 171.6164 | 23.2952 | 1.1676 | 154.284 | 2.5909 | 141.1371 | -11.6299 | 0 | 125.273 | 54.727 | 114.1003 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8207 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4156 | 4 | 15.9 | 0 | 0 | 0 | 0 | 0 | 174 | 4156 | 240 | 171.6164 | 23.2952 | 1.1676 | 214.284 | 3.5909 | 126.1371 | -4.7468 | 0 | 125.273 | 54.727 | 114.1003 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2779 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4157 | 5 | 15.5 | 0 | 0 | 0 | 0 | 0 | 174 | 4157 | 300 | 171.6164 | 23.2952 | 1.1676 | 274.284 | 4.5909 | 111.1371 | 3.518 | 3.518 | 120.8736 | 59.1264 | 108.5888 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.0027 | 4.0027 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4158 | 6 | 16.2 | 4.64 | 20.83 | 25.47 | 20.83 | 10.42 | 174 | 4158 | 360 | 171.6164 | 23.2952 | 1.1676 | 334.284 | 5.5909 | 96.1371 | 12.764 | 12.764 | 110.552 | 69.448 | 94.9264 | -1.8035 | 0 | 17.7795 | 17.7795 | -6.1263 | 0% | 8.0399 | 0 | 0 | 17.7113 | 17.7113 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4159 | 7 | 17.7 | 55.64 | 51.67 | 107.31 | 51.67 | 25.84 | 174 | 4159 | 420 | 171.6164 | 23.2952 | 1.1676 | 394.284 | 6.5909 | 81.1371 | 22.6494 | 22.6494 | 100.4701 | 79.5299 | 81.1579 | 22.2092 | 22.2092 | 44.1031 | 66.3123 | -1.0034 | 0% | 29.9864 | 0 | 0 | 189.1252 | 189.1252 | 0% | 11.44% | 11.44% | 80% | 9.156% | 2.7455 | 5.4151 | 5.4151 | 14.8672 | 6.0715 | 7.861% | 7.861%
6 | 174 | 23 | 4160 | 8 | 20.8 | 125 | 73.25 | 198.25 | 73.25 | 36.63 | 174 | 4160 | 480 | 171.6164 | 23.2952 | 1.1676 | 454.284 | 7.5909 | 66.1371 | 32.8637 | 32.8637 | 90.0043 | 89.9957 | 67.4393 | 88.3782 | 88.3782 | 62.5228 | 150.901 | 0.055158 | 5.516% | 68.2374 | 3.7638 | 2.6347 | 164.4282 | 164.4282 | 1.602% | 11.32% | 11.32% | 80% | 9.059% | 6.1815 | 4.7875 | 4.7875 | 29.5936 | 13.6697 | 18% | 18%
6 | 174 | 23 | 4161 | 9 | 23 | 221.86 | 101.58 | 323.44 | 101.58 | 50.79 | 174 | 4161 | 540 | 171.6164 | 23.2952 | 1.1676 | 514.284 | 8.5909 | 51.1371 | 43.0669 | 43.0669 | 78.2212 | 101.7788 | 53.9635 | 191.1402 | 191.1402 | 86.704 | 277.8441 | 0.41452 | 41.45% | 125.6411 | 52.0807 | 36.4565 | 174.0865 | 174.0865 | 20.94% | 11.27% | 11.27% | 80% | 9.013% | 11.3236 | 4.3829 | 4.3829 | 49.6303 | 25.0412 | 28.51% | 28.51%
6 | 174 | 23 | 4162 | 10 | 23.2 | 349.08 | 121.11 | 470.19 | 121.11 | 60.56 | 174 | 4162 | 600 | 171.6164 | 23.2952 | 1.1676 | 574.284 | 9.5909 | 36.1371 | 52.7655 | 52.7655 | 63.5296 | 116.4704 | 41.0894 | 330.4541 | 330.4541 | 103.3739 | 433.8279 | 0.55555 | 55.56% | 196.177 | 108.9869 | 76.2908 | 181.0837 | 181.0837 | 42.13% | 11.29% | 11.29% | 85% | 9.594% | 18.822 | 4.3478 | 4.3478 | 81.8345 | 41.6233 | 45.19% | 45.19%
6 | 174 | 23 | 4163 | 11 | 24 | 411.31 | 167.5 | 578.81 | 167.5 | 83.75 | 174 | 4163 | 660 | 171.6164 | 23.2952 | 1.1676 | 634.284 | 10.5909 | 21.1371 | 61.0285 | 61.0285 | 43.1396 | 136.8604 | 29.7104 | 408.3391 | 408.3391 | 142.9702 | 551.3093 | 0.61162 | 61.16% | 249.3021 | 152.4782 | 106.7348 | 192.1113 | 192.1113 | 55.56% | 11.3% | 11.3% | 90% | 10.17% | 25.3479 | 4.2102 | 4.2102 | 106.7199 | 56.0547 | 55.55% | 55.55%
6 | 174 | 23 | 4164 | 12 | 24.9 | 610.75 | 161.03 | 771.78 | 161.03 | 80.52 | 174 | 4164 | 720 | 171.6164 | 23.2952 | 1.1676 | 694.284 | 11.5909 | 6.1371 | 66.0042 | 66.0042 | 13.9725 | 166.0275 | 22.3247 | 618.4186 | 618.4186 | 137.4477 | 755.8663 | 0.66623 | 66.62% | 341.8027 | 227.7202 | 159.4042 | 204.1751 | 204.1751 | 78.07% | 11.34% | 11.34% | 90% | 10.21% | 34.8847 | 4.0608 | 4.0608 | 141.6583 | 77.1444 | 69.38% | 69.38%
6 | 174 | 23 | 4165 | 13 | 27.1 | 489.44 | 190.92 | 680.36 | 190.92 | 95.46 | 174 | 4165 | 780 | 171.6164 | 23.2952 | 1.1676 | 754.284 | 12.5909 | -8.8629 | 65.4597 | 65.4597 | 19.9205 | 199.9205 | 23.1694 | 494.6462 | 494.6462 | 162.9604 | 657.6066 | 0.65274 | 65.27% | 297.3697 | 194.1057 | 135.874 | 238.9358 | 238.9358 | 56.87% | 11.3% | 11.3% | 90% | 10.17% | 30.2329 | 3.7193 | 3.7193 | 112.4455 | 66.8573 | 47.06% | 47.06%
6 | 174 | 23 | 4166 | 14 | 28.8 | 267.86 | 222.31 | 490.17 | 222.31 | 111.16 | 174 | 4166 | 840 | 171.6164 | 23.2952 | 1.1676 | 814.284 | 13.5909 | -23.8629 | 59.7017 | 59.7017 | 47.4349 | 227.4349 | 31.5887 | 264.2672 | 264.2672 | 189.7535 | 454.0207 | 0.59276 | 59.28% | 205.3082 | 121.6984 | 85.1889 | 272.1503 | 272.1503 | 31.3% | 11.18% | 11.18% | 85% | 9.507% | 19.5184 | 3.4787 | 3.4787 | 67.8982 | 43.1631 | 24.95% | 24.95%
6 | 174 | 23 | 4167 | 15 | 29.8 | 222.69 | 175.47 | 398.16 | 175.47 | 87.74 | 174 | 4167 | 900 | 171.6164 | 23.2952 | 1.1676 | 874.284 | 14.5909 | -38.8629 | 51.0733 | 51.0733 | 66.522 | 246.522 | 43.3562 | 208.1337 | 208.1337 | 149.773 | 357.9067 | 0.54183 | 54.18% | 161.8454 | 87.6933 | 61.3853 | 275.6138 | 275.6138 | 22.27% | 11.11% | 11.11% | 85% | 9.447% | 15.289 | 3.3466 | 3.3466 | 51.1658 | 33.8102 | 18.56% | 18.56%
6 | 174 | 23 | 4168 | 16 | 24.9 | 358.81 | 124.81 | 483.62 | 124.81 | 62.41 | 174 | 4168 | 960 | 171.6164 | 23.2952 | 1.1676 | 934.284 | 15.5909 | -53.8629 | 41.2323 | 41.2323 | 80.5194 | 260.5194 | 56.3819 | 301.3998 | 301.3998 | 106.532 | 407.9318 | 0.54873 | 54.87% | 184.4668 | 101.2221 | 70.8555 | 249.5347 | 249.5347 | 28.4% | 11.25% | 11.25% | 85% | 9.559% | 17.6339 | 4.0608 | 4.0608 | 71.6069 | 38.9958 | 28.7% | 28.7%
6 | 174 | 23 | 4169 | 17 | 21 | 295.92 | 116.94 | 412.86 | 116.94 | 58.47 | 174 | 4169 | 1020 | 171.6164 | 23.2952 | 1.1676 | 994.284 | 16.5909 | -68.8629 | 30.9973 | 30.9973 | 91.9707 | 271.9707 | 69.921 | 197.2702 | 197.2702 | 99.8145 | 297.0847 | 0.42511 | 42.51% | 134.3417 | 57.1097 | 39.9768 | 140.1203 | 140.1203 | 28.53% | 11.32% | 11.32% | 80% | 9.059% | 12.1707 | 4.7493 | 4.7493 | 57.8021 | 26.9143 | 41.25% | 41.25%
6 | 174 | 23 | 4170 | 18 | 20.6 | 216.86 | 96.75 | 313.61 | 96.75 | 48.38 | 174 | 4170 | 1080 | 171.6164 | 23.2952 | 1.1676 | 1054.284 | 17.5909 | -83.8629 | 20.8195 | 20.8195 | 102.3097 | 282.3097 | 83.6607 | 67.3692 | 67.3692 | 82.5813 | 149.9505 | 0.047488 | 4.749% | 67.8076 | 3.2201 | 2.254 | 130.8644 | 130.8644 | 1.722% | 11.33% | 11.33% | 80% | 9.064% | 6.1464 | 4.8259 | 4.8259 | 29.6621 | 13.5922 | 22.67% | 22.67%
6 | 174 | 23 | 4171 | 19 | 20.2 | 115.47 | 76.19 | 191.66 | 76.19 | 38.1 | 174 | 4171 | 1140 | 171.6164 | 23.2952 | 1.1676 | 1114.284 | 18.5909 | -98.8629 | 11.0269 | 11.0269 | 112.3945 | 292.3945 | 97.4218 | -77.9814 | 0 | 65.0322 | 65.0322 | -0.95386 | 0% | 29.4076 | 0 | 0 | 119.574 | 119.574 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.9037 | 4.9037 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4172 | 20 | 18.8 | 43.25 | 37.5 | 80.75 | 37.5 | 18.75 | 174 | 4172 | 1200 | 171.6164 | 23.2952 | 1.1676 | 1174.284 | 19.5909 | -113.8629 | 1.9323 | 1.9323 | 122.8132 | 302.8132 | 111.0462 | 0 | 0 | 32.0083 | 32.0083 | -2.8641 | 0% | 14.4741 | 0 | 0 | 146.2252 | 146.2252 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4173 | 21 | 16.8 | 0 | 10.36 | 10.36 | 10.36 | 5.18 | 174 | 4173 | 1260 | 171.6164 | 23.2952 | 1.1676 | 1234.284 | 20.5909 | -128.8629 | -6.1131 | 0 | 125.273 | 305.273 | 114.1003 | 0 | 0 | 8.8428 | 8.8428 | -12.9777 | 0% | 3.9987 | 0 | 0 | -9.4748 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4174 | 22 | 16.5 | 0 | 0 | 0 | 0 | 0 | 174 | 4174 | 1320 | 171.6164 | 23.2952 | 1.1676 | 1294.284 | 21.5909 | -143.8629 | -12.6975 | 0 | 125.273 | 305.273 | 114.1003 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1402 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4175 | 23 | 16.5 | 0 | 0 | 0 | 0 | 0 | 174 | 4175 | 1380 | 171.6164 | 23.2952 | 1.1676 | 1354.284 | 22.5909 | -158.8629 | -17.3675 | 0 | 125.273 | 305.273 | 114.1003 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5848 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
6 | 174 | 23 | 4176 | 24 | 16.4 | 0 | 0 | 0 | 0 | 0 | 174 | 4176 | 1440 | 171.6164 | 23.2952 | 1.1676 | 1414.284 | 23.5909 | -173.8629 | -19.7072 | 0 | 125.273 | 305.273 | 114.1003 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1819 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4177 | 1 | 15.6 | 0 | 0 | 0 | 0 | 0 | 175 | 4177 | 60 | 172.6027 | 23.2753 | 0.71954 | 34.284 | 0.58339 | 171.2491 | -19.5009 | 0 | 125.2403 | 54.7597 | 114.0796 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8149 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4178 | 2 | 15.4 | 0 | 0 | 0 | 0 | 0 | 175 | 4178 | 120 | 172.6027 | 23.2753 | 0.71954 | 94.284 | 1.5834 | 156.2491 | -16.7301 | 0 | 125.2403 | 54.7597 | 114.0796 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4407 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4179 | 3 | 15.1 | 0 | 0 | 0 | 0 | 0 | 175 | 4179 | 180 | 172.6027 | 23.2753 | 0.71954 | 154.284 | 2.5834 | 141.2491 | -11.6929 | 0 | 125.2403 | 54.7597 | 114.0796 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2189 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4180 | 4 | 14.1 | 0 | 0 | 0 | 0 | 0 | 175 | 4180 | 240 | 172.6027 | 23.2753 | 0.71954 | 214.284 | 3.5834 | 126.2491 | -4.8204 | 0 | 125.2403 | 54.7597 | 114.0796 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7429 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4181 | 5 | 13.1 | 0 | 0 | 0 | 0 | 0 | 175 | 4181 | 300 | 172.6027 | 23.2753 | 0.71954 | 274.284 | 4.5834 | 111.2491 | 3.4369 | 3.4369 | 120.9401 | 59.0599 | 108.6936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.7381 | 5.7381 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4182 | 6 | 13.3 | 5.28 | 14.25 | 19.53 | 14.25 | 7.13 | 175 | 4182 | 360 | 172.6027 | 23.2753 | 0.71954 | 334.284 | 5.5834 | 96.2491 | 12.6779 | 12.6779 | 110.6133 | 69.3867 | 95.0304 | -2.1095 | 0 | 12.1631 | 12.1631 | -9.868 | 0% | 5.5002 | 0 | 0 | 20.7146 | 20.7146 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4183 | 7 | 14.4 | 65.83 | 58.53 | 124.36 | 58.53 | 29.27 | 175 | 4183 | 420 | 172.6027 | 23.2753 | 0.71954 | 394.284 | 6.5834 | 81.2491 | 22.5604 | 22.5604 | 100.5301 | 79.4699 | 81.26 | 26.0724 | 26.0724 | 49.9585 | 76.0309 | -0.87023 | 0% | 34.3812 | 0 | 0 | 196.7568 | 196.7568 | 0% | 11.57% | 11.57% | 80% | 9.26% | 3.1837 | 6.1571 | 6 | 19.1021 | 7.0404 | 9.709% | 9.709%
6 | 175 | 24 | 4184 | 8 | 15.6 | 136.03 | 107.97 | 244 | 107.97 | 53.99 | 175 | 4184 | 480 | 172.6027 | 23.2753 | 0.71954 | 454.284 | 7.5834 | 66.2491 | 32.7737 | 32.7737 | 90.0682 | 89.9318 | 67.5384 | 96.0099 | 96.0099 | 92.1582 | 188.168 | 0.14198 | 14.2% | 85.0896 | 12.0807 | 8.4565 | 172.1405 | 172.1405 | 4.913% | 11.5% | 11.5% | 80% | 9.2% | 7.8283 | 5.8784 | 5.8784 | 46.0181 | 17.3116 | 26.73% | 26.73%
6 | 175 | 24 | 4185 | 9 | 16.3 | 291.75 | 147.86 | 439.61 | 147.86 | 73.93 | 175 | 4185 | 540 | 172.6027 | 23.2753 | 0.71954 | 514.284 | 8.5834 | 51.2491 | 42.9782 | 42.9782 | 78.2976 | 101.7024 | 54.0571 | 251.2041 | 251.2041 | 126.2064 | 377.4105 | 0.47811 | 47.81% | 170.665 | 81.5973 | 57.1181 | 183.0527 | 183.0527 | 31.2% | 11.44% | 11.44% | 85% | 9.722% | 16.5926 | 5.7206 | 5.7206 | 94.9187 | 36.693 | 51.85% | 51.85%
6 | 175 | 24 | 4186 | 10 | 17.4 | 360.08 | 132.31 | 492.39 | 132.31 | 66.16 | 175 | 4186 | 600 | 172.6027 | 23.2753 | 0.71954 | 574.284 | 9.5834 | 36.2491 | 52.682 | 52.682 | 63.6341 | 116.3659 | 41.173 | 340.8112 | 340.8112 | 112.9336 | 453.7449 | 0.53838 | 53.84% | 205.1834 | 110.4659 | 77.3261 | 182.9035 | 182.9035 | 42.28% | 11.4% | 11.4% | 85% | 9.691% | 19.8849 | 5.4794 | 5.4794 | 108.957 | 43.9737 | 59.57% | 59.57%
6 | 175 | 24 | 4187 | 11 | 17.9 | 452.22 | 200.83 | 653.05 | 200.83 | 100.42 | 175 | 4187 | 660 | 172.6027 | 23.2753 | 0.71954 | 634.284 | 10.5834 | 21.2491 | 60.9589 | 60.9589 | 43.3011 | 136.6989 | 29.7717 | 448.9817 | 448.9817 | 171.4191 | 620.4008 | 0.61153 | 61.15% | 280.5452 | 171.5616 | 120.0931 | 180.382 | 180.382 | 66.58% | 11.37% | 11.37% | 90% | 10.24% | 28.7151 | 5.3726 | 5.3726 | 154.2736 | 63.5009 | 85.53% | 85.53%
6 | 175 | 24 | 4188 | 12 | 18.1 | 524.36 | 251.86 | 776.22 | 251.86 | 125.93 | 175 | 4188 | 720 | 172.6027 | 23.2753 | 0.71954 | 694.284 | 11.5834 | 6.2491 | 65.9659 | 65.9659 | 14.2122 | 165.7878 | 22.3348 | 531.0632 | 531.0632 | 214.976 | 746.0391 | 0.64454 | 64.45% | 337.3589 | 217.4412 | 152.2089 | 170.8909 | 170.8909 | 89.07% | 11.36% | 11.36% | 90% | 10.22% | 34.4844 | 5.3303 | 5.3303 | 183.8127 | 76.2592 | 107.6% | 107.6%
6 | 175 | 24 | 4189 | 13 | 19 | 650.14 | 136.67 | 786.81 | 136.67 | 68.34 | 175 | 4189 | 780 | 172.6027 | 23.2753 | 0.71954 | 754.284 | 12.5834 | -8.7509 | 65.4665 | 65.4665 | 19.6687 | 199.6687 | 23.111 | 657.3065 | 657.3065 | 116.6551 | 773.9616 | 0.65287 | 65.29% | 349.9854 | 228.4966 | 159.9476 | 168.4625 | 168.4625 | 94.95% | 11.35% | 11.35% | 90% | 10.22% | 35.7618 | 5.1437 | 5.1437 | 183.9481 | 79.0841 | 109.2% | 109.2%
6 | 175 | 24 | 4190 | 14 | 20 | 727.03 | 151.47 | 878.5 | 151.47 | 75.74 | 175 | 4190 | 840 | 172.6027 | 23.2753 | 0.71954 | 814.284 | 13.5834 | -23.7509 | 59.7415 | 59.7415 | 47.2426 | 227.2426 | 31.4967 | 717.6949 | 717.6949 | 129.2877 | 846.9827 | 0.66851 | 66.85% | 383.0056 | 256.0431 | 179.2302 | 172.1353 | 172.1353 | 104.1% | 11.35% | 11.35% | 95% | 10.78% | 41.3049 | 4.943 | 4.943 | 204.1699 | 91.342 | 118.6% | 118.6%
6 | 175 | 24 | 4191 | 15 | 20 | 478.47 | 180.28 | 658.75 | 180.28 | 90.14 | 175 | 4191 | 900 | 172.6027 | 23.2753 | 0.71954 | 874.284 | 14.5834 | -38.7509 | 51.1291 | 51.1291 | 66.3807 | 246.3807 | 43.2542 | 447.5941 | 447.5941 | 153.8786 | 601.4727 | 0.61321 | 61.32% | 271.986 | 166.7834 | 116.7484 | 160.7503 | 160.7503 | 72.63% | 11.35% | 11.35% | 90% | 10.22% | 27.7883 | 4.943 | 4.943 | 137.3574 | 61.4513 | 85.45% | 85.45%
6 | 175 | 24 | 4192 | 16 | 20.1 | 461.47 | 127.14 | 588.61 | 127.14 | 63.57 | 175 | 4192 | 960 | 172.6027 | 23.2753 | 0.71954 | 934.284 | 15.5834 | -53.7509 | 41.2945 | 41.2945 | 80.4072 | 260.4072 | 56.2773 | 388.2176 | 388.2176 | 108.5208 | 496.7384 | 0.57342 | 57.34% | 224.6251 | 128.8047 | 90.1633 | 155.5715 | 155.5715 | 57.96% | 11.35% | 11.35% | 85% | 9.648% | 21.6713 | 4.9233 | 4.9233 | 106.6948 | 47.9242 | 68.58% | 68.58%
6 | 175 | 24 | 4193 | 17 | 20.4 | 376.39 | 157.78 | 534.17 | 157.78 | 78.89 | 175 | 4193 | 1020 | 172.6027 | 23.2753 | 0.71954 | 994.284 | 16.5834 | -68.7509 | 31.0607 | 31.0607 | 91.8733 | 271.8733 | 69.8165 | 251.7029 | 251.7029 | 134.6737 | 386.3765 | 0.50927 | 50.93% | 174.7195 | 88.9787 | 62.2851 | 150.7498 | 150.7498 | 41.32% | 11.34% | 11.34% | 85% | 9.641% | 16.8455 | 4.8647 | 4.8647 | 81.948 | 37.2524 | 54.36% | 54.36%
6 | 175 | 24 | 4194 | 18 | 19.4 | 159.25 | 105.08 | 264.33 | 105.08 | 52.54 | 175 | 4194 | 1080 | 172.6027 | 23.2753 | 0.71954 | 1054.284 | 17.5834 | -83.7509 | 20.8809 | 20.8809 | 102.2187 | 282.2187 | 83.5576 | 50.1328 | 50.1328 | 89.6914 | 139.8242 | -0.026189 | 0% | 63.2285 | 0 | 0 | 131.2414 | 131.2414 | 0% | 11.37% | 11.37% | 80% | 9.099% | 5.7532 | 5.0626 | 5.0626 | 29.1259 | 12.7226 | 22.19% | 22.19%
6 | 175 | 24 | 4195 | 19 | 19.2 | 90.56 | 74.17 | 164.73 | 74.17 | 37.09 | 175 | 4195 | 1140 | 172.6027 | 23.2753 | 0.71954 | 1114.284 | 18.5834 | -98.7509 | 11.0835 | 11.0835 | 112.3046 | 292.3046 | 97.3211 | -60.0296 | 0 | 63.3081 | 63.3081 | -1.0366 | 0% | 28.6279 | 0 | 0 | 120.2644 | 120.2644 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4196 | 20 | 19 | 19.58 | 50.42 | 70 | 50.42 | 25.21 | 175 | 4196 | 1200 | 172.6027 | 23.2753 | 0.71954 | 1174.284 | 19.5834 | -113.7509 | 1.9813 | 1.9813 | 122.7205 | 302.7205 | 110.9495 | 0 | 0 | 43.0362 | 43.0362 | -1.9138 | 0% | 19.461 | 0 | 0 | 147.5632 | 147.5632 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4197 | 21 | 17.2 | 0 | 16.75 | 16.75 | 16.75 | 8.38 | 175 | 4197 | 1260 | 172.6027 | 23.2753 | 0.71954 | 1234.284 | 20.5834 | -128.7509 | -6.0746 | 0 | 125.2403 | 305.2403 | 114.0796 | 0 | 0 | 14.297 | 14.297 | -7.6574 | 0% | 6.4651 | 0 | 0 | -6.5792 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4198 | 22 | 17 | 0 | 0 | 0 | 0 | 0 | 175 | 4198 | 1320 | 172.6027 | 23.2753 | 0.71954 | 1294.284 | 21.5834 | -143.7509 | -12.673 | 0 | 125.2403 | 305.2403 | 114.0796 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.7184 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4199 | 23 | 15.9 | 0 | 0 | 0 | 0 | 0 | 175 | 4199 | 1380 | 172.6027 | 23.2753 | 0.71954 | 1354.284 | 22.5834 | -158.7509 | -17.36 | 0 | 125.2403 | 305.2403 | 114.0796 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7158 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
6 | 175 | 24 | 4200 | 24 | 14.7 | 0 | 0 | 0 | 0 | 0 | 175 | 4200 | 1440 | 172.6027 | 23.2753 | 0.71954 | 1414.284 | 23.5834 | -173.7509 | -19.719 | 0 | 125.2403 | 305.2403 | 114.0796 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8655 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4201 | 1 | 13.7 | 0 | 0 | 0 | 0 | 0 | 176 | 4201 | 60 | 173.589 | 23.249 | 0.272 | 34.284 | 0.57593 | 171.361 | -19.5384 | 0 | 125.197 | 54.803 | 114.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8821 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4202 | 2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 176 | 4202 | 120 | 173.589 | 23.249 | 0.272 | 94.284 | 1.5759 | 156.361 | -16.7849 | 0 | 125.197 | 54.803 | 114.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6424 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4203 | 3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 176 | 4203 | 180 | 173.589 | 23.249 | 0.272 | 154.284 | 2.5759 | 141.361 | -11.7616 | 0 | 125.197 | 54.803 | 114.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2692 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4204 | 4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 176 | 4204 | 240 | 173.589 | 23.249 | 0.272 | 214.284 | 3.5759 | 126.361 | -4.8993 | 0 | 125.197 | 54.803 | 114.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4216 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4205 | 5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 176 | 4205 | 300 | 173.589 | 23.249 | 0.272 | 274.284 | 4.5759 | 111.361 | 3.351 | 3.351 | 121.0024 | 58.9976 | 108.7995 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.3465 | 2.3465 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4206 | 6 | 11.5 | 4.36 | 15.08 | 19.44 | 15.08 | 7.54 | 176 | 4206 | 360 | 173.589 | 23.249 | 0.272 | 334.284 | 5.5759 | 96.361 | 12.5873 | 12.5873 | 110.6699 | 69.3301 | 95.1348 | -1.7906 | 0 | 12.8716 | 12.8716 | -9.6026 | 0% | 5.8205 | 0 | 0 | 16.6601 | 16.6601 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4207 | 7 | 12.6 | 47.97 | 59.08 | 107.05 | 59.08 | 29.54 | 176 | 4207 | 420 | 173.589 | 23.249 | 0.272 | 394.284 | 6.5759 | 81.361 | 22.4672 | 22.4672 | 100.5849 | 79.4151 | 81.362 | 18.8529 | 18.8529 | 50.4279 | 69.2808 | -1.0928 | 0% | 31.3288 | 0 | 0 | 191.4577 | 191.4577 | 0% | 11.65% | 11.65% | 80% | 9.32% | 2.9197 | 6.5939 | 6 | 17.5182 | 6.4566 | 9.15% | 9.15%
6 | 176 | 25 | 4208 | 8 | 13.4 | 151.31 | 100.75 | 252.06 | 100.75 | 50.38 | 176 | 4208 | 480 | 173.589 | 23.249 | 0.272 | 454.284 | 7.5759 | 66.361 | 32.6795 | 32.6795 | 90.1263 | 89.8737 | 67.6364 | 106.6247 | 106.6247 | 85.9955 | 192.6202 | 0.1313 | 13.13% | 87.1029 | 11.4365 | 8.0055 | 167.4694 | 167.4694 | 4.78% | 11.57% | 11.57% | 80% | 9.258% | 8.064 | 6.397 | 6 | 48.3838 | 17.8327 | 28.89% | 28.89%
6 | 176 | 25 | 4209 | 9 | 16.5 | 306.94 | 130.28 | 437.22 | 130.28 | 65.14 | 176 | 4209 | 540 | 173.589 | 23.249 | 0.272 | 514.284 | 8.5759 | 51.361 | 42.8851 | 42.8851 | 78.3672 | 101.6328 | 54.149 | 264.159 | 264.159 | 111.2009 | 375.3599 | 0.47753 | 47.75% | 169.7378 | 81.0552 | 56.7386 | 181.3267 | 181.3267 | 31.29% | 11.43% | 11.43% | 85% | 9.719% | 16.4963 | 5.6761 | 5.6761 | 93.6341 | 36.48 | 51.64% | 51.64%
6 | 176 | 25 | 4210 | 10 | 18 | 436.47 | 156.94 | 593.41 | 156.94 | 78.47 | 176 | 4210 | 600 | 173.589 | 23.249 | 0.272 | 574.284 | 9.5759 | 36.361 | 52.5937 | 52.5937 | 63.7311 | 116.2689 | 41.2537 | 413.0897 | 413.0897 | 133.9567 | 547.0464 | 0.58613 | 58.61% | 247.3744 | 144.9929 | 101.4951 | 186.3614 | 186.3614 | 54.46% | 11.38% | 11.38% | 90% | 10.24% | 25.3357 | 5.3514 | 5.3514 | 135.5814 | 56.0276 | 72.75% | 72.75%
6 | 176 | 25 | 4211 | 11 | 19.5 | 558.81 | 141.86 | 700.67 | 141.86 | 70.93 | 176 | 4211 | 660 | 173.589 | 23.249 | 0.272 | 634.284 | 10.5759 | 21.361 | 60.8836 | 60.8836 | 43.455 | 136.545 | 29.8288 | 554.8971 | 554.8971 | 121.0851 | 675.9822 | 0.63261 | 63.26% | 305.6791 | 193.3743 | 135.362 | 182.5704 | 182.5704 | 74.14% | 11.36% | 11.36% | 90% | 10.22% | 31.24 | 5.0425 | 5.0425 | 157.527 | 69.0845 | 86.28% | 86.28%
6 | 176 | 25 | 4212 | 12 | 20 | 656.58 | 162.14 | 818.72 | 162.14 | 81.07 | 176 | 4212 | 720 | 173.589 | 23.249 | 0.272 | 694.284 | 11.5759 | 6.361 | 65.9211 | 65.9211 | 14.4481 | 165.5519 | 22.3393 | 665.1849 | 665.1849 | 138.3951 | 803.58 | 0.66119 | 66.12% | 363.3789 | 240.2633 | 168.1843 | 173.0573 | 173.0573 | 97.18% | 11.35% | 11.35% | 95% | 10.78% | 39.1882 | 4.943 | 4.943 | 193.7074 | 86.6613 | 111.9% | 111.9%
6 | 176 | 25 | 4213 | 13 | 21.2 | 649.36 | 183.69 | 833.05 | 183.69 | 91.85 | 176 | 4213 | 780 | 173.589 | 23.249 | 0.272 | 754.284 | 12.5759 | -8.639 | 65.4666 | 65.4666 | 19.4131 | 199.4131 | 23.047 | 656.8298 | 656.8298 | 156.7892 | 813.619 | 0.66619 | 66.62% | 367.9185 | 245.1031 | 171.5722 | 171.9411 | 171.9411 | 99.79% | 11.35% | 11.35% | 95% | 10.79% | 39.6809 | 4.7114 | 4.7114 | 186.9528 | 87.7509 | 108.7% | 108.7%
6 | 176 | 25 | 4214 | 14 | 22.2 | 751.67 | 147.64 | 899.31 | 147.64 | 73.82 | 176 | 4214 | 840 | 173.589 | 23.249 | 0.272 | 814.284 | 13.5759 | -23.639 | 59.7756 | 59.7756 | 47.0431 | 227.0431 | 31.4008 | 742.5215 | 742.5215 | 126.0186 | 868.5402 | 0.67741 | 67.74% | 392.7539 | 266.0557 | 186.239 | 174.112 | 174.112 | 107% | 11.36% | 11.36% | 95% | 10.79% | 42.3871 | 4.5261 | 4.5261 | 191.8482 | 93.7353 | 110.2% | 110.2%
6 | 176 | 25 | 4215 | 15 | 21.1 | 679.08 | 146.86 | 825.94 | 146.86 | 73.43 | 176 | 4215 | 900 | 173.589 | 23.249 | 0.272 | 874.284 | 14.5759 | -38.639 | 51.18 | 51.18 | 66.2322 | 246.2322 | 43.1496 | 635.8937 | 635.8937 | 125.3529 | 761.2465 | 0.65642 | 65.64% | 344.2357 | 225.9633 | 158.1743 | 167.1424 | 167.1424 | 94.63% | 11.35% | 11.35% | 90% | 10.21% | 35.1626 | 4.7303 | 4.7303 | 166.3302 | 77.759 | 99.51% | 99.51%
6 | 176 | 25 | 4216 | 16 | 20.1 | 554.72 | 139.08 | 693.8 | 139.08 | 69.54 | 176 | 4216 | 960 | 173.589 | 23.249 | 0.272 | 934.284 | 15.5759 | -53.639 | 41.3521 | 41.3521 | 80.2885 | 260.2885 | 56.1712 | 467.4243 | 467.4243 | 118.7122 | 586.1365 | 0.60859 | 60.86% | 265.0509 | 161.3071 | 112.915 | 158.2398 | 158.2398 | 71.36% | 11.35% | 11.35% | 90% | 10.22% | 27.0769 | 4.9233 | 4.9233 | 133.3082 | 59.8782 | 84.24% | 84.24%
6 | 176 | 25 | 4217 | 17 | 19.9 | 318.89 | 119.92 | 438.81 | 119.92 | 59.96 | 176 | 4217 | 1020 | 173.589 | 23.249 | 0.272 | 994.284 | 16.5759 | -68.639 | 31.1197 | 31.1197 | 91.7703 | 271.7703 | 69.7112 | 213.9506 | 213.9506 | 102.3581 | 316.3087 | 0.4405 | 44.05% | 143.0348 | 63.0071 | 44.105 | 143.5641 | 143.5641 | 30.72% | 11.35% | 11.35% | 85% | 9.651% | 13.8049 | 4.9628 | 4.9628 | 68.5106 | 30.5284 | 47.72% | 47.72%
6 | 176 | 25 | 4218 | 18 | 19.6 | 176.67 | 87.5 | 264.17 | 87.5 | 43.75 | 176 | 4218 | 1080 | 173.589 | 23.249 | 0.272 | 1054.284 | 17.5759 | -83.639 | 20.9377 | 20.9377 | 102.1228 | 282.1228 | 83.4544 | 56.357 | 56.357 | 74.6859 | 131.043 | -0.078451 | 0% | 59.2576 | 0 | 0 | 129.9221 | 129.9221 | 0% | 11.37% | 11.37% | 80% | 9.093% | 5.3885 | 5.0224 | 5.0224 | 27.0635 | 11.9162 | 20.83% | 20.83%
6 | 176 | 25 | 4219 | 19 | 16.2 | 140.56 | 77.42 | 217.98 | 77.42 | 38.71 | 176 | 4219 | 1140 | 173.589 | 23.249 | 0.272 | 1114.284 | 18.5759 | -98.639 | 11.1353 | 11.1353 | 112.2102 | 292.2102 | 97.221 | -91.4844 | 0 | 66.0821 | 66.0821 | -1.0606 | 0% | 29.8823 | 0 | 0 | 117.6962 | 117.6962 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4220 | 20 | 15.6 | 53.89 | 52.86 | 106.75 | 52.86 | 26.43 | 176 | 4220 | 1200 | 173.589 | 23.249 | 0.272 | 1174.284 | 19.5759 | -113.639 | 2.0253 | 2.0253 | 122.6238 | 302.6238 | 110.854 | 0 | 0 | 45.1188 | 45.1188 | -1.957 | 0% | 20.4027 | 0 | 0 | 144.7702 | 144.7702 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4221 | 21 | 14.7 | 0 | 10.47 | 10.47 | 10.47 | 5.24 | 176 | 4221 | 1260 | 173.589 | 23.249 | 0.272 | 1234.284 | 20.5759 | -128.639 | -6.0416 | 0 | 125.197 | 305.197 | 114.0522 | 0 | 0 | 8.9367 | 8.9367 | -13.3635 | 0% | 4.0412 | 0 | 0 | -11.003 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4222 | 22 | 14.5 | 0 | 0 | 0 | 0 | 0 | 176 | 4222 | 1320 | 173.589 | 23.249 | 0.272 | 1294.284 | 21.5759 | -143.639 | -12.6543 | 0 | 125.197 | 305.197 | 114.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6971 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4223 | 23 | 14.3 | 0 | 0 | 0 | 0 | 0 | 176 | 4223 | 1380 | 173.589 | 23.249 | 0.272 | 1354.284 | 22.5759 | -158.639 | -17.3587 | 0 | 125.197 | 305.197 | 114.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3238 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
6 | 176 | 25 | 4224 | 24 | 13.4 | 0 | 0 | 0 | 0 | 0 | 176 | 4224 | 1440 | 173.589 | 23.249 | 0.272 | 1414.284 | 23.5759 | -173.639 | -19.7371 | 0 | 125.197 | 305.197 | 114.0522 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0174 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4225 | 1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 177 | 4225 | 60 | 174.5753 | 23.2161 | -0.17463 | 34.284 | 0.56849 | 171.4727 | -19.5822 | 0 | 125.1431 | 54.8569 | 114.0181 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7909 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4226 | 2 | 12.6 | 0 | 0 | 0 | 0 | 0 | 177 | 4226 | 120 | 174.5753 | 23.2161 | -0.17463 | 94.284 | 1.5685 | 156.4727 | -16.8458 | 0 | 125.1431 | 54.8569 | 114.0181 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9446 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4227 | 3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 177 | 4227 | 180 | 174.5753 | 23.2161 | -0.17463 | 154.284 | 2.5685 | 141.4727 | -11.8359 | 0 | 125.1431 | 54.8569 | 114.0181 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0316 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4228 | 4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 177 | 4228 | 240 | 174.5753 | 23.2161 | -0.17463 | 214.284 | 3.5685 | 126.4727 | -4.9834 | 0 | 125.1431 | 54.8569 | 114.0181 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6411 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4229 | 5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 177 | 4229 | 300 | 174.5753 | 23.2161 | -0.17463 | 274.284 | 4.5685 | 111.4727 | 3.2602 | 3.2602 | 121.0605 | 58.9395 | 108.9064 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.5682 | 5.5682 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4230 | 6 | 11.4 | 3.61 | 15.56 | 19.17 | 15.56 | 7.78 | 177 | 4230 | 360 | 174.5753 | 23.2161 | -0.17463 | 334.284 | 5.5685 | 96.4727 | 12.4923 | 12.4923 | 110.7218 | 69.2782 | 95.2396 | -1.5241 | 0 | 13.2813 | 13.2813 | -9.2991 | 0% | 6.0058 | 0 | 0 | 20.3641 | 20.3641 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4231 | 7 | 11 | 48.69 | 56.03 | 104.72 | 56.03 | 28.02 | 177 | 4231 | 420 | 174.5753 | 23.2161 | -0.17463 | 394.284 | 6.5685 | 81.4727 | 22.3696 | 22.3696 | 100.6345 | 79.3655 | 81.4635 | 18.9908 | 18.9908 | 47.8246 | 66.8154 | -1.2181 | 0% | 30.2139 | 0 | 0 | 195.1782 | 195.1782 | 0% | 11.71% | 11.71% | 80% | 9.372% | 2.8316 | 7.0013 | 6 | 16.9898 | 6.2619 | 8.705% | 8.705%
6 | 177 | 26 | 4232 | 8 | 11.6 | 150.47 | 108.81 | 259.28 | 108.81 | 54.41 | 177 | 4232 | 480 | 174.5753 | 23.2161 | -0.17463 | 454.284 | 7.5685 | 66.4727 | 32.5811 | 32.5811 | 90.1785 | 89.8215 | 67.7334 | 105.8798 | 105.8798 | 92.8751 | 198.7549 | 0.13122 | 13.12% | 89.877 | 11.7935 | 8.2555 | 172.0809 | 172.0809 | 4.797% | 11.63% | 11.63% | 80% | 9.304% | 8.362 | 6.8464 | 6 | 50.1719 | 18.4918 | 29.16% | 29.16%
6 | 177 | 26 | 4233 | 9 | 14.4 | 330.19 | 117.22 | 447.41 | 117.22 | 58.61 | 177 | 4233 | 540 | 174.5753 | 23.2161 | -0.17463 | 514.284 | 8.5685 | 51.4727 | 42.7878 | 42.7878 | 78.4301 | 101.5699 | 54.2391 | 284.07 | 284.07 | 100.0535 | 384.1236 | 0.47261 | 47.26% | 173.7007 | 82.0934 | 57.4653 | 185.6206 | 185.6206 | 30.96% | 11.48% | 11.48% | 85% | 9.758% | 16.9498 | 6.1571 | 6 | 101.6991 | 37.4831 | 54.79% | 54.79%
6 | 177 | 26 | 4234 | 10 | 17.6 | 500.56 | 119.25 | 619.81 | 119.25 | 59.63 | 177 | 4234 | 600 | 174.5753 | 23.2161 | -0.17463 | 574.284 | 9.5685 | 36.4727 | 52.5007 | 52.5007 | 63.8205 | 116.1795 | 41.3316 | 473.7701 | 473.7701 | 101.7862 | 575.5563 | 0.59537 | 59.54% | 260.2666 | 154.9548 | 108.4684 | 193.0189 | 193.0189 | 56.2% | 11.38% | 11.38% | 90% | 10.24% | 26.6603 | 5.4364 | 5.4364 | 144.9372 | 58.9569 | 75.09% | 75.09%
6 | 177 | 26 | 4235 | 11 | 18.7 | 591.19 | 127.31 | 718.5 | 127.31 | 63.66 | 177 | 4235 | 660 | 174.5753 | 23.2161 | -0.17463 | 634.284 | 10.5685 | 21.4727 | 60.8028 | 60.8028 | 43.6011 | 136.3989 | 29.8817 | 587.2014 | 587.2014 | 108.6659 | 695.8673 | 0.63496 | 63.5% | 314.6712 | 199.8033 | 139.8623 | 186.9412 | 186.9412 | 74.82% | 11.36% | 11.36% | 90% | 10.22% | 32.1704 | 5.2053 | 5.2053 | 167.4558 | 71.142 | 89.58% | 89.58%
6 | 177 | 26 | 4236 | 12 | 19.1 | 587.97 | 180.36 | 768.33 | 180.36 | 90.18 | 177 | 4236 | 720 | 174.5753 | 23.2161 | -0.17463 | 694.284 | 11.5685 | 6.4727 | 65.8696 | 65.8696 | 14.6798 | 165.3202 | 22.3381 | 595.9204 | 595.9204 | 153.9469 | 749.8673 | 0.64831 | 64.83% | 339.09 | 219.8368 | 153.8858 | 172.9718 | 172.9718 | 88.97% | 11.35% | 11.35% | 90% | 10.22% | 34.6517 | 5.1233 | 5.1233 | 177.5317 | 76.6292 | 102.6% | 102.6%
6 | 177 | 26 | 4237 | 13 | 20 | 584.72 | 183.47 | 768.19 | 183.47 | 91.74 | 177 | 4237 | 780 | 174.5753 | 23.2161 | -0.17463 | 754.284 | 12.5685 | -8.5273 | 65.46 | 65.46 | 19.1542 | 199.1542 | 22.9775 | 591.782 | 591.782 | 156.6014 | 748.3834 | 0.65066 | 65.07% | 338.419 | 220.1955 | 154.1369 | 170.3649 | 170.3649 | 90.47% | 11.35% | 11.35% | 90% | 10.22% | 34.5756 | 4.943 | 4.943 | 170.9071 | 76.4608 | 100.3% | 100.3%
6 | 177 | 26 | 4238 | 14 | 21.1 | 657.22 | 203.19 | 860.41 | 203.19 | 101.6 | 177 | 4238 | 840 | 174.5753 | 23.2161 | -0.17463 | 814.284 | 13.5685 | -23.5273 | 59.8039 | 59.8039 | 46.8365 | 226.8365 | 31.3009 | 649.7238 | 649.7238 | 173.4335 | 823.1573 | 0.66752 | 66.75% | 372.2317 | 248.4721 | 173.9305 | 173.8759 | 173.8759 | 100% | 11.35% | 11.35% | 95% | 10.79% | 40.1479 | 4.7303 | 4.7303 | 189.9123 | 88.7835 | 109.2% | 109.2%
6 | 177 | 26 | 4239 | 15 | 20.8 | 532.97 | 192.42 | 725.39 | 192.42 | 96.21 | 177 | 4239 | 900 | 174.5753 | 23.2161 | -0.17463 | 874.284 | 14.5685 | -38.5273 | 51.2259 | 51.2259 | 66.0767 | 246.0767 | 43.0425 | 499.6268 | 499.6268 | 164.2407 | 663.8676 | 0.63378 | 63.38% | 300.2009 | 190.2625 | 133.1837 | 165.1153 | 165.1153 | 80.66% | 11.35% | 11.35% | 90% | 10.21% | 30.6547 | 4.7875 | 4.7875 | 146.759 | 67.7902 | 88.88% | 88.88%
6 | 177 | 26 | 4240 | 16 | 20.9 | 242.03 | 132.22 | 374.25 | 132.22 | 66.11 | 177 | 4240 | 960 | 174.5753 | 23.2161 | -0.17463 | 934.284 | 15.5685 | -53.5273 | 41.4052 | 41.4052 | 80.1636 | 260.1636 | 56.0636 | 204.2979 | 204.2979 | 112.8568 | 317.1547 | 0.44839 | 44.84% | 143.4174 | 64.3075 | 45.0153 | 147.3599 | 147.3599 | 30.55% | 11.33% | 11.33% | 85% | 9.629% | 13.8095 | 4.7684 | 4.7684 | 65.8486 | 30.5385 | 44.69% | 44.69%
6 | 177 | 26 | 4241 | 17 | 19.5 | 267.14 | 179.53 | 446.67 | 179.53 | 89.77 | 177 | 4241 | 1020 | 174.5753 | 23.2161 | -0.17463 | 994.284 | 16.5685 | -68.5273 | 31.1743 | 31.1743 | 91.6618 | 271.6618 | 69.6054 | 179.8424 | 179.8424 | 153.2384 | 333.0808 | 0.45616 | 45.62% | 150.6192 | 68.7061 | 48.0942 | 145.2519 | 145.2519 | 33.11% | 11.36% | 11.36% | 85% | 9.66% | 14.55 | 5.0425 | 5.0425 | 73.3679 | 32.176 | 50.51% | 50.51%
6 | 177 | 26 | 4242 | 18 | 19.5 | 236.19 | 132.97 | 369.16 | 132.97 | 66.49 | 177 | 4242 | 1080 | 174.5753 | 23.2161 | -0.17463 | 1054.284 | 17.5685 | -83.5273 | 20.99 | 20.99 | 102.0219 | 282.0219 | 83.3513 | 76.3431 | 76.3431 | 113.497 | 189.8401 | 0.1937 | 19.37% | 85.8457 | 16.6282 | 11.6397 | 136.6421 | 136.6421 | 8.518% | 11.37% | 11.37% | 80% | 9.095% | 7.8077 | 5.0425 | 5.0425 | 39.3701 | 17.266 | 28.81% | 28.81%
6 | 177 | 26 | 4243 | 19 | 18.4 | 162.14 | 99.17 | 261.31 | 99.17 | 49.59 | 177 | 4243 | 1140 | 174.5753 | 23.2161 | -0.17463 | 1114.284 | 18.5685 | -98.5273 | 11.1823 | 11.1823 | 112.1114 | 292.1114 | 97.1217 | -103.6535 | 0 | 84.6469 | 84.6469 | -0.59353 | 0% | 38.2773 | 0 | 0 | 124.7571 | 124.7571 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4244 | 20 | 18.4 | 56.75 | 66.11 | 122.86 | 66.11 | 33.06 | 177 | 4244 | 1200 | 174.5753 | 23.2161 | -0.17463 | 1174.284 | 19.5685 | -113.5273 | 2.0642 | 2.0642 | 122.5233 | 302.5233 | 110.76 | 0 | 0 | 56.4284 | 56.4284 | -1.2924 | 0% | 25.5169 | 0 | 0 | 150.7163 | 150.7163 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4245 | 21 | 17.5 | 0 | 14.81 | 14.81 | 14.81 | 7.41 | 177 | 4245 | 1260 | 174.5753 | 23.2161 | -0.17463 | 1234.284 | 20.5685 | -128.5273 | -6.0141 | 0 | 125.1431 | 305.1431 | 114.0181 | 0 | 0 | 12.6411 | 12.6411 | -8.7127 | 0% | 5.7163 | 0 | 0 | -5.8185 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4246 | 22 | 15.3 | 0 | 0 | 0 | 0 | 0 | 177 | 4246 | 1320 | 174.5753 | 23.2161 | -0.17463 | 1294.284 | 21.5685 | -143.5273 | -12.6414 | 0 | 125.1431 | 305.1431 | 114.0181 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8726 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4247 | 23 | 14.3 | 0 | 0 | 0 | 0 | 0 | 177 | 4247 | 1380 | 174.5753 | 23.2161 | -0.17463 | 1354.284 | 22.5685 | -158.5273 | -17.3635 | 0 | 125.1431 | 305.1431 | 114.0181 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6359 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
6 | 177 | 26 | 4248 | 24 | 13.3 | 0 | 0 | 0 | 0 | 0 | 177 | 4248 | 1440 | 174.5753 | 23.2161 | -0.17463 | 1414.284 | 23.5685 | -173.5273 | -19.7614 | 0 | 125.1431 | 305.1431 | 114.0181 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3992 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4249 | 1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 178 | 4249 | 60 | 175.5616 | 23.1769 | -0.61995 | 34.284 | 0.56107 | 171.584 | -19.6322 | 0 | 125.0787 | 54.9213 | 113.9773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1984 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4250 | 2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 178 | 4250 | 120 | 175.5616 | 23.1769 | -0.61995 | 94.284 | 1.5611 | 156.584 | -16.9126 | 0 | 125.0787 | 54.9213 | 113.9773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4963 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4251 | 3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 178 | 4251 | 180 | 175.5616 | 23.1769 | -0.61995 | 154.284 | 2.5611 | 141.584 | -11.9158 | 0 | 125.0787 | 54.9213 | 113.9773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.2701 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4252 | 4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 178 | 4252 | 240 | 175.5616 | 23.1769 | -0.61995 | 214.284 | 3.5611 | 126.584 | -5.0727 | 0 | 125.0787 | 54.9213 | 113.9773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9653 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4253 | 5 | 11.4 | 0 | 0 | 0 | 0 | 0 | 178 | 4253 | 300 | 175.5616 | 23.1769 | -0.61995 | 274.284 | 4.5611 | 111.584 | 3.1646 | 3.1646 | 121.1143 | 58.8857 | 109.0142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.0165 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4254 | 6 | 11.4 | 4.17 | 17.69 | 21.86 | 17.69 | 8.85 | 178 | 4254 | 360 | 175.5616 | 23.1769 | -0.61995 | 334.284 | 5.5611 | 96.584 | 12.3928 | 12.3928 | 110.769 | 69.231 | 95.3445 | -1.8098 | 0 | 15.0994 | 15.0994 | -8.0826 | 0% | 6.8279 | 0 | 0 | 6.1995 | 6.1995 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4255 | 7 | 12.7 | 13.33 | 45.83 | 59.16 | 45.83 | 22.92 | 178 | 4255 | 420 | 175.5616 | 23.1769 | -0.61995 | 394.284 | 6.5611 | 81.584 | 22.268 | 22.268 | 100.6787 | 79.3213 | 81.5646 | 5.1603 | 5.1603 | 39.1184 | 44.2786 | -2.1586 | 0% | 20.0228 | 0 | 0 | 170.3975 | 170.3975 | 0% | 11.66% | 11.66% | 80% | 9.324% | 1.867 | 6.5691 | 6 | 11.202 | 4.1287 | 6.574% | 6.574%
6 | 178 | 27 | 4256 | 8 | 15 | 39.81 | 128.53 | 168.34 | 128.53 | 64.27 | 178 | 4256 | 480 | 175.5616 | 23.1769 | -0.61995 | 454.284 | 7.5611 | 66.584 | 32.4787 | 32.4787 | 90.2247 | 89.7753 | 67.8293 | 27.9765 | 27.9765 | 109.7072 | 137.6837 | -0.11063 | 0% | 62.2606 | 0 | 0 | 144.9169 | 144.9169 | 0% | 11.53% | 11.53% | 80% | 9.227% | 5.745 | 6.0165 | 6 | 34.4698 | 12.7045 | 23.79% | 23.79%
6 | 178 | 27 | 4257 | 9 | 17.8 | 152.69 | 192.31 | 345 | 192.31 | 96.16 | 178 | 4257 | 540 | 175.5616 | 23.1769 | -0.61995 | 514.284 | 8.5611 | 51.584 | 42.6863 | 42.6863 | 78.4863 | 101.5137 | 54.3272 | 131.3335 | 131.3335 | 164.1469 | 295.4804 | 0.39913 | 39.91% | 133.6162 | 53.3298 | 37.3309 | 158.6655 | 158.6655 | 23.53% | 11.41% | 11.41% | 80% | 9.13% | 12.1997 | 5.3938 | 5.3938 | 65.8027 | 26.9787 | 41.47% | 41.47%
6 | 178 | 27 | 4258 | 10 | 19.8 | 233.33 | 228.25 | 461.58 | 228.25 | 114.13 | 178 | 4258 | 600 | 175.5616 | 23.1769 | -0.61995 | 574.284 | 9.5611 | 36.584 | 52.403 | 52.403 | 63.9022 | 116.0978 | 41.4066 | 220.8768 | 220.8768 | 194.8236 | 415.7004 | 0.52688 | 52.69% | 187.9797 | 99.0432 | 69.3302 | 165.2281 | 165.2281 | 41.96% | 11.36% | 11.36% | 85% | 9.653% | 18.1453 | 4.9826 | 4.9826 | 90.4104 | 40.1267 | 54.72% | 54.72%
6 | 178 | 27 | 4259 | 11 | 21.3 | 201.47 | 207.86 | 409.33 | 207.86 | 103.93 | 178 | 4259 | 660 | 175.5616 | 23.1769 | -0.61995 | 634.284 | 10.5611 | 21.584 | 60.7165 | 60.7165 | 43.7394 | 136.2606 | 29.9304 | 200.1817 | 200.1817 | 177.4196 | 377.6013 | 0.50764 | 50.76% | 170.7513 | 86.6795 | 60.6756 | 158.7888 | 158.7888 | 38.21% | 11.32% | 11.32% | 85% | 9.624% | 16.4323 | 4.6926 | 4.6926 | 77.1095 | 36.3386 | 48.56% | 48.56%
6 | 178 | 27 | 4260 | 12 | 22.3 | 345.56 | 248.69 | 594.25 | 248.69 | 124.35 | 178 | 4260 | 720 | 175.5616 | 23.1769 | -0.61995 | 694.284 | 11.5611 | 6.584 | 65.8116 | 65.8116 | 14.907 | 165.093 | 22.3312 | 350.4089 | 350.4089 | 212.2702 | 562.6791 | 0.60899 | 60.9% | 254.4435 | 154.9524 | 108.4667 | 158.6949 | 158.6949 | 68.35% | 11.32% | 11.32% | 90% | 10.19% | 25.9272 | 4.508 | 4.508 | 116.8788 | 57.3358 | 73.65% | 73.65%
6 | 178 | 27 | 4261 | 13 | 22.9 | 528.06 | 249.53 | 777.59 | 249.53 | 124.77 | 178 | 4261 | 780 | 175.5616 | 23.1769 | -0.61995 | 754.284 | 12.5611 | -8.416 | 65.4468 | 65.4468 | 18.8923 | 198.8923 | 22.9025 | 534.7903 | 534.7903 | 212.9872 | 747.7774 | 0.659 | 65.9% | 338.145 | 222.8361 | 155.9853 | 165.9396 | 165.9396 | 94% | 11.34% | 11.34% | 90% | 10.21% | 34.5222 | 4.4006 | 4.4006 | 151.917 | 76.3429 | 91.55% | 91.55%
6 | 178 | 27 | 4262 | 14 | 23.6 | 271.67 | 276.11 | 547.78 | 276.11 | 138.06 | 178 | 4262 | 840 | 175.5616 | 23.1769 | -0.61995 | 814.284 | 13.5611 | -23.416 | 59.8264 | 59.8264 | 46.6232 | 226.6232 | 31.1972 | 268.8049 | 268.8049 | 235.6746 | 504.4796 | 0.59206 | 59.21% | 228.1257 | 135.0635 | 94.5444 | 259.6364 | 259.6364 | 36.41% | 11.29% | 11.29% | 90% | 10.16% | 23.187 | 4.2784 | 4.2784 | 99.2042 | 51.276 | 38.21% | 38.21%
6 | 178 | 27 | 4263 | 15 | 24.2 | 387.03 | 269.25 | 656.28 | 269.25 | 134.63 | 178 | 4263 | 900 | 175.5616 | 23.1769 | -0.61995 | 874.284 | 14.5611 | -38.416 | 51.2668 | 51.2668 | 65.9143 | 245.9143 | 42.9331 | 363.2553 | 363.2553 | 229.8193 | 593.0746 | 0.62589 | 62.59% | 268.1883 | 167.8569 | 117.4998 | 266.8116 | 266.8116 | 44.04% | 11.3% | 11.3% | 90% | 10.17% | 27.2849 | 4.1765 | 4.1765 | 113.9553 | 60.3381 | 42.71% | 42.71%
6 | 178 | 27 | 4264 | 16 | 24.6 | 405.19 | 196.19 | 601.38 | 196.19 | 98.1 | 178 | 4264 | 960 | 175.5616 | 23.1769 | -0.61995 | 934.284 | 15.5611 | -53.416 | 41.4537 | 41.4537 | 80.0325 | 260.0325 | 55.9548 | 342.6582 | 342.6582 | 167.4586 | 510.1169 | 0.59861 | 59.86% | 230.6749 | 138.0835 | 96.6584 | 262.5741 | 262.5741 | 36.81% | 11.28% | 11.28% | 90% | 10.15% | 23.4153 | 4.1099 | 4.1099 | 96.2356 | 51.7809 | 36.65% | 36.65%
6 | 178 | 27 | 4265 | 17 | 24.5 | 317.03 | 176.39 | 493.42 | 176.39 | 88.2 | 178 | 4265 | 1020 | 175.5616 | 23.1769 | -0.61995 | 994.284 | 16.5611 | -68.416 | 31.2243 | 31.2243 | 91.5477 | 271.5477 | 69.499 | 214.1858 | 214.1858 | 150.5583 | 364.7441 | 0.51616 | 51.62% | 164.9373 | 85.1337 | 59.5936 | 255.2424 | 255.2424 | 23.35% | 11.24% | 11.24% | 85% | 9.558% | 15.7641 | 4.1265 | 4.1265 | 65.0502 | 34.8609 | 25.49% | 25.49%
6 | 178 | 27 | 4266 | 18 | 24.3 | 303.25 | 127.31 | 430.56 | 127.31 | 63.66 | 178 | 4266 | 1080 | 175.5616 | 23.1769 | -0.61995 | 1054.284 | 17.5611 | -83.416 | 21.0377 | 21.0377 | 101.9162 | 281.9162 | 83.2483 | 99.3142 | 99.3142 | 108.6659 | 207.98 | 0.29714 | 29.71% | 94.0486 | 27.9454 | 19.5618 | 245.8 | 245.8 | 7.958% | 11.21% | 11.21% | 80% | 8.97% | 8.4358 | 4.1598 | 4.1598 | 35.0907 | 18.655 | 14.28% | 14.28%
6 | 178 | 27 | 4267 | 19 | 24.6 | 138.14 | 98.97 | 237.11 | 98.97 | 49.49 | 178 | 4267 | 1140 | 175.5616 | 23.1769 | -0.61995 | 1114.284 | 18.5611 | -98.416 | 11.2246 | 11.2246 | 112.0083 | 292.0083 | 97.0232 | -86.7715 | 0 | 84.4762 | 84.4762 | -0.43629 | 0% | 38.2001 | 0 | 0 | 233.9033 | 233.9033 | 0% | 11.17% | 0% | 80% | 0% | 0 | 4.1099 | 4.1099 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4268 | 20 | 23.7 | 69.72 | 57.97 | 127.69 | 57.97 | 28.99 | 178 | 4268 | 1200 | 175.5616 | 23.1769 | -0.61995 | 1174.284 | 19.5611 | -113.416 | 2.098 | 2.098 | 122.419 | 302.419 | 110.6675 | 0 | 0 | 49.4805 | 49.4805 | -1.3525 | 0% | 22.3751 | 0 | 0 | 169.5981 | 169.5981 | 0% | 11.2% | 0% | 80% | 0% | 0 | 4.2613 | 4.2613 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4269 | 21 | 22.5 | 0 | 14.36 | 14.36 | 14.36 | 7.18 | 178 | 4269 | 1260 | 175.5616 | 23.1769 | -0.61995 | 1234.284 | 20.5611 | -128.416 | -5.9919 | 0 | 125.0787 | 305.0787 | 113.9773 | 0 | 0 | 12.257 | 12.257 | -8.1131 | 0% | 5.5426 | 0 | 0 | 0.01248 | 0.01248 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4719 | 4.4719 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4270 | 22 | 22.2 | 0 | 0 | 0 | 0 | 0 | 178 | 4270 | 1320 | 175.5616 | 23.1769 | -0.61995 | 1294.284 | 21.5611 | -143.416 | -12.6343 | 0 | 125.0787 | 305.0787 | 113.9773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.0086 | 0 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.5261 | 4.5261 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4271 | 23 | 21.2 | 0 | 0 | 0 | 0 | 0 | 178 | 4271 | 1380 | 175.5616 | 23.1769 | -0.61995 | 1354.284 | 22.5611 | -158.416 | -17.3744 | 0 | 125.0787 | 305.0787 | 113.9773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.154 | 0 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.7114 | 4.7114 | 0 | 0 | 0% | 0%
6 | 178 | 27 | 4272 | 24 | 18.7 | 0 | 0 | 0 | 0 | 0 | 178 | 4272 | 1440 | 175.5616 | 23.1769 | -0.61995 | 1414.284 | 23.5611 | -173.416 | -19.7921 | 0 | 125.0787 | 305.0787 | 113.9773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5854 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2053 | 5.2053 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4273 | 1 | 16.4 | 0 | 0 | 0 | 0 | 0 | 179 | 4273 | 60 | 176.5479 | 23.1312 | -1.0636 | 34.284 | 0.55367 | 171.6949 | -19.6884 | 0 | 125.0039 | 54.9961 | 113.9299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.161 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4274 | 2 | 14.8 | 0 | 0 | 0 | 0 | 0 | 179 | 4274 | 120 | 176.5479 | 23.1312 | -1.0636 | 94.284 | 1.5537 | 156.6949 | -16.9853 | 0 | 125.0039 | 54.9961 | 113.9299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1257 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4275 | 3 | 14.8 | 0 | 0 | 0 | 0 | 0 | 179 | 4275 | 180 | 176.5479 | 23.1312 | -1.0636 | 154.284 | 2.5537 | 141.6949 | -12.0012 | 0 | 125.0039 | 54.9961 | 113.9299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6519 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4276 | 4 | 14.7 | 0 | 0 | 0 | 0 | 0 | 179 | 4276 | 240 | 176.5479 | 23.1312 | -1.0636 | 214.284 | 3.5537 | 126.6949 | -5.167 | 0 | 125.0039 | 54.9961 | 113.9299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8043 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4277 | 5 | 13.9 | 0 | 0 | 0 | 0 | 0 | 179 | 4277 | 300 | 176.5479 | 23.1312 | -1.0636 | 274.284 | 4.5537 | 111.6949 | 3.0645 | 3.0645 | 121.1638 | 58.8362 | 109.1228 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.85089 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4278 | 6 | 13.7 | 1.31 | 14.64 | 15.95 | 14.64 | 7.32 | 179 | 4278 | 360 | 176.5479 | 23.1312 | -1.0636 | 334.284 | 5.5537 | 96.6949 | 12.289 | 12.289 | 110.8113 | 69.1887 | 95.4496 | -0.58452 | 0 | 12.496 | 12.496 | -9.5105 | 0% | 5.6507 | 0 | 0 | 9.7389 | 9.7389 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4279 | 7 | 15 | 28.97 | 59.64 | 88.61 | 59.64 | 29.82 | 179 | 4279 | 420 | 176.5479 | 23.1312 | -1.0636 | 394.284 | 6.5537 | 81.6949 | 22.1622 | 22.1622 | 100.7177 | 79.2823 | 81.6652 | 11.1322 | 11.1322 | 50.9059 | 62.0381 | -1.2259 | 0% | 28.0536 | 0 | 0 | 177.4265 | 177.4265 | 0% | 11.55% | 11.55% | 80% | 9.244% | 2.5933 | 6.0165 | 6 | 15.5596 | 5.7348 | 8.77% | 8.77%
6 | 179 | 28 | 4280 | 8 | 17 | 89.72 | 129.72 | 219.44 | 129.72 | 64.86 | 179 | 4280 | 480 | 176.5479 | 23.1312 | -1.0636 | 454.284 | 7.5537 | 66.6949 | 32.3723 | 32.3723 | 90.2651 | 89.7349 | 67.9241 | 62.9786 | 62.9786 | 110.7229 | 173.7016 | 0.10498 | 10.5% | 78.5479 | 8.246 | 5.7722 | 152.7834 | 152.7834 | 3.778% | 11.46% | 11.46% | 80% | 9.164% | 7.1983 | 5.5661 | 5.5661 | 40.0667 | 15.9185 | 26.22% | 26.22%
6 | 179 | 28 | 4281 | 9 | 19.9 | 53.06 | 178.53 | 231.59 | 178.53 | 89.27 | 179 | 4281 | 540 | 176.5479 | 23.1312 | -1.0636 | 514.284 | 8.5537 | 51.6949 | 42.5806 | 42.5806 | 78.5358 | 101.4642 | 54.4135 | 45.6342 | 45.6342 | 152.3849 | 198.019 | 0.22336 | 22.34% | 89.5442 | 20.0006 | 14.0005 | 158.3857 | 158.3857 | 8.839% | 11.36% | 11.36% | 80% | 9.084% | 8.1344 | 4.9628 | 4.9628 | 40.3691 | 17.9885 | 25.49% | 25.49%
6 | 179 | 28 | 4282 | 10 | 21 | 211.03 | 186.31 | 397.34 | 186.31 | 93.16 | 179 | 4282 | 600 | 176.5479 | 23.1312 | -1.0636 | 574.284 | 9.5537 | 36.6949 | 52.3009 | 52.3009 | 63.9763 | 116.0237 | 41.4787 | 199.8197 | 199.8197 | 159.0255 | 358.8453 | 0.49032 | 49.03% | 162.2698 | 79.5639 | 55.6947 | 165.8141 | 165.8141 | 33.59% | 11.33% | 11.33% | 85% | 9.629% | 15.6243 | 4.7493 | 4.7493 | 74.2044 | 34.5517 | 44.75% | 44.75%
6 | 179 | 28 | 4283 | 11 | 22.9 | 280.28 | 215.75 | 496.03 | 215.75 | 107.88 | 179 | 4283 | 660 | 176.5479 | 23.1312 | -1.0636 | 634.284 | 10.5537 | 21.6949 | 60.6248 | 60.6248 | 43.8698 | 136.1302 | 29.9749 | 278.6135 | 278.6135 | 184.1541 | 462.7677 | 0.56969 | 56.97% | 209.2635 | 119.2154 | 83.4508 | 166.1229 | 166.1229 | 50.23% | 11.3% | 11.3% | 85% | 9.603% | 20.0966 | 4.4006 | 4.4006 | 88.4361 | 44.4418 | 53.24% | 53.24%
6 | 179 | 28 | 4284 | 12 | 25.4 | 271.25 | 232.22 | 503.47 | 232.22 | 116.11 | 179 | 4284 | 720 | 176.5479 | 23.1312 | -1.0636 | 694.284 | 11.5537 | 6.6949 | 65.7471 | 65.7471 | 15.1294 | 164.8706 | 22.3187 | 275.22 | 275.22 | 198.2122 | 473.4322 | 0.5863 | 58.63% | 214.086 | 125.5181 | 87.8626 | 200.9946 | 200.9946 | 43.71% | 11.26% | 11.26% | 85% | 9.567% | 20.4811 | 3.9802 | 3.9802 | 81.5184 | 45.2921 | 40.56% | 40.56%
6 | 179 | 28 | 4285 | 13 | 26.8 | 215.14 | 380.56 | 595.7 | 380.56 | 190.28 | 179 | 4285 | 780 | 176.5479 | 23.1312 | -1.0636 | 754.284 | 12.5537 | -8.3051 | 65.4269 | 65.4269 | 18.6278 | 198.6278 | 22.822 | 218.0457 | 218.0457 | 324.8283 | 542.874 | 0.61961 | 61.96% | 245.4876 | 152.1066 | 106.4746 | 273.2938 | 273.2938 | 38.96% | 11.26% | 11.26% | 90% | 10.13% | 24.8685 | 3.7639 | 3.7639 | 93.6021 | 54.9945 | 34.25% | 34.25%
6 | 179 | 28 | 4286 | 14 | 27.2 | 370.28 | 350.14 | 720.42 | 350.14 | 175.07 | 179 | 4286 | 840 | 176.5479 | 23.1312 | -1.0636 | 814.284 | 13.5537 | -23.3051 | 59.8431 | 59.8431 | 46.4034 | 226.4034 | 31.0897 | 366.7284 | 366.7284 | 298.8632 | 665.5916 | 0.65487 | 65.49% | 300.9805 | 197.104 | 137.9728 | 278.17 | 278.17 | 49.6% | 11.3% | 11.3% | 90% | 10.17% | 30.6064 | 3.7046 | 3.7046 | 113.3845 | 67.6833 | 40.76% | 40.76%
6 | 179 | 28 | 4287 | 15 | 27.3 | 575.36 | 200.47 | 775.83 | 200.47 | 100.24 | 179 | 4287 | 900 | 176.5479 | 23.1312 | -1.0636 | 874.284 | 14.5537 | -38.3051 | 51.3026 | 51.3026 | 65.7451 | 245.7451 | 42.8214 | 540.7242 | 540.7242 | 171.1118 | 711.836 | 0.66486 | 66.49% | 321.8923 | 214.0122 | 149.8086 | 287.0147 | 287.0147 | 52.2% | 11.32% | 11.32% | 90% | 10.18% | 32.7845 | 3.69 | 3.69 | 120.9735 | 72.5001 | 42.15% | 42.15%
6 | 179 | 28 | 4288 | 16 | 27.1 | 196.47 | 225.28 | 421.75 | 225.28 | 112.64 | 179 | 4288 | 960 | 176.5479 | 23.1312 | -1.0636 | 934.284 | 15.5537 | -53.3051 | 41.4974 | 41.4974 | 79.8953 | 259.8953 | 55.8446 | 166.4778 | 166.4778 | 192.2885 | 358.7663 | 0.52675 | 52.67% | 162.2341 | 85.4567 | 59.8197 | 267.1136 | 267.1136 | 22.39% | 11.18% | 11.18% | 85% | 9.503% | 15.4167 | 3.7193 | 3.7193 | 57.3395 | 34.0926 | 21.47% | 21.47%
6 | 179 | 28 | 4289 | 17 | 27.7 | 136.94 | 200.56 | 337.5 | 200.56 | 100.28 | 179 | 4289 | 1020 | 176.5479 | 23.1312 | -1.0636 | 994.284 | 16.5537 | -68.3051 | 31.2697 | 31.2697 | 91.4284 | 271.4284 | 69.3921 | 92.8566 | 92.8566 | 171.1887 | 264.0453 | 0.43207 | 43.21% | 119.4013 | 51.5894 | 36.1126 | 262.7654 | 262.7654 | 13.74% | 11.13% | 11.13% | 80% | 8.9% | 10.6267 | 3.6321 | 3.6321 | 38.5971 | 23.5001 | 14.69% | 14.69%
6 | 179 | 28 | 4290 | 18 | 26.5 | 66.58 | 143.33 | 209.91 | 143.33 | 71.67 | 179 | 4290 | 1080 | 176.5479 | 23.1312 | -1.0636 | 1054.284 | 17.5537 | -83.3051 | 21.0808 | 21.0808 | 101.8058 | 281.8058 | 83.1456 | 22.0919 | 22.0919 | 122.3398 | 144.4317 | 0.10655 | 10.65% | 65.312 | 6.9589 | 4.8712 | 240.9705 | 240.9705 | 2.022% | 11.12% | 11.12% | 80% | 8.894% | 5.8089 | 3.8091 | 3.8091 | 22.1266 | 12.8459 | 9.182% | 9.182%
6 | 179 | 28 | 4291 | 19 | 25.6 | 70.64 | 119.72 | 190.36 | 119.72 | 59.86 | 179 | 4291 | 1140 | 176.5479 | 23.1312 | -1.0636 | 1114.284 | 18.5537 | -98.3051 | 11.2621 | 11.2621 | 111.901 | 291.901 | 96.9256 | -43.6144 | 0 | 102.1874 | 102.1874 | -0.20045 | 0% | 46.2091 | 0 | 0 | 170.8239 | 170.8239 | 0% | 11.14% | 0% | 80% | 0% | 0 | 3.9484 | 3.9484 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4292 | 20 | 23.6 | 21.47 | 66.58 | 88.05 | 66.58 | 33.29 | 179 | 4292 | 1200 | 176.5479 | 23.1312 | -1.0636 | 1174.284 | 19.5537 | -113.3051 | 2.1267 | 2.1267 | 122.3109 | 302.3109 | 110.5765 | 0 | 0 | 56.8296 | 56.8296 | -1.0774 | 0% | 25.6983 | 0 | 0 | 162.9842 | 162.9842 | 0% | 11.2% | 0% | 80% | 0% | 0 | 4.2784 | 4.2784 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4293 | 21 | 22.5 | 0 | 17.31 | 17.31 | 17.31 | 8.66 | 179 | 4293 | 1260 | 176.5479 | 23.1312 | -1.0636 | 1234.284 | 20.5537 | -128.3051 | -5.9753 | 0 | 125.0039 | 305.0039 | 113.9299 | 0 | 0 | 14.775 | 14.775 | -6.5934 | 0% | 6.6813 | 0 | 0 | -0.82183 | 0 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4719 | 4.4719 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4294 | 22 | 19.9 | 0 | 0 | 0 | 0 | 0 | 179 | 4294 | 1320 | 176.5479 | 23.1312 | -1.0636 | 1294.284 | 21.5537 | -143.3051 | -12.633 | 0 | 125.0039 | 305.0039 | 113.9299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2481 | 0 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4295 | 23 | 18.1 | 0 | 0 | 0 | 0 | 0 | 179 | 4295 | 1380 | 176.5479 | 23.1312 | -1.0636 | 1354.284 | 22.5537 | -158.3051 | -17.3915 | 0 | 125.0039 | 305.0039 | 113.9299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5176 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
6 | 179 | 28 | 4296 | 24 | 17.2 | 0 | 0 | 0 | 0 | 0 | 179 | 4296 | 1440 | 176.5479 | 23.1312 | -1.0636 | 1414.284 | 23.5537 | -173.3051 | -19.829 | 0 | 125.0039 | 305.0039 | 113.9299 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4155 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4297 | 1 | 16.7 | 0 | 0 | 0 | 0 | 0 | 180 | 4297 | 60 | 177.5342 | 23.0792 | -1.5051 | 34.284 | 0.54631 | 171.8053 | -19.7507 | 0 | 124.9186 | 55.0814 | 113.8759 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1614 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4298 | 2 | 15.9 | 0 | 0 | 0 | 0 | 0 | 180 | 4298 | 120 | 177.5342 | 23.0792 | -1.5051 | 94.284 | 1.5463 | 156.8053 | -17.0639 | 0 | 124.9186 | 55.0814 | 113.8759 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5907 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4299 | 3 | 16.1 | 0 | 0 | 0 | 0 | 0 | 180 | 4299 | 180 | 177.5342 | 23.0792 | -1.5051 | 154.284 | 2.5463 | 141.8053 | -12.0921 | 0 | 124.9186 | 55.0814 | 113.8759 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4961 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4300 | 4 | 15.6 | 0 | 0 | 0 | 0 | 0 | 180 | 4300 | 240 | 177.5342 | 23.0792 | -1.5051 | 214.284 | 3.5463 | 126.8053 | -5.2663 | 0 | 124.9186 | 55.0814 | 113.8759 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2581 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4301 | 5 | 15.2 | 0 | 0 | 0 | 0 | 0 | 180 | 4301 | 300 | 177.5342 | 23.0792 | -1.5051 | 274.284 | 4.5463 | 111.8053 | 2.9597 | 2.9597 | 121.209 | 58.791 | 109.2321 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.4812 | 8.4812 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4302 | 6 | 15 | 8.42 | 18.61 | 27.03 | 18.61 | 9.31 | 180 | 4302 | 360 | 177.5342 | 23.0792 | -1.5051 | 334.284 | 5.5463 | 96.8053 | 12.181 | 12.181 | 110.8489 | 69.1511 | 95.5547 | -3.8627 | 0 | 15.8846 | 15.8846 | -7.1238 | 0% | 7.183 | 0 | 0 | 25.3136 | 25.3136 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4303 | 7 | 15.5 | 98.14 | 53.89 | 152.03 | 53.89 | 26.95 | 180 | 4303 | 420 | 177.5342 | 23.0792 | -1.5051 | 394.284 | 6.5463 | 81.8053 | 22.0525 | 22.0525 | 100.7514 | 79.2486 | 81.7653 | 37.4384 | 37.4384 | 45.998 | 83.4364 | -0.69172 | 0% | 37.73 | 0 | 0 | 162.5641 | 162.5641 | 0% | 11.53% | 11.53% | 80% | 9.223% | 3.48 | 5.9013 | 5.9013 | 20.5365 | 7.6957 | 12.63% | 12.63%
6 | 180 | 29 | 4304 | 8 | 17.7 | 222.58 | 76.31 | 298.89 | 76.31 | 38.16 | 180 | 4304 | 480 | 177.5342 | 23.0792 | -1.5051 | 454.284 | 7.5463 | 66.8053 | 32.262 | 32.262 | 90.2995 | 89.7005 | 68.0176 | 156.0847 | 156.0847 | 65.1347 | 221.2194 | 0.26221 | 26.22% | 100.0354 | 26.2299 | 18.3609 | 183.838 | 183.838 | 9.988% | 11.43% | 11.43% | 80% | 9.14% | 9.1434 | 5.4151 | 5.4151 | 49.5122 | 20.2198 | 26.93% | 26.93%
6 | 180 | 29 | 4305 | 9 | 20.9 | 280.92 | 92.86 | 373.78 | 92.86 | 46.43 | 180 | 4305 | 540 | 177.5342 | 23.0792 | -1.5051 | 514.284 | 8.5463 | 51.8053 | 42.471 | 42.471 | 78.5785 | 101.4215 | 54.4977 | 241.6116 | 241.6116 | 79.261 | 320.8725 | 0.45251 | 45.25% | 145.0986 | 65.6592 | 45.9614 | 192.1672 | 192.1672 | 23.92% | 11.33% | 11.33% | 85% | 9.629% | 13.9716 | 4.7684 | 4.7684 | 66.6215 | 30.8969 | 34.67% | 34.67%
6 | 180 | 29 | 4306 | 10 | 22.6 | 330.75 | 126.39 | 457.14 | 126.39 | 63.2 | 180 | 4306 | 600 | 177.5342 | 23.0792 | -1.5051 | 574.284 | 9.5463 | 36.8053 | 52.1943 | 52.1943 | 64.0427 | 115.9573 | 41.5479 | 313.2964 | 313.2964 | 107.8806 | 421.177 | 0.54501 | 54.5% | 190.4563 | 103.8008 | 72.6605 | 193.4175 | 193.4175 | 37.57% | 11.3% | 11.3% | 85% | 9.603% | 18.2898 | 4.4539 | 4.4539 | 81.4617 | 40.4463 | 42.12% | 42.12%
6 | 180 | 29 | 4307 | 11 | 24.9 | 451.39 | 211.58 | 662.97 | 211.58 | 105.79 | 180 | 4307 | 660 | 177.5342 | 23.0792 | -1.5051 | 634.284 | 10.5463 | 21.8053 | 60.5278 | 60.5278 | 43.9921 | 136.0079 | 30.0151 | 448.9524 | 448.9524 | 180.5948 | 629.5472 | 0.63859 | 63.86% | 284.6812 | 181.7946 | 127.2562 | 226.6621 | 226.6621 | 56.14% | 11.31% | 11.31% | 90% | 10.18% | 28.9676 | 4.0608 | 4.0608 | 117.6304 | 64.0593 | 51.9% | 51.9%
6 | 180 | 29 | 4308 | 12 | 26 | 499.92 | 242.03 | 741.95 | 242.03 | 121.02 | 180 | 4308 | 720 | 177.5342 | 23.0792 | -1.5051 | 694.284 | 11.5463 | 6.8053 | 65.6762 | 65.6762 | 15.3468 | 164.6532 | 22.3007 | 507.5856 | 507.5856 | 206.5855 | 714.1711 | 0.66147 | 66.15% | 322.9482 | 213.6197 | 149.5338 | 233.3375 | 233.3375 | 64.08% | 11.32% | 11.32% | 90% | 10.19% | 32.9126 | 3.8858 | 3.8858 | 127.892 | 72.7834 | 54.81% | 54.81%
6 | 180 | 29 | 4309 | 13 | 27.4 | 524.58 | 197.92 | 722.5 | 197.92 | 98.96 | 180 | 4309 | 780 | 177.5342 | 23.0792 | -1.5051 | 754.284 | 12.5463 | -8.1947 | 65.4003 | 65.4003 | 18.3612 | 198.3612 | 22.7361 | 532.1127 | 532.1127 | 168.9353 | 701.048 | 0.66302 | 66.3% | 317.0139 | 210.1851 | 147.1296 | 277.3785 | 277.3785 | 53.04% | 11.31% | 11.31% | 90% | 10.18% | 32.2738 | 3.6754 | 3.6754 | 118.6184 | 71.3706 | 42.76% | 42.76%
6 | 180 | 29 | 4310 | 14 | 28.4 | 656.11 | 209.44 | 865.55 | 209.44 | 104.72 | 180 | 4310 | 840 | 177.5342 | 23.0792 | -1.5051 | 814.284 | 13.5463 | -23.1947 | 59.854 | 59.854 | 46.1773 | 226.1773 | 30.9786 | 650.5045 | 650.5045 | 178.7682 | 829.2727 | 0.68734 | 68.73% | 374.9971 | 257.751 | 180.4257 | 294.487 | 294.487 | 61.27% | 11.37% | 11.37% | 95% | 10.8% | 40.4894 | 3.5335 | 3.5335 | 143.0684 | 89.5386 | 48.58% | 48.58%
6 | 180 | 29 | 4311 | 15 | 28.5 | 442.86 | 203.89 | 646.75 | 203.89 | 101.95 | 180 | 4311 | 900 | 177.5342 | 23.0792 | -1.5051 | 874.284 | 14.5463 | -38.1947 | 51.3333 | 51.3333 | 65.5693 | 245.5693 | 42.7074 | 416.788 | 416.788 | 174.031 | 590.819 | 0.64061 | 64.06% | 267.1684 | 171.1511 | 119.8058 | 283.0135 | 283.0135 | 42.33% | 11.25% | 11.25% | 90% | 10.13% | 27.0609 | 3.5197 | 3.5197 | 95.2456 | 59.8428 | 33.65% | 33.65%
6 | 180 | 29 | 4312 | 16 | 28.7 | 452.31 | 187.5 | 639.81 | 187.5 | 93.75 | 180 | 4312 | 960 | 177.5342 | 23.0792 | -1.5051 | 934.284 | 15.5463 | -53.1947 | 41.5364 | 41.5364 | 79.7521 | 259.7521 | 55.7333 | 384.0633 | 384.0633 | 160.0413 | 544.1046 | 0.62735 | 62.74% | 246.0441 | 154.3558 | 108.0491 | 283.5391 | 283.5391 | 38.11% | 11.23% | 11.23% | 90% | 10.11% | 24.8667 | 3.4923 | 3.4923 | 86.8413 | 54.9905 | 30.63% | 30.63%
6 | 180 | 29 | 4313 | 17 | 28.3 | 356.31 | 161.58 | 517.89 | 161.58 | 80.79 | 180 | 4313 | 1020 | 177.5342 | 23.0792 | -1.5051 | 994.284 | 16.5463 | -68.1947 | 31.3106 | 31.3106 | 91.3037 | 271.3037 | 69.2849 | 242.5249 | 242.5249 | 137.9172 | 380.4421 | 0.54916 | 54.92% | 172.0359 | 94.4757 | 66.133 | 282.439 | 282.439 | 23.41% | 11.16% | 11.16% | 85% | 9.486% | 16.32 | 3.5474 | 3.5474 | 57.8929 | 36.0903 | 20.5% | 20.5%
6 | 180 | 29 | 4314 | 18 | 28.2 | 231.03 | 166.58 | 397.61 | 166.58 | 83.29 | 180 | 4314 | 1080 | 177.5342 | 23.0792 | -1.5051 | 1054.284 | 17.5463 | -83.1947 | 21.1192 | 21.1192 | 101.6906 | 281.6906 | 83.0432 | 77.6631 | 77.6631 | 142.1849 | 219.848 | 0.36206 | 36.21% | 99.4153 | 35.9942 | 25.196 | 270.993 | 270.993 | 9.298% | 11.09% | 11.09% | 80% | 8.872% | 8.8204 | 3.5613 | 3.5613 | 31.4121 | 19.5055 | 11.59% | 11.59%
6 | 180 | 29 | 4315 | 19 | 27.5 | 170 | 109.72 | 279.72 | 109.72 | 54.86 | 180 | 4315 | 1140 | 177.5342 | 23.0792 | -1.5051 | 1114.284 | 18.5463 | -98.1947 | 11.2946 | 11.2946 | 111.7896 | 291.7896 | 96.8288 | -103.2075 | 0 | 93.6519 | 93.6519 | -0.24912 | 0% | 42.3494 | 0 | 0 | 256.7038 | 256.7038 | 0% | 11.06% | 0% | 80% | 0% | 0 | 3.6609 | 3.6609 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4316 | 20 | 26.8 | 53.97 | 55.47 | 109.44 | 55.47 | 27.74 | 180 | 4316 | 1200 | 177.5342 | 23.0792 | -1.5051 | 1174.284 | 19.5463 | -113.1947 | 2.1502 | 2.1502 | 122.1992 | 302.1992 | 110.4871 | 0 | 0 | 47.3466 | 47.3466 | -1.3102 | 0% | 21.4101 | 0 | 0 | 267.8577 | 267.8577 | 0% | 11.07% | 0% | 80% | 0% | 0 | 3.7639 | 3.7639 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4317 | 21 | 25 | 0 | 16.31 | 16.31 | 16.31 | 8.16 | 180 | 4317 | 1260 | 177.5342 | 23.0792 | -1.5051 | 1234.284 | 20.5463 | -128.1947 | -5.9641 | 0 | 124.9186 | 304.9186 | 113.8759 | 0 | 0 | 13.9215 | 13.9215 | -6.6607 | 0% | 6.2953 | 0 | 0 | 2.0947 | 2.0947 | 0% | 11.14% | 0% | 80% | 0% | 0 | 4.0445 | 4.0445 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4318 | 22 | 24.7 | 0 | 0 | 0 | 0 | 0 | 180 | 4318 | 1320 | 177.5342 | 23.0792 | -1.5051 | 1294.284 | 21.5463 | -143.1947 | -12.6376 | 0 | 124.9186 | 304.9186 | 113.8759 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.339 | 0 | 0% | 11.15% | 0% | 80% | 0% | 0 | 4.0935 | 4.0935 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4319 | 23 | 23.3 | 0 | 0 | 0 | 0 | 0 | 180 | 4319 | 1380 | 177.5342 | 23.0792 | -1.5051 | 1354.284 | 22.5463 | -158.1947 | -17.4146 | 0 | 124.9186 | 304.9186 | 113.8759 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.6828 | 0 | 0% | 11.21% | 0% | 80% | 0% | 0 | 4.3304 | 4.3304 | 0 | 0 | 0% | 0%
6 | 180 | 29 | 4320 | 24 | 21.2 | 0 | 0 | 0 | 0 | 0 | 180 | 4320 | 1440 | 177.5342 | 23.0792 | -1.5051 | 1414.284 | 23.5463 | -173.1947 | -19.8721 | 0 | 124.9186 | 304.9186 | 113.8759 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.0933 | 0 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.7114 | 4.7114 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4321 | 1 | 19.9 | 0 | 0 | 0 | 0 | 0 | 181 | 4321 | 60 | 178.5205 | 23.0209 | -1.9442 | 34.284 | 0.539 | 171.915 | -19.8191 | 0 | 124.8231 | 55.1769 | 113.8153 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.6734 | 0 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4322 | 2 | 17.4 | 0 | 0 | 0 | 0 | 0 | 181 | 4322 | 120 | 178.5205 | 23.0209 | -1.9442 | 94.284 | 1.539 | 156.915 | -17.1483 | 0 | 124.8231 | 55.1769 | 113.8153 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8067 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4323 | 3 | 17.6 | 0 | 0 | 0 | 0 | 0 | 181 | 4323 | 180 | 178.5205 | 23.0209 | -1.9442 | 154.284 | 2.539 | 141.915 | -12.1883 | 0 | 124.8231 | 55.1769 | 113.8153 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8252 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4324 | 4 | 18 | 0 | 0 | 0 | 0 | 0 | 181 | 4324 | 240 | 178.5205 | 23.0209 | -1.9442 | 214.284 | 3.539 | 126.915 | -5.3706 | 0 | 124.8231 | 55.1769 | 113.8153 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2156 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4325 | 5 | 18.5 | 0 | 0 | 0 | 0 | 0 | 181 | 4325 | 300 | 178.5205 | 23.0209 | -1.9442 | 274.284 | 4.539 | 111.915 | 2.8505 | 2.8505 | 121.2499 | 58.7501 | 109.3422 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.3066 | 9.3066 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4326 | 6 | 16.7 | 4.17 | 12.31 | 16.48 | 12.31 | 6.16 | 181 | 4326 | 360 | 178.5205 | 23.0209 | -1.9442 | 334.284 | 5.539 | 96.915 | 12.0689 | 12.0689 | 110.8817 | 69.1183 | 95.6598 | -1.9669 | 0 | 10.5072 | 10.5072 | -10.816 | 0% | 4.7514 | 0 | 0 | 20.0871 | 20.0871 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4327 | 7 | 18.9 | 49.92 | 43.69 | 93.61 | 43.69 | 21.85 | 181 | 4327 | 420 | 178.5205 | 23.0209 | -1.9442 | 394.284 | 6.539 | 81.915 | 21.9389 | 21.9389 | 100.7797 | 79.2203 | 81.8646 | 18.9078 | 18.9078 | 37.2917 | 56.1996 | -1.2812 | 0% | 25.4134 | 0 | 0 | 194.5534 | 194.5534 | 0% | 11.4% | 11.4% | 80% | 9.118% | 2.3171 | 5.1642 | 5.1642 | 11.9658 | 5.1241 | 6.15% | 6.15%
6 | 181 | 30 | 4328 | 8 | 21 | 160.19 | 88.06 | 248.25 | 88.06 | 44.03 | 181 | 4328 | 480 | 178.5205 | 23.0209 | -1.9442 | 454.284 | 7.539 | 66.915 | 32.1479 | 32.1479 | 90.3279 | 89.6721 | 68.1098 | 112.24 | 112.24 | 75.1639 | 187.4039 | 0.20336 | 20.34% | 84.744 | 17.2331 | 12.0632 | 172.5998 | 172.5998 | 6.989% | 11.32% | 11.32% | 80% | 9.055% | 7.6733 | 4.7493 | 4.7493 | 36.4427 | 16.9688 | 21.11% | 21.11%
6 | 181 | 30 | 4329 | 9 | 23.2 | 195.75 | 113.42 | 309.17 | 113.42 | 56.71 | 181 | 4329 | 540 | 178.5205 | 23.0209 | -1.9442 | 514.284 | 8.539 | 51.915 | 42.3574 | 42.3574 | 78.6144 | 101.3856 | 54.5799 | 168.3853 | 168.3853 | 96.81 | 265.1953 | 0.39757 | 39.76% | 119.9213 | 47.6773 | 33.3741 | 182.2599 | 182.2599 | 18.31% | 11.26% | 11.26% | 80% | 9.006% | 10.8005 | 4.3478 | 4.3478 | 46.9583 | 23.8843 | 25.76% | 25.76%
6 | 181 | 30 | 4330 | 10 | 24.5 | 304.53 | 190.28 | 494.81 | 190.28 | 95.14 | 181 | 4330 | 600 | 178.5205 | 23.0209 | -1.9442 | 574.284 | 9.539 | 36.915 | 52.0834 | 52.0834 | 64.1013 | 115.8987 | 41.6142 | 288.5983 | 288.5983 | 162.4141 | 451.0125 | 0.57122 | 57.12% | 203.9478 | 116.4982 | 81.5487 | 210.72 | 210.72 | 38.7% | 11.27% | 11.27% | 85% | 9.576% | 19.5296 | 4.1265 | 4.1265 | 80.5884 | 43.188 | 38.24% | 38.24%
6 | 181 | 30 | 4331 | 11 | 25.9 | 404.72 | 141.67 | 546.39 | 141.67 | 70.84 | 181 | 4331 | 660 | 178.5205 | 23.0209 | -1.9442 | 634.284 | 10.539 | 21.915 | 60.4256 | 60.4256 | 44.1062 | 135.8938 | 30.0513 | 402.7943 | 402.7943 | 120.9229 | 523.7172 | 0.60923 | 60.92% | 236.8249 | 144.2807 | 100.9965 | 228.7474 | 228.7474 | 44.15% | 11.26% | 11.26% | 90% | 10.14% | 24.0048 | 3.9014 | 3.9014 | 93.6514 | 53.0846 | 40.94% | 40.94%
6 | 181 | 30 | 4332 | 12 | 26.4 | 386.67 | 203.25 | 589.92 | 203.25 | 101.63 | 181 | 4332 | 720 | 178.5205 | 23.0209 | -1.9442 | 694.284 | 11.539 | 6.915 | 65.599 | 65.599 | 15.5587 | 164.4413 | 22.2772 | 392.9048 | 392.9048 | 173.4847 | 566.3896 | 0.62577 | 62.58% | 256.1214 | 160.274 | 112.1918 | 225.8163 | 225.8163 | 49.68% | 11.27% | 11.27% | 90% | 10.14% | 25.9779 | 3.8243 | 3.8243 | 99.3466 | 57.4477 | 43.99% | 43.99%
6 | 181 | 30 | 4333 | 13 | 27 | 381.39 | 314.72 | 696.11 | 314.72 | 157.36 | 181 | 4333 | 780 | 178.5205 | 23.0209 | -1.9442 | 754.284 | 12.539 | -8.085 | 65.3671 | 65.3671 | 18.0928 | 198.0928 | 22.6448 | 387.2272 | 387.2272 | 268.6303 | 655.8575 | 0.65202 | 65.2% | 296.5788 | 193.3746 | 135.3622 | 238.479 | 238.479 | 56.76% | 11.3% | 11.3% | 90% | 10.17% | 30.1527 | 3.7341 | 3.7341 | 112.5933 | 66.6801 | 47.21% | 47.21%
6 | 181 | 30 | 4334 | 14 | 27.6 | 162.08 | 263.89 | 425.97 | 263.89 | 131.95 | 181 | 4334 | 840 | 178.5205 | 23.0209 | -1.9442 | 814.284 | 13.539 | -23.085 | 59.8588 | 59.8588 | 45.9452 | 225.9452 | 30.8637 | 160.8803 | 160.8803 | 225.2442 | 386.1245 | 0.54912 | 54.91% | 174.6055 | 95.8787 | 67.1151 | 258.7019 | 258.7019 | 25.94% | 11.18% | 11.18% | 85% | 9.502% | 16.5913 | 3.6464 | 3.6464 | 60.4991 | 36.6901 | 23.39% | 23.39%
6 | 181 | 30 | 4335 | 15 | 27.6 | 328.69 | 218.25 | 546.94 | 218.25 | 109.13 | 181 | 4335 | 900 | 178.5205 | 23.0209 | -1.9442 | 874.284 | 14.539 | -38.085 | 51.3588 | 51.3588 | 65.387 | 245.387 | 42.5914 | 309.8069 | 309.8069 | 186.288 | 496.095 | 0.60562 | 60.56% | 224.3341 | 135.8605 | 95.1024 | 269.285 | 269.285 | 35.32% | 11.22% | 11.22% | 85% | 9.541% | 21.4042 | 3.6464 | 3.6464 | 78.0492 | 47.3335 | 28.98% | 28.98%
6 | 181 | 30 | 4336 | 16 | 28.2 | 288.53 | 221.31 | 509.84 | 221.31 | 110.66 | 181 | 4336 | 960 | 178.5205 | 23.0209 | -1.9442 | 934.284 | 15.539 | -53.085 | 41.5707 | 41.5707 | 79.6031 | 259.6031 | 55.621 | 245.5344 | 245.5344 | 188.8999 | 434.4343 | 0.58035 | 58.04% | 196.4512 | 114.0111 | 79.8078 | 272.6311 | 272.6311 | 29.27% | 11.19% | 11.19% | 85% | 9.509% | 18.6807 | 3.5613 | 3.5613 | 66.5274 | 41.3106 | 24.4% | 24.4%
6 | 181 | 30 | 4337 | 17 | 27.51 | 181.39 | 234.72 | 416.11 | 234.72 | 117.36 | 181 | 4337 | 1020 | 178.5205 | 23.0209 | -1.9442 | 994.284 | 16.539 | -68.085 | 31.3468 | 31.3468 | 91.1739 | 271.1739 | 69.1774 | 123.9481 | 123.9481 | 200.3461 | 324.2942 | 0.49994 | 49.99% | 146.6458 | 73.3137 | 51.3196 | 260.6924 | 260.6924 | 19.69% | 11.16% | 11.16% | 85% | 9.482% | 13.9052 | 3.6594 | 3.6594 | 50.8852 | 30.7502 | 19.52% | 19.52%
6 | 181 | 30 | 4338 | 18 | 27.19 | 71.31 | 132.86 | 204.17 | 132.86 | 66.43 | 181 | 4338 | 1080 | 178.5205 | 23.0209 | -1.9442 | 1054.284 | 17.539 | -83.085 | 21.1529 | 21.1529 | 101.5709 | 281.5709 | 82.9411 | 24.2845 | 24.2845 | 113.4031 | 137.6876 | 0.082957 | 8.296% | 62.2623 | 5.1651 | 3.6156 | 240.3607 | 240.3607 | 1.504% | 11.09% | 11.09% | 80% | 8.872% | 5.524 | 3.7061 | 3.7061 | 20.4722 | 12.2157 | 8.517% | 8.517%
6 | 181 | 30 | 4339 | 19 | 27.11 | 23.14 | 104.72 | 127.86 | 104.72 | 52.36 | 181 | 4339 | 1140 | 178.5205 | 23.0209 | -1.9442 | 1114.284 | 18.539 | -98.085 | 11.3223 | 11.3223 | 111.674 | 291.674 | 96.7331 | -13.8189 | 0 | 89.3841 | 89.3841 | -0.30858 | 0% | 40.4195 | 0 | 0 | 265.6348 | 265.6348 | 0% | 11.07% | 0% | 80% | 0% | 0 | 3.7178 | 3.7178 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4340 | 20 | 26.67 | 27.5 | 59.08 | 86.58 | 59.08 | 29.54 | 181 | 4340 | 1200 | 178.5205 | 23.0209 | -1.9442 | 1174.284 | 19.539 | -113.085 | 2.1686 | 2.1686 | 122.084 | 302.084 | 110.3994 | 0 | 0 | 50.4279 | 50.4279 | -1.1865 | 0% | 22.8035 | 0 | 0 | 219.0099 | 219.0099 | 0% | 11.08% | 0% | 80% | 0% | 0 | 3.7834 | 3.7834 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4341 | 21 | 26.45 | 0 | 8.06 | 8.06 | 8.06 | 4.03 | 181 | 4341 | 1260 | 178.5205 | 23.0209 | -1.9442 | 1234.284 | 20.539 | -128.085 | -5.9585 | 0 | 124.8231 | 304.8231 | 113.8153 | 0 | 0 | 6.8796 | 6.8796 | -13.8537 | 0% | 3.111 | 0 | 0 | 3.3669 | 3.3669 | 0% | 11.07% | 0% | 80% | 0% | 0 | 3.8167 | 3.8167 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4342 | 22 | 26.03 | 0 | 0 | 0 | 0 | 0 | 181 | 4342 | 1320 | 178.5205 | 23.0209 | -1.9442 | 1294.284 | 21.539 | -143.085 | -12.648 | 0 | 124.8231 | 304.8231 | 113.8153 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.63869 | 0.63869 | 0% | 11.09% | 0% | 80% | 0% | 0 | 3.8811 | 3.8811 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4343 | 23 | 25.35 | 0 | 0 | 0 | 0 | 0 | 181 | 4343 | 1380 | 178.5205 | 23.0209 | -1.9442 | 1354.284 | 22.539 | -158.085 | -17.4438 | 0 | 124.8231 | 304.8231 | 113.8153 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.27905 | 0.27905 | 0% | 11.12% | 0% | 80% | 0% | 0 | 3.9882 | 3.9882 | 0 | 0 | 0% | 0%
6 | 181 | 30 | 4344 | 24 | 22.5 | 0 | 0 | 0 | 0 | 0 | 181 | 4344 | 1440 | 178.5205 | 23.0209 | -1.9442 | 1414.284 | 23.539 | -173.085 | -19.9214 | 0 | 124.8231 | 304.8231 | 113.8153 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.3877 | 0 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4719 | 4.4719 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4345 | 1 | 19.57 | 0 | 0 | 0 | 0 | 0 | 182 | 4345 | 60 | 179.5068 | 22.9563 | -2.3804 | 34.284 | 0.53173 | 172.0241 | -19.8936 | 0 | 124.7174 | 55.2826 | 113.7482 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.4945 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0284 | 5.0284 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4346 | 2 | 17.59 | 0 | 0 | 0 | 0 | 0 | 182 | 4346 | 120 | 179.5068 | 22.9563 | -2.3804 | 94.284 | 1.5317 | 157.0241 | -17.2384 | 0 | 124.7174 | 55.2826 | 113.7482 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.8335 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4386 | 5.4386 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4347 | 3 | 17.5 | 0 | 0 | 0 | 0 | 0 | 182 | 4347 | 180 | 179.5068 | 22.9563 | -2.3804 | 154.284 | 2.5317 | 142.0241 | -12.2899 | 0 | 124.7174 | 55.2826 | 113.7482 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2921 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4348 | 4 | 17.32 | 0 | 0 | 0 | 0 | 0 | 182 | 4348 | 240 | 179.5068 | 22.9563 | -2.3804 | 214.284 | 3.5317 | 127.0241 | -5.4798 | 0 | 124.7174 | 55.2826 | 113.7482 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5664 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4966 | 5.4966 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4349 | 5 | 17.02 | 0 | 0 | 0 | 0 | 0 | 182 | 4349 | 300 | 179.5068 | 22.9563 | -2.3804 | 274.284 | 4.5317 | 112.0241 | 2.7368 | 2.7368 | 121.2863 | 58.7137 | 109.4528 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.6353 | 9.6353 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5617 | 5.5617 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4350 | 6 | 16.85 | 8 | 19.31 | 27.31 | 19.31 | 9.66 | 182 | 4350 | 360 | 179.5068 | 22.9563 | -2.3804 | 334.284 | 5.5317 | 97.0241 | 11.9527 | 11.9527 | 110.9096 | 69.0904 | 95.7649 | -3.88 | 0 | 16.4821 | 16.4821 | -6.5832 | 0% | 7.4532 | 0 | 0 | 24.4864 | 24.4864 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.5989 | 5.5989 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4351 | 7 | 17 | 64.31 | 62.83 | 127.14 | 62.83 | 31.42 | 182 | 4351 | 420 | 179.5068 | 22.9563 | -2.3804 | 394.284 | 6.5317 | 82.0241 | 21.8214 | 21.8214 | 100.8027 | 79.1973 | 81.9633 | 24.1879 | 24.1879 | 53.6288 | 77.8167 | -0.75634 | 0% | 35.1887 | 0 | 0 | 198.0038 | 198.0038 | 0% | 11.47% | 11.47% | 80% | 9.177% | 3.2292 | 5.5661 | 5.5661 | 17.9743 | 7.1412 | 9.078% | 9.078%
7 | 182 | 1 | 4352 | 8 | 17.3 | 180.33 | 90.61 | 270.94 | 90.61 | 45.31 | 182 | 4352 | 480 | 179.5068 | 22.9563 | -2.3804 | 454.284 | 7.5317 | 67.0241 | 32.03 | 32.03 | 90.3504 | 89.6496 | 68.2006 | 126.2662 | 126.2662 | 77.3405 | 203.6066 | 0.21095 | 21.09% | 92.0709 | 19.4223 | 13.5956 | 173.1033 | 173.1033 | 7.854% | 11.44% | 11.44% | 80% | 9.152% | 8.4267 | 5.501 | 5.501 | 46.3552 | 18.635 | 26.78% | 26.78%
7 | 182 | 1 | 4353 | 9 | 17.5 | 266.06 | 138.89 | 404.95 | 138.89 | 69.45 | 182 | 4353 | 540 | 179.5068 | 22.9563 | -2.3804 | 514.284 | 8.5317 | 52.0241 | 42.24 | 42.24 | 78.6436 | 101.3564 | 54.6601 | 228.931 | 228.931 | 118.55 | 347.481 | 0.45779 | 45.78% | 157.1309 | 71.9327 | 50.3529 | 179.7492 | 179.7492 | 28.01% | 11.41% | 11.41% | 85% | 9.702% | 15.245 | 5.4579 | 5.4579 | 83.2052 | 33.7129 | 46.29% | 46.29%
7 | 182 | 1 | 4354 | 10 | 18 | 389.17 | 179.44 | 568.61 | 179.44 | 89.72 | 182 | 4354 | 600 | 179.5068 | 22.9563 | -2.3804 | 574.284 | 9.5317 | 37.0241 | 51.9682 | 51.9682 | 64.1523 | 115.8477 | 41.6775 | 369.027 | 369.027 | 153.1616 | 522.1886 | 0.57576 | 57.58% | 236.1337 | 135.9554 | 95.1688 | 183.3163 | 183.3163 | 51.92% | 11.38% | 11.38% | 90% | 10.24% | 24.1903 | 5.3514 | 5.3514 | 129.4517 | 53.4946 | 70.62% | 70.62%
7 | 182 | 1 | 4355 | 11 | 19.3 | 487 | 192.08 | 679.08 | 192.08 | 96.04 | 182 | 4355 | 660 | 179.5068 | 22.9563 | -2.3804 | 634.284 | 10.5317 | 22.0241 | 60.3184 | 60.3184 | 44.2122 | 135.7878 | 30.0832 | 485.0426 | 485.0426 | 163.9505 | 648.9932 | 0.6248 | 62.48% | 293.4747 | 183.3621 | 128.3535 | 179.3968 | 179.3968 | 71.55% | 11.36% | 11.36% | 90% | 10.22% | 29.9991 | 5.0828 | 5.0828 | 152.478 | 66.3403 | 84.99% | 84.99%
7 | 182 | 1 | 4356 | 12 | 20.8 | 466.06 | 227.44 | 693.5 | 227.44 | 113.72 | 182 | 4356 | 720 | 179.5068 | 22.9563 | -2.3804 | 694.284 | 11.5317 | 7.0241 | 65.5156 | 65.5156 | 15.7651 | 164.2349 | 22.2481 | 473.9869 | 473.9869 | 194.1322 | 668.1191 | 0.63487 | 63.49% | 302.1235 | 191.8082 | 134.2658 | 167.2973 | 167.2973 | 80.26% | 11.35% | 11.35% | 90% | 10.21% | 30.8516 | 4.7875 | 4.7875 | 147.7013 | 68.2255 | 88.29% | 88.29%
7 | 182 | 1 | 4357 | 13 | 22.4 | 448.89 | 267.92 | 716.81 | 267.92 | 133.96 | 182 | 4357 | 780 | 179.5068 | 22.9563 | -2.3804 | 754.284 | 12.5317 | -7.9759 | 65.3273 | 65.3273 | 17.823 | 197.823 | 22.5482 | 456.226 | 456.226 | 228.684 | 684.91 | 0.6441 | 64.41% | 309.7163 | 199.4898 | 139.6429 | 167.6856 | 167.6856 | 83.28% | 11.34% | 11.34% | 90% | 10.2% | 31.6008 | 4.4899 | 4.4899 | 141.8836 | 69.8822 | 84.61% | 84.61%
7 | 182 | 1 | 4358 | 14 | 23.2 | 389.5 | 238.56 | 628.06 | 238.56 | 119.28 | 182 | 4358 | 840 | 179.5068 | 22.9563 | -2.3804 | 814.284 | 13.5317 | -22.9759 | 59.8578 | 59.8578 | 45.7075 | 225.7075 | 30.7454 | 387.0976 | 387.0976 | 203.6237 | 590.7213 | 0.62154 | 62.15% | 267.1242 | 166.0284 | 116.2199 | 166.9715 | 166.9715 | 69.6% | 11.32% | 11.32% | 90% | 10.18% | 27.203 | 4.3478 | 4.3478 | 118.2732 | 60.157 | 70.83% | 70.83%
7 | 182 | 1 | 4359 | 15 | 24.1 | 333.39 | 226.94 | 560.33 | 226.94 | 113.47 | 182 | 4359 | 900 | 179.5068 | 22.9563 | -2.3804 | 874.284 | 14.5317 | -37.9759 | 51.379 | 51.379 | 65.1986 | 245.1986 | 42.4733 | 314.7429 | 314.7429 | 193.7054 | 508.4483 | 0.59583 | 59.58% | 229.9203 | 136.9923 | 95.8946 | 178.1823 | 178.1823 | 53.82% | 11.29% | 11.29% | 90% | 10.16% | 23.3545 | 4.1933 | 4.1933 | 97.9326 | 51.6463 | 54.96% | 54.96%
7 | 182 | 1 | 4360 | 16 | 23.3 | 326.17 | 203.75 | 529.92 | 203.75 | 101.88 | 182 | 4360 | 960 | 179.5068 | 22.9563 | -2.3804 | 934.284 | 15.5317 | -52.9759 | 41.6001 | 41.6001 | 79.4484 | 259.4484 | 55.5076 | 278.2067 | 278.2067 | 173.9115 | 452.1182 | 0.56608 | 56.61% | 204.4478 | 115.7342 | 81.0139 | 159.5615 | 159.5615 | 50.77% | 11.29% | 11.29% | 85% | 9.596% | 19.6179 | 4.3304 | 4.3304 | 84.9523 | 43.3831 | 53.24% | 53.24%
7 | 182 | 1 | 4361 | 17 | 23.8 | 308.28 | 177.78 | 486.06 | 177.78 | 88.89 | 182 | 4361 | 1020 | 179.5068 | 22.9563 | -2.3804 | 994.284 | 16.5317 | -67.9759 | 31.3783 | 31.3783 | 91.0391 | 271.0391 | 69.0696 | 211.5053 | 211.5053 | 151.7447 | 363.25 | 0.51084 | 51.08% | 164.2616 | 83.9114 | 58.738 | 164.1197 | 164.1197 | 35.79% | 11.26% | 11.26% | 85% | 9.572% | 15.7225 | 4.2442 | 4.2442 | 66.7291 | 34.7689 | 40.66% | 40.66%
7 | 182 | 1 | 4362 | 18 | 24.3 | 225 | 143.56 | 368.56 | 143.56 | 71.78 | 182 | 4362 | 1080 | 179.5068 | 22.9563 | -2.3804 | 1054.284 | 17.5317 | -82.9759 | 21.1819 | 21.1819 | 101.4467 | 281.4467 | 82.8395 | 77.6191 | 77.6191 | 122.5361 | 200.1553 | 0.27732 | 27.73% | 90.5102 | 25.1006 | 17.5704 | 163.4237 | 163.4237 | 10.75% | 11.21% | 11.21% | 80% | 8.968% | 8.1171 | 4.1598 | 4.1598 | 33.765 | 17.9501 | 20.66% | 20.66%
7 | 182 | 1 | 4363 | 19 | 23.8 | 107.44 | 93.33 | 200.77 | 93.33 | 46.67 | 182 | 4363 | 1140 | 179.5068 | 22.9563 | -2.3804 | 1114.284 | 18.5317 | -97.9759 | 11.3451 | 11.3451 | 111.5545 | 291.5545 | 96.6385 | -63.1388 | 0 | 79.6621 | 79.6621 | -0.53278 | 0% | 36.0232 | 0 | 0 | 140.5348 | 140.5348 | 0% | 11.2% | 0% | 80% | 0% | 0 | 4.2442 | 4.2442 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4364 | 20 | 22.8 | 32.56 | 51.44 | 84 | 51.44 | 25.72 | 182 | 4364 | 1200 | 179.5068 | 22.9563 | -2.3804 | 1174.284 | 19.5317 | -112.9759 | 2.1817 | 2.1817 | 121.9652 | 301.9652 | 110.3134 | 0 | 0 | 43.9068 | 43.9068 | -1.6705 | 0% | 19.8546 | 0 | 0 | 152.4945 | 152.4945 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4183 | 4.4183 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4365 | 21 | 21.2 | 0 | 9.86 | 9.86 | 9.86 | 4.93 | 182 | 4365 | 1260 | 179.5068 | 22.9563 | -2.3804 | 1234.284 | 20.5317 | -127.9759 | -5.9583 | 0 | 124.7174 | 304.7174 | 113.7482 | 0 | 0 | 8.416 | 8.416 | -12.5189 | 0% | 3.8057 | 0 | 0 | -2.6441 | 0 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.7114 | 4.7114 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4366 | 22 | 18.8 | 0 | 0 | 0 | 0 | 0 | 182 | 4366 | 1320 | 179.5068 | 22.9563 | -2.3804 | 1294.284 | 21.5317 | -142.9759 | -12.6641 | 0 | 124.7174 | 304.7174 | 113.7482 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7036 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4367 | 23 | 17.3 | 0 | 0 | 0 | 0 | 0 | 182 | 4367 | 1380 | 179.5068 | 22.9563 | -2.3804 | 1354.284 | 22.5317 | -157.9759 | -17.4791 | 0 | 124.7174 | 304.7174 | 113.7482 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3111 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
7 | 182 | 1 | 4368 | 24 | 16.9 | 0 | 0 | 0 | 0 | 0 | 182 | 4368 | 1440 | 179.5068 | 22.9563 | -2.3804 | 1414.284 | 23.5317 | -172.9759 | -19.9769 | 0 | 124.7174 | 304.7174 | 113.7482 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2421 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4369 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 183 | 4369 | 60 | 180.4932 | 22.8855 | -2.8134 | 34.284 | 0.52451 | 172.1323 | -19.974 | 0 | 124.6016 | 55.3984 | 113.6746 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1278 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4370 | 2 | 15.1 | 0 | 0 | 0 | 0 | 0 | 183 | 4370 | 120 | 180.4932 | 22.8855 | -2.8134 | 94.284 | 1.5245 | 157.1323 | -17.3343 | 0 | 124.6016 | 55.3984 | 113.6746 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0003 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4371 | 3 | 14.7 | 0 | 0 | 0 | 0 | 0 | 183 | 4371 | 180 | 180.4932 | 22.8855 | -2.8134 | 154.284 | 2.5245 | 142.1323 | -12.3968 | 0 | 124.6016 | 55.3984 | 113.6746 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1109 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4372 | 4 | 15.9 | 0 | 0 | 0 | 0 | 0 | 183 | 4372 | 240 | 180.4932 | 22.8855 | -2.8134 | 214.284 | 3.5245 | 127.1323 | -5.5937 | 0 | 124.6016 | 55.3984 | 113.6746 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2822 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4373 | 5 | 16.9 | 0 | 0 | 0 | 0 | 0 | 183 | 4373 | 300 | 180.4932 | 22.8855 | -2.8134 | 274.284 | 4.5245 | 112.1323 | 2.6187 | 2.6187 | 121.3184 | 58.6816 | 109.5639 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.0711 | 4.0711 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4374 | 6 | 16.4 | 3.33 | 15.83 | 19.16 | 15.83 | 7.92 | 183 | 4374 | 360 | 180.4932 | 22.8855 | -2.8134 | 334.284 | 5.5245 | 97.1323 | 11.8325 | 11.8325 | 110.9326 | 69.0674 | 95.8697 | -1.6608 | 0 | 13.5118 | 13.5118 | -8.282 | 0% | 6.11 | 0 | 0 | 14.8283 | 14.8283 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4375 | 7 | 17 | 30.97 | 49.5 | 80.47 | 49.5 | 24.75 | 183 | 4375 | 420 | 180.4932 | 22.8855 | -2.8134 | 394.284 | 6.5245 | 82.1323 | 21.7002 | 21.7002 | 100.8203 | 79.1797 | 82.0612 | 11.5685 | 11.5685 | 42.2509 | 53.8193 | -1.4521 | 0% | 24.3371 | 0 | 0 | 182.0471 | 182.0471 | 0% | 11.48% | 11.48% | 80% | 9.18% | 2.2342 | 5.5661 | 5.5661 | 12.4356 | 4.9407 | 6.831% | 6.831%
7 | 183 | 2 | 4376 | 8 | 18.7 | 90.61 | 112.28 | 202.89 | 112.28 | 56.14 | 183 | 4376 | 480 | 180.4932 | 22.8855 | -2.8134 | 454.284 | 7.5245 | 67.1323 | 31.9085 | 31.9085 | 90.3669 | 89.6331 | 68.29 | 63.4121 | 63.4121 | 95.837 | 159.249 | 0.065345 | 6.534% | 72.0124 | 4.7056 | 3.2939 | 156.5165 | 156.5165 | 2.105% | 11.4% | 11.4% | 80% | 9.118% | 6.5663 | 5.2053 | 5.2053 | 34.1793 | 14.5207 | 21.84% | 21.84%
7 | 183 | 2 | 4377 | 9 | 20.7 | 207.22 | 154.94 | 362.16 | 154.94 | 77.47 | 183 | 4377 | 540 | 180.4932 | 22.8855 | -2.8134 | 514.284 | 8.5245 | 52.1323 | 42.1188 | 42.1188 | 78.666 | 101.334 | 54.7381 | 178.3754 | 178.3754 | 132.2496 | 310.6249 | 0.43951 | 43.95% | 140.4646 | 61.7354 | 43.2148 | 167.7322 | 167.7322 | 25.76% | 11.33% | 11.33% | 85% | 9.633% | 13.5312 | 4.8067 | 4.8067 | 65.0401 | 29.9231 | 38.78% | 38.78%
7 | 183 | 2 | 4378 | 10 | 22.8 | 292.83 | 193.11 | 485.94 | 193.11 | 96.56 | 183 | 4378 | 600 | 180.4932 | 22.8855 | -2.8134 | 574.284 | 9.5245 | 37.1323 | 51.8488 | 51.8488 | 64.1955 | 115.8045 | 41.7377 | 277.8666 | 277.8666 | 164.8297 | 442.6963 | 0.55858 | 55.86% | 200.1873 | 111.8203 | 78.2742 | 173.6827 | 173.6827 | 45.07% | 11.3% | 11.3% | 85% | 9.602% | 19.2228 | 4.4183 | 4.4183 | 84.9319 | 42.5096 | 48.9% | 48.9%
7 | 183 | 2 | 4379 | 11 | 23.8 | 454.78 | 223.67 | 678.45 | 223.67 | 111.84 | 183 | 4379 | 660 | 180.4932 | 22.8855 | -2.8134 | 634.284 | 10.5245 | 22.1323 | 60.2061 | 60.2061 | 44.3099 | 135.6901 | 30.111 | 453.3321 | 453.3321 | 190.9143 | 644.2464 | 0.63871 | 63.87% | 291.3282 | 186.0729 | 130.251 | 189.4246 | 189.4246 | 68.76% | 11.32% | 11.32% | 90% | 10.19% | 29.6791 | 4.2442 | 4.2442 | 125.9633 | 65.6326 | 66.5% | 66.5%
7 | 183 | 2 | 4380 | 12 | 25.5 | 562.64 | 224.86 | 787.5 | 224.86 | 112.43 | 183 | 4380 | 720 | 180.4932 | 22.8855 | -2.8134 | 694.284 | 11.5245 | 7.1323 | 65.426 | 65.426 | 15.9655 | 164.0345 | 22.2136 | 572.7592 | 572.7592 | 191.93 | 764.6892 | 0.66949 | 66.95% | 345.7925 | 231.5063 | 162.0544 | 213.9611 | 213.9611 | 75.74% | 11.34% | 11.34% | 90% | 10.21% | 35.2957 | 3.9643 | 3.9643 | 139.9218 | 78.0533 | 65.4% | 65.4%
7 | 183 | 2 | 4381 | 13 | 27.2 | 548.89 | 202.78 | 751.67 | 202.78 | 101.39 | 183 | 4381 | 780 | 180.4932 | 22.8855 | -2.8134 | 754.284 | 12.5245 | -7.8677 | 65.2808 | 65.2808 | 17.5522 | 197.5522 | 22.4462 | 558.48 | 558.48 | 173.0836 | 731.5635 | 0.66832 | 66.83% | 330.813 | 221.0894 | 154.7626 | 241.6001 | 241.6001 | 64.06% | 11.32% | 11.32% | 90% | 10.19% | 33.7178 | 3.7046 | 3.7046 | 124.911 | 74.5639 | 51.7% | 51.7%
7 | 183 | 2 | 4382 | 14 | 28.3 | 556.17 | 178.28 | 734.45 | 178.28 | 89.14 | 183 | 4382 | 840 | 180.4932 | 22.8855 | -2.8134 | 814.284 | 13.5245 | -22.8677 | 59.8507 | 59.8507 | 45.4644 | 225.4644 | 30.6235 | 553.4772 | 553.4772 | 152.1715 | 705.6487 | 0.66661 | 66.66% | 319.0944 | 212.7107 | 148.8975 | 272.2519 | 272.2519 | 54.69% | 11.31% | 11.31% | 90% | 10.18% | 32.4775 | 3.5474 | 3.5474 | 115.2094 | 71.8212 | 42.32% | 42.32%
7 | 183 | 2 | 4383 | 15 | 28.4 | 514.44 | 189.22 | 703.66 | 189.22 | 94.61 | 183 | 4383 | 900 | 180.4932 | 22.8855 | -2.8134 | 874.284 | 14.5245 | -37.8677 | 51.3939 | 51.3939 | 65.0041 | 245.0041 | 42.3532 | 486.4956 | 486.4956 | 161.5094 | 648.005 | 0.65471 | 65.47% | 293.0278 | 191.8477 | 134.2934 | 301.9129 | 301.9129 | 44.48% | 11.28% | 11.28% | 90% | 10.15% | 29.7529 | 3.5335 | 3.5335 | 105.1312 | 65.7958 | 34.82% | 34.82%
7 | 183 | 2 | 4384 | 16 | 29.5 | 411.72 | 171.06 | 582.78 | 171.06 | 85.53 | 183 | 4384 | 960 | 180.4932 | 22.8855 | -2.8134 | 934.284 | 15.5245 | -52.8677 | 41.6246 | 41.6246 | 79.2882 | 259.2882 | 55.3934 | 352.0255 | 352.0255 | 146.0088 | 498.0343 | 0.61435 | 61.43% | 225.2111 | 138.3582 | 96.8508 | 286.2011 | 286.2011 | 33.84% | 11.19% | 11.19% | 85% | 9.515% | 21.429 | 3.3855 | 3.3855 | 72.5475 | 47.3884 | 25.35% | 25.35%
7 | 183 | 2 | 4385 | 17 | 25.8 | 330.33 | 135.56 | 465.89 | 135.56 | 67.78 | 183 | 4385 | 1020 | 180.4932 | 22.8855 | -2.8134 | 994.284 | 16.5245 | -67.8677 | 31.405 | 31.405 | 90.8993 | 270.8993 | 68.9618 | 227.574 | 227.574 | 115.7077 | 343.2817 | 0.50624 | 50.62% | 155.232 | 78.584 | 55.0088 | 196.6671 | 196.6671 | 27.97% | 11.21% | 11.21% | 85% | 9.525% | 14.7864 | 3.917 | 3.917 | 57.9181 | 32.6988 | 29.45% | 29.45%
7 | 183 | 2 | 4386 | 18 | 17.3 | 206.72 | 102.5 | 309.22 | 102.5 | 51.25 | 183 | 4386 | 1080 | 180.4932 | 22.8855 | -2.8134 | 1054.284 | 17.5245 | -82.8677 | 21.206 | 21.206 | 101.3182 | 281.3182 | 82.7384 | 72.2355 | 72.2355 | 87.4892 | 159.7247 | 0.048018 | 4.802% | 72.2275 | 3.4682 | 2.4278 | 124.5154 | 124.5154 | 1.95% | 11.45% | 11.45% | 80% | 9.158% | 6.6144 | 5.501 | 5.501 | 36.3853 | 14.6271 | 29.22% | 29.22%
7 | 183 | 2 | 4387 | 19 | 17 | 111.11 | 86.94 | 198.05 | 86.94 | 43.47 | 183 | 4387 | 1140 | 180.4932 | 22.8855 | -2.8134 | 1114.284 | 18.5245 | -97.8677 | 11.3629 | 11.3629 | 111.4311 | 291.4311 | 96.545 | -64.2803 | 0 | 74.2079 | 74.2079 | -0.83222 | 0% | 33.5568 | 0 | 0 | 113.9243 | 113.9243 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4388 | 20 | 16.7 | 52.08 | 54.78 | 106.86 | 54.78 | 27.39 | 183 | 4388 | 1200 | 180.4932 | 22.8855 | -2.8134 | 1174.284 | 19.5245 | -112.8677 | 2.1897 | 2.1897 | 121.8431 | 301.8431 | 110.2292 | 0 | 0 | 46.7577 | 46.7577 | -1.8072 | 0% | 21.1438 | 0 | 0 | 143.7501 | 143.7501 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4389 | 21 | 16.4 | 0 | 10.89 | 10.89 | 10.89 | 5.45 | 183 | 4389 | 1260 | 180.4932 | 22.8855 | -2.8134 | 1234.284 | 20.5245 | -127.8677 | -5.9636 | 0 | 124.6016 | 304.6016 | 113.6746 | 0 | 0 | 9.2952 | 9.2952 | -12.4037 | 0% | 4.2033 | 0 | 0 | -10.8217 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4390 | 22 | 15.6 | 0 | 0 | 0 | 0 | 0 | 183 | 4390 | 1320 | 180.4932 | 22.8855 | -2.8134 | 1294.284 | 21.5245 | -142.8677 | -12.6861 | 0 | 124.6016 | 304.6016 | 113.6746 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2344 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4391 | 23 | 14.9 | 0 | 0 | 0 | 0 | 0 | 183 | 4391 | 1380 | 180.4932 | 22.8855 | -2.8134 | 1354.284 | 22.5245 | -157.8677 | -17.5204 | 0 | 124.6016 | 304.6016 | 113.6746 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8022 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
7 | 183 | 2 | 4392 | 24 | 13.7 | 0 | 0 | 0 | 0 | 0 | 183 | 4392 | 1440 | 180.4932 | 22.8855 | -2.8134 | 1414.284 | 23.5245 | -172.8677 | -20.0385 | 0 | 124.6016 | 304.6016 | 113.6746 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1319 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4393 | 1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 184 | 4393 | 60 | 181.4795 | 22.8084 | -3.2428 | 34.284 | 0.51735 | 172.2397 | -20.0605 | 0 | 124.4758 | 55.5242 | 113.5946 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3292 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4394 | 2 | 12.7 | 0 | 0 | 0 | 0 | 0 | 184 | 4394 | 120 | 181.4795 | 22.8084 | -3.2428 | 94.284 | 1.5174 | 157.2397 | -17.4358 | 0 | 124.4758 | 55.5242 | 113.5946 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4814 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4395 | 3 | 12.6 | 0 | 0 | 0 | 0 | 0 | 184 | 4395 | 180 | 181.4795 | 22.8084 | -3.2428 | 154.284 | 2.5174 | 142.2397 | -12.5089 | 0 | 124.4758 | 55.5242 | 113.5946 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.024 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4396 | 4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 184 | 4396 | 240 | 181.4795 | 22.8084 | -3.2428 | 214.284 | 3.5174 | 127.2397 | -5.7124 | 0 | 124.4758 | 55.5242 | 113.5946 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2432 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4397 | 5 | 11.4 | 0 | 0 | 0 | 0 | 0 | 184 | 4397 | 300 | 181.4795 | 22.8084 | -3.2428 | 274.284 | 4.5174 | 112.2397 | 2.4964 | 2.4964 | 121.3459 | 58.6541 | 109.6754 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.2122 | 1.2122 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4398 | 6 | 11 | 3.75 | 17.22 | 20.97 | 17.22 | 8.61 | 184 | 4398 | 360 | 181.4795 | 22.8084 | -3.2428 | 334.284 | 5.5174 | 97.2397 | 11.7083 | 11.7083 | 110.9507 | 69.0493 | 95.9743 | -1.9234 | 0 | 14.6982 | 14.6982 | -8.3882 | 0% | 6.6465 | 0 | 0 | 13.8214 | 13.8214 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4399 | 7 | 12.7 | 64.31 | 68.75 | 133.06 | 68.75 | 34.38 | 184 | 4399 | 420 | 181.4795 | 22.8084 | -3.2428 | 394.284 | 6.5174 | 82.2397 | 21.5754 | 21.5754 | 100.8326 | 79.1674 | 82.1582 | 23.8612 | 23.8612 | 58.6818 | 82.543 | -0.78525 | 0% | 37.3259 | 0 | 0 | 188.7603 | 188.7603 | 0% | 11.64% | 11.64% | 80% | 9.312% | 3.4758 | 6.5691 | 6 | 20.8549 | 7.6864 | 11.05% | 11.05%
7 | 184 | 3 | 4400 | 8 | 14.4 | 164.94 | 106.17 | 271.11 | 106.17 | 53.09 | 184 | 4400 | 480 | 181.4795 | 22.8084 | -3.2428 | 454.284 | 7.5174 | 67.2397 | 31.7835 | 31.7835 | 90.3774 | 89.6226 | 68.378 | 115.3904 | 115.3904 | 90.6218 | 206.0121 | 0.18611 | 18.61% | 93.1587 | 17.3376 | 12.1363 | 164.8718 | 164.8718 | 7.361% | 11.53% | 11.53% | 80% | 9.228% | 8.5966 | 6.1571 | 6 | 51.5799 | 19.0107 | 31.28% | 31.28%
7 | 184 | 3 | 4401 | 9 | 16.2 | 248.67 | 151.61 | 400.28 | 151.61 | 75.81 | 184 | 4401 | 540 | 181.4795 | 22.8084 | -3.2428 | 514.284 | 8.5174 | 52.2397 | 41.994 | 41.994 | 78.6817 | 101.3183 | 54.814 | 214.1711 | 214.1711 | 129.4072 | 343.5783 | 0.44537 | 44.54% | 155.3661 | 69.1952 | 48.4366 | 173.8451 | 173.8451 | 27.86% | 11.45% | 11.45% | 85% | 9.73% | 15.1176 | 5.7429 | 5.7429 | 86.8187 | 33.4311 | 49.94% | 49.94%
7 | 184 | 3 | 4402 | 10 | 17.5 | 352.64 | 192.92 | 545.56 | 192.92 | 96.46 | 184 | 4402 | 600 | 181.4795 | 22.8084 | -3.2428 | 574.284 | 9.5174 | 37.2397 | 51.7254 | 51.7254 | 64.231 | 115.769 | 41.795 | 334.8893 | 334.8893 | 164.6675 | 499.5569 | 0.56318 | 56.32% | 225.8996 | 127.2228 | 89.0559 | 178.6081 | 178.6081 | 49.86% | 11.39% | 11.39% | 85% | 9.684% | 21.8768 | 5.4579 | 5.4579 | 119.401 | 48.3787 | 66.85% | 66.85%
7 | 184 | 3 | 4403 | 11 | 18.5 | 406.06 | 227.22 | 633.28 | 227.22 | 113.61 | 184 | 4403 | 660 | 181.4795 | 22.8084 | -3.2428 | 634.284 | 10.5174 | 22.2397 | 60.0889 | 60.0889 | 44.3993 | 135.6007 | 30.1346 | 405.1458 | 405.1458 | 193.9444 | 599.0902 | 0.60691 | 60.69% | 270.9086 | 164.4174 | 115.0922 | 174.5543 | 174.5543 | 65.93% | 11.37% | 11.37% | 90% | 10.23% | 27.7186 | 5.2467 | 5.2467 | 145.4305 | 61.2972 | 83.32% | 83.32%
7 | 184 | 3 | 4404 | 12 | 19.4 | 597.72 | 199.03 | 796.75 | 199.03 | 99.52 | 184 | 4404 | 720 | 181.4795 | 22.8084 | -3.2428 | 694.284 | 11.5174 | 7.2397 | 65.3303 | 65.3303 | 16.1598 | 163.8402 | 22.1736 | 609.1095 | 609.1095 | 169.8827 | 778.9922 | 0.65499 | 65.5% | 352.2603 | 230.7257 | 161.508 | 168.8753 | 168.8753 | 95.64% | 11.35% | 11.35% | 90% | 10.22% | 35.9919 | 5.0626 | 5.0626 | 182.212 | 79.5929 | 107.9% | 107.9%
7 | 184 | 3 | 4405 | 13 | 19.6 | 567.22 | 198.28 | 765.5 | 198.28 | 99.14 | 184 | 4405 | 780 | 181.4795 | 22.8084 | -3.2428 | 754.284 | 12.5174 | -7.7603 | 65.2277 | 65.2277 | 17.2809 | 197.2809 | 22.3389 | 577.8223 | 577.8223 | 169.2426 | 747.0649 | 0.64921 | 64.92% | 337.8227 | 219.3175 | 153.5223 | 164.7199 | 164.7199 | 93.2% | 11.35% | 11.35% | 90% | 10.22% | 34.5182 | 5.0224 | 5.0224 | 173.3657 | 76.334 | 105.2% | 105.2%
7 | 184 | 3 | 4406 | 14 | 20.4 | 489.39 | 151.72 | 641.11 | 151.72 | 75.86 | 184 | 4406 | 840 | 181.4795 | 22.8084 | -3.2428 | 814.284 | 13.5174 | -22.7603 | 59.8376 | 59.8376 | 45.2162 | 225.2162 | 30.4983 | 487.7145 | 487.7145 | 129.5011 | 617.2156 | 0.6195 | 61.95% | 279.1049 | 172.9046 | 121.0332 | 159.1818 | 159.1818 | 76.03% | 11.35% | 11.35% | 90% | 10.21% | 28.5055 | 4.8647 | 4.8647 | 138.6701 | 63.0373 | 87.11% | 87.11%
7 | 184 | 3 | 4407 | 15 | 20.2 | 453.83 | 180.14 | 633.97 | 180.14 | 90.07 | 184 | 4407 | 900 | 181.4795 | 22.8084 | -3.2428 | 874.284 | 14.5174 | -37.7603 | 51.4035 | 51.4035 | 64.8037 | 244.8037 | 42.2313 | 429.952 | 429.952 | 153.7591 | 583.7111 | 0.60815 | 60.82% | 263.9541 | 160.5247 | 112.3673 | 156.3471 | 156.3471 | 71.87% | 11.35% | 11.35% | 90% | 10.21% | 26.962 | 4.9037 | 4.9037 | 132.2136 | 59.6241 | 84.56% | 84.56%
7 | 184 | 3 | 4408 | 16 | 19.5 | 473.19 | 198.61 | 671.8 | 198.61 | 99.31 | 184 | 4408 | 960 | 181.4795 | 22.8084 | -3.2428 | 934.284 | 15.5174 | -52.7603 | 41.6441 | 41.6441 | 79.1225 | 259.1225 | 55.2783 | 405.6039 | 405.6039 | 169.5242 | 575.1282 | 0.60255 | 60.25% | 260.073 | 156.7069 | 109.6948 | 155.2479 | 155.2479 | 70.66% | 11.36% | 11.36% | 90% | 10.22% | 26.5856 | 5.0425 | 5.0425 | 134.0573 | 58.7917 | 86.35% | 86.35%
7 | 184 | 3 | 4409 | 17 | 18.5 | 322.28 | 192.22 | 514.5 | 192.22 | 96.11 | 184 | 4409 | 1020 | 181.4795 | 22.8084 | -3.2428 | 994.284 | 16.5174 | -67.7603 | 31.427 | 31.427 | 90.7546 | 270.7546 | 68.8539 | 222.9746 | 222.9746 | 164.07 | 387.0447 | 0.49893 | 49.89% | 175.0216 | 87.3243 | 61.127 | 144.1624 | 144.1624 | 42.4% | 11.39% | 11.39% | 85% | 9.678% | 16.9389 | 5.2467 | 5.2467 | 88.8727 | 37.4588 | 61.65% | 61.65%
7 | 184 | 3 | 4410 | 18 | 18.2 | 142.36 | 117.78 | 260.14 | 117.78 | 58.89 | 184 | 4410 | 1080 | 181.4795 | 22.8084 | -3.2428 | 1054.284 | 17.5174 | -82.7603 | 21.2254 | 21.2254 | 101.1853 | 281.1853 | 82.638 | 50.3863 | 50.3863 | 100.5315 | 150.9178 | 0.017208 | 1.721% | 68.245 | 1.1743 | 0.82203 | 127.1642 | 127.1642 | 0.6464% | 11.42% | 11.42% | 80% | 9.133% | 6.2328 | 5.3093 | 5.3093 | 33.0919 | 13.7833 | 26.02% | 26.02%
7 | 184 | 3 | 4411 | 19 | 17.4 | 60.56 | 65 | 125.56 | 65 | 32.5 | 184 | 4411 | 1140 | 181.4795 | 22.8084 | -3.2428 | 1114.284 | 18.5174 | -97.7603 | 11.3758 | 11.3758 | 111.3039 | 291.3039 | 96.4527 | -34.5053 | 0 | 55.481 | 55.481 | -1.3684 | 0% | 25.0885 | 0 | 0 | 156.0834 | 156.0834 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4412 | 20 | 17 | 33.56 | 49.11 | 82.67 | 49.11 | 24.56 | 184 | 4412 | 1200 | 181.4795 | 22.8084 | -3.2428 | 1174.284 | 19.5174 | -112.7603 | 2.1925 | 2.1925 | 121.7177 | 301.7177 | 110.1468 | 0 | 0 | 41.918 | 41.918 | -2.0926 | 0% | 18.9553 | 0 | 0 | 145.4437 | 145.4437 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4413 | 21 | 16.3 | 0 | 12.56 | 12.56 | 12.56 | 6.28 | 184 | 4413 | 1260 | 181.4795 | 22.8084 | -3.2428 | 1234.284 | 20.5174 | -127.7603 | -5.9745 | 0 | 124.4758 | 304.4758 | 113.5946 | 0 | 0 | 10.7206 | 10.7206 | -10.6685 | 0% | 4.8479 | 0 | 0 | -8.0329 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4414 | 22 | 15.6 | 0 | 0 | 0 | 0 | 0 | 184 | 4414 | 1320 | 181.4795 | 22.8084 | -3.2428 | 1294.284 | 21.5174 | -142.7603 | -12.7139 | 0 | 124.4758 | 304.4758 | 113.5946 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.501 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4415 | 23 | 15.1 | 0 | 0 | 0 | 0 | 0 | 184 | 4415 | 1380 | 181.4795 | 22.8084 | -3.2428 | 1354.284 | 22.5174 | -157.7603 | -17.5677 | 0 | 124.4758 | 304.4758 | 113.5946 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6532 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
7 | 184 | 3 | 4416 | 24 | 13.7 | 0 | 0 | 0 | 0 | 0 | 184 | 4416 | 1440 | 181.4795 | 22.8084 | -3.2428 | 1414.284 | 23.5174 | -172.7603 | -20.1062 | 0 | 124.4758 | 304.4758 | 113.5946 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.177 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4417 | 1 | 13.4 | 0 | 0 | 0 | 0 | 0 | 185 | 4417 | 60 | 182.4658 | 22.7253 | -3.6682 | 34.284 | 0.51026 | 172.346 | -20.1529 | 0 | 124.34 | 55.66 | 113.5082 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5891 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4418 | 2 | 13.3 | 0 | 0 | 0 | 0 | 0 | 185 | 4418 | 120 | 182.4658 | 22.7253 | -3.6682 | 94.284 | 1.5103 | 157.346 | -17.5429 | 0 | 124.34 | 55.66 | 113.5082 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0785 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4419 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 185 | 4419 | 180 | 182.4658 | 22.7253 | -3.6682 | 154.284 | 2.5103 | 142.346 | -12.6261 | 0 | 124.34 | 55.66 | 113.5082 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8727 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4420 | 4 | 12.4 | 0 | 0 | 0 | 0 | 0 | 185 | 4420 | 240 | 182.4658 | 22.7253 | -3.6682 | 214.284 | 3.5103 | 127.346 | -5.8357 | 0 | 124.34 | 55.66 | 113.5082 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7871 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4421 | 5 | 11.4 | 0 | 0 | 0 | 0 | 0 | 185 | 4421 | 300 | 182.4658 | 22.7253 | -3.6682 | 274.284 | 4.5103 | 112.346 | 2.3699 | 2.3699 | 121.369 | 58.631 | 109.7873 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.7592 | 2.7592 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4422 | 6 | 11.4 | 2.56 | 11.53 | 14.09 | 11.53 | 5.77 | 185 | 4422 | 360 | 182.4658 | 22.7253 | -3.6682 | 334.284 | 5.5103 | 97.346 | 11.5804 | 11.5804 | 110.964 | 69.036 | 96.0786 | -1.3504 | 0 | 9.8415 | 9.8415 | -12.8303 | 0% | 4.4503 | 0 | 0 | 16.2338 | 16.2338 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4423 | 7 | 12.8 | 53.33 | 43.89 | 97.22 | 43.89 | 21.95 | 185 | 4423 | 420 | 182.4658 | 22.7253 | -3.6682 | 394.284 | 6.5103 | 82.346 | 21.4469 | 21.4469 | 100.8394 | 79.1606 | 82.2543 | 19.6578 | 19.6578 | 37.4625 | 57.1202 | -1.4886 | 0% | 25.8298 | 0 | 0 | 190.4652 | 190.4652 | 0% | 11.65% | 11.65% | 80% | 9.317% | 2.4065 | 6.5443 | 6 | 14.4393 | 5.3219 | 7.581% | 7.581%
7 | 185 | 4 | 4424 | 8 | 15 | 144.94 | 75.78 | 220.72 | 75.78 | 37.89 | 185 | 4424 | 480 | 182.4658 | 22.7253 | -3.6682 | 454.284 | 7.5103 | 67.346 | 31.6549 | 31.6549 | 90.382 | 89.618 | 68.4644 | 101.3798 | 101.3798 | 64.6823 | 166.0621 | 0.045669 | 4.567% | 75.0933 | 3.4295 | 2.4006 | 167.2075 | 167.2075 | 1.436% | 11.53% | 11.53% | 80% | 9.221% | 6.9244 | 6.0165 | 6 | 41.5464 | 15.3127 | 24.85% | 24.85%
7 | 185 | 4 | 4425 | 9 | 16.4 | 252.22 | 96.67 | 348.89 | 96.67 | 48.34 | 185 | 4425 | 540 | 182.4658 | 22.7253 | -3.6682 | 514.284 | 8.5103 | 52.346 | 41.8656 | 41.8656 | 78.6906 | 101.3094 | 54.8877 | 217.374 | 217.374 | 82.513 | 299.887 | 0.39462 | 39.46% | 135.6089 | 53.5139 | 37.4597 | 175.658 | 175.658 | 21.33% | 11.45% | 11.45% | 80% | 9.161% | 12.4229 | 5.6983 | 5.6983 | 70.7891 | 27.4721 | 40.3% | 40.3%
7 | 185 | 4 | 4426 | 10 | 17.6 | 283.47 | 150.14 | 433.61 | 150.14 | 75.07 | 185 | 4426 | 600 | 182.4658 | 22.7253 | -3.6682 | 574.284 | 9.5103 | 37.346 | 51.5979 | 51.5979 | 64.2588 | 115.7412 | 41.8492 | 269.4467 | 269.4467 | 128.1525 | 397.5992 | 0.50199 | 50.2% | 179.7944 | 90.2552 | 63.1786 | 177.0139 | 177.0139 | 35.69% | 11.41% | 11.41% | 85% | 9.694% | 17.4299 | 5.4364 | 5.4364 | 94.7566 | 38.5447 | 53.53% | 53.53%
7 | 185 | 4 | 4427 | 11 | 18.4 | 427.28 | 228 | 655.28 | 228 | 114 | 185 | 4427 | 660 | 182.4658 | 22.7253 | -3.6682 | 634.284 | 10.5103 | 22.346 | 59.9668 | 59.9668 | 44.4804 | 135.5196 | 30.1541 | 426.7578 | 426.7578 | 194.6102 | 621.368 | 0.61362 | 61.36% | 280.9826 | 172.4164 | 120.6915 | 178.004 | 178.004 | 67.8% | 11.37% | 11.37% | 90% | 10.23% | 28.7472 | 5.2675 | 5.2675 | 151.4252 | 63.5718 | 85.07% | 85.07%
7 | 185 | 4 | 4428 | 12 | 19.4 | 452.56 | 274.94 | 727.5 | 274.94 | 137.47 | 185 | 4428 | 720 | 182.4658 | 22.7253 | -3.6682 | 694.284 | 11.5103 | 7.346 | 65.2285 | 65.2285 | 16.3479 | 163.6521 | 22.1283 | 461.7094 | 461.7094 | 234.676 | 696.3854 | 0.63731 | 63.73% | 314.9055 | 200.6924 | 140.4847 | 168.198 | 168.198 | 83.52% | 11.36% | 11.36% | 90% | 10.22% | 32.183 | 5.0626 | 5.0626 | 162.9288 | 71.1697 | 96.87% | 96.87%
7 | 185 | 4 | 4429 | 13 | 20.2 | 420.69 | 299.72 | 720.41 | 299.72 | 149.86 | 185 | 4429 | 780 | 182.4658 | 22.7253 | -3.6682 | 754.284 | 12.5103 | -7.654 | 65.168 | 65.168 | 17.0094 | 197.0094 | 22.2264 | 429.1049 | 429.1049 | 255.827 | 684.9319 | 0.6371 | 63.71% | 309.7262 | 197.3255 | 138.1278 | 166.0152 | 166.0152 | 83.2% | 11.35% | 11.35% | 90% | 10.22% | 31.6406 | 4.9037 | 4.9037 | 155.1559 | 69.9703 | 93.46% | 93.46%
7 | 185 | 4 | 4430 | 14 | 19.8 | 429.67 | 296.61 | 726.28 | 296.61 | 148.31 | 185 | 4430 | 840 | 182.4658 | 22.7253 | -3.6682 | 814.284 | 13.5103 | -22.654 | 59.8184 | 59.8184 | 44.9631 | 224.9631 | 30.3697 | 428.8474 | 428.8474 | 253.1725 | 682.0198 | 0.63509 | 63.51% | 308.4094 | 195.8686 | 137.108 | 163.8535 | 163.8535 | 83.68% | 11.35% | 11.35% | 90% | 10.22% | 31.5132 | 4.9826 | 4.9826 | 157.0169 | 69.6886 | 95.83% | 95.83%
7 | 185 | 4 | 4431 | 15 | 21.2 | 372.92 | 251.61 | 624.53 | 251.61 | 125.81 | 185 | 4431 | 900 | 182.4658 | 22.7253 | -3.6682 | 874.284 | 14.5103 | -37.654 | 51.4077 | 51.4077 | 64.5977 | 244.5977 | 42.1076 | 353.9697 | 353.9697 | 214.7626 | 568.7323 | 0.60685 | 60.68% | 257.1807 | 156.07 | 109.249 | 158.8299 | 158.8299 | 68.78% | 11.34% | 11.34% | 90% | 10.2% | 26.2403 | 4.7114 | 4.7114 | 123.6286 | 58.0281 | 77.84% | 77.84%
7 | 185 | 4 | 4432 | 16 | 21.3 | 268.33 | 183.94 | 452.27 | 183.94 | 91.97 | 185 | 4432 | 960 | 182.4658 | 22.7253 | -3.6682 | 934.284 | 15.5103 | -52.654 | 41.6587 | 41.6587 | 78.9515 | 258.9515 | 55.1625 | 230.6085 | 230.6085 | 157.0026 | 387.6111 | 0.51529 | 51.53% | 175.2777 | 90.3187 | 63.2231 | 148.9733 | 148.9733 | 42.44% | 11.32% | 11.32% | 85% | 9.624% | 16.869 | 4.6926 | 4.6926 | 79.1586 | 37.3042 | 53.14% | 53.14%
7 | 185 | 4 | 4433 | 17 | 21.9 | 247.17 | 146.06 | 393.23 | 146.06 | 73.03 | 185 | 4433 | 1020 | 182.4658 | 22.7253 | -3.6682 | 994.284 | 16.5103 | -67.654 | 31.4441 | 31.4441 | 90.6052 | 270.6052 | 68.7461 | 171.7562 | 171.7562 | 124.67 | 296.4262 | 0.43089 | 43.09% | 134.0439 | 57.7581 | 40.4307 | 144.3038 | 144.3038 | 28.02% | 11.3% | 11.3% | 80% | 9.04% | 12.1169 | 4.581 | 4.581 | 55.507 | 26.7955 | 38.47% | 38.47%
7 | 185 | 4 | 4434 | 18 | 21.5 | 187.17 | 138.89 | 326.06 | 138.89 | 69.45 | 185 | 4434 | 1080 | 182.4658 | 22.7253 | -3.6682 | 1054.284 | 17.5103 | -82.654 | 21.2399 | 21.2399 | 101.0482 | 281.0482 | 82.5382 | 67.0951 | 67.0951 | 118.55 | 185.6451 | 0.20355 | 20.35% | 83.9487 | 17.0876 | 11.9613 | 136.1519 | 136.1519 | 8.785% | 11.3% | 11.3% | 80% | 9.041% | 7.5898 | 4.6551 | 4.6551 | 35.3313 | 16.7843 | 25.95% | 25.95%
7 | 185 | 4 | 4435 | 19 | 20.5 | 120.42 | 90.14 | 210.56 | 90.14 | 45.07 | 185 | 4435 | 1140 | 182.4658 | 22.7253 | -3.6682 | 1114.284 | 18.5103 | -97.654 | 11.3836 | 11.3836 | 111.1729 | 291.1729 | 96.3617 | -67.6021 | 0 | 76.9393 | 76.9393 | -0.67325 | 0% | 34.792 | 0 | 0 | 124.2145 | 124.2145 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8453 | 4.8453 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4436 | 20 | 17 | 38.33 | 45 | 83.33 | 45 | 22.5 | 185 | 4436 | 1200 | 182.4658 | 22.7253 | -3.6682 | 1174.284 | 19.5103 | -112.654 | 2.19 | 2.19 | 121.589 | 301.589 | 110.0662 | 0 | 0 | 38.4099 | 38.4099 | -2.3572 | 0% | 17.369 | 0 | 0 | 145.9974 | 145.9974 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4437 | 21 | 16.3 | 0 | 8.33 | 8.33 | 8.33 | 4.17 | 185 | 4437 | 1260 | 182.4658 | 22.7253 | -3.6682 | 1234.284 | 20.5103 | -127.654 | -5.9908 | 0 | 124.34 | 304.34 | 113.5082 | 0 | 0 | 7.1101 | 7.1101 | -16.4943 | 0% | 3.2152 | 0 | 0 | -7.9152 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4438 | 22 | 13.5 | 0 | 0 | 0 | 0 | 0 | 185 | 4438 | 1320 | 182.4658 | 22.7253 | -3.6682 | 1294.284 | 21.5103 | -142.654 | -12.7475 | 0 | 124.34 | 304.34 | 113.5082 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4257 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4439 | 23 | 13.6 | 0 | 0 | 0 | 0 | 0 | 185 | 4439 | 1380 | 182.4658 | 22.7253 | -3.6682 | 1354.284 | 22.5103 | -157.654 | -17.621 | 0 | 124.34 | 304.34 | 113.5082 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6103 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
7 | 185 | 4 | 4440 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 185 | 4440 | 1440 | 182.4658 | 22.7253 | -3.6682 | 1414.284 | 23.5103 | -172.654 | -20.1799 | 0 | 124.34 | 304.34 | 113.5082 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8617 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4441 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 186 | 4441 | 60 | 183.4521 | 22.636 | -4.0892 | 34.284 | 0.50325 | 172.4513 | -20.2511 | 0 | 124.1944 | 55.8056 | 113.4155 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8236 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4442 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 186 | 4442 | 120 | 183.4521 | 22.636 | -4.0892 | 94.284 | 1.5032 | 157.4513 | -17.6556 | 0 | 124.1944 | 55.8056 | 113.4155 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2008 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4443 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 186 | 4443 | 180 | 183.4521 | 22.636 | -4.0892 | 154.284 | 2.5032 | 142.4513 | -12.7484 | 0 | 124.1944 | 55.8056 | 113.4155 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5779 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4444 | 4 | 12.9 | 0 | 0 | 0 | 0 | 0 | 186 | 4444 | 240 | 183.4521 | 22.636 | -4.0892 | 214.284 | 3.5032 | 127.4513 | -5.9635 | 0 | 124.1944 | 55.8056 | 113.4155 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7303 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4445 | 5 | 13 | 0 | 0 | 0 | 0 | 0 | 186 | 4445 | 300 | 183.4521 | 22.636 | -4.0892 | 274.284 | 4.5032 | 112.4513 | 2.2393 | 2.2393 | 121.3876 | 58.6124 | 109.8993 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.1004 | 5.1004 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4446 | 6 | 13 | 2.17 | 10.5 | 12.67 | 10.5 | 5.25 | 186 | 4446 | 360 | 183.4521 | 22.636 | -4.0892 | 334.284 | 5.5032 | 97.4513 | 11.4487 | 11.4487 | 110.9722 | 69.0278 | 96.1824 | -1.1774 | 0 | 8.9623 | 8.9623 | -13.7562 | 0% | 4.0528 | 0 | 0 | 18.0462 | 18.0462 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4447 | 7 | 13.1 | 51.81 | 38.11 | 89.92 | 38.11 | 19.06 | 186 | 4447 | 420 | 183.4521 | 22.636 | -4.0892 | 394.284 | 6.5032 | 82.4513 | 21.315 | 21.315 | 100.8409 | 79.1591 | 82.3494 | 18.9758 | 18.9758 | 32.5289 | 51.5047 | -1.7252 | 0% | 23.2904 | 0 | 0 | 189.8932 | 189.8932 | 0% | 11.64% | 11.64% | 80% | 9.309% | 2.1681 | 6.4703 | 6 | 13.0084 | 4.7945 | 6.85% | 6.85%
7 | 186 | 5 | 4448 | 8 | 14.1 | 169.44 | 59.72 | 229.16 | 59.72 | 29.86 | 186 | 4448 | 480 | 183.4521 | 22.636 | -4.0892 | 454.284 | 7.5032 | 67.4513 | 31.523 | 31.523 | 90.3806 | 89.6194 | 68.5493 | 118.5147 | 118.5147 | 50.9742 | 169.4889 | 0.048926 | 4.893% | 76.6429 | 3.7498 | 2.6249 | 165.4846 | 165.4846 | 1.586% | 11.56% | 11.56% | 80% | 9.245% | 7.0858 | 6.2283 | 6 | 42.5151 | 15.6697 | 25.69% | 25.69%
7 | 186 | 5 | 4449 | 9 | 15.6 | 268.33 | 86.44 | 354.77 | 86.44 | 43.22 | 186 | 4449 | 540 | 183.4521 | 22.636 | -4.0892 | 514.284 | 8.5032 | 52.4513 | 41.7336 | 41.7336 | 78.6927 | 101.3073 | 54.9591 | 231.4433 | 231.4433 | 73.7812 | 305.2245 | 0.39587 | 39.59% | 138.0225 | 54.6388 | 38.2472 | 173.7813 | 173.7813 | 22.01% | 11.47% | 11.47% | 85% | 9.751% | 13.4585 | 5.8784 | 5.8784 | 79.1152 | 29.7624 | 45.53% | 45.53%
7 | 186 | 5 | 4450 | 10 | 16.6 | 392.08 | 91.06 | 483.14 | 91.06 | 45.53 | 186 | 4450 | 600 | 183.4521 | 22.636 | -4.0892 | 574.284 | 9.5032 | 37.4513 | 51.4666 | 51.4666 | 64.2789 | 115.7211 | 41.9004 | 373.0642 | 373.0642 | 77.7246 | 450.7888 | 0.53266 | 53.27% | 203.8467 | 108.5804 | 76.0063 | 176.8339 | 176.8339 | 42.98% | 11.42% | 11.42% | 85% | 9.705% | 19.7827 | 5.6539 | 5.6539 | 111.8503 | 43.7477 | 63.25% | 63.25%
7 | 186 | 5 | 4451 | 11 | 17.3 | 465.89 | 125.14 | 591.03 | 125.14 | 62.57 | 186 | 4451 | 660 | 183.4521 | 22.636 | -4.0892 | 634.284 | 10.5032 | 22.4513 | 59.84 | 59.84 | 44.5531 | 135.4469 | 30.1695 | 465.8452 | 465.8452 | 106.8137 | 572.6589 | 0.59314 | 59.31% | 258.9564 | 153.5982 | 107.5187 | 172.5975 | 172.5975 | 62.29% | 11.39% | 11.39% | 90% | 10.25% | 26.5357 | 5.501 | 5.501 | 145.9719 | 58.6814 | 84.57% | 84.57%
7 | 186 | 5 | 4452 | 12 | 17.3 | 529.86 | 148.89 | 678.75 | 148.89 | 74.45 | 186 | 4452 | 720 | 183.4521 | 22.636 | -4.0892 | 694.284 | 11.5032 | 7.4513 | 65.1208 | 65.1208 | 16.5293 | 163.4707 | 22.0776 | 541.237 | 541.237 | 127.0856 | 668.3225 | 0.62333 | 62.33% | 302.2155 | 188.3785 | 131.865 | 162.0242 | 162.0242 | 81.39% | 11.37% | 11.37% | 90% | 10.23% | 30.9299 | 5.501 | 5.501 | 170.1442 | 68.3988 | 105% | 105%
7 | 186 | 5 | 4453 | 13 | 17.2 | 511.31 | 191.94 | 703.25 | 191.94 | 95.97 | 186 | 4453 | 780 | 183.4521 | 22.636 | -4.0892 | 754.284 | 12.5032 | -7.5487 | 65.1017 | 65.1017 | 16.7381 | 196.7381 | 22.1088 | 522.2541 | 522.2541 | 163.831 | 686.0851 | 0.62768 | 62.77% | 310.2477 | 194.7352 | 136.3147 | 160.2139 | 160.2139 | 85.08% | 11.37% | 11.37% | 90% | 10.23% | 31.7464 | 5.5226 | 5.5226 | 175.3225 | 70.2043 | 109.4% | 109.4%
7 | 186 | 5 | 4454 | 14 | 17.4 | 475.06 | 202.78 | 677.84 | 202.78 | 101.39 | 186 | 4454 | 840 | 183.4521 | 22.636 | -4.0892 | 814.284 | 13.5032 | -22.5487 | 59.7932 | 59.7932 | 44.7057 | 224.7057 | 30.2378 | 474.9105 | 474.9105 | 173.0836 | 647.994 | 0.618 | 61.8% | 293.0229 | 181.0888 | 126.7622 | 158.3111 | 158.3111 | 80.07% | 11.37% | 11.37% | 90% | 10.24% | 29.9949 | 5.4794 | 5.4794 | 164.3534 | 66.331 | 103.8% | 103.8%
7 | 186 | 5 | 4455 | 15 | 17.6 | 495.19 | 221.19 | 716.38 | 221.19 | 110.6 | 186 | 4455 | 900 | 183.4521 | 22.636 | -4.0892 | 874.284 | 14.5032 | -37.5487 | 51.4065 | 51.4065 | 64.3862 | 244.3862 | 41.9823 | 470.9629 | 470.9629 | 188.7975 | 659.7604 | 0.622 | 62.2% | 298.3436 | 185.5688 | 129.8982 | 158.1695 | 158.1695 | 82.13% | 11.37% | 11.37% | 90% | 10.23% | 30.5309 | 5.4364 | 5.4364 | 165.9793 | 67.5163 | 104.9% | 104.9%
7 | 186 | 5 | 4456 | 16 | 17.8 | 505.97 | 175.83 | 681.8 | 175.83 | 87.92 | 186 | 4456 | 960 | 183.4521 | 22.636 | -4.0892 | 934.284 | 15.5032 | -52.5487 | 41.6682 | 41.6682 | 78.7753 | 258.7753 | 55.0461 | 436.0282 | 436.0282 | 150.0803 | 586.1085 | 0.59989 | 59.99% | 265.0383 | 158.9931 | 111.2952 | 155.2403 | 155.2403 | 71.69% | 11.38% | 11.38% | 90% | 10.24% | 27.1402 | 5.3938 | 5.3938 | 146.3881 | 60.0181 | 94.3% | 94.3%
7 | 186 | 5 | 4457 | 17 | 18.1 | 334.39 | 139.94 | 474.33 | 139.94 | 69.97 | 186 | 4457 | 1020 | 183.4521 | 22.636 | -4.0892 | 994.284 | 16.5032 | -67.5487 | 31.4563 | 31.4563 | 90.4512 | 270.4512 | 68.6385 | 233.4054 | 233.4054 | 119.4463 | 352.8516 | 0.46685 | 46.69% | 159.5595 | 74.4905 | 52.1434 | 143.8097 | 143.8097 | 36.26% | 11.4% | 11.4% | 85% | 9.689% | 15.4596 | 5.3303 | 5.3303 | 82.4045 | 34.1875 | 57.3% | 57.3%
7 | 186 | 5 | 4458 | 18 | 17.5 | 235.69 | 124.58 | 360.27 | 124.58 | 62.29 | 186 | 4458 | 1080 | 183.4521 | 22.636 | -4.0892 | 1054.284 | 17.5032 | -82.5487 | 21.2495 | 21.2495 | 100.907 | 280.907 | 82.4392 | 85.5656 | 85.5656 | 106.3357 | 191.9013 | 0.17711 | 17.71% | 86.7778 | 15.3688 | 10.7582 | 133.021 | 133.021 | 8.088% | 11.44% | 11.44% | 80% | 9.148% | 7.9389 | 5.4579 | 5.4579 | 43.3293 | 17.5561 | 32.57% | 32.57%
7 | 186 | 5 | 4459 | 19 | 15 | 170 | 95.69 | 265.69 | 95.69 | 47.85 | 186 | 4459 | 1140 | 183.4521 | 22.636 | -4.0892 | 1114.284 | 18.5032 | -97.5487 | 11.3864 | 11.3864 | 111.0384 | 291.0384 | 96.2721 | -94.0731 | 0 | 81.6765 | 81.6765 | -0.73781 | 0% | 36.9341 | 0 | 0 | 119.8718 | 119.8718 | 0% | 11.55% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4460 | 20 | 15.1 | 40.5 | 41.89 | 82.39 | 41.89 | 20.95 | 186 | 4460 | 1200 | 183.4521 | 22.636 | -4.0892 | 1174.284 | 19.5032 | -112.5487 | 2.1823 | 2.1823 | 121.4572 | 301.4572 | 109.9877 | 0 | 0 | 35.7554 | 35.7554 | -2.7116 | 0% | 16.1686 | 0 | 0 | 143.7402 | 143.7402 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4461 | 21 | 14.5 | 0 | 9.22 | 9.22 | 9.22 | 4.61 | 186 | 4461 | 1260 | 183.4521 | 22.636 | -4.0892 | 1234.284 | 20.5032 | -127.5487 | -6.0127 | 0 | 124.1944 | 304.1944 | 113.4155 | 0 | 0 | 7.8698 | 7.8698 | -15.3421 | 0% | 3.5587 | 0 | 0 | -10.0748 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4462 | 22 | 14.1 | 0 | 0 | 0 | 0 | 0 | 186 | 4462 | 1320 | 183.4521 | 22.636 | -4.0892 | 1294.284 | 21.5032 | -142.5487 | -12.7868 | 0 | 124.1944 | 304.1944 | 113.4155 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0159 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4463 | 23 | 13.6 | 0 | 0 | 0 | 0 | 0 | 186 | 4463 | 1380 | 183.4521 | 22.636 | -4.0892 | 1354.284 | 22.5032 | -157.5487 | -17.6803 | 0 | 124.1944 | 304.1944 | 113.4155 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.155 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
7 | 186 | 5 | 4464 | 24 | 13.7 | 0 | 0 | 0 | 0 | 0 | 186 | 4464 | 1440 | 183.4521 | 22.636 | -4.0892 | 1414.284 | 23.5032 | -172.5487 | -20.2597 | 0 | 124.1944 | 304.1944 | 113.4155 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3797 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4465 | 1 | 13.3 | 0 | 0 | 0 | 0 | 0 | 187 | 4465 | 60 | 184.4384 | 22.5406 | -4.5055 | 34.284 | 0.49631 | 172.5554 | -20.3552 | 0 | 124.0391 | 55.9609 | 113.3164 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2724 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4466 | 2 | 13.7 | 0 | 0 | 0 | 0 | 0 | 187 | 4466 | 120 | 184.4384 | 22.5406 | -4.5055 | 94.284 | 1.4963 | 157.5554 | -17.7737 | 0 | 124.0391 | 55.9609 | 113.3164 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.102 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4467 | 3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 187 | 4467 | 180 | 184.4384 | 22.5406 | -4.5055 | 154.284 | 2.4963 | 142.5554 | -12.8757 | 0 | 124.0391 | 55.9609 | 113.3164 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2843 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4468 | 4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 187 | 4468 | 240 | 184.4384 | 22.5406 | -4.5055 | 214.284 | 3.4963 | 127.5554 | -6.0959 | 0 | 124.0391 | 55.9609 | 113.3164 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4367 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4469 | 5 | 11.8 | 0 | 0 | 0 | 0 | 0 | 187 | 4469 | 300 | 184.4384 | 22.5406 | -4.5055 | 274.284 | 4.4963 | 112.5554 | 2.1046 | 2.1046 | 121.4016 | 58.5984 | 110.0116 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.88586 | 0.88586 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4470 | 6 | 11.9 | 3.75 | 12.92 | 16.67 | 12.92 | 6.46 | 187 | 4470 | 360 | 184.4384 | 22.5406 | -4.5055 | 334.284 | 5.4963 | 97.5554 | 11.3134 | 11.3134 | 110.9756 | 69.0244 | 96.2858 | -2.0929 | 0 | 11.0279 | 11.0279 | -11.2586 | 0% | 4.9868 | 0 | 0 | 13.4623 | 13.4623 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4471 | 7 | 11.6 | 51.06 | 52 | 103.06 | 52 | 26 | 187 | 4471 | 420 | 184.4384 | 22.5406 | -4.5055 | 394.284 | 6.4963 | 82.5554 | 21.1797 | 21.1797 | 100.837 | 79.163 | 82.4434 | 18.5852 | 18.5852 | 44.3848 | 62.9699 | -1.3195 | 0% | 28.475 | 0 | 0 | 183.0667 | 183.0667 | 0% | 11.69% | 11.69% | 80% | 9.354% | 2.6636 | 6.8464 | 6 | 15.9813 | 5.8902 | 8.73% | 8.73%
7 | 187 | 6 | 4472 | 8 | 12.5 | 151.06 | 88.94 | 240 | 88.94 | 44.47 | 187 | 4472 | 480 | 184.4384 | 22.5406 | -4.5055 | 454.284 | 7.4963 | 67.5554 | 31.3878 | 31.3878 | 90.3732 | 89.6268 | 68.6325 | 105.6752 | 105.6752 | 75.915 | 181.5902 | 0.079061 | 7.906% | 82.1151 | 6.4921 | 4.5445 | 157.6143 | 157.6143 | 2.883% | 11.61% | 11.61% | 80% | 9.286% | 7.6249 | 6.6189 | 6 | 45.7496 | 16.8619 | 29.03% | 29.03%
7 | 187 | 6 | 4473 | 9 | 12.9 | 220.06 | 138.67 | 358.73 | 138.67 | 69.34 | 187 | 4473 | 540 | 184.4384 | 22.5406 | -4.5055 | 514.284 | 8.4963 | 52.5554 | 41.5983 | 41.5983 | 78.6881 | 101.3119 | 55.0283 | 189.9857 | 189.9857 | 118.3622 | 308.3479 | 0.38006 | 38.01% | 139.4349 | 52.993 | 37.0951 | 163.964 | 163.964 | 22.62% | 11.54% | 11.54% | 85% | 9.812% | 13.6819 | 6.5196 | 6 | 82.0914 | 30.2563 | 50.07% | 50.07%
7 | 187 | 6 | 4474 | 10 | 14.2 | 355.69 | 169.58 | 525.27 | 169.58 | 84.79 | 187 | 4474 | 600 | 184.4384 | 22.5406 | -4.5055 | 574.284 | 9.4963 | 37.5554 | 51.3314 | 51.3314 | 64.2914 | 115.7086 | 41.9486 | 338.8214 | 338.8214 | 144.7456 | 483.567 | 0.53982 | 53.98% | 218.669 | 118.0419 | 82.6293 | 169.8739 | 169.8739 | 48.64% | 11.45% | 11.45% | 85% | 9.735% | 21.2874 | 6.2045 | 6 | 127.7246 | 47.0753 | 75.19% | 75.19%
7 | 187 | 6 | 4475 | 11 | 15.9 | 499.03 | 176.61 | 675.64 | 176.61 | 88.31 | 187 | 4475 | 660 | 184.4384 | 22.5406 | -4.5055 | 634.284 | 10.4963 | 22.5554 | 59.7086 | 59.7086 | 44.6174 | 135.3826 | 30.1807 | 499.5924 | 499.5924 | 150.7461 | 650.3384 | 0.61349 | 61.35% | 294.083 | 180.4178 | 126.2925 | 169.8487 | 169.8487 | 74.36% | 11.39% | 11.39% | 90% | 10.25% | 30.1352 | 5.8104 | 5.8104 | 175.0962 | 66.6413 | 103.1% | 103.1%
7 | 187 | 6 | 4476 | 12 | 17.7 | 450.56 | 152.31 | 602.87 | 152.31 | 76.16 | 187 | 4476 | 720 | 184.4384 | 22.5406 | -4.5055 | 694.284 | 11.4963 | 7.5554 | 65.0072 | 65.0072 | 16.7041 | 163.2959 | 22.0216 | 460.8411 | 460.8411 | 130.0047 | 590.8459 | 0.60115 | 60.11% | 267.1805 | 160.6146 | 112.4302 | 156.3127 | 156.3127 | 71.93% | 11.38% | 11.38% | 90% | 10.24% | 27.3609 | 5.4151 | 5.4151 | 148.1614 | 60.5062 | 94.79% | 94.79%
7 | 187 | 6 | 4477 | 13 | 18 | 496.75 | 182.97 | 679.72 | 182.97 | 91.49 | 187 | 4477 | 780 | 184.4384 | 22.5406 | -4.5055 | 754.284 | 12.4963 | -7.4446 | 65.0288 | 65.0288 | 16.4674 | 196.4674 | 21.986 | 508.1233 | 508.1233 | 156.1747 | 664.298 | 0.62458 | 62.46% | 300.3956 | 187.622 | 131.3354 | 157.5248 | 157.5248 | 83.37% | 11.37% | 11.37% | 90% | 10.23% | 30.7312 | 5.3514 | 5.3514 | 164.4548 | 67.9592 | 104.4% | 104.4%
7 | 187 | 6 | 4478 | 14 | 18.3 | 474.17 | 213 | 687.17 | 213 | 106.5 | 187 | 4478 | 840 | 184.4384 | 22.5406 | -4.5055 | 814.284 | 13.4963 | -22.4446 | 59.7617 | 59.7617 | 44.444 | 224.444 | 30.1028 | 474.8221 | 474.8221 | 181.8069 | 656.6289 | 0.6235 | 62.35% | 296.9276 | 185.1357 | 129.595 | 157.4188 | 157.4188 | 82.32% | 11.37% | 11.37% | 90% | 10.23% | 30.3723 | 5.2884 | 5.2884 | 160.6196 | 67.1657 | 102% | 102%
7 | 187 | 6 | 4479 | 15 | 20.3 | 375.97 | 213 | 588.97 | 213 | 106.5 | 187 | 4479 | 900 | 184.4384 | 22.5406 | -4.5055 | 874.284 | 14.4963 | -37.4446 | 51.3997 | 51.3997 | 64.1694 | 244.1694 | 41.8554 | 358.3212 | 358.3212 | 181.8069 | 540.1281 | 0.59276 | 59.28% | 244.2459 | 144.7787 | 101.3451 | 154.4663 | 154.4663 | 65.61% | 11.35% | 11.35% | 90% | 10.21% | 24.9447 | 4.8842 | 4.8842 | 121.8337 | 55.163 | 78.87% | 78.87%
7 | 187 | 6 | 4480 | 16 | 19.9 | 399.03 | 215.42 | 614.45 | 215.42 | 107.71 | 187 | 4480 | 960 | 184.4384 | 22.5406 | -4.5055 | 934.284 | 15.4963 | -52.4446 | 41.6727 | 41.6727 | 78.5942 | 258.5942 | 54.9292 | 344.844 | 344.844 | 183.8725 | 528.7165 | 0.58653 | 58.65% | 239.0856 | 140.2319 | 98.1623 | 153.3609 | 153.3609 | 64.01% | 11.35% | 11.35% | 90% | 10.22% | 24.4301 | 4.9628 | 4.9628 | 121.2406 | 54.025 | 79.06% | 79.06%
7 | 187 | 6 | 4481 | 17 | 21.7 | 349.11 | 174.22 | 523.33 | 174.22 | 87.11 | 187 | 4481 | 1020 | 184.4384 | 22.5406 | -4.5055 | 994.284 | 16.4963 | -67.4446 | 31.4636 | 31.4636 | 90.2928 | 270.2928 | 68.531 | 244.7968 | 244.7968 | 148.7061 | 393.5029 | 0.52183 | 52.18% | 177.942 | 92.8553 | 64.9987 | 149.6523 | 149.6523 | 43.43% | 11.31% | 11.31% | 85% | 9.617% | 17.1125 | 4.6179 | 4.6179 | 79.0234 | 37.8428 | 52.8% | 52.8%
7 | 187 | 6 | 4482 | 18 | 21.3 | 251.33 | 134.86 | 386.19 | 134.86 | 67.43 | 187 | 4482 | 1080 | 184.4384 | 22.5406 | -4.5055 | 1054.284 | 17.4963 | -82.4446 | 21.2542 | 21.2542 | 100.7618 | 280.7618 | 82.3411 | 92.4016 | 92.4016 | 115.1102 | 207.5118 | 0.26472 | 26.47% | 93.8369 | 24.8402 | 17.3882 | 138.4896 | 138.4896 | 12.56% | 11.31% | 11.31% | 80% | 9.048% | 8.4901 | 4.6926 | 4.6926 | 39.8402 | 18.7751 | 28.77% | 28.77%
7 | 187 | 6 | 4483 | 19 | 20.6 | 164.31 | 108 | 272.31 | 108 | 54 | 187 | 4483 | 1140 | 184.4384 | 22.5406 | -4.5055 | 1114.284 | 18.4963 | -97.4446 | 11.3842 | 11.3842 | 110.9003 | 290.9003 | 96.1838 | -89.6676 | 0 | 92.1838 | 92.1838 | -0.42658 | 0% | 41.6855 | 0 | 0 | 127.2798 | 127.2798 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8259 | 4.8259 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4484 | 20 | 19.2 | 54.03 | 52.44 | 106.47 | 52.44 | 26.22 | 187 | 4484 | 1200 | 184.4384 | 22.5406 | -4.5055 | 1174.284 | 19.4963 | -112.4446 | 2.1694 | 2.1694 | 121.3223 | 301.3223 | 109.9111 | 0 | 0 | 44.7603 | 44.7603 | -1.7993 | 0% | 20.2406 | 0 | 0 | 150.6763 | 150.6763 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4485 | 21 | 16.5 | 0 | 13.39 | 13.39 | 13.39 | 6.7 | 187 | 4485 | 1260 | 184.4384 | 22.5406 | -4.5055 | 1234.284 | 20.4963 | -127.4446 | -6.04 | 0 | 124.0391 | 304.0391 | 113.3164 | 0 | 0 | 11.4291 | 11.4291 | -9.918 | 0% | 5.1682 | 0 | 0 | -7.6451 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4486 | 22 | 16.3 | 0 | 0 | 0 | 0 | 0 | 187 | 4486 | 1320 | 184.4384 | 22.5406 | -4.5055 | 1294.284 | 21.4963 | -142.4446 | -12.832 | 0 | 124.0391 | 304.0391 | 113.3164 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3831 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4487 | 23 | 15.3 | 0 | 0 | 0 | 0 | 0 | 187 | 4487 | 1380 | 184.4384 | 22.5406 | -4.5055 | 1354.284 | 22.4963 | -157.4446 | -17.7455 | 0 | 124.0391 | 304.0391 | 113.3164 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3462 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
7 | 187 | 6 | 4488 | 24 | 14.6 | 0 | 0 | 0 | 0 | 0 | 187 | 4488 | 1440 | 184.4384 | 22.5406 | -4.5055 | 1414.284 | 23.4963 | -172.4446 | -20.3455 | 0 | 124.0391 | 304.0391 | 113.3164 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8521 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4489 | 1 | 13.8 | 0 | 0 | 0 | 0 | 0 | 188 | 4489 | 60 | 185.4247 | 22.4392 | -4.9168 | 34.284 | 0.48945 | 172.6582 | -20.4651 | 0 | 123.8742 | 56.1258 | 113.2111 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7401 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4490 | 2 | 13.3 | 0 | 0 | 0 | 0 | 0 | 188 | 4490 | 120 | 185.4247 | 22.4392 | -4.9168 | 94.284 | 1.4895 | 157.6582 | -17.8972 | 0 | 123.8742 | 56.1258 | 113.2111 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6329 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4491 | 3 | 12.8 | 0 | 0 | 0 | 0 | 0 | 188 | 4491 | 180 | 185.4247 | 22.4392 | -4.9168 | 154.284 | 2.4895 | 142.6582 | -13.008 | 0 | 123.8742 | 56.1258 | 113.2111 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5256 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4492 | 4 | 12.6 | 0 | 0 | 0 | 0 | 0 | 188 | 4492 | 240 | 185.4247 | 22.4392 | -4.9168 | 214.284 | 3.4895 | 127.6582 | -6.2327 | 0 | 123.8742 | 56.1258 | 113.2111 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8304 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4493 | 5 | 12.5 | 0 | 0 | 0 | 0 | 0 | 188 | 4493 | 300 | 185.4247 | 22.4392 | -4.9168 | 274.284 | 4.4895 | 112.6582 | 1.966 | 1.966 | 121.411 | 58.589 | 110.1238 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.3106 | 9.3106 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4494 | 6 | 13 | 3.67 | 14.72 | 18.39 | 14.72 | 7.36 | 188 | 4494 | 360 | 185.4247 | 22.4392 | -4.9168 | 334.284 | 5.4895 | 97.6582 | 11.1744 | 11.1744 | 110.9739 | 69.0261 | 96.3886 | -2.1072 | 0 | 12.5643 | 12.5643 | -9.582 | 0% | 5.6816 | 0 | 0 | 26.6491 | 26.6491 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4495 | 7 | 13.3 | 79.44 | 49.78 | 129.22 | 49.78 | 24.89 | 188 | 4495 | 420 | 185.4247 | 22.4392 | -4.9168 | 394.284 | 6.4895 | 82.6582 | 21.041 | 21.041 | 100.8277 | 79.1723 | 82.5362 | 28.7414 | 28.7414 | 42.4899 | 71.2313 | -1.0183 | 0% | 32.2108 | 0 | 0 | 207.0874 | 207.0874 | 0% | 11.62% | 11.62% | 80% | 9.296% | 2.9945 | 6.4214 | 6 | 17.9667 | 6.622 | 8.676% | 8.676%
7 | 188 | 7 | 4496 | 8 | 13.8 | 165.69 | 57.78 | 223.47 | 57.78 | 28.89 | 188 | 4496 | 480 | 185.4247 | 22.4392 | -4.9168 | 454.284 | 7.4895 | 67.6582 | 31.2493 | 31.2493 | 90.3599 | 89.6401 | 68.714 | 115.9478 | 115.9478 | 49.3183 | 165.2661 | 0.02549 | 2.549% | 74.7333 | 1.905 | 1.3335 | 181.5027 | 181.5027 | 0.7347% | 11.57% | 11.57% | 80% | 9.255% | 6.9164 | 6.3002 | 6 | 41.4983 | 15.295 | 22.86% | 22.86%
7 | 188 | 7 | 4497 | 9 | 14.6 | 376.81 | 85.83 | 462.64 | 85.83 | 42.92 | 188 | 4497 | 540 | 185.4247 | 22.4392 | -4.9168 | 514.284 | 8.4895 | 52.6582 | 41.4596 | 41.4596 | 78.6769 | 101.3231 | 55.0951 | 325.6596 | 325.6596 | 73.2605 | 398.9201 | 0.48605 | 48.6% | 180.3917 | 87.6786 | 61.375 | 194.4653 | 194.4653 | 31.56% | 11.47% | 11.47% | 85% | 9.75% | 17.589 | 6.1099 | 6 | 105.534 | 38.8965 | 54.27% | 54.27%
7 | 188 | 7 | 4498 | 10 | 15.7 | 447.22 | 130.22 | 577.44 | 130.22 | 65.11 | 188 | 4498 | 600 | 185.4247 | 22.4392 | -4.9168 | 574.284 | 9.4895 | 37.6582 | 51.1925 | 51.1925 | 64.2961 | 115.7039 | 41.9936 | 426.5382 | 426.5382 | 111.1497 | 537.6879 | 0.57274 | 57.27% | 243.1425 | 139.2574 | 97.4802 | 195.5617 | 195.5617 | 49.85% | 11.41% | 11.41% | 90% | 10.27% | 24.9771 | 5.8557 | 5.8557 | 146.258 | 55.2347 | 74.79% | 74.79%
7 | 188 | 7 | 4499 | 11 | 17.3 | 571.89 | 152.17 | 724.06 | 152.17 | 76.09 | 188 | 4499 | 660 | 185.4247 | 22.4392 | -4.9168 | 634.284 | 10.4895 | 22.6582 | 59.5725 | 59.5725 | 44.6734 | 135.3266 | 30.1879 | 573.2894 | 573.2894 | 129.8852 | 703.1746 | 0.63228 | 63.23% | 317.9756 | 201.0496 | 140.7348 | 191.3107 | 191.3107 | 73.56% | 11.37% | 11.37% | 90% | 10.23% | 32.5281 | 5.501 | 5.501 | 178.9355 | 71.9329 | 93.53% | 93.53%
7 | 188 | 7 | 4500 | 12 | 19.6 | 514.36 | 112.03 | 626.39 | 112.03 | 56.02 | 188 | 4500 | 720 | 185.4247 | 22.4392 | -4.9168 | 694.284 | 11.4895 | 7.6582 | 64.8878 | 64.8878 | 16.872 | 163.128 | 21.9603 | 526.8372 | 526.8372 | 95.6236 | 622.4608 | 0.61822 | 61.82% | 281.4768 | 174.0154 | 121.8108 | 171.919 | 171.919 | 70.85% | 11.36% | 11.36% | 90% | 10.22% | 28.7678 | 5.0224 | 5.0224 | 144.4846 | 63.6175 | 84.04% | 84.04%
7 | 188 | 7 | 4501 | 13 | 20.3 | 554.36 | 115.08 | 669.44 | 115.08 | 57.54 | 188 | 4501 | 780 | 185.4247 | 22.4392 | -4.9168 | 754.284 | 12.4895 | -7.3418 | 64.9495 | 64.9495 | 16.1976 | 196.1976 | 21.858 | 567.929 | 567.929 | 98.2269 | 666.1559 | 0.63272 | 63.27% | 301.2357 | 190.5985 | 133.4189 | 170.0051 | 170.0051 | 78.48% | 11.35% | 11.35% | 90% | 10.21% | 30.7707 | 4.8842 | 4.8842 | 150.2887 | 68.0466 | 88.4% | 88.4%
7 | 188 | 7 | 4502 | 14 | 20.4 | 804.03 | 104.58 | 908.61 | 104.58 | 52.29 | 188 | 4502 | 840 | 185.4247 | 22.4392 | -4.9168 | 814.284 | 13.4895 | -22.3418 | 59.7242 | 59.7242 | 44.1785 | 224.1785 | 29.9647 | 806.5667 | 806.5667 | 89.2646 | 895.8313 | 0.67688 | 67.69% | 405.0949 | 274.2006 | 191.9404 | 176.7416 | 176.7416 | 108.6% | 11.35% | 11.35% | 95% | 10.79% | 43.6952 | 4.8647 | 4.8647 | 212.563 | 96.628 | 120.3% | 120.3%
7 | 188 | 7 | 4503 | 15 | 20.3 | 508.69 | 180.08 | 688.77 | 180.08 | 90.04 | 188 | 4503 | 900 | 185.4247 | 22.4392 | -4.9168 | 874.284 | 14.4895 | -37.3418 | 51.3875 | 51.3875 | 63.9476 | 243.9476 | 41.727 | 485.8661 | 485.8661 | 153.7079 | 639.574 | 0.6256 | 62.56% | 289.2154 | 180.9341 | 126.6539 | 164.6694 | 164.6694 | 76.91% | 11.35% | 11.35% | 90% | 10.21% | 29.5417 | 4.8842 | 4.8842 | 144.2861 | 65.3288 | 87.62% | 87.62%
7 | 188 | 7 | 4504 | 16 | 23.2 | 377.08 | 123.75 | 500.83 | 123.75 | 61.88 | 188 | 4504 | 960 | 185.4247 | 22.4392 | -4.9168 | 934.284 | 15.4895 | -52.3418 | 41.672 | 41.672 | 78.4081 | 258.4081 | 54.8119 | 326.8292 | 326.8292 | 105.6272 | 432.4564 | 0.55477 | 55.48% | 195.5568 | 108.4882 | 75.9418 | 161.1894 | 161.1894 | 47.11% | 11.29% | 11.29% | 85% | 9.594% | 18.7621 | 4.3478 | 4.3478 | 81.574 | 41.4908 | 50.61% | 50.61%
7 | 188 | 7 | 4505 | 17 | 23.8 | 300.28 | 149.31 | 449.59 | 149.31 | 74.66 | 188 | 4505 | 1020 | 185.4247 | 22.4392 | -4.9168 | 994.284 | 16.4895 | -67.3418 | 31.4659 | 31.4659 | 90.1299 | 270.1299 | 68.4239 | 211.5435 | 211.5435 | 127.4441 | 338.9876 | 0.48986 | 48.99% | 153.2902 | 75.0903 | 52.5632 | 166.5079 | 166.5079 | 31.57% | 11.26% | 11.26% | 85% | 9.567% | 14.6657 | 4.2442 | 4.2442 | 62.244 | 32.432 | 37.38% | 37.38%
7 | 188 | 7 | 4506 | 18 | 22.8 | 225.83 | 122.64 | 348.47 | 122.64 | 61.32 | 188 | 4506 | 1080 | 185.4247 | 22.4392 | -4.9168 | 1054.284 | 17.4895 | -82.3418 | 21.2539 | 21.2539 | 100.6127 | 280.6127 | 82.2439 | 84.0751 | 84.0751 | 104.6798 | 188.7549 | 0.2284 | 22.84% | 85.355 | 19.4951 | 13.6466 | 141.2127 | 141.2127 | 9.664% | 11.26% | 11.26% | 80% | 9.006% | 7.6873 | 4.4183 | 4.4183 | 33.9647 | 16.9998 | 24.05% | 24.05%
7 | 188 | 7 | 4507 | 19 | 20.4 | 125.78 | 76.39 | 202.17 | 76.39 | 38.2 | 188 | 4507 | 1140 | 185.4247 | 22.4392 | -4.9168 | 1114.284 | 18.4895 | -97.3418 | 11.3769 | 11.3769 | 110.7588 | 290.7588 | 96.097 | -67.7245 | 0 | 65.2029 | 65.2029 | -0.94252 | 0% | 29.4848 | 0 | 0 | 125.0269 | 125.0269 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.8647 | 4.8647 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4508 | 20 | 19.9 | 59.67 | 47.44 | 107.11 | 47.44 | 23.72 | 188 | 4508 | 1200 | 185.4247 | 22.4392 | -4.9168 | 1174.284 | 19.4895 | -112.3418 | 2.1511 | 2.1511 | 121.1845 | 301.1845 | 109.8365 | 0 | 0 | 40.4926 | 40.4926 | -2.0355 | 0% | 18.3107 | 0 | 0 | 152.4101 | 152.4101 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4509 | 21 | 18.1 | 0 | 13.39 | 13.39 | 13.39 | 6.7 | 188 | 4509 | 1260 | 185.4247 | 22.4392 | -4.9168 | 1234.284 | 20.4895 | -127.3418 | -6.0729 | 0 | 123.8742 | 303.8742 | 113.2111 | 0 | 0 | 11.4291 | 11.4291 | -9.6049 | 0% | 5.1682 | 0 | 0 | -5.0618 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4510 | 22 | 17.3 | 0 | 0 | 0 | 0 | 0 | 188 | 4510 | 1320 | 185.4247 | 22.4392 | -4.9168 | 1294.284 | 21.4895 | -142.3418 | -12.8829 | 0 | 123.8742 | 303.8742 | 113.2111 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0137 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4511 | 23 | 16.8 | 0 | 0 | 0 | 0 | 0 | 188 | 4511 | 1380 | 185.4247 | 22.4392 | -4.9168 | 1354.284 | 22.4895 | -157.3418 | -17.8167 | 0 | 123.8742 | 303.8742 | 113.2111 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.9065 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
7 | 188 | 7 | 4512 | 24 | 16.6 | 0 | 0 | 0 | 0 | 0 | 188 | 4512 | 1440 | 185.4247 | 22.4392 | -4.9168 | 1414.284 | 23.4895 | -172.3418 | -20.4372 | 0 | 123.8742 | 303.8742 | 113.2111 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3421 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4513 | 1 | 16.8 | 0 | 0 | 0 | 0 | 0 | 189 | 4513 | 60 | 186.411 | 22.3318 | -5.3226 | 34.284 | 0.48269 | 172.7597 | -20.5808 | 0 | 123.6997 | 56.3003 | 113.0996 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.0096 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4514 | 2 | 16.6 | 0 | 0 | 0 | 0 | 0 | 189 | 4514 | 120 | 186.411 | 22.3318 | -5.3226 | 94.284 | 1.4827 | 157.7597 | -18.0262 | 0 | 123.6997 | 56.3003 | 113.0996 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.7029 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4515 | 3 | 16.5 | 0 | 0 | 0 | 0 | 0 | 189 | 4515 | 180 | 186.411 | 22.3318 | -5.3226 | 154.284 | 2.4827 | 142.7597 | -13.1451 | 0 | 123.6997 | 56.3003 | 113.0996 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.2438 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4516 | 4 | 16.5 | 0 | 0 | 0 | 0 | 0 | 189 | 4516 | 240 | 186.411 | 22.3318 | -5.3226 | 214.284 | 3.4827 | 127.7597 | -6.3739 | 0 | 123.6997 | 56.3003 | 113.0996 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.2438 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4517 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 189 | 4517 | 300 | 186.411 | 22.3318 | -5.3226 | 274.284 | 4.4827 | 112.7597 | 1.8235 | 1.8235 | 121.4158 | 58.5842 | 110.2361 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.817 | 9.817 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4518 | 6 | 15.3 | 3.67 | 13 | 16.67 | 13 | 6.5 | 189 | 4518 | 360 | 186.411 | 22.3318 | -5.3226 | 334.284 | 5.4827 | 97.7597 | 11.032 | 11.032 | 110.9673 | 69.0327 | 96.4907 | -2.168 | 0 | 11.0962 | 11.0962 | -10.4837 | 0% | 5.0177 | 0 | 0 | 22.3893 | 22.3893 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4519 | 7 | 15.3 | 68 | 43.61 | 111.61 | 43.61 | 21.81 | 189 | 4519 | 420 | 186.411 | 22.3318 | -5.3226 | 394.284 | 6.4827 | 82.7597 | 20.8991 | 20.8991 | 100.813 | 79.187 | 82.6279 | 24.4595 | 24.4595 | 37.2235 | 61.6829 | -1.2265 | 0% | 27.893 | 0 | 0 | 194.9407 | 194.9407 | 0% | 11.54% | 11.54% | 80% | 9.234% | 2.5757 | 5.9472 | 5.9472 | 15.3182 | 5.696 | 7.858% | 7.858%
7 | 189 | 8 | 4520 | 8 | 16.3 | 136.39 | 97.92 | 234.31 | 97.92 | 48.96 | 189 | 4520 | 480 | 186.411 | 22.3318 | -5.3226 | 454.284 | 7.4827 | 67.7597 | 31.1076 | 31.1076 | 90.3406 | 89.6594 | 68.7938 | 95.4922 | 95.4922 | 83.5799 | 179.0722 | 0.11717 | 11.72% | 80.9764 | 9.4877 | 6.6414 | 169.3894 | 169.3894 | 3.921% | 11.48% | 11.48% | 80% | 9.183% | 7.4358 | 5.7206 | 5.7206 | 42.537 | 16.4436 | 25.11% | 25.11%
7 | 189 | 8 | 4521 | 9 | 17.4 | 221.39 | 169.31 | 390.7 | 169.31 | 84.66 | 189 | 4521 | 540 | 186.411 | 22.3318 | -5.3226 | 514.284 | 8.4827 | 52.7597 | 41.3177 | 41.3177 | 78.6589 | 101.3411 | 55.1596 | 191.5662 | 191.5662 | 144.5151 | 336.0813 | 0.44538 | 44.54% | 151.976 | 67.6871 | 47.381 | 178.8607 | 178.8607 | 26.49% | 11.42% | 11.42% | 85% | 9.706% | 14.7502 | 5.4794 | 5.4794 | 80.8218 | 32.6187 | 45.19% | 45.19%
7 | 189 | 8 | 4522 | 10 | 16.4 | 382.17 | 164.11 | 546.28 | 164.11 | 82.06 | 189 | 4522 | 600 | 186.411 | 22.3318 | -5.3226 | 574.284 | 9.4827 | 37.7597 | 51.0499 | 51.0499 | 64.2933 | 115.7067 | 42.0356 | 364.9875 | 364.9875 | 140.0766 | 505.0642 | 0.56093 | 56.09% | 228.39 | 128.1099 | 89.6769 | 180.5619 | 180.5619 | 49.67% | 11.41% | 11.41% | 90% | 10.27% | 23.4542 | 5.6983 | 5.6983 | 133.6485 | 51.8668 | 74.02% | 74.02%
7 | 189 | 8 | 4523 | 11 | 14.5 | 420.78 | 200.83 | 621.61 | 200.83 | 100.42 | 189 | 4523 | 660 | 186.411 | 22.3318 | -5.3226 | 634.284 | 10.4827 | 22.7597 | 59.432 | 59.432 | 44.7209 | 135.2791 | 30.1911 | 422.406 | 422.406 | 171.4191 | 593.8252 | 0.59002 | 59% | 268.5277 | 158.4372 | 110.906 | 171.2053 | 171.2053 | 64.78% | 11.41% | 11.41% | 90% | 10.27% | 27.5857 | 6.1335 | 6 | 165.514 | 61.0032 | 96.68% | 96.68%
7 | 189 | 8 | 4524 | 12 | 15.4 | 475.42 | 236.33 | 711.75 | 236.33 | 118.17 | 189 | 4524 | 720 | 186.411 | 22.3318 | -5.3226 | 694.284 | 11.4827 | 7.7597 | 64.7627 | 64.7627 | 17.0328 | 162.9672 | 21.8937 | 487.6805 | 487.6805 | 201.7203 | 689.4008 | 0.62265 | 62.26% | 311.747 | 194.1088 | 135.8762 | 162.436 | 162.436 | 83.65% | 11.38% | 11.38% | 90% | 10.24% | 31.9291 | 5.9242 | 5.9242 | 189.1536 | 70.6083 | 116.4% | 116.4%
7 | 189 | 8 | 4525 | 13 | 17.3 | 567.78 | 190.78 | 758.56 | 190.78 | 95.39 | 189 | 4525 | 780 | 186.411 | 22.3318 | -5.3226 | 754.284 | 12.4827 | -7.2403 | 64.8636 | 64.8636 | 15.9292 | 195.9292 | 21.7251 | 582.6262 | 582.6262 | 162.8409 | 745.4672 | 0.64202 | 64.2% | 337.1003 | 216.4259 | 151.4981 | 164.1214 | 164.1214 | 92.31% | 11.36% | 11.36% | 90% | 10.22% | 34.4654 | 5.501 | 5.501 | 189.5928 | 76.2172 | 115.5% | 115.5%
7 | 189 | 8 | 4526 | 14 | 17.7 | 453.94 | 172.28 | 626.22 | 172.28 | 86.14 | 189 | 4526 | 840 | 186.411 | 22.3318 | -5.3226 | 814.284 | 13.4827 | -22.2403 | 59.6804 | 59.6804 | 43.9095 | 223.9095 | 29.8237 | 456.2207 | 456.2207 | 147.0502 | 603.2708 | 0.60532 | 60.53% | 272.7991 | 165.1319 | 115.5923 | 158.1574 | 158.1574 | 73.09% | 11.38% | 11.38% | 90% | 10.24% | 27.9324 | 5.4151 | 5.4151 | 151.2562 | 61.7701 | 95.64% | 95.64%
7 | 189 | 8 | 4527 | 15 | 17.8 | 366.39 | 242.92 | 609.31 | 242.92 | 121.46 | 189 | 4527 | 900 | 186.411 | 22.3318 | -5.3226 | 874.284 | 14.4827 | -37.2403 | 51.3696 | 51.3696 | 63.7209 | 243.7209 | 41.5972 | 350.744 | 350.744 | 207.3452 | 558.0892 | 0.58964 | 58.96% | 252.3679 | 148.8062 | 104.1643 | 155.6545 | 155.6545 | 66.92% | 11.38% | 11.38% | 90% | 10.24% | 25.8504 | 5.3938 | 5.3938 | 139.4314 | 57.1659 | 89.58% | 89.58%
7 | 189 | 8 | 4528 | 16 | 16 | 442.22 | 213.47 | 655.69 | 213.47 | 106.74 | 189 | 4528 | 960 | 186.411 | 22.3318 | -5.3226 | 934.284 | 15.4827 | -52.2403 | 41.6661 | 41.6661 | 78.2174 | 258.2174 | 54.6942 | 384.4484 | 384.4484 | 182.208 | 566.6564 | 0.58576 | 58.58% | 256.242 | 150.0956 | 105.0669 | 152.9434 | 152.9434 | 68.7% | 11.4% | 11.4% | 90% | 10.26% | 26.2981 | 5.7878 | 5.7878 | 152.2083 | 58.156 | 99.52% | 99.52%
7 | 189 | 8 | 4529 | 17 | 16 | 405.33 | 115.42 | 520.75 | 115.42 | 57.71 | 189 | 4529 | 1020 | 186.411 | 22.3318 | -5.3226 | 994.284 | 16.4827 | -67.2403 | 31.4633 | 31.4633 | 89.9627 | 269.9627 | 68.3172 | 286.9162 | 286.9162 | 98.5171 | 385.4333 | 0.48314 | 48.31% | 174.293 | 84.2085 | 58.946 | 144.2083 | 144.2083 | 40.88% | 11.44% | 11.44% | 85% | 9.727% | 16.953 | 5.7878 | 5.7878 | 98.1205 | 37.49 | 68.04% | 68.04%
7 | 189 | 8 | 4530 | 18 | 14.3 | 271.39 | 114.5 | 385.89 | 114.5 | 57.25 | 189 | 4530 | 1080 | 186.411 | 22.3318 | -5.3226 | 1054.284 | 17.4827 | -82.2403 | 21.2486 | 21.2486 | 100.4598 | 280.4598 | 82.1477 | 102.3067 | 102.3067 | 97.7319 | 200.0385 | 0.16652 | 16.65% | 90.4574 | 15.0628 | 10.544 | 130.7599 | 130.7599 | 8.064% | 11.54% | 11.54% | 80% | 9.232% | 8.3511 | 6.1808 | 6 | 50.1066 | 18.4677 | 38.32% | 38.32%
7 | 189 | 8 | 4531 | 19 | 13.7 | 178.75 | 83.19 | 261.94 | 83.19 | 41.6 | 189 | 4531 | 1140 | 186.411 | 22.3318 | -5.3226 | 1114.284 | 18.4827 | -97.2403 | 11.3645 | 11.3645 | 110.6139 | 290.6139 | 96.0118 | -95.0075 | 0 | 71.0071 | 71.0071 | -1.0112 | 0% | 32.1094 | 0 | 0 | 118.6689 | 118.6689 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4532 | 20 | 12.4 | 54.22 | 45.78 | 100 | 45.78 | 22.89 | 189 | 4532 | 1200 | 186.411 | 22.3318 | -5.3226 | 1174.284 | 19.4827 | -112.2403 | 2.1276 | 2.1276 | 121.0438 | 301.0438 | 109.764 | 0 | 0 | 39.0757 | 39.0757 | -2.5708 | 0% | 17.67 | 0 | 0 | 141.2551 | 141.2551 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4533 | 21 | 11.1 | 0 | 11.03 | 11.03 | 11.03 | 5.52 | 189 | 4533 | 1260 | 186.411 | 22.3318 | -5.3226 | 1234.284 | 20.4827 | -127.2403 | -6.1114 | 0 | 123.6997 | 303.6997 | 113.0996 | 0 | 0 | 9.4147 | 9.4147 | -13.5222 | 0% | 4.2573 | 0 | 0 | -14.9992 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4534 | 22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 189 | 4534 | 1320 | 186.411 | 22.3318 | -5.3226 | 1294.284 | 21.4827 | -142.2403 | -12.9395 | 0 | 123.6997 | 303.6997 | 113.0996 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4453 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4535 | 23 | 10.6 | 0 | 0 | 0 | 0 | 0 | 189 | 4535 | 1380 | 186.411 | 22.3318 | -5.3226 | 1354.284 | 22.4827 | -157.2403 | -17.8938 | 0 | 123.6997 | 303.6997 | 113.0996 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6814 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
7 | 189 | 8 | 4536 | 24 | 10.2 | 0 | 0 | 0 | 0 | 0 | 189 | 4536 | 1440 | 186.411 | 22.3318 | -5.3226 | 1414.284 | 23.4827 | -172.2403 | -20.5349 | 0 | 123.6997 | 303.6997 | 113.0996 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6795 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4537 | 1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 190 | 4537 | 60 | 187.3973 | 22.2185 | -5.7227 | 34.284 | 0.47602 | 172.8597 | -20.7021 | 0 | 123.5159 | 56.4841 | 112.982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2334 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4538 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 190 | 4538 | 120 | 187.3973 | 22.2185 | -5.7227 | 94.284 | 1.476 | 157.8597 | -18.1604 | 0 | 123.5159 | 56.4841 | 112.982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5273 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4539 | 3 | 9.3 | 0 | 0 | 0 | 0 | 0 | 190 | 4539 | 180 | 187.3973 | 22.2185 | -5.7227 | 154.284 | 2.476 | 142.8597 | -13.287 | 0 | 123.5159 | 56.4841 | 112.982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7355 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4540 | 4 | 8.5 | 0 | 0 | 0 | 0 | 0 | 190 | 4540 | 240 | 187.3973 | 22.2185 | -5.7227 | 214.284 | 3.476 | 127.8597 | -6.5193 | 0 | 123.5159 | 56.4841 | 112.982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9547 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4541 | 5 | 9.1 | 0 | 0 | 0 | 0 | 0 | 190 | 4541 | 300 | 187.3973 | 22.2185 | -5.7227 | 274.284 | 4.476 | 112.8597 | 1.6771 | 1.6771 | 121.416 | 58.584 | 110.3482 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.2704 | 8.2704 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4542 | 6 | 9.1 | 3.83 | 11.81 | 15.64 | 11.81 | 5.91 | 190 | 4542 | 360 | 187.3973 | 22.2185 | -5.7227 | 334.284 | 5.476 | 97.8597 | 10.8861 | 10.8861 | 110.9557 | 69.0443 | 96.5921 | -2.3281 | 0 | 10.0805 | 10.0805 | -13.0391 | 0% | 4.5584 | 0 | 0 | 24.5587 | 24.5587 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4543 | 7 | 9.3 | 59.78 | 42.92 | 102.7 | 42.92 | 21.46 | 190 | 4543 | 420 | 187.3973 | 22.2185 | -5.7227 | 394.284 | 6.476 | 82.8597 | 20.754 | 20.754 | 100.7928 | 79.2072 | 82.7183 | 21.3824 | 21.3824 | 36.6345 | 58.0169 | -1.5932 | 0% | 26.2352 | 0 | 0 | 203.6494 | 203.6494 | 0% | 11.79% | 11.79% | 80% | 9.431% | 2.4742 | 7.4538 | 6 | 14.8454 | 5.4715 | 7.29% | 7.29%
7 | 190 | 9 | 4544 | 8 | 10.3 | 210.42 | 68.47 | 278.89 | 68.47 | 34.24 | 190 | 4544 | 480 | 187.3973 | 22.2185 | -5.7227 | 454.284 | 7.476 | 67.8597 | 30.9629 | 30.9629 | 90.3154 | 89.6846 | 68.8717 | 147.4244 | 147.4244 | 58.4428 | 205.8672 | 0.1398 | 13.98% | 93.0931 | 13.0141 | 9.1099 | 183.2743 | 183.2743 | 4.971% | 11.67% | 11.67% | 80% | 9.335% | 8.6904 | 7.1852 | 6 | 52.1425 | 19.2181 | 28.45% | 28.45%
7 | 190 | 9 | 4545 | 9 | 11.2 | 381.17 | 96.39 | 477.56 | 96.39 | 48.2 | 190 | 4545 | 540 | 187.3973 | 22.2185 | -5.7227 | 514.284 | 8.476 | 52.8597 | 41.1725 | 41.1725 | 78.6342 | 101.3658 | 55.2217 | 330.2608 | 330.2608 | 82.274 | 412.5348 | 0.47762 | 47.76% | 186.5482 | 89.0983 | 62.3688 | 193.9596 | 193.9596 | 32.16% | 11.54% | 11.54% | 85% | 9.809% | 18.2978 | 6.9494 | 6 | 109.7867 | 40.4639 | 56.6% | 56.6%
7 | 190 | 9 | 4546 | 10 | 10.5 | 448.28 | 134.58 | 582.86 | 134.58 | 67.29 | 190 | 4546 | 600 | 187.3973 | 22.2185 | -5.7227 | 574.284 | 9.476 | 37.8597 | 50.9038 | 50.9038 | 64.2828 | 115.7172 | 42.0745 | 428.7487 | 428.7487 | 114.8712 | 543.6199 | 0.55333 | 55.33% | 245.8249 | 136.0212 | 95.2148 | 191.4082 | 191.4082 | 49.74% | 11.49% | 11.49% | 90% | 10.34% | 25.4118 | 7.1323 | 6 | 152.4709 | 56.196 | 79.66% | 79.66%
7 | 190 | 9 | 4547 | 11 | 10.9 | 613.28 | 121.39 | 734.67 | 121.39 | 60.7 | 190 | 4547 | 660 | 187.3973 | 22.2185 | -5.7227 | 634.284 | 10.476 | 22.8597 | 59.287 | 59.287 | 44.7601 | 135.2399 | 30.1901 | 616.5788 | 616.5788 | 103.6128 | 720.1917 | 0.61608 | 61.61% | 325.6707 | 200.6378 | 140.4465 | 185.1099 | 185.1099 | 75.87% | 11.39% | 11.39% | 90% | 10.25% | 33.3902 | 7.0274 | 6 | 200.3412 | 73.8394 | 108.2% | 108.2%
7 | 190 | 9 | 4548 | 12 | 11.2 | 646.58 | 133.42 | 780 | 133.42 | 66.71 | 190 | 4548 | 720 | 187.3973 | 22.2185 | -5.7227 | 694.284 | 11.476 | 7.8597 | 64.632 | 64.632 | 17.1864 | 162.8136 | 21.822 | 664.304 | 664.304 | 113.8811 | 778.1851 | 0.63098 | 63.1% | 351.8953 | 222.0373 | 155.4261 | 168.5258 | 168.5258 | 92.23% | 11.36% | 11.36% | 90% | 10.23% | 35.9859 | 6.9494 | 6 | 215.9153 | 79.5796 | 128.1% | 128.1%
7 | 190 | 9 | 4549 | 13 | 11.7 | 649.17 | 162.22 | 811.39 | 162.22 | 81.11 | 190 | 4549 | 780 | 187.3973 | 22.2185 | -5.7227 | 754.284 | 12.476 | -7.1403 | 64.7713 | 64.7713 | 15.6625 | 195.6625 | 21.5871 | 667.2872 | 667.2872 | 138.4634 | 805.7506 | 0.63833 | 63.83% | 364.3604 | 232.5828 | 162.808 | 166.0891 | 166.0891 | 98.02% | 11.35% | 11.35% | 95% | 10.78% | 39.285 | 6.8209 | 6 | 235.71 | 86.8753 | 141.9% | 141.9%
7 | 190 | 9 | 4550 | 14 | 11.7 | 603.19 | 138.19 | 741.38 | 138.19 | 69.1 | 190 | 4550 | 840 | 187.3973 | 22.2185 | -5.7227 | 814.284 | 13.476 | -22.1403 | 59.6305 | 59.6305 | 43.6373 | 223.6373 | 29.6797 | 607.4017 | 607.4017 | 117.9525 | 725.3542 | 0.61997 | 62% | 328.0052 | 203.3532 | 142.3472 | 160.7972 | 160.7972 | 88.53% | 11.39% | 11.39% | 90% | 10.25% | 33.6122 | 6.8209 | 6 | 201.6734 | 74.3304 | 125.4% | 125.4%
7 | 190 | 9 | 4551 | 15 | 10.1 | 465.08 | 150.19 | 615.27 | 150.19 | 75.1 | 190 | 4551 | 900 | 187.3973 | 22.2185 | -5.7227 | 874.284 | 14.476 | -37.1403 | 51.3461 | 51.3461 | 63.4897 | 243.4897 | 41.4662 | 446.2685 | 446.2685 | 128.1952 | 574.4636 | 0.56516 | 56.52% | 259.7725 | 146.8134 | 102.7694 | 150.1383 | 150.1383 | 68.45% | 11.47% | 11.47% | 90% | 10.33% | 26.8275 | 7.2383 | 6 | 160.9653 | 59.3267 | 107.2% | 107.2%
7 | 190 | 9 | 4552 | 16 | 11.1 | 517 | 167.22 | 684.22 | 167.22 | 83.61 | 190 | 4552 | 960 | 187.3973 | 22.2185 | -5.7227 | 934.284 | 15.476 | -52.1403 | 41.655 | 41.655 | 78.0221 | 258.0221 | 54.5763 | 450.8625 | 450.8625 | 142.7312 | 593.5937 | 0.57678 | 57.68% | 268.4231 | 154.8207 | 108.3745 | 152.1091 | 152.1091 | 71.25% | 11.45% | 11.45% | 90% | 10.31% | 27.6683 | 6.9753 | 6 | 166.01 | 61.186 | 109.1% | 109.1%
7 | 190 | 9 | 4553 | 17 | 10 | 358.83 | 78.19 | 437.02 | 78.19 | 39.1 | 190 | 4553 | 1020 | 187.3973 | 22.2185 | -5.7227 | 994.284 | 16.476 | -67.1403 | 31.4556 | 31.4556 | 89.7915 | 269.7915 | 68.211 | 255.2408 | 255.2408 | 66.7393 | 321.9801 | 0.37715 | 37.71% | 145.5994 | 54.9127 | 38.4389 | 135.9041 | 135.9041 | 28.28% | 11.61% | 11.61% | 85% | 9.873% | 14.3746 | 7.265 | 6 | 86.2473 | 31.7881 | 63.46% | 63.46%
7 | 190 | 9 | 4554 | 18 | 11.1 | 231.81 | 93.19 | 325 | 93.19 | 46.6 | 190 | 4554 | 1080 | 187.3973 | 22.2185 | -5.7227 | 1054.284 | 17.476 | -82.1403 | 21.2383 | 21.2383 | 100.3033 | 280.3033 | 82.0525 | 88.479 | 88.479 | 79.5426 | 168.0217 | 0.0012636 | 0.1264% | 75.9794 | 0.096008 | 0.067205 | 126.8071 | 126.8071 | 0.053% | 11.66% | 11.66% | 80% | 9.329% | 7.0882 | 6.9753 | 6 | 42.5291 | 15.6749 | 33.54% | 33.54%
7 | 190 | 9 | 4555 | 19 | 10.2 | 172.83 | 80.42 | 253.25 | 80.42 | 40.21 | 190 | 4555 | 1140 | 187.3973 | 22.2185 | -5.7227 | 1114.284 | 18.476 | -97.1403 | 11.3469 | 11.3469 | 110.4657 | 290.4657 | 95.9282 | -90.7263 | 0 | 68.6428 | 68.6428 | -1.1914 | 0% | 31.0403 | 0 | 0 | 116.8536 | 116.8536 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4556 | 20 | 10 | 64.72 | 45.22 | 109.94 | 45.22 | 22.61 | 190 | 4556 | 1200 | 187.3973 | 22.2185 | -5.7227 | 1174.284 | 19.476 | -112.1403 | 2.0987 | 2.0987 | 120.9002 | 300.9002 | 109.6937 | 0 | 0 | 38.5977 | 38.5977 | -2.7568 | 0% | 17.4539 | 0 | 0 | 141.876 | 141.876 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4557 | 21 | 9.8 | 0 | 10.33 | 10.33 | 10.33 | 5.17 | 190 | 4557 | 1260 | 187.3973 | 22.2185 | -5.7227 | 1234.284 | 20.476 | -127.1403 | -6.1553 | 0 | 123.5159 | 303.5159 | 112.982 | 0 | 0 | 8.8172 | 8.8172 | -14.8364 | 0% | 3.9871 | 0 | 0 | -13.6631 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4558 | 22 | 9.5 | 0 | 0 | 0 | 0 | 0 | 190 | 4558 | 1320 | 187.3973 | 22.2185 | -5.7227 | 1294.284 | 21.476 | -142.1403 | -13.0019 | 0 | 123.5159 | 303.5159 | 112.982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7235 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4559 | 23 | 8.6 | 0 | 0 | 0 | 0 | 0 | 190 | 4559 | 1380 | 187.3973 | 22.2185 | -5.7227 | 1354.284 | 22.476 | -157.1403 | -17.9768 | 0 | 123.5159 | 303.5159 | 112.982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.2365 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
7 | 190 | 9 | 4560 | 24 | 8.8 | 0 | 0 | 0 | 0 | 0 | 190 | 4560 | 1440 | 187.3973 | 22.2185 | -5.7227 | 1414.284 | 23.476 | -172.1403 | -20.6384 | 0 | 123.5159 | 303.5159 | 112.982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0732 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4561 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 191 | 4561 | 60 | 188.3836 | 22.0993 | -6.1167 | 34.284 | 0.46946 | 172.9582 | -20.829 | 0 | 123.3227 | 56.6773 | 112.8582 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4417 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4562 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 191 | 4562 | 120 | 188.3836 | 22.0993 | -6.1167 | 94.284 | 1.4695 | 157.9582 | -18.2999 | 0 | 123.3227 | 56.6773 | 112.8582 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1234 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4563 | 3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 191 | 4563 | 180 | 188.3836 | 22.0993 | -6.1167 | 154.284 | 2.4695 | 142.9582 | -13.4336 | 0 | 123.3227 | 56.6773 | 112.8582 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7864 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4564 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 191 | 4564 | 240 | 188.3836 | 22.0993 | -6.1167 | 214.284 | 3.4695 | 127.9582 | -6.669 | 0 | 123.3227 | 56.6773 | 112.8582 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3292 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4565 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 191 | 4565 | 300 | 188.3836 | 22.0993 | -6.1167 | 274.284 | 4.4695 | 112.9582 | 1.5271 | 1.5271 | 121.4116 | 58.5884 | 110.4602 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.2736 | 5.2736 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4566 | 6 | 11 | 3.11 | 13.11 | 16.22 | 13.11 | 6.56 | 191 | 4566 | 360 | 188.3836 | 22.0993 | -6.1167 | 334.284 | 5.4695 | 97.9582 | 10.7369 | 10.7369 | 110.939 | 69.061 | 96.6927 | -1.9455 | 0 | 11.1901 | 11.1901 | -11.27 | 0% | 5.0602 | 0 | 0 | 22.0848 | 22.0848 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4567 | 7 | 11.1 | 57.28 | 55.14 | 112.42 | 55.14 | 27.57 | 191 | 4567 | 420 | 188.3836 | 22.0993 | -6.1167 | 394.284 | 6.4695 | 82.9582 | 20.6058 | 20.6058 | 100.7673 | 79.2327 | 82.8074 | 20.3781 | 20.3781 | 47.0649 | 67.443 | -1.1959 | 0% | 30.4977 | 0 | 0 | 198.7055 | 198.7055 | 0% | 11.71% | 11.71% | 80% | 9.368% | 2.8572 | 6.9753 | 6 | 17.143 | 6.3184 | 8.627% | 8.627%
7 | 191 | 10 | 4568 | 8 | 12.2 | 173.19 | 85.28 | 258.47 | 85.28 | 42.64 | 191 | 4568 | 480 | 188.3836 | 22.0993 | -6.1167 | 454.284 | 7.4695 | 67.9582 | 30.8152 | 30.8152 | 90.2842 | 89.7158 | 68.9478 | 121.4453 | 121.4453 | 72.791 | 194.2364 | 0.1227 | 12.27% | 87.8337 | 10.7773 | 7.5441 | 176.1911 | 176.1911 | 4.282% | 11.61% | 11.61% | 80% | 9.289% | 8.1593 | 6.6941 | 6 | 48.9559 | 18.0436 | 27.79% | 27.79%
7 | 191 | 10 | 4569 | 9 | 13.9 | 312.72 | 114.72 | 427.44 | 114.72 | 57.36 | 191 | 4569 | 540 | 188.3836 | 22.0993 | -6.1167 | 514.284 | 8.4695 | 52.9582 | 41.0243 | 41.0243 | 78.603 | 101.397 | 55.2814 | 271.35 | 271.35 | 97.9196 | 369.2696 | 0.4562 | 45.62% | 166.9837 | 76.1775 | 53.3243 | 186.9319 | 186.9319 | 28.53% | 11.5% | 11.5% | 85% | 9.772% | 16.3177 | 6.2762 | 6 | 97.9062 | 36.0851 | 52.38% | 52.38%
7 | 191 | 10 | 4570 | 10 | 14.7 | 461.25 | 121.17 | 582.42 | 121.17 | 60.59 | 191 | 4570 | 600 | 188.3836 | 22.0993 | -6.1167 | 574.284 | 9.4695 | 37.9582 | 50.7541 | 50.7541 | 64.2648 | 115.7352 | 42.1103 | 441.8441 | 441.8441 | 103.4251 | 545.2692 | 0.5718 | 57.18% | 246.5707 | 140.9894 | 98.6926 | 189.8443 | 189.8443 | 51.99% | 11.43% | 11.43% | 90% | 10.28% | 25.3564 | 6.0865 | 6 | 152.1385 | 56.0735 | 80.14% | 80.14%
7 | 191 | 10 | 4571 | 11 | 15.8 | 524.03 | 162.5 | 686.53 | 162.5 | 81.25 | 191 | 4571 | 660 | 188.3836 | 22.0993 | -6.1167 | 634.284 | 10.4695 | 22.9582 | 59.1378 | 59.1378 | 44.791 | 135.209 | 30.1852 | 527.6936 | 527.6936 | 138.7024 | 666.396 | 0.61774 | 61.77% | 301.3443 | 186.1538 | 130.3076 | 184.0114 | 184.0114 | 70.81% | 11.38% | 11.38% | 90% | 10.24% | 30.8714 | 5.833 | 5.833 | 180.0725 | 68.2694 | 97.86% | 97.86%
7 | 191 | 10 | 4572 | 12 | 16.8 | 578.39 | 187.72 | 766.11 | 187.72 | 93.86 | 191 | 4572 | 720 | 188.3836 | 22.0993 | -6.1167 | 694.284 | 11.4695 | 7.9582 | 64.4956 | 64.4956 | 17.3328 | 162.6672 | 21.7451 | 595.2368 | 595.2368 | 160.229 | 755.4658 | 0.64268 | 64.27% | 341.6217 | 219.5545 | 153.6882 | 171.8347 | 171.8347 | 89.44% | 11.36% | 11.36% | 90% | 10.22% | 34.9269 | 5.6099 | 5.6099 | 195.9357 | 77.2377 | 114% | 114%
7 | 191 | 10 | 4573 | 13 | 16.7 | 577.92 | 211.61 | 789.53 | 211.61 | 105.81 | 191 | 4573 | 780 | 188.3836 | 22.0993 | -6.1167 | 754.284 | 12.4695 | -7.0418 | 64.6725 | 64.6725 | 15.3979 | 195.3979 | 21.4441 | 595.1176 | 595.1176 | 180.6204 | 775.738 | 0.64661 | 64.66% | 350.7887 | 226.8233 | 158.7763 | 168.3628 | 168.3628 | 94.31% | 11.36% | 11.36% | 90% | 10.22% | 35.8533 | 5.6319 | 5.6319 | 201.9212 | 79.2863 | 119.9% | 119.9%
7 | 191 | 10 | 4574 | 14 | 18.2 | 413.61 | 261.44 | 675.05 | 261.44 | 130.72 | 191 | 4574 | 840 | 188.3836 | 22.0993 | -6.1167 | 814.284 | 13.4695 | -22.0418 | 59.5743 | 59.5743 | 43.3622 | 223.3622 | 29.5329 | 417.3445 | 417.3445 | 223.153 | 640.4975 | 0.61861 | 61.86% | 289.633 | 179.1702 | 125.4192 | 164.09 | 164.09 | 76.43% | 11.37% | 11.37% | 90% | 10.23% | 29.6324 | 5.3093 | 5.3093 | 157.3272 | 65.5294 | 95.88% | 95.88%
7 | 191 | 10 | 4575 | 15 | 18.1 | 500.83 | 197.42 | 698.25 | 197.42 | 98.71 | 191 | 4575 | 900 | 188.3836 | 22.0993 | -6.1167 | 874.284 | 14.4695 | -37.0418 | 51.317 | 51.317 | 63.254 | 243.254 | 41.334 | 481.7469 | 481.7469 | 168.5085 | 650.2554 | 0.62105 | 62.11% | 294.0455 | 182.6172 | 127.8321 | 161.0322 | 161.0322 | 79.38% | 11.37% | 11.37% | 90% | 10.23% | 30.0835 | 5.3303 | 5.3303 | 160.3543 | 66.5269 | 99.58% | 99.58%
7 | 191 | 10 | 4576 | 16 | 17.8 | 422.92 | 179.86 | 602.78 | 179.86 | 89.93 | 191 | 4576 | 960 | 188.3836 | 22.0993 | -6.1167 | 934.284 | 15.4695 | -52.0418 | 41.6386 | 41.6386 | 77.8225 | 257.8225 | 54.4583 | 370.0042 | 370.0042 | 153.5201 | 523.5243 | 0.57549 | 57.55% | 236.7377 | 136.2394 | 95.3676 | 153.8306 | 153.8306 | 62% | 11.39% | 11.39% | 90% | 10.25% | 24.2583 | 5.3938 | 5.3938 | 130.8439 | 53.6451 | 85.06% | 85.06%
7 | 191 | 10 | 4577 | 17 | 17.1 | 213 | 146.33 | 359.33 | 146.33 | 73.17 | 191 | 4577 | 1020 | 188.3836 | 22.0993 | -6.1167 | 994.284 | 16.4695 | -67.0418 | 31.4428 | 31.4428 | 89.6162 | 269.6162 | 68.1053 | 152.264 | 152.264 | 124.9005 | 277.1645 | 0.36673 | 36.67% | 125.3338 | 45.9632 | 32.1742 | 138.354 | 138.354 | 23.26% | 11.44% | 11.44% | 80% | 9.148% | 11.4659 | 5.5443 | 5.5443 | 63.5707 | 25.3559 | 45.95% | 45.95%
7 | 191 | 10 | 4578 | 18 | 16.4 | 152.92 | 105.42 | 258.34 | 105.42 | 52.71 | 191 | 4578 | 1080 | 188.3836 | 22.0993 | -6.1167 | 1054.284 | 17.4695 | -82.0418 | 21.2229 | 21.2229 | 100.1431 | 280.1431 | 81.9585 | 59.0942 | 59.0942 | 89.9816 | 149.0758 | -0.019527 | 0% | 67.4121 | 0 | 0 | 127.4455 | 127.4455 | 0% | 11.48% | 11.48% | 80% | 9.185% | 6.1916 | 5.6983 | 5.6983 | 35.2815 | 13.6922 | 27.68% | 27.68%
7 | 191 | 10 | 4579 | 19 | 16.1 | 108 | 92.83 | 200.83 | 92.83 | 46.42 | 191 | 4579 | 1140 | 188.3836 | 22.0993 | -6.1167 | 1114.284 | 18.4695 | -97.0418 | 11.3242 | 11.3242 | 110.3144 | 290.3144 | 95.8463 | -56.0239 | 0 | 79.2354 | 79.2354 | -0.75393 | 0% | 35.8302 | 0 | 0 | 119.1421 | 119.1421 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4580 | 20 | 14.5 | 40 | 55.92 | 95.92 | 55.92 | 27.96 | 191 | 4580 | 1200 | 188.3836 | 22.0993 | -6.1167 | 1174.284 | 19.4695 | -112.0418 | 2.0645 | 2.0645 | 120.754 | 300.754 | 109.6256 | 0 | 0 | 47.7307 | 47.7307 | -1.8581 | 0% | 21.5838 | 0 | 0 | 144.5689 | 144.5689 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4581 | 21 | 14 | 0 | 11.39 | 11.39 | 11.39 | 5.7 | 191 | 4581 | 1260 | 188.3836 | 22.0993 | -6.1167 | 1234.284 | 20.4695 | -127.0418 | -6.2048 | 0 | 123.3227 | 303.3227 | 112.8582 | 0 | 0 | 9.722 | 9.722 | -12.3831 | 0% | 4.3963 | 0 | 0 | -9.7019 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4582 | 22 | 13.9 | 0 | 0 | 0 | 0 | 0 | 191 | 4582 | 1320 | 188.3836 | 22.0993 | -6.1167 | 1294.284 | 21.4695 | -142.0418 | -13.07 | 0 | 123.3227 | 303.3227 | 112.8582 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3568 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4583 | 23 | 13.7 | 0 | 0 | 0 | 0 | 0 | 191 | 4583 | 1380 | 188.3836 | 22.0993 | -6.1167 | 1354.284 | 22.4695 | -157.0418 | -18.0657 | 0 | 123.3227 | 303.3227 | 112.8582 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8674 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
7 | 191 | 10 | 4584 | 24 | 13.2 | 0 | 0 | 0 | 0 | 0 | 191 | 4584 | 1440 | 188.3836 | 22.0993 | -6.1167 | 1414.284 | 23.4695 | -172.0418 | -20.7479 | 0 | 123.3227 | 303.3227 | 112.8582 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8352 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4585 | 1 | 13.8 | 0 | 0 | 0 | 0 | 0 | 192 | 4585 | 60 | 189.3699 | 21.9742 | -6.5042 | 34.284 | 0.463 | 173.055 | -20.9616 | 0 | 123.1204 | 56.8796 | 112.7284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.75 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4586 | 2 | 13.4 | 0 | 0 | 0 | 0 | 0 | 192 | 4586 | 120 | 189.3699 | 21.9742 | -6.5042 | 94.284 | 1.463 | 158.055 | -18.4445 | 0 | 123.1204 | 56.8796 | 112.7284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8254 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4587 | 3 | 13.1 | 0 | 0 | 0 | 0 | 0 | 192 | 4587 | 180 | 189.3699 | 21.9742 | -6.5042 | 154.284 | 2.463 | 143.055 | -13.585 | 0 | 123.1204 | 56.8796 | 112.7284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7485 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4588 | 4 | 13.1 | 0 | 0 | 0 | 0 | 0 | 192 | 4588 | 240 | 189.3699 | 21.9742 | -6.5042 | 214.284 | 3.463 | 128.055 | -6.8227 | 0 | 123.1204 | 56.8796 | 112.7284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7485 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4589 | 5 | 13 | 0 | 0 | 0 | 0 | 0 | 192 | 4589 | 300 | 189.3699 | 21.9742 | -6.5042 | 274.284 | 4.463 | 113.055 | 1.3734 | 1.3734 | 121.4024 | 58.5976 | 110.5718 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.8686 | 1.8686 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4590 | 6 | 13.8 | 1.94 | 11.81 | 13.75 | 11.81 | 5.91 | 192 | 4590 | 360 | 189.3699 | 21.9742 | -6.5042 | 334.284 | 5.463 | 98.055 | 10.5845 | 10.5845 | 110.9174 | 69.0826 | 96.7924 | -1.2491 | 0 | 10.0805 | 10.0805 | -11.9594 | 0% | 4.5584 | 0 | 0 | 14.0098 | 14.0098 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4591 | 7 | 14.1 | 43.75 | 54.17 | 97.92 | 54.17 | 27.09 | 192 | 4591 | 420 | 189.3699 | 21.9742 | -6.5042 | 394.284 | 6.463 | 83.055 | 20.4546 | 20.4546 | 100.7364 | 79.2636 | 82.895 | 15.4846 | 15.4846 | 46.237 | 61.7216 | -1.2694 | 0% | 27.9105 | 0 | 0 | 182.5208 | 182.5208 | 0% | 11.59% | 11.59% | 80% | 9.273% | 2.5882 | 6.2283 | 6 | 15.5293 | 5.7236 | 8.508% | 8.508%
7 | 192 | 11 | 4592 | 8 | 14.8 | 125.78 | 94.03 | 219.81 | 94.03 | 47.02 | 192 | 4592 | 480 | 189.3699 | 21.9742 | -6.5042 | 454.284 | 7.463 | 68.055 | 30.6646 | 30.6646 | 90.2472 | 89.7528 | 69.022 | 88.2928 | 88.2928 | 80.2596 | 168.5524 | 0.054181 | 5.418% | 76.2194 | 4.1296 | 2.8907 | 154.9398 | 154.9398 | 1.866% | 11.53% | 11.53% | 80% | 9.226% | 7.0321 | 6.0631 | 6 | 42.1924 | 15.5508 | 27.23% | 27.23%
7 | 192 | 11 | 4593 | 9 | 15 | 206.44 | 116.53 | 322.97 | 116.53 | 58.27 | 192 | 4593 | 540 | 189.3699 | 21.9742 | -6.5042 | 514.284 | 8.463 | 53.055 | 40.873 | 40.873 | 78.5651 | 101.4349 | 55.3387 | 179.4165 | 179.4165 | 99.4646 | 278.8811 | 0.35245 | 35.24% | 126.11 | 44.4469 | 31.1128 | 160.1461 | 160.1461 | 19.43% | 11.5% | 11.5% | 80% | 9.196% | 11.5974 | 6.0165 | 6 | 69.5843 | 25.6466 | 43.45% | 43.45%
7 | 192 | 11 | 4594 | 10 | 15.7 | 268.33 | 133 | 401.33 | 133 | 66.5 | 192 | 4594 | 600 | 189.3699 | 21.9742 | -6.5042 | 574.284 | 9.463 | 38.055 | 50.601 | 50.601 | 64.2393 | 115.7607 | 42.1429 | 257.4711 | 257.4711 | 113.5226 | 370.9937 | 0.46883 | 46.88% | 167.7633 | 78.6526 | 55.0568 | 160.9226 | 160.9226 | 34.21% | 11.45% | 11.45% | 85% | 9.735% | 16.3325 | 5.8557 | 5.8557 | 95.6378 | 36.1179 | 59.43% | 59.43%
7 | 192 | 11 | 4595 | 11 | 17.4 | 324.58 | 119.78 | 444.36 | 119.78 | 59.89 | 192 | 4595 | 660 | 189.3699 | 21.9742 | -6.5042 | 634.284 | 10.463 | 23.055 | 58.9843 | 58.9843 | 44.8135 | 135.1865 | 30.1763 | 327.4042 | 327.4042 | 102.2386 | 429.6428 | 0.52348 | 52.35% | 194.2845 | 101.7031 | 71.1922 | 156.9046 | 156.9046 | 45.37% | 11.4% | 11.4% | 85% | 9.694% | 18.8344 | 5.4794 | 5.4794 | 103.2006 | 41.6505 | 65.77% | 65.77%
7 | 192 | 11 | 4596 | 12 | 17.9 | 253.97 | 134.25 | 388.22 | 134.25 | 67.13 | 192 | 4596 | 720 | 189.3699 | 21.9742 | -6.5042 | 694.284 | 11.463 | 8.055 | 64.3539 | 64.3539 | 17.4716 | 162.5284 | 21.6631 | 261.8263 | 261.8263 | 114.5895 | 376.4158 | 0.48677 | 48.68% | 170.2152 | 82.8562 | 57.9994 | 143.5912 | 143.5912 | 40.39% | 11.4% | 11.4% | 85% | 9.691% | 16.4952 | 5.3726 | 5.3726 | 88.6213 | 36.4777 | 61.72% | 61.72%
7 | 192 | 11 | 4597 | 13 | 19.2 | 227.64 | 174.03 | 401.67 | 174.03 | 87.02 | 192 | 4597 | 780 | 189.3699 | 21.9742 | -6.5042 | 754.284 | 12.463 | -6.945 | 64.5673 | 64.5673 | 15.1356 | 195.1356 | 21.2963 | 234.8553 | 234.8553 | 148.5439 | 383.3992 | 0.50008 | 50.01% | 173.3731 | 86.7005 | 60.6903 | 143.9828 | 143.9828 | 42.15% | 11.37% | 11.37% | 85% | 9.665% | 16.7561 | 5.103 | 5.103 | 85.5065 | 37.0547 | 59.39% | 59.39%
7 | 192 | 11 | 4598 | 14 | 20.3 | 138.47 | 218.19 | 356.66 | 218.19 | 109.1 | 192 | 4598 | 840 | 189.3699 | 21.9742 | -6.5042 | 814.284 | 13.463 | -21.945 | 59.5119 | 59.5119 | 43.0846 | 223.0846 | 29.3835 | 140.0159 | 140.0159 | 186.2368 | 326.2527 | 0.45428 | 45.43% | 147.5315 | 67.0203 | 46.9142 | 142.9025 | 142.9025 | 32.83% | 11.34% | 11.34% | 85% | 9.643% | 14.2258 | 4.8842 | 4.8842 | 69.481 | 31.4591 | 48.62% | 48.62%
7 | 192 | 11 | 4599 | 15 | 21 | 182.72 | 195.28 | 378 | 195.28 | 97.64 | 192 | 4599 | 900 | 189.3699 | 21.9742 | -6.5042 | 874.284 | 14.463 | -36.945 | 51.2821 | 51.2821 | 63.0142 | 243.0142 | 41.2008 | 176.2026 | 176.2026 | 166.6819 | 342.8846 | 0.47572 | 47.57% | 155.0524 | 73.761 | 51.6327 | 142.3903 | 142.3903 | 36.26% | 11.33% | 11.33% | 85% | 9.628% | 14.9282 | 4.7493 | 4.7493 | 70.8984 | 33.0123 | 49.79% | 49.79%
7 | 192 | 11 | 4600 | 16 | 20.6 | 211.89 | 154.31 | 366.2 | 154.31 | 77.16 | 192 | 4600 | 960 | 189.3699 | 21.9742 | -6.5042 | 934.284 | 15.463 | -51.945 | 41.6169 | 41.6169 | 77.6186 | 257.6186 | 54.3402 | 185.9919 | 185.9919 | 131.7118 | 317.7037 | 0.44694 | 44.69% | 143.6656 | 64.2099 | 44.9469 | 139.1986 | 139.1986 | 32.29% | 11.34% | 11.34% | 85% | 9.636% | 13.8431 | 4.8259 | 4.8259 | 66.8062 | 30.6129 | 47.99% | 47.99%
7 | 192 | 11 | 4601 | 17 | 21.2 | 243 | 135 | 378 | 135 | 67.5 | 192 | 4601 | 1020 | 189.3699 | 21.9742 | -6.5042 | 994.284 | 16.463 | -66.945 | 31.4248 | 31.4248 | 89.437 | 269.437 | 68.0004 | 174.5905 | 174.5905 | 115.2297 | 289.8202 | 0.41712 | 41.71% | 131.0567 | 54.6662 | 38.2664 | 138.574 | 138.574 | 27.61% | 11.32% | 11.32% | 80% | 9.055% | 11.8667 | 4.7114 | 4.7114 | 55.909 | 26.2422 | 40.35% | 40.35%
7 | 192 | 11 | 4602 | 18 | 20.7 | 157.08 | 106.06 | 263.14 | 106.06 | 53.03 | 192 | 4602 | 1080 | 189.3699 | 21.9742 | -6.5042 | 1054.284 | 17.463 | -81.945 | 21.2024 | 21.2024 | 99.9794 | 279.9794 | 81.8658 | 61.4537 | 61.4537 | 90.5279 | 151.9816 | 0.059041 | 5.904% | 68.7261 | 4.0576 | 2.8403 | 128.9084 | 128.9084 | 2.203% | 11.33% | 11.33% | 80% | 9.062% | 6.2277 | 4.8067 | 4.8067 | 29.9346 | 13.772 | 23.22% | 23.22%
7 | 192 | 11 | 4603 | 19 | 20.8 | 100.69 | 85.06 | 185.75 | 85.06 | 42.53 | 192 | 4603 | 1140 | 189.3699 | 21.9742 | -6.5042 | 1114.284 | 18.463 | -96.945 | 11.2963 | 11.2963 | 110.16 | 290.16 | 95.7661 | -51.6433 | 0 | 72.6033 | 72.6033 | -0.75242 | 0% | 32.8312 | 0 | 0 | 121.4464 | 121.4464 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.7875 | 4.7875 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4604 | 20 | 19.2 | 43.19 | 48.83 | 92.02 | 48.83 | 24.42 | 192 | 4604 | 1200 | 189.3699 | 21.9742 | -6.5042 | 1174.284 | 19.463 | -111.945 | 2.025 | 2.025 | 120.6051 | 300.6051 | 109.5597 | 0 | 0 | 41.679 | 41.679 | -1.9917 | 0% | 18.8472 | 0 | 0 | 149.8368 | 149.8368 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4605 | 21 | 17.7 | 0 | 8.19 | 8.19 | 8.19 | 4.1 | 192 | 4605 | 1260 | 189.3699 | 21.9742 | -6.5042 | 1234.284 | 20.463 | -126.945 | -6.2598 | 0 | 123.1204 | 303.1204 | 112.7284 | 0 | 0 | 6.9906 | 6.9906 | -16.3412 | 0% | 3.1612 | 0 | 0 | -5.5416 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4606 | 22 | 17.3 | 0 | 0 | 0 | 0 | 0 | 192 | 4606 | 1320 | 189.3699 | 21.9742 | -6.5042 | 1294.284 | 21.463 | -141.945 | -13.1438 | 0 | 123.1204 | 303.1204 | 112.7284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0186 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4607 | 23 | 17.2 | 0 | 0 | 0 | 0 | 0 | 192 | 4607 | 1380 | 189.3699 | 21.9742 | -6.5042 | 1354.284 | 22.463 | -156.945 | -18.1604 | 0 | 123.1204 | 303.1204 | 112.7284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.6368 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
7 | 192 | 11 | 4608 | 24 | 17.2 | 0 | 0 | 0 | 0 | 0 | 192 | 4608 | 1440 | 189.3699 | 21.9742 | -6.5042 | 1414.284 | 23.463 | -171.945 | -20.8631 | 0 | 123.1204 | 303.1204 | 112.7284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.1026 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4609 | 1 | 16.7 | 0 | 0 | 0 | 0 | 0 | 193 | 4609 | 60 | 190.3562 | 21.8434 | -6.8849 | 34.284 | 0.45665 | 173.1502 | -21.0997 | 0 | 122.909 | 57.091 | 112.5926 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2376 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4610 | 2 | 16.8 | 0 | 0 | 0 | 0 | 0 | 193 | 4610 | 120 | 190.3562 | 21.8434 | -6.8849 | 94.284 | 1.4567 | 158.1502 | -18.5943 | 0 | 122.909 | 57.091 | 112.5926 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.6029 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4611 | 3 | 15.5 | 0 | 0 | 0 | 0 | 0 | 193 | 4611 | 180 | 190.3562 | 21.8434 | -6.8849 | 154.284 | 2.4567 | 143.1502 | -13.7409 | 0 | 122.909 | 57.091 | 112.5926 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1017 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4612 | 4 | 14.5 | 0 | 0 | 0 | 0 | 0 | 193 | 4612 | 240 | 190.3562 | 21.8434 | -6.8849 | 214.284 | 3.4567 | 128.1502 | -6.9806 | 0 | 122.909 | 57.091 | 112.5926 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6256 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4613 | 5 | 13.7 | 0 | 0 | 0 | 0 | 0 | 193 | 4613 | 300 | 190.3562 | 21.8434 | -6.8849 | 274.284 | 4.4567 | 113.1502 | 1.2162 | 1.2162 | 121.3886 | 58.6114 | 110.683 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.7637 | 2.7637 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4614 | 6 | 13.1 | 2.17 | 8.19 | 10.36 | 8.19 | 4.1 | 193 | 4614 | 360 | 190.3562 | 21.8434 | -6.8849 | 334.284 | 5.4567 | 98.1502 | 10.4288 | 10.4288 | 110.8907 | 69.1093 | 96.8911 | -1.4384 | 0 | 6.9906 | 6.9906 | -17.8301 | 0% | 3.1612 | 0 | 0 | 12.5724 | 12.5724 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4615 | 7 | 13.3 | 8.89 | 37.69 | 46.58 | 37.69 | 18.85 | 193 | 4615 | 420 | 190.3562 | 21.8434 | -6.8849 | 394.284 | 6.4567 | 83.1502 | 20.3005 | 20.3005 | 100.7 | 79.3 | 82.9812 | 3.1311 | 3.1311 | 32.1704 | 35.3015 | -2.873 | 0% | 15.9633 | 0 | 0 | 177.461 | 177.461 | 0% | 11.63% | 11.63% | 80% | 9.307% | 1.4857 | 6.4214 | 6 | 8.9143 | 3.2855 | 5.023% | 5.023%
7 | 193 | 12 | 4616 | 8 | 15.5 | 107.64 | 76.81 | 184.45 | 76.81 | 38.41 | 193 | 4616 | 480 | 190.3562 | 21.8434 | -6.8849 | 454.284 | 7.4567 | 68.1502 | 30.5112 | 30.5112 | 90.2042 | 89.7958 | 69.0943 | 75.6527 | 75.6527 | 65.5614 | 141.2141 | -0.079748 | 0% | 63.857 | 0 | 0 | 153.7292 | 153.7292 | 0% | 11.52% | 11.52% | 80% | 9.212% | 5.8825 | 5.9013 | 5.9013 | 34.7145 | 13.0087 | 22.58% | 22.58%
7 | 193 | 12 | 4617 | 9 | 18.9 | 184.11 | 108.11 | 292.22 | 108.11 | 54.06 | 193 | 4617 | 540 | 190.3562 | 21.8434 | -6.8849 | 514.284 | 8.4567 | 53.1502 | 40.7188 | 40.7188 | 78.5206 | 101.4794 | 55.3934 | 160.2874 | 160.2874 | 92.2777 | 252.565 | 0.34001 | 34% | 114.2099 | 38.8329 | 27.1831 | 164.2551 | 164.2551 | 16.55% | 11.39% | 11.39% | 80% | 9.108% | 10.4023 | 5.1642 | 5.1642 | 53.7193 | 23.0039 | 32.7% | 32.7%
7 | 193 | 12 | 4618 | 10 | 19.2 | 183.06 | 163.33 | 346.39 | 163.33 | 81.67 | 193 | 4618 | 600 | 190.3562 | 21.8434 | -6.8849 | 574.284 | 9.4567 | 38.1502 | 50.4446 | 50.4446 | 64.2063 | 115.7937 | 42.1725 | 175.9651 | 175.9651 | 139.4109 | 315.376 | 0.43453 | 43.45% | 142.613 | 61.9694 | 43.3786 | 163.8205 | 163.8205 | 26.48% | 11.37% | 11.37% | 85% | 9.667% | 13.7869 | 5.103 | 5.103 | 70.3544 | 30.4884 | 42.95% | 42.95%
7 | 193 | 12 | 4619 | 11 | 20.2 | 227 | 198.11 | 425.11 | 198.11 | 99.06 | 193 | 4619 | 660 | 190.3562 | 21.8434 | -6.8849 | 634.284 | 10.4567 | 23.1502 | 58.8266 | 58.8266 | 44.8277 | 135.1723 | 30.1634 | 229.3855 | 229.3855 | 169.0975 | 398.4829 | 0.51712 | 51.71% | 180.194 | 93.1816 | 65.2271 | 161.0303 | 161.0303 | 40.51% | 11.35% | 11.35% | 85% | 9.645% | 17.3805 | 4.9037 | 4.9037 | 85.2288 | 38.4355 | 52.93% | 52.93%
7 | 193 | 12 | 4620 | 12 | 21.7 | 43.06 | 241.86 | 284.92 | 241.86 | 120.93 | 193 | 4620 | 720 | 190.3562 | 21.8434 | -6.8849 | 694.284 | 11.4567 | 8.1502 | 64.2067 | 64.2067 | 17.603 | 162.397 | 21.5759 | 44.4738 | 44.4738 | 206.4404 | 250.9142 | 0.36148 | 36.15% | 113.4634 | 41.0145 | 28.7101 | 146.5693 | 146.5693 | 19.59% | 11.3% | 11.3% | 80% | 9.041% | 10.2577 | 4.6179 | 4.6179 | 47.3687 | 22.684 | 32.32% | 32.32%
7 | 193 | 12 | 4621 | 13 | 20.3 | 120.36 | 269.81 | 390.17 | 269.81 | 134.91 | 193 | 4621 | 780 | 190.3562 | 21.8434 | -6.8849 | 754.284 | 12.4567 | -6.8498 | 64.4557 | 64.4557 | 14.8761 | 194.8761 | 21.1436 | 124.4189 | 124.4189 | 230.2972 | 354.7162 | 0.48234 | 48.23% | 160.4027 | 77.3687 | 54.1581 | 147.4968 | 147.4968 | 36.72% | 11.34% | 11.34% | 85% | 9.643% | 15.4676 | 4.8842 | 4.8842 | 75.5459 | 34.2051 | 51.22% | 51.22%
7 | 193 | 12 | 4622 | 14 | 19.4 | 125.83 | 175.56 | 301.39 | 175.56 | 87.78 | 193 | 4622 | 840 | 190.3562 | 21.8434 | -6.8849 | 814.284 | 13.4567 | -21.8498 | 59.4432 | 59.4432 | 42.8048 | 222.8048 | 29.2315 | 127.5146 | 127.5146 | 149.8498 | 277.3644 | 0.38549 | 38.55% | 125.4242 | 48.3494 | 33.8446 | 141.1767 | 141.1767 | 23.97% | 11.37% | 11.37% | 80% | 9.095% | 11.4078 | 5.0626 | 5.0626 | 57.753 | 25.2274 | 40.91% | 40.91%
7 | 193 | 12 | 4623 | 15 | 19.2 | 213.81 | 121.58 | 335.39 | 121.58 | 60.79 | 193 | 4623 | 900 | 190.3562 | 21.8434 | -6.8849 | 874.284 | 14.4567 | -36.8498 | 51.2415 | 51.2415 | 62.7704 | 242.7704 | 41.0667 | 206.7233 | 206.7233 | 103.775 | 310.4983 | 0.42872 | 42.87% | 140.4073 | 60.196 | 42.1372 | 140.0457 | 140.0457 | 30.09% | 11.37% | 11.37% | 85% | 9.668% | 13.5739 | 5.103 | 5.103 | 69.2676 | 30.0174 | 49.46% | 49.46%
7 | 193 | 12 | 4624 | 16 | 19.7 | 293.89 | 154.11 | 448 | 154.11 | 77.06 | 193 | 4624 | 960 | 190.3562 | 21.8434 | -6.8849 | 934.284 | 15.4567 | -51.8498 | 41.5898 | 41.5898 | 77.4106 | 257.4106 | 54.2222 | 258.847 | 258.847 | 131.5411 | 390.3881 | 0.50835 | 50.83% | 176.5335 | 89.7407 | 62.8185 | 144.3313 | 144.3313 | 43.52% | 11.36% | 11.36% | 85% | 9.655% | 17.0442 | 5.0025 | 5.0025 | 85.2632 | 37.6918 | 59.07% | 59.07%
7 | 193 | 12 | 4625 | 17 | 19.7 | 342.36 | 148.67 | 491.03 | 148.67 | 74.34 | 193 | 4625 | 1020 | 190.3562 | 21.8434 | -6.8849 | 994.284 | 16.4567 | -66.8498 | 31.4017 | 31.4017 | 89.254 | 269.254 | 67.8962 | 247.2484 | 247.2484 | 126.8978 | 374.1462 | 0.49552 | 49.55% | 169.1889 | 83.8357 | 58.685 | 144.4524 | 144.4524 | 40.63% | 11.36% | 11.36% | 85% | 9.655% | 16.3355 | 5.0025 | 5.0025 | 81.7178 | 36.1245 | 56.57% | 56.57%
7 | 193 | 12 | 4626 | 18 | 20.8 | 155.42 | 92.56 | 247.98 | 92.56 | 46.28 | 193 | 4626 | 1080 | 190.3562 | 21.8434 | -6.8849 | 1054.284 | 17.4567 | -81.8498 | 21.1768 | 21.1768 | 99.8124 | 279.8124 | 81.7744 | 61.5539 | 61.5539 | 79.0049 | 140.5588 | 5.9032e-05 | 0.005903% | 63.5607 | 0.0037521 | 0.0026265 | 130.608 | 130.608 | 0.002011% | 11.32% | 11.32% | 80% | 9.058% | 5.7576 | 4.7875 | 4.7875 | 27.5643 | 12.7324 | 21.1% | 21.1%
7 | 193 | 12 | 4627 | 19 | 20.3 | 89.86 | 63.67 | 153.53 | 63.67 | 31.84 | 193 | 4627 | 1140 | 190.3562 | 21.8434 | -6.8849 | 1114.284 | 18.4567 | -96.8498 | 11.2633 | 11.2633 | 110.0026 | 290.0026 | 95.6877 | -45.5959 | 0 | 54.3457 | 54.3457 | -1.2955 | 0% | 24.5751 | 0 | 0 | 120.4336 | 120.4336 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.8842 | 4.8842 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4628 | 20 | 18.6 | 26.72 | 37.08 | 63.8 | 37.08 | 18.54 | 193 | 4628 | 1200 | 190.3562 | 21.8434 | -6.8849 | 1174.284 | 19.4567 | -111.8498 | 1.9802 | 1.9802 | 120.4536 | 300.4536 | 109.4961 | 0 | 0 | 31.6498 | 31.6498 | -2.9196 | 0% | 14.312 | 0 | 0 | 147.6635 | 147.6635 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4629 | 21 | 17.3 | 0 | 7.44 | 7.44 | 7.44 | 3.72 | 193 | 4629 | 1260 | 190.3562 | 21.8434 | -6.8849 | 1234.284 | 20.4567 | -126.8498 | -6.3203 | 0 | 122.909 | 302.909 | 112.5926 | 0 | 0 | 6.3504 | 6.3504 | -18.2103 | 0% | 2.8717 | 0 | 0 | -5.7594 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4630 | 22 | 16.5 | 0 | 0 | 0 | 0 | 0 | 193 | 4630 | 1320 | 190.3562 | 21.8434 | -6.8849 | 1294.284 | 21.4567 | -141.8498 | -13.2234 | 0 | 122.909 | 302.909 | 112.5926 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.9896 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4631 | 23 | 14.7 | 0 | 0 | 0 | 0 | 0 | 193 | 4631 | 1380 | 190.3562 | 21.8434 | -6.8849 | 1354.284 | 22.4567 | -156.8498 | -18.2609 | 0 | 122.909 | 302.909 | 112.5926 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2504 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
7 | 193 | 12 | 4632 | 24 | 13.8 | 0 | 0 | 0 | 0 | 0 | 193 | 4632 | 1440 | 190.3562 | 21.8434 | -6.8849 | 1414.284 | 23.4567 | -171.8498 | -20.9841 | 0 | 122.909 | 302.909 | 112.5926 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1396 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4633 | 1 | 13.9 | 0 | 0 | 0 | 0 | 0 | 194 | 4633 | 60 | 191.3425 | 21.7068 | -7.2586 | 34.284 | 0.45042 | 173.2436 | -21.2433 | 0 | 122.6887 | 57.3113 | 112.4508 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7522 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4634 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 194 | 4634 | 120 | 191.3425 | 21.7068 | -7.2586 | 94.284 | 1.4504 | 158.2436 | -18.7491 | 0 | 122.6887 | 57.3113 | 112.4508 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7713 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4635 | 3 | 14.1 | 0 | 0 | 0 | 0 | 0 | 194 | 4635 | 180 | 191.3425 | 21.7068 | -7.2586 | 154.284 | 2.4504 | 143.2436 | -13.9013 | 0 | 122.6887 | 57.3113 | 112.4508 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7904 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4636 | 4 | 14.2 | 0 | 0 | 0 | 0 | 0 | 194 | 4636 | 240 | 191.3425 | 21.7068 | -7.2586 | 214.284 | 3.4504 | 128.2436 | -7.1423 | 0 | 122.6887 | 57.3113 | 112.4508 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.638 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4637 | 5 | 14 | 0 | 0 | 0 | 0 | 0 | 194 | 4637 | 300 | 191.3425 | 21.7068 | -7.2586 | 274.284 | 4.4504 | 113.2436 | 1.0555 | 1.0555 | 121.37 | 58.63 | 110.7938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.4984 | 8.4984 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4638 | 6 | 13.9 | 4.11 | 12.5 | 16.61 | 12.5 | 6.25 | 194 | 4638 | 360 | 191.3425 | 21.7068 | -7.2586 | 334.284 | 5.4504 | 98.2436 | 10.2701 | 10.2701 | 110.8589 | 69.1411 | 96.9888 | -2.8049 | 0 | 10.6694 | 10.6694 | -11.2335 | 0% | 4.8247 | 0 | 0 | 24.1341 | 24.1341 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4639 | 7 | 14.5 | 54.22 | 51.61 | 105.83 | 51.61 | 25.81 | 194 | 4639 | 420 | 191.3425 | 21.7068 | -7.2586 | 394.284 | 6.4504 | 83.2436 | 20.1435 | 20.1435 | 100.6582 | 79.3418 | 83.0659 | 19.0081 | 19.0081 | 44.0519 | 63.06 | -1.211 | 0% | 28.5157 | 0 | 0 | 202.6377 | 202.6377 | 0% | 11.57% | 11.57% | 80% | 9.26% | 2.6405 | 6.1335 | 6 | 15.8432 | 5.8393 | 7.819% | 7.819%
7 | 194 | 13 | 4640 | 8 | 16 | 171.72 | 80.5 | 252.22 | 80.5 | 40.25 | 194 | 4640 | 480 | 191.3425 | 21.7068 | -7.2586 | 454.284 | 7.4504 | 68.2436 | 30.355 | 30.355 | 90.1553 | 89.8447 | 69.1645 | 120.8623 | 120.8623 | 68.711 | 189.5733 | 0.15165 | 15.16% | 85.725 | 13 | 9.1 | 180.9921 | 180.9921 | 5.028% | 11.49% | 11.49% | 80% | 9.189% | 7.8773 | 5.7878 | 5.7878 | 45.5923 | 17.42 | 25.19% | 25.19%
7 | 194 | 13 | 4641 | 9 | 17.4 | 351.33 | 93.28 | 444.61 | 93.28 | 46.64 | 194 | 4641 | 540 | 191.3425 | 21.7068 | -7.2586 | 514.284 | 8.4504 | 53.2436 | 40.5617 | 40.5617 | 78.4696 | 101.5304 | 55.4457 | 306.4431 | 306.4431 | 79.6195 | 386.0626 | 0.49181 | 49.18% | 174.5775 | 85.8587 | 60.1011 | 192.3885 | 192.3885 | 31.24% | 11.41% | 11.41% | 85% | 9.7% | 16.9332 | 5.4794 | 5.4794 | 92.7833 | 37.4462 | 48.23% | 48.23%
7 | 194 | 13 | 4642 | 10 | 19.1 | 486.67 | 99.67 | 586.34 | 99.67 | 49.84 | 194 | 4642 | 600 | 191.3425 | 21.7068 | -7.2586 | 574.284 | 9.4504 | 38.2436 | 50.2849 | 50.2849 | 64.1659 | 115.8341 | 42.1989 | 468.6935 | 468.6935 | 85.0737 | 553.7671 | 0.59318 | 59.32% | 250.4135 | 148.5409 | 103.9786 | 195.4475 | 195.4475 | 53.2% | 11.36% | 11.36% | 90% | 10.23% | 25.6117 | 5.1233 | 5.1233 | 131.2169 | 56.638 | 67.14% | 67.14%
7 | 194 | 13 | 4643 | 11 | 21.7 | 629.36 | 120.47 | 749.83 | 120.47 | 60.24 | 194 | 4643 | 660 | 191.3425 | 21.7068 | -7.2586 | 634.284 | 10.4504 | 23.2436 | 58.6648 | 58.6648 | 44.8337 | 135.1663 | 30.1466 | 637.1732 | 637.1732 | 102.8276 | 740.0008 | 0.65395 | 65.4% | 334.6284 | 218.8311 | 153.1818 | 193.576 | 193.576 | 79.13% | 11.35% | 11.35% | 90% | 10.21% | 34.1714 | 4.6179 | 4.6179 | 157.7993 | 75.567 | 81.52% | 81.52%
7 | 194 | 13 | 4644 | 12 | 23.6 | 535.28 | 173.25 | 708.53 | 173.25 | 86.63 | 194 | 4644 | 720 | 191.3425 | 21.7068 | -7.2586 | 694.284 | 11.4504 | 8.2436 | 64.0541 | 64.0541 | 17.7267 | 162.2733 | 21.4838 | 553.9202 | 553.9202 | 147.8781 | 701.7984 | 0.65165 | 65.16% | 317.3532 | 206.8024 | 144.7617 | 187.0934 | 187.0934 | 77.37% | 11.33% | 11.33% | 90% | 10.2% | 32.3678 | 4.2784 | 4.2784 | 138.4837 | 71.5785 | 74.02% | 74.02%
7 | 194 | 13 | 4645 | 13 | 25.4 | 448.61 | 170.42 | 619.03 | 170.42 | 85.21 | 194 | 4645 | 780 | 191.3425 | 21.7068 | -7.2586 | 754.284 | 12.4504 | -6.7564 | 64.3379 | 64.3379 | 14.6196 | 194.6196 | 20.9861 | 464.6878 | 464.6878 | 145.4626 | 610.1503 | 0.63508 | 63.51% | 275.91 | 175.2245 | 122.6572 | 212.7027 | 212.7027 | 57.67% | 11.3% | 11.3% | 90% | 10.17% | 28.0492 | 3.9802 | 3.9802 | 111.6407 | 62.0282 | 52.49% | 52.49%
7 | 194 | 13 | 4646 | 14 | 25.4 | 599.94 | 186.44 | 786.38 | 186.44 | 93.22 | 194 | 4646 | 840 | 191.3425 | 21.7068 | -7.2586 | 814.284 | 13.4504 | -21.7564 | 59.3683 | 59.3683 | 42.523 | 222.523 | 29.0769 | 609.3582 | 609.3582 | 159.1365 | 768.4947 | 0.66988 | 66.99% | 347.5133 | 232.7936 | 162.9555 | 217.0082 | 217.0082 | 75.09% | 11.34% | 11.34% | 90% | 10.21% | 35.4755 | 3.9802 | 3.9802 | 141.1988 | 78.4509 | 65.07% | 65.07%
7 | 194 | 13 | 4647 | 15 | 25.9 | 531.19 | 170.36 | 701.55 | 170.36 | 85.18 | 194 | 4647 | 900 | 191.3425 | 21.7068 | -7.2586 | 874.284 | 14.4504 | -36.7564 | 51.1951 | 51.1951 | 62.523 | 242.523 | 40.9317 | 514.9714 | 514.9714 | 145.4114 | 660.3827 | 0.64954 | 64.95% | 298.6251 | 193.968 | 135.7776 | 272.114 | 272.114 | 49.9% | 11.31% | 11.31% | 90% | 10.18% | 30.3882 | 3.9014 | 3.9014 | 118.555 | 67.2007 | 43.57% | 43.57%
7 | 194 | 13 | 4648 | 16 | 26.1 | 528.67 | 167.72 | 696.39 | 167.72 | 83.86 | 194 | 4648 | 960 | 191.3425 | 21.7068 | -7.2586 | 934.284 | 15.4504 | -51.7564 | 41.5574 | 41.5574 | 77.1987 | 257.1987 | 54.1044 | 467.2582 | 467.2582 | 143.158 | 610.4161 | 0.63759 | 63.76% | 276.0302 | 175.9935 | 123.1954 | 279.2447 | 279.2447 | 44.12% | 11.29% | 11.29% | 90% | 10.16% | 28.0434 | 3.8703 | 3.8703 | 108.5369 | 62.0156 | 38.87% | 38.87%
7 | 194 | 13 | 4649 | 17 | 25.8 | 306.61 | 173.11 | 479.72 | 173.11 | 86.56 | 194 | 4649 | 1020 | 191.3425 | 21.7068 | -7.2586 | 994.284 | 16.4504 | -66.7564 | 31.3735 | 31.3735 | 89.0674 | 269.0674 | 67.7929 | 222.5932 | 222.5932 | 147.7586 | 370.3518 | 0.528 | 52.8% | 167.4731 | 88.4258 | 61.8981 | 267.4723 | 267.4723 | 23.14% | 11.21% | 11.21% | 85% | 9.533% | 15.9647 | 3.917 | 3.917 | 62.5334 | 35.3045 | 23.38% | 23.38%
7 | 194 | 13 | 4650 | 18 | 25.7 | 233.11 | 151.25 | 384.36 | 151.25 | 75.63 | 194 | 4650 | 1080 | 191.3425 | 21.7068 | -7.2586 | 1054.284 | 17.4504 | -81.7564 | 21.1461 | 21.1461 | 99.642 | 279.642 | 81.6843 | 93.4559 | 93.4559 | 129.1 | 222.5559 | 0.34376 | 34.38% | 100.6398 | 34.5958 | 24.217 | 257.4777 | 257.4777 | 9.405% | 11.17% | 11.17% | 80% | 8.937% | 8.994 | 3.9327 | 3.9327 | 35.3703 | 19.8893 | 13.74% | 13.74%
7 | 194 | 13 | 4651 | 19 | 25.5 | 70.5 | 96.94 | 167.44 | 96.94 | 48.47 | 194 | 4651 | 1140 | 191.3425 | 21.7068 | -7.2586 | 1114.284 | 18.4504 | -96.7564 | 11.225 | 11.225 | 109.8423 | 289.8423 | 95.6112 | -35.4114 | 0 | 82.7435 | 82.7435 | -0.43905 | 0% | 37.4166 | 0 | 0 | 235.6933 | 235.6933 | 0% | 11.14% | 0% | 80% | 0% | 0 | 3.9643 | 3.9643 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4652 | 20 | 24.9 | 43.19 | 65.56 | 108.75 | 65.56 | 32.78 | 194 | 4652 | 1200 | 191.3425 | 21.7068 | -7.2586 | 1174.284 | 19.4504 | -111.7564 | 1.93 | 1.93 | 120.2997 | 300.2997 | 109.4349 | 0 | 0 | 55.959 | 55.959 | -1.0569 | 0% | 25.3046 | 0 | 0 | 255.2423 | 255.2423 | 0% | 11.15% | 0% | 80% | 0% | 0 | 4.0608 | 4.0608 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4653 | 21 | 23 | 0 | 10.5 | 10.5 | 10.5 | 5.25 | 194 | 4653 | 1260 | 191.3425 | 21.7068 | -7.2586 | 1234.284 | 20.4504 | -126.7564 | -6.3863 | 0 | 122.6887 | 302.6887 | 112.4508 | 0 | 0 | 8.9623 | 8.9623 | -11.2704 | 0% | 4.0528 | 0 | 0 | 0.14014 | 0.14014 | 0% | 11.22% | 0% | 80% | 0% | 0 | 4.3829 | 4.3829 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4654 | 22 | 19.8 | 0 | 0 | 0 | 0 | 0 | 194 | 4654 | 1320 | 191.3425 | 21.7068 | -7.2586 | 1294.284 | 21.4504 | -141.7564 | -13.3086 | 0 | 122.6887 | 302.6887 | 112.4508 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2464 | 0 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9826 | 4.9826 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4655 | 23 | 16.7 | 0 | 0 | 0 | 0 | 0 | 194 | 4655 | 1380 | 191.3425 | 21.7068 | -7.2586 | 1354.284 | 22.4504 | -156.7564 | -18.3671 | 0 | 122.6887 | 302.6887 | 112.4508 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1422 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
7 | 194 | 13 | 4656 | 24 | 15.3 | 0 | 0 | 0 | 0 | 0 | 194 | 4656 | 1440 | 191.3425 | 21.7068 | -7.2586 | 1414.284 | 23.4504 | -171.7564 | -21.1108 | 0 | 122.6887 | 302.6887 | 112.4508 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4472 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4657 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 195 | 4657 | 60 | 192.3288 | 21.5646 | -7.6248 | 34.284 | 0.44432 | 173.3352 | -21.3923 | 0 | 122.4596 | 57.5404 | 112.3032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.01 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4658 | 2 | 14.3 | 0 | 0 | 0 | 0 | 0 | 195 | 4658 | 120 | 192.3288 | 21.5646 | -7.6248 | 94.284 | 1.4443 | 158.3352 | -18.909 | 0 | 122.4596 | 57.5404 | 112.3032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3826 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4659 | 3 | 13.5 | 0 | 0 | 0 | 0 | 0 | 195 | 4659 | 180 | 192.3288 | 21.5646 | -7.6248 | 154.284 | 2.4443 | 143.3352 | -14.0662 | 0 | 122.4596 | 57.5404 | 112.3032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9076 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4660 | 4 | 13.6 | 0 | 0 | 0 | 0 | 0 | 195 | 4660 | 240 | 192.3288 | 21.5646 | -7.6248 | 214.284 | 3.4443 | 128.3352 | -7.308 | 0 | 122.4596 | 57.5404 | 112.3032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7552 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4661 | 5 | 13.4 | 0 | 0 | 0 | 0 | 0 | 195 | 4661 | 300 | 192.3288 | 21.5646 | -7.6248 | 274.284 | 4.4443 | 113.3352 | 0.89136 | 0.89136 | 121.3466 | 58.6534 | 110.9039 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.6509 | 3.6509 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4662 | 6 | 13.8 | 1.94 | 9.22 | 11.16 | 9.22 | 4.61 | 195 | 4662 | 360 | 192.3288 | 21.5646 | -7.6248 | 334.284 | 5.4443 | 98.3352 | 10.1083 | 10.1083 | 110.8221 | 69.1779 | 97.0854 | -1.3634 | 0 | 7.8698 | 7.8698 | -15.5448 | 0% | 3.5587 | 0 | 0 | 18.5756 | 18.5756 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4663 | 7 | 16.1 | 58.67 | 50.28 | 108.95 | 50.28 | 25.14 | 195 | 4663 | 420 | 192.3288 | 21.5646 | -7.6248 | 394.284 | 6.4443 | 83.3352 | 19.9837 | 19.9837 | 100.6111 | 79.3889 | 83.1489 | 20.4787 | 20.4787 | 42.9167 | 63.3954 | -1.1432 | 0% | 28.6674 | 0 | 0 | 197.7132 | 197.7132 | 0% | 11.51% | 11.51% | 80% | 9.208% | 2.6397 | 5.7653 | 5.7653 | 15.2187 | 5.8374 | 7.697% | 7.697%
7 | 195 | 14 | 4664 | 8 | 17.2 | 189.72 | 83.56 | 273.28 | 83.56 | 41.78 | 195 | 4664 | 480 | 192.3288 | 21.5646 | -7.6248 | 454.284 | 7.4443 | 68.3352 | 30.1961 | 30.1961 | 90.1006 | 89.8994 | 69.2327 | 133.7475 | 133.7475 | 71.3229 | 205.0704 | 0.21409 | 21.41% | 92.7328 | 19.8533 | 13.8973 | 175.7294 | 175.7294 | 7.908% | 11.44% | 11.44% | 80% | 9.155% | 8.4896 | 5.5226 | 5.5226 | 46.8846 | 18.774 | 26.68% | 26.68%
7 | 195 | 14 | 4665 | 9 | 21.8 | 279.44 | 125.83 | 405.27 | 125.83 | 62.92 | 195 | 4665 | 540 | 192.3288 | 21.5646 | -7.6248 | 514.284 | 8.4443 | 53.3352 | 40.4018 | 40.4018 | 78.412 | 101.588 | 55.4954 | 244.228 | 244.228 | 107.4026 | 351.6306 | 0.48885 | 48.88% | 159.0073 | 77.7303 | 54.4112 | 188.9596 | 188.9596 | 28.8% | 11.31% | 11.31% | 85% | 9.611% | 15.2829 | 4.5994 | 4.5994 | 70.2921 | 33.7969 | 37.2% | 37.2%
7 | 195 | 14 | 4666 | 10 | 23.5 | 386.11 | 162.22 | 548.33 | 162.22 | 81.11 | 195 | 4666 | 600 | 192.3288 | 21.5646 | -7.6248 | 574.284 | 9.4443 | 38.3352 | 50.1219 | 50.1219 | 64.1181 | 115.8819 | 42.2223 | 372.5923 | 372.5923 | 138.4634 | 511.0557 | 0.59436 | 59.44% | 231.0994 | 137.357 | 96.1499 | 201.8702 | 201.8702 | 47.63% | 11.3% | 11.3% | 90% | 10.17% | 23.4953 | 4.2957 | 4.2957 | 100.9281 | 51.9577 | 50% | 50%
7 | 195 | 14 | 4667 | 11 | 25.2 | 533.33 | 161.53 | 694.86 | 161.53 | 80.77 | 195 | 4667 | 660 | 192.3288 | 21.5646 | -7.6248 | 634.284 | 10.4443 | 23.3352 | 58.4991 | 58.4991 | 44.8314 | 135.1686 | 30.1258 | 541.0199 | 541.0199 | 137.8745 | 678.8944 | 0.65156 | 65.16% | 306.996 | 200.0251 | 140.0175 | 228.6509 | 228.6509 | 61.24% | 11.32% | 11.32% | 90% | 10.19% | 31.2695 | 4.0122 | 4.0122 | 125.4594 | 69.1497 | 54.87% | 54.87%
7 | 195 | 14 | 4668 | 12 | 26.2 | 508.33 | 213.06 | 721.39 | 213.06 | 106.53 | 195 | 4668 | 720 | 192.3288 | 21.5646 | -7.6248 | 694.284 | 11.4443 | 8.3352 | 63.8964 | 63.8964 | 17.8427 | 162.1573 | 21.3866 | 527.0903 | 527.0903 | 181.8581 | 708.9484 | 0.66102 | 66.1% | 320.5865 | 211.9125 | 148.3388 | 232.5857 | 232.5857 | 63.78% | 11.32% | 11.32% | 90% | 10.19% | 32.6641 | 3.8549 | 3.8549 | 125.9168 | 72.2337 | 54.14% | 54.14%
7 | 195 | 14 | 4669 | 13 | 27.5 | 516.33 | 221.25 | 737.58 | 221.25 | 110.63 | 195 | 4669 | 780 | 192.3288 | 21.5646 | -7.6248 | 754.284 | 12.4443 | -6.6648 | 64.2138 | 64.2138 | 14.3664 | 194.3664 | 20.8238 | 535.9729 | 535.9729 | 188.8487 | 724.8215 | 0.66793 | 66.79% | 327.7643 | 218.9234 | 153.2464 | 254.4264 | 254.4264 | 60.23% | 11.32% | 11.32% | 90% | 10.19% | 33.3955 | 3.6609 | 3.6609 | 122.2569 | 73.8513 | 48.05% | 48.05%
7 | 195 | 14 | 4670 | 14 | 29.1 | 472.86 | 226.47 | 699.33 | 226.47 | 113.24 | 195 | 4670 | 840 | 192.3288 | 21.5646 | -7.6248 | 814.284 | 13.4443 | -21.6648 | 59.2871 | 59.2871 | 42.2397 | 222.2397 | 28.92 | 481.4175 | 481.4175 | 193.3042 | 674.7217 | 0.66278 | 66.28% | 305.1091 | 202.2207 | 141.5545 | 287.3723 | 287.3723 | 49.26% | 11.29% | 11.29% | 90% | 10.16% | 31.0002 | 3.4383 | 3.4383 | 106.5885 | 68.5542 | 37.09% | 37.09%
7 | 195 | 14 | 4671 | 15 | 28.7 | 584.39 | 177.83 | 762.22 | 177.83 | 88.92 | 195 | 4671 | 900 | 192.3288 | 21.5646 | -7.6248 | 874.284 | 14.4443 | -36.6648 | 51.1429 | 51.1429 | 62.272 | 242.272 | 40.796 | 568.1254 | 568.1254 | 151.7874 | 719.9128 | 0.67049 | 67.05% | 325.5446 | 218.2742 | 152.7919 | 273.8637 | 273.8637 | 55.79% | 11.31% | 11.31% | 90% | 10.18% | 33.148 | 3.4923 | 3.4923 | 115.7618 | 73.3038 | 42.27% | 42.27%
7 | 195 | 14 | 4672 | 16 | 29.7 | 582.5 | 139.72 | 722.22 | 139.72 | 69.86 | 195 | 4672 | 960 | 192.3288 | 21.5646 | -7.6248 | 934.284 | 15.4443 | -51.6648 | 41.5195 | 41.5195 | 76.9831 | 256.9831 | 53.9868 | 516.6789 | 516.6789 | 119.2585 | 635.9374 | 0.65613 | 65.61% | 287.5709 | 188.6829 | 132.078 | 289.0229 | 289.0229 | 45.7% | 11.26% | 11.26% | 90% | 10.14% | 29.154 | 3.3595 | 3.3595 | 97.9422 | 64.4715 | 33.89% | 33.89%
7 | 195 | 14 | 4673 | 17 | 30.2 | 453.61 | 119.39 | 573 | 119.39 | 59.7 | 195 | 4673 | 1020 | 192.3288 | 21.5646 | -7.6248 | 994.284 | 16.4443 | -66.6648 | 31.3399 | 31.3399 | 88.8773 | 268.8773 | 67.6905 | 331.0712 | 331.0712 | 101.9057 | 432.977 | 0.5892 | 58.92% | 195.7922 | 115.3603 | 80.7522 | 289.0671 | 289.0671 | 27.94% | 11.15% | 11.15% | 85% | 9.474% | 18.5497 | 3.2957 | 3.2957 | 61.1343 | 41.021 | 21.15% | 21.15%
7 | 195 | 14 | 4674 | 18 | 29.6 | 281.72 | 111.67 | 393.39 | 111.67 | 55.84 | 195 | 4674 | 1080 | 192.3288 | 21.5646 | -7.6248 | 1054.284 | 17.4443 | -81.6648 | 21.1101 | 21.1101 | 99.4685 | 279.4685 | 81.5958 | 114.3239 | 114.3239 | 95.3163 | 209.6403 | 0.35444 | 35.44% | 94.7993 | 33.6009 | 23.5206 | 268.5745 | 268.5745 | 8.758% | 11.04% | 11.04% | 80% | 8.832% | 8.3729 | 3.3724 | 3.3724 | 28.2371 | 18.5159 | 10.51% | 10.51%
7 | 195 | 14 | 4675 | 19 | 28.3 | 133.89 | 104.86 | 238.75 | 104.86 | 52.43 | 195 | 4675 | 1140 | 192.3288 | 21.5646 | -7.6248 | 1114.284 | 18.4443 | -96.6648 | 11.1815 | 11.1815 | 109.6793 | 289.6793 | 95.5366 | -66.615 | 0 | 89.5036 | 89.5036 | -0.27921 | 0% | 40.4735 | 0 | 0 | 240.7671 | 240.7671 | 0% | 11.03% | 0% | 80% | 0% | 0 | 3.5474 | 3.5474 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4676 | 20 | 26.9 | 28 | 45.56 | 73.56 | 45.56 | 22.78 | 195 | 4676 | 1200 | 192.3288 | 21.5646 | -7.6248 | 1174.284 | 19.4443 | -111.6648 | 1.8745 | 1.8745 | 120.1435 | 300.1435 | 109.376 | 0 | 0 | 38.8879 | 38.8879 | -1.7647 | 0% | 17.5851 | 0 | 0 | 223.7994 | 223.7994 | 0% | 11.06% | 0% | 80% | 0% | 0 | 3.749 | 3.749 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4677 | 21 | 23.7 | 0 | 9.94 | 9.94 | 9.94 | 4.97 | 195 | 4677 | 1260 | 192.3288 | 21.5646 | -7.6248 | 1234.284 | 20.4443 | -126.6648 | -6.4579 | 0 | 122.4596 | 302.4596 | 112.3032 | 0 | 0 | 8.4843 | 8.4843 | -11.7728 | 0% | 3.8366 | 0 | 0 | -0.22164 | 0 | 0% | 11.19% | 0% | 80% | 0% | 0 | 4.2613 | 4.2613 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4678 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 195 | 4678 | 1320 | 192.3288 | 21.5646 | -7.6248 | 1294.284 | 21.4443 | -141.6648 | -13.3995 | 0 | 122.4596 | 302.4596 | 112.3032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.4247 | 0 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.5626 | 4.5626 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4679 | 23 | 20.2 | 0 | 0 | 0 | 0 | 0 | 195 | 4679 | 1380 | 192.3288 | 21.5646 | -7.6248 | 1354.284 | 22.4443 | -156.6648 | -18.4792 | 0 | 122.4596 | 302.4596 | 112.3032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.4737 | 0 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.9037 | 4.9037 | 0 | 0 | 0% | 0%
7 | 195 | 14 | 4680 | 24 | 20 | 0 | 0 | 0 | 0 | 0 | 195 | 4680 | 1440 | 192.3288 | 21.5646 | -7.6248 | 1414.284 | 23.4443 | -171.6648 | -21.2433 | 0 | 122.4596 | 302.4596 | 112.3032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.0843 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4681 | 1 | 18.3 | 0 | 0 | 0 | 0 | 0 | 196 | 4681 | 60 | 193.3151 | 21.4167 | -7.9833 | 34.284 | 0.43834 | 173.4248 | -21.5468 | 0 | 122.2217 | 57.7783 | 112.1497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.5852 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4682 | 2 | 17.8 | 0 | 0 | 0 | 0 | 0 | 196 | 4682 | 120 | 193.3151 | 21.4167 | -7.9833 | 94.284 | 1.4383 | 158.4248 | -19.0738 | 0 | 122.2217 | 57.7783 | 112.1497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9272 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4683 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 196 | 4683 | 180 | 193.3151 | 21.4167 | -7.9833 | 154.284 | 2.4383 | 143.4248 | -14.2355 | 0 | 122.2217 | 57.7783 | 112.1497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7264 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4684 | 4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 196 | 4684 | 240 | 193.3151 | 21.4167 | -7.9833 | 214.284 | 3.4383 | 128.4248 | -7.4775 | 0 | 122.2217 | 57.7783 | 112.1497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9644 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4685 | 5 | 17.7 | 0 | 0 | 0 | 0 | 0 | 196 | 4685 | 300 | 193.3151 | 21.4167 | -7.9833 | 274.284 | 4.4383 | 113.4248 | 0.72391 | 0.72391 | 121.3185 | 58.6815 | 111.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.606 | 6.606 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4686 | 6 | 17 | 2.08 | 8 | 10.08 | 8 | 4 | 196 | 4686 | 360 | 193.3151 | 21.4167 | -7.9833 | 334.284 | 5.4383 | 98.4248 | 9.9436 | 9.9436 | 110.7802 | 69.2198 | 97.1808 | 0 | 0 | 6.8284 | 6.8284 | -16.9777 | 0% | 3.0878 | 0 | 0 | 16.2181 | 16.2181 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4687 | 7 | 15.6 | 30.78 | 36.06 | 66.84 | 36.06 | 18.03 | 196 | 4687 | 420 | 193.3151 | 21.4167 | -7.9833 | 394.284 | 6.4383 | 83.4248 | 19.8213 | 19.8213 | 100.5585 | 79.4415 | 83.2304 | 10.7001 | 10.7001 | 30.7791 | 41.4793 | -2.1992 | 0% | 18.7569 | 0 | 0 | 179.4726 | 179.4726 | 0% | 11.54% | 11.54% | 80% | 9.228% | 1.731 | 5.8784 | 5.8784 | 10.1754 | 3.8279 | 5.67% | 5.67%
7 | 196 | 15 | 4688 | 8 | 16.1 | 105.69 | 59.72 | 165.41 | 59.72 | 29.86 | 196 | 4688 | 480 | 193.3151 | 21.4167 | -7.9833 | 454.284 | 7.4383 | 68.4248 | 30.0346 | 30.0346 | 90.04 | 89.96 | 69.2988 | 74.6438 | 74.6438 | 50.9742 | 125.618 | -0.17869 | 0% | 56.8045 | 0 | 0 | 150.8937 | 150.8937 | 0% | 11.5% | 11.5% | 80% | 9.197% | 5.2245 | 5.7653 | 5.7653 | 30.1208 | 11.5535 | 19.96% | 19.96%
7 | 196 | 15 | 4689 | 9 | 16.5 | 189.11 | 86.33 | 275.44 | 86.33 | 43.17 | 196 | 4689 | 540 | 193.3151 | 21.4167 | -7.9833 | 514.284 | 8.4383 | 53.4248 | 40.2392 | 40.2392 | 78.348 | 101.652 | 55.5426 | 165.6355 | 165.6355 | 73.6873 | 239.3227 | 0.29196 | 29.2% | 108.2217 | 31.5963 | 22.1174 | 157.2178 | 157.2178 | 14.07% | 11.46% | 11.46% | 80% | 9.168% | 9.9217 | 5.6761 | 5.6761 | 56.3164 | 21.941 | 35.82% | 35.82%
7 | 196 | 15 | 4690 | 10 | 18.4 | 265.83 | 133.61 | 399.44 | 133.61 | 66.81 | 196 | 4690 | 600 | 193.3151 | 21.4167 | -7.9833 | 574.284 | 9.4383 | 38.4248 | 49.9559 | 49.9559 | 64.0629 | 115.9371 | 42.2425 | 257.0648 | 257.0648 | 114.0433 | 371.1081 | 0.48524 | 48.52% | 167.8151 | 81.4298 | 57.0008 | 163.243 | 163.243 | 34.92% | 11.39% | 11.39% | 85% | 9.681% | 16.2466 | 5.2675 | 5.2675 | 85.5789 | 35.928 | 52.42% | 52.42%
7 | 196 | 15 | 4691 | 11 | 19.7 | 412.83 | 200.89 | 613.72 | 200.89 | 100.45 | 196 | 4691 | 660 | 193.3151 | 21.4167 | -7.9833 | 634.284 | 10.4383 | 23.4248 | 58.3293 | 58.3293 | 44.821 | 135.179 | 30.1012 | 419.6505 | 419.6505 | 171.4703 | 591.1208 | 0.60875 | 60.87% | 267.3048 | 162.7209 | 113.9046 | 167.4556 | 167.4556 | 68.02% | 11.36% | 11.36% | 90% | 10.22% | 27.3183 | 5.0025 | 5.0025 | 136.6591 | 60.412 | 81.61% | 81.61%
7 | 196 | 15 | 4692 | 12 | 17.9 | 448.11 | 129.39 | 577.5 | 129.39 | 64.7 | 196 | 4692 | 720 | 193.3151 | 21.4167 | -7.9833 | 694.284 | 11.4383 | 8.4248 | 63.7334 | 63.7334 | 17.951 | 162.049 | 21.2845 | 465.6221 | 465.6221 | 110.4413 | 576.0634 | 0.59672 | 59.67% | 260.4959 | 155.4419 | 108.8093 | 151.9753 | 151.9753 | 71.6% | 11.38% | 11.38% | 90% | 10.24% | 26.675 | 5.3726 | 5.3726 | 143.3128 | 58.9893 | 94.3% | 94.3%
7 | 196 | 15 | 4693 | 13 | 18.4 | 450.56 | 181.31 | 631.87 | 181.31 | 90.66 | 196 | 4693 | 780 | 193.3151 | 21.4167 | -7.9833 | 754.284 | 12.4383 | -6.5752 | 64.0834 | 64.0834 | 14.1169 | 194.1169 | 20.6568 | 468.7337 | 468.7337 | 154.7578 | 623.4914 | 0.61427 | 61.43% | 281.9428 | 173.1885 | 121.2319 | 153.9982 | 153.9982 | 78.72% | 11.37% | 11.37% | 90% | 10.23% | 28.8449 | 5.2675 | 5.2675 | 151.9402 | 63.788 | 98.66% | 98.66%
7 | 196 | 15 | 4694 | 14 | 19 | 424.72 | 193.42 | 618.14 | 193.42 | 96.71 | 196 | 4694 | 840 | 193.3151 | 21.4167 | -7.9833 | 814.284 | 13.4383 | -21.5752 | 59.1996 | 59.1996 | 41.9552 | 221.9552 | 28.7608 | 433.4621 | 433.4621 | 165.0943 | 598.5564 | 0.60859 | 60.86% | 270.6672 | 164.7248 | 115.3073 | 154.2751 | 154.2751 | 74.74% | 11.36% | 11.36% | 90% | 10.23% | 27.6805 | 5.1437 | 5.1437 | 142.3803 | 61.213 | 92.29% | 92.29%
7 | 196 | 15 | 4695 | 15 | 19.1 | 511.17 | 155 | 666.17 | 155 | 77.5 | 196 | 4695 | 900 | 193.3151 | 21.4167 | -7.9833 | 874.284 | 14.4383 | -36.5752 | 51.0849 | 51.0849 | 62.0178 | 242.0178 | 40.6597 | 498.369 | 498.369 | 132.3008 | 630.6697 | 0.61889 | 61.89% | 285.1889 | 176.5003 | 123.5502 | 155.054 | 155.054 | 79.68% | 11.36% | 11.36% | 90% | 10.22% | 29.1587 | 5.1233 | 5.1233 | 149.3891 | 64.4818 | 96.35% | 96.35%
7 | 196 | 15 | 4696 | 16 | 18.5 | 472.28 | 149.11 | 621.39 | 149.11 | 74.56 | 196 | 4696 | 960 | 193.3151 | 21.4167 | -7.9833 | 934.284 | 15.4383 | -51.5752 | 41.4761 | 41.4761 | 76.7639 | 256.7639 | 53.8696 | 420.4506 | 420.4506 | 127.2733 | 547.7239 | 0.58843 | 58.84% | 247.6808 | 145.7422 | 102.0196 | 151.5309 | 151.5309 | 67.33% | 11.37% | 11.37% | 90% | 10.24% | 25.3514 | 5.2467 | 5.2467 | 133.0108 | 56.0625 | 87.78% | 87.78%
7 | 196 | 15 | 4697 | 17 | 17.3 | 478.56 | 119.72 | 598.28 | 119.72 | 59.86 | 196 | 4697 | 1020 | 193.3151 | 21.4167 | -7.9833 | 994.284 | 16.4383 | -66.5752 | 31.3012 | 31.3012 | 88.6838 | 268.6838 | 67.5891 | 351.177 | 351.177 | 102.1874 | 453.3644 | 0.53766 | 53.77% | 205.0114 | 110.2264 | 77.1585 | 147.0362 | 147.0362 | 52.48% | 11.4% | 11.4% | 85% | 9.693% | 19.8717 | 5.501 | 5.501 | 109.3131 | 43.9444 | 74.34% | 74.34%
7 | 196 | 15 | 4698 | 18 | 16.4 | 279.78 | 109.94 | 389.72 | 109.94 | 54.97 | 196 | 4698 | 1080 | 193.3151 | 21.4167 | -7.9833 | 1054.284 | 17.4383 | -81.5752 | 21.069 | 21.069 | 99.292 | 279.292 | 81.5087 | 114.9176 | 114.9176 | 93.8397 | 208.7573 | 0.21591 | 21.59% | 94.4 | 20.382 | 14.2674 | 131.8457 | 131.8457 | 10.82% | 11.47% | 11.47% | 80% | 9.175% | 8.6614 | 5.6983 | 5.6983 | 49.3553 | 19.154 | 37.43% | 37.43%
7 | 196 | 15 | 4699 | 19 | 16.3 | 174.86 | 75.61 | 250.47 | 75.61 | 37.81 | 196 | 4699 | 1140 | 193.3151 | 21.4167 | -7.9833 | 1114.284 | 18.4383 | -96.5752 | 11.1327 | 11.1327 | 109.5135 | 289.5135 | 95.4639 | -86.2324 | 0 | 64.5372 | 64.5372 | -1.1018 | 0% | 29.1837 | 0 | 0 | 119.8371 | 119.8371 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4700 | 20 | 16.3 | 65.69 | 44.11 | 109.8 | 44.11 | 22.06 | 196 | 4700 | 1200 | 193.3151 | 21.4167 | -7.9833 | 1174.284 | 19.4383 | -111.5752 | 1.8136 | 1.8136 | 119.9849 | 299.9849 | 109.3195 | 0 | 0 | 37.6502 | 37.6502 | -2.4627 | 0% | 17.0254 | 0 | 0 | 146.6373 | 146.6373 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4701 | 21 | 16 | 0 | 8.56 | 8.56 | 8.56 | 4.28 | 196 | 4701 | 1260 | 193.3151 | 21.4167 | -7.9833 | 1234.284 | 20.4383 | -126.5752 | -6.535 | 0 | 122.2217 | 302.2217 | 112.1497 | 0 | 0 | 7.3064 | 7.3064 | -16.122 | 0% | 3.304 | 0 | 0 | -9.0815 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4702 | 22 | 15.7 | 0 | 0 | 0 | 0 | 0 | 196 | 4702 | 1320 | 193.3151 | 21.4167 | -7.9833 | 1294.284 | 21.4383 | -141.5752 | -13.4961 | 0 | 122.2217 | 302.2217 | 112.1497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8076 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4703 | 23 | 15.8 | 0 | 0 | 0 | 0 | 0 | 196 | 4703 | 1380 | 193.3151 | 21.4167 | -7.9833 | 1354.284 | 22.4383 | -156.5752 | -18.597 | 0 | 122.2217 | 302.2217 | 112.1497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2352 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
7 | 196 | 15 | 4704 | 24 | 15.4 | 0 | 0 | 0 | 0 | 0 | 196 | 4704 | 1440 | 193.3151 | 21.4167 | -7.9833 | 1414.284 | 23.4383 | -171.5752 | -21.3814 | 0 | 122.2217 | 302.2217 | 112.1497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4248 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4705 | 1 | 14.8 | 0 | 0 | 0 | 0 | 0 | 197 | 4705 | 60 | 194.3014 | 21.2632 | -8.3339 | 34.284 | 0.4325 | 173.5125 | -21.7066 | 0 | 121.9753 | 58.0247 | 111.9904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5617 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4706 | 2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 197 | 4706 | 120 | 194.3014 | 21.2632 | -8.3339 | 94.284 | 1.4325 | 158.5125 | -19.2435 | 0 | 121.9753 | 58.0247 | 111.9904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.969 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4707 | 3 | 13.6 | 0 | 0 | 0 | 0 | 0 | 197 | 4707 | 180 | 194.3014 | 21.2632 | -8.3339 | 154.284 | 2.4325 | 143.5125 | -14.409 | 0 | 121.9753 | 58.0247 | 111.9904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9002 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4708 | 4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 197 | 4708 | 240 | 194.3014 | 21.2632 | -8.3339 | 214.284 | 3.4325 | 128.5125 | -7.6508 | 0 | 121.9753 | 58.0247 | 111.9904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3574 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4709 | 5 | 13.2 | 0 | 0 | 0 | 0 | 0 | 197 | 4709 | 300 | 194.3014 | 21.2632 | -8.3339 | 274.284 | 4.4325 | 113.5125 | 0.55321 | 0.55321 | 121.2856 | 58.7144 | 111.1222 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.6406 | 9.6406 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4710 | 6 | 13.4 | 2.22 | 7.78 | 10 | 7.78 | 3.89 | 197 | 4710 | 360 | 194.3014 | 21.2632 | -8.3339 | 334.284 | 5.4325 | 98.5125 | 9.776 | 9.776 | 110.7333 | 69.2667 | 97.2749 | 0 | 0 | 6.6406 | 6.6406 | -18.7086 | 0% | 3.0029 | 0 | 0 | 23.7817 | 23.7817 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4711 | 7 | 13.6 | 52.64 | 38.06 | 90.7 | 38.06 | 19.03 | 197 | 4711 | 420 | 194.3014 | 21.2632 | -8.3339 | 394.284 | 6.4325 | 83.5125 | 19.6562 | 19.6562 | 100.5005 | 79.4995 | 83.31 | 18.2307 | 18.2307 | 32.4862 | 50.717 | -1.7419 | 0% | 22.9342 | 0 | 0 | 198.0385 | 198.0385 | 0% | 11.62% | 11.62% | 80% | 9.293% | 2.1312 | 6.3484 | 6 | 12.7871 | 4.7129 | 6.457% | 6.457%
7 | 197 | 16 | 4712 | 8 | 13.7 | 164.72 | 64.03 | 228.75 | 64.03 | 32.02 | 197 | 4712 | 480 | 194.3014 | 21.2632 | -8.3339 | 454.284 | 7.4325 | 68.5125 | 29.8705 | 29.8705 | 89.9736 | 90.0264 | 69.3627 | 116.5679 | 116.5679 | 54.653 | 171.2209 | 0.051232 | 5.123% | 77.4261 | 3.9667 | 2.7767 | 172.7062 | 172.7062 | 1.608% | 11.57% | 11.57% | 80% | 9.256% | 7.1665 | 6.3243 | 6 | 42.9989 | 15.848 | 24.9% | 24.9%
7 | 197 | 16 | 4713 | 9 | 13.8 | 280.22 | 72.72 | 352.94 | 72.72 | 36.36 | 197 | 4713 | 540 | 194.3014 | 21.2632 | -8.3339 | 514.284 | 8.4325 | 53.5125 | 40.0739 | 40.0739 | 78.2775 | 101.7225 | 55.5871 | 245.9972 | 245.9972 | 62.0704 | 308.0676 | 0.38636 | 38.64% | 139.3082 | 53.8231 | 37.6762 | 178.6887 | 178.6887 | 21.08% | 11.52% | 11.52% | 85% | 9.792% | 13.6408 | 6.3002 | 6 | 81.8445 | 30.1653 | 45.8% | 45.8%
7 | 197 | 16 | 4714 | 10 | 13.8 | 298.19 | 118.28 | 416.47 | 118.28 | 59.14 | 197 | 4714 | 600 | 194.3014 | 21.2632 | -8.3339 | 574.284 | 9.4325 | 38.5125 | 49.7867 | 49.7867 | 64.0006 | 115.9994 | 42.2595 | 288.998 | 288.998 | 100.9583 | 389.9563 | 0.47406 | 47.41% | 176.3382 | 83.5953 | 58.5167 | 176.3237 | 176.3237 | 33.19% | 11.49% | 11.49% | 85% | 9.768% | 17.2248 | 6.3002 | 6 | 103.3489 | 38.0911 | 58.61% | 58.61%
7 | 197 | 16 | 4715 | 11 | 14 | 324.94 | 140.83 | 465.77 | 140.83 | 70.42 | 197 | 4715 | 660 | 194.3014 | 21.2632 | -8.3339 | 634.284 | 10.4325 | 23.5125 | 58.1558 | 58.1558 | 44.8026 | 135.1974 | 30.0727 | 331.0238 | 331.0238 | 120.2059 | 451.2297 | 0.51988 | 51.99% | 204.0461 | 106.0789 | 74.2552 | 167.669 | 167.669 | 44.29% | 11.47% | 11.47% | 85% | 9.747% | 19.8884 | 6.2522 | 6 | 119.3306 | 43.9815 | 71.17% | 71.17%
7 | 197 | 16 | 4716 | 12 | 14.5 | 400.06 | 178.39 | 578.45 | 178.39 | 89.2 | 197 | 4716 | 720 | 194.3014 | 21.2632 | -8.3339 | 694.284 | 11.4325 | 8.5125 | 63.5654 | 63.5654 | 18.0515 | 161.9485 | 21.1774 | 416.6009 | 416.6009 | 152.2654 | 568.8663 | 0.58063 | 58.06% | 257.2414 | 149.363 | 104.5541 | 157.5921 | 157.5921 | 66.34% | 11.42% | 11.42% | 90% | 10.28% | 26.4437 | 6.1335 | 6 | 158.6622 | 58.4779 | 100.7% | 100.7%
7 | 197 | 16 | 4717 | 13 | 14.8 | 337.42 | 251.03 | 588.45 | 251.03 | 125.52 | 197 | 4717 | 780 | 194.3014 | 21.2632 | -8.3339 | 754.284 | 12.4325 | -6.4875 | 63.9469 | 63.9469 | 13.8713 | 193.8713 | 20.4851 | 351.8334 | 351.8334 | 214.2675 | 566.1009 | 0.58075 | 58.07% | 255.9908 | 148.6658 | 104.0661 | 155.0244 | 155.0244 | 67.13% | 11.42% | 11.42% | 90% | 10.28% | 26.3082 | 6.0631 | 6 | 157.8491 | 58.1782 | 101.8% | 101.8%
7 | 197 | 16 | 4718 | 14 | 14.6 | 379.86 | 142.28 | 522.14 | 142.28 | 71.14 | 197 | 4718 | 840 | 194.3014 | 21.2632 | -8.3339 | 814.284 | 13.4325 | -21.4875 | 59.1058 | 59.1058 | 41.6697 | 221.6697 | 28.5994 | 388.6562 | 388.6562 | 121.4436 | 510.0998 | 0.55535 | 55.53% | 230.6671 | 128.1001 | 89.6701 | 148.9354 | 148.9354 | 60.21% | 11.44% | 11.44% | 90% | 10.29% | 23.7455 | 6.1099 | 6 | 142.4733 | 52.5112 | 95.66% | 95.66%
7 | 197 | 16 | 4719 | 15 | 14.2 | 296.61 | 167.36 | 463.97 | 167.36 | 83.68 | 197 | 4719 | 900 | 194.3014 | 21.2632 | -8.3339 | 874.284 | 14.4325 | -36.4875 | 51.021 | 51.021 | 61.7607 | 241.7607 | 40.523 | 290.0355 | 290.0355 | 142.8507 | 432.8862 | 0.50889 | 50.89% | 195.7512 | 99.616 | 69.7312 | 142.9628 | 142.9628 | 48.78% | 11.47% | 11.47% | 85% | 9.749% | 19.0833 | 6.2045 | 6 | 114.4997 | 42.201 | 80.09% | 80.09%
7 | 197 | 16 | 4720 | 16 | 14.1 | 292.44 | 137.92 | 430.36 | 137.92 | 68.96 | 197 | 4720 | 960 | 194.3014 | 21.2632 | -8.3339 | 934.284 | 15.4325 | -51.4875 | 41.4273 | 41.4273 | 76.5413 | 256.5413 | 53.753 | 261.3247 | 261.3247 | 117.7221 | 379.0468 | 0.46637 | 46.64% | 171.405 | 79.9386 | 55.957 | 138.5725 | 138.5725 | 40.38% | 11.49% | 11.49% | 85% | 9.765% | 16.7382 | 6.2283 | 6 | 100.4293 | 37.0151 | 72.47% | 72.47%
7 | 197 | 16 | 4721 | 17 | 14.4 | 215.61 | 105.06 | 320.67 | 105.06 | 52.53 | 197 | 4721 | 1020 | 194.3014 | 21.2632 | -8.3339 | 994.284 | 16.4325 | -66.4875 | 31.2571 | 31.2571 | 88.487 | 268.487 | 67.4889 | 159.0913 | 159.0913 | 89.6743 | 248.7656 | 0.2923 | 29.23% | 112.4918 | 32.8814 | 23.017 | 131.09 | 131.09 | 17.56% | 11.52% | 11.52% | 80% | 9.217% | 10.3688 | 6.1571 | 6 | 62.2131 | 22.9298 | 47.46% | 47.46%
7 | 197 | 16 | 4722 | 18 | 14.2 | 150.5 | 111.94 | 262.44 | 111.94 | 55.97 | 197 | 4722 | 1080 | 194.3014 | 21.2632 | -8.3339 | 1054.284 | 17.4325 | -81.4875 | 21.0227 | 21.0227 | 99.1124 | 279.1124 | 81.4233 | 62.5655 | 62.5655 | 95.5468 | 158.1122 | -0.003962 | 0% | 71.4984 | 0 | 0 | 123.604 | 123.604 | 0% | 11.56% | 11.56% | 80% | 9.245% | 6.6103 | 6.2045 | 6 | 39.6619 | 14.6181 | 32.09% | 32.09%
7 | 197 | 16 | 4723 | 19 | 14.1 | 72.08 | 60.78 | 132.86 | 60.78 | 30.39 | 197 | 4723 | 1140 | 194.3014 | 21.2632 | -8.3339 | 1114.284 | 18.4325 | -96.4875 | 11.0787 | 11.0787 | 109.3451 | 289.3451 | 95.3933 | -35.2574 | 0 | 51.879 | 51.879 | -1.6628 | 0% | 23.4597 | 0 | 0 | 154.3683 | 154.3683 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4724 | 20 | 14.2 | 32.83 | 38.19 | 71.02 | 38.19 | 19.1 | 197 | 4724 | 1200 | 194.3014 | 21.2632 | -8.3339 | 1174.284 | 19.4325 | -111.4875 | 1.7474 | 1.7474 | 119.8241 | 299.8241 | 109.2655 | 0 | 0 | 32.5972 | 32.5972 | -3.115 | 0% | 14.7405 | 0 | 0 | 143.5387 | 143.5387 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4725 | 21 | 14 | 0 | 10.83 | 10.83 | 10.83 | 5.42 | 197 | 4725 | 1260 | 194.3014 | 21.2632 | -8.3339 | 1234.284 | 20.4325 | -126.4875 | -6.6176 | 0 | 121.9753 | 301.9753 | 111.9904 | 0 | 0 | 9.244 | 9.244 | -13.065 | 0% | 4.1801 | 0 | 0 | -8.7358 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4726 | 22 | 13.8 | 0 | 0 | 0 | 0 | 0 | 197 | 4726 | 1320 | 194.3014 | 21.2632 | -8.3339 | 1294.284 | 21.4325 | -141.4875 | -13.5983 | 0 | 121.9753 | 301.9753 | 111.9904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3212 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4727 | 23 | 13.6 | 0 | 0 | 0 | 0 | 0 | 197 | 4727 | 1380 | 194.3014 | 21.2632 | -8.3339 | 1354.284 | 22.4325 | -156.4875 | -18.7205 | 0 | 121.9753 | 301.9753 | 111.9904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8808 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
7 | 197 | 16 | 4728 | 24 | 13.1 | 0 | 0 | 0 | 0 | 0 | 197 | 4728 | 1440 | 194.3014 | 21.2632 | -8.3339 | 1414.284 | 23.4325 | -171.4875 | -21.5251 | 0 | 121.9753 | 301.9753 | 111.9904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8977 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4729 | 1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 198 | 4729 | 60 | 195.2877 | 21.1041 | -8.6761 | 34.284 | 0.4268 | 173.598 | -21.8717 | 0 | 121.7204 | 58.2796 | 111.8253 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0375 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4730 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 198 | 4730 | 120 | 195.2877 | 21.1041 | -8.6761 | 94.284 | 1.4268 | 158.598 | -19.418 | 0 | 121.7204 | 58.2796 | 111.8253 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0481 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4731 | 3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 198 | 4731 | 180 | 195.2877 | 21.1041 | -8.6761 | 154.284 | 2.4268 | 143.598 | -14.5869 | 0 | 121.7204 | 58.2796 | 111.8253 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2112 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4732 | 4 | 10.7 | 0 | 0 | 0 | 0 | 0 | 198 | 4732 | 240 | 195.2877 | 21.1041 | -8.6761 | 214.284 | 3.4268 | 128.598 | -7.8277 | 0 | 121.7204 | 58.2796 | 111.8253 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4304 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4733 | 5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 198 | 4733 | 300 | 195.2877 | 21.1041 | -8.6761 | 274.284 | 4.4268 | 113.598 | 0.37934 | 0.37934 | 121.2478 | 58.7522 | 111.2302 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.3271 | 1.3271 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4734 | 6 | 10.7 | 2.17 | 8 | 10.17 | 8 | 4 | 198 | 4734 | 360 | 195.2877 | 21.1041 | -8.6761 | 334.284 | 5.4268 | 98.598 | 9.6056 | 9.6056 | 110.6812 | 69.3188 | 97.3676 | 0 | 0 | 6.8284 | 6.8284 | -19.0844 | 0% | 3.0878 | 0 | 0 | 13.2044 | 13.2044 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4735 | 7 | 11.3 | 31.81 | 39.58 | 71.39 | 39.58 | 19.79 | 198 | 4735 | 420 | 195.2877 | 21.1041 | -8.6761 | 394.284 | 6.4268 | 83.598 | 19.4886 | 19.4886 | 100.4372 | 79.5628 | 83.3879 | 10.979 | 10.979 | 33.7836 | 44.7626 | -2.1988 | 0% | 20.2416 | 0 | 0 | 183.3846 | 183.3846 | 0% | 11.71% | 11.71% | 80% | 9.371% | 1.8968 | 6.9236 | 6 | 11.3807 | 4.1946 | 6.206% | 6.206%
7 | 198 | 17 | 4736 | 8 | 13.7 | 135.5 | 64.86 | 200.36 | 64.86 | 32.43 | 198 | 4736 | 480 | 195.2877 | 21.1041 | -8.6761 | 454.284 | 7.4268 | 68.598 | 29.704 | 29.704 | 89.9014 | 90.0986 | 69.4245 | 96.1019 | 96.1019 | 55.3615 | 151.4633 | -0.046963 | 0% | 68.4917 | 0 | 0 | 160.1976 | 160.1976 | 0% | 11.58% | 11.58% | 80% | 9.261% | 6.3433 | 6.3243 | 6 | 38.0597 | 14.0276 | 23.76% | 23.76%
7 | 198 | 17 | 4737 | 9 | 15.4 | 235.69 | 107.17 | 342.86 | 107.17 | 53.59 | 198 | 4737 | 540 | 195.2877 | 21.1041 | -8.6761 | 514.284 | 8.4268 | 53.598 | 39.906 | 39.906 | 78.2006 | 101.7994 | 55.6291 | 207.4076 | 207.4076 | 91.4753 | 298.8829 | 0.3857 | 38.57% | 135.1549 | 52.1287 | 36.4901 | 169.6703 | 169.6703 | 21.51% | 11.48% | 11.48% | 80% | 9.183% | 12.4113 | 5.9242 | 5.9242 | 73.5268 | 27.4465 | 43.34% | 43.34%
7 | 198 | 17 | 4738 | 10 | 15.8 | 311.89 | 144.67 | 456.56 | 144.67 | 72.34 | 198 | 4738 | 600 | 195.2877 | 21.1041 | -8.6761 | 574.284 | 9.4268 | 38.598 | 49.6146 | 49.6146 | 63.9309 | 116.0691 | 42.2735 | 302.9798 | 302.9798 | 123.4836 | 426.4634 | 0.51296 | 51.3% | 192.8467 | 98.9218 | 69.2452 | 171.3741 | 171.3741 | 40.41% | 11.44% | 11.44% | 85% | 9.723% | 18.7496 | 5.833 | 5.833 | 109.3661 | 41.4631 | 63.82% | 63.82%
7 | 198 | 17 | 4739 | 11 | 16.8 | 436.44 | 129.58 | 566.02 | 129.58 | 64.79 | 198 | 4739 | 660 | 195.2877 | 21.1041 | -8.6761 | 634.284 | 10.4268 | 23.598 | 57.9784 | 57.9784 | 44.776 | 135.224 | 30.0404 | 445.6155 | 445.6155 | 110.6034 | 556.2189 | 0.5849 | 58.49% | 251.5222 | 147.1145 | 102.9802 | 168.1117 | 168.1117 | 61.26% | 11.39% | 11.39% | 90% | 10.26% | 25.7946 | 5.6099 | 5.6099 | 144.7049 | 57.0426 | 86.08% | 86.08%
7 | 198 | 17 | 4740 | 12 | 17.9 | 434.64 | 136.03 | 570.67 | 136.03 | 68.02 | 198 | 4740 | 720 | 195.2877 | 21.1041 | -8.6761 | 694.284 | 11.4268 | 8.598 | 63.3924 | 63.3924 | 18.1442 | 161.8558 | 21.0655 | 453.6356 | 453.6356 | 116.1089 | 569.7445 | 0.59442 | 59.44% | 257.6385 | 153.1445 | 107.2012 | 156.4787 | 156.4787 | 68.51% | 11.38% | 11.38% | 90% | 10.24% | 26.3841 | 5.3726 | 5.3726 | 141.7499 | 58.346 | 90.59% | 90.59%
7 | 198 | 17 | 4741 | 13 | 18 | 371.25 | 113.33 | 484.58 | 113.33 | 56.67 | 198 | 4741 | 780 | 195.2877 | 21.1041 | -8.6761 | 754.284 | 12.4268 | -6.402 | 63.8042 | 63.8042 | 13.6298 | 193.6298 | 20.3089 | 388.0251 | 388.0251 | 96.7332 | 484.7583 | 0.55813 | 55.81% | 219.2077 | 122.3469 | 85.6429 | 150.1335 | 150.1335 | 57.04% | 11.39% | 11.39% | 85% | 9.679% | 21.2164 | 5.3514 | 5.3514 | 113.5374 | 46.9182 | 75.62% | 75.62%
7 | 198 | 17 | 4742 | 14 | 18.8 | 325 | 180.5 | 505.5 | 180.5 | 90.25 | 198 | 4742 | 840 | 195.2877 | 21.1041 | -8.6761 | 814.284 | 13.4268 | -21.402 | 59.0057 | 59.0057 | 41.3836 | 221.3836 | 28.436 | 333.3904 | 333.3904 | 154.0664 | 487.4568 | 0.56314 | 56.31% | 220.428 | 124.132 | 86.8924 | 151.2243 | 151.2243 | 57.46% | 11.37% | 11.37% | 85% | 9.667% | 21.3082 | 5.1847 | 5.1847 | 110.4761 | 47.1212 | 73.05% | 73.05%
7 | 198 | 17 | 4743 | 15 | 19.6 | 320.22 | 206.44 | 526.66 | 206.44 | 103.22 | 198 | 4743 | 900 | 195.2877 | 21.1041 | -8.6761 | 874.284 | 14.4268 | -36.402 | 50.9512 | 50.9512 | 61.5007 | 241.5007 | 40.3858 | 314.0718 | 314.0718 | 176.2076 | 490.2793 | 0.56814 | 56.81% | 221.7043 | 125.9583 | 88.1708 | 151.0739 | 151.0739 | 58.36% | 11.36% | 11.36% | 85% | 9.655% | 21.4055 | 5.0224 | 5.0224 | 107.508 | 47.3364 | 71.16% | 71.16%
7 | 198 | 17 | 4744 | 16 | 18.9 | 206.53 | 221.06 | 427.59 | 221.06 | 110.53 | 198 | 4744 | 960 | 195.2877 | 21.1041 | -8.6761 | 934.284 | 15.4268 | -51.402 | 41.3729 | 41.3729 | 76.3155 | 256.3155 | 53.6369 | 185.2645 | 185.2645 | 188.6865 | 373.951 | 0.49063 | 49.06% | 169.1006 | 82.9651 | 58.0756 | 143.7225 | 143.7225 | 40.41% | 11.38% | 11.38% | 85% | 9.671% | 16.3539 | 5.1642 | 5.1642 | 84.4541 | 36.1652 | 58.76% | 58.76%
7 | 198 | 17 | 4745 | 17 | 19.7 | 126.17 | 142.44 | 268.61 | 142.44 | 71.22 | 198 | 4745 | 1020 | 195.2877 | 21.1041 | -8.6761 | 994.284 | 16.4268 | -66.402 | 31.2077 | 31.2077 | 88.2871 | 268.2871 | 67.3898 | 93.6177 | 93.6177 | 121.5801 | 215.1978 | 0.26766 | 26.77% | 97.3125 | 26.047 | 18.2329 | 134.7239 | 134.7239 | 13.53% | 11.36% | 11.36% | 80% | 9.089% | 8.845 | 5.0025 | 5.0025 | 44.2471 | 19.56 | 32.84% | 32.84%
7 | 198 | 17 | 4746 | 18 | 20.4 | 157.69 | 123.14 | 280.83 | 123.14 | 61.57 | 198 | 4746 | 1080 | 195.2877 | 21.1041 | -8.6761 | 1054.284 | 17.4268 | -81.402 | 20.9711 | 20.9711 | 98.9301 | 278.9301 | 81.3396 | 66.3452 | 66.3452 | 105.1066 | 171.4517 | 0.1398 | 13.98% | 77.5305 | 10.8388 | 7.5872 | 132.1773 | 132.1773 | 5.74% | 11.34% | 11.34% | 80% | 9.071% | 7.0324 | 4.8647 | 4.8647 | 34.2105 | 15.5516 | 25.88% | 25.88%
7 | 198 | 17 | 4747 | 19 | 19.7 | 130.56 | 77.78 | 208.34 | 77.78 | 38.89 | 198 | 4747 | 1140 | 195.2877 | 21.1041 | -8.6761 | 1114.284 | 18.4268 | -96.402 | 11.0194 | 11.0194 | 109.1742 | 289.1742 | 95.3249 | -63.389 | 0 | 66.3894 | 66.3894 | -0.93451 | 0% | 30.0213 | 0 | 0 | 123.4183 | 123.4183 | 0% | 11.36% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4748 | 20 | 18.5 | 44.31 | 41.39 | 85.7 | 41.39 | 20.7 | 198 | 4748 | 1200 | 195.2877 | 21.1041 | -8.6761 | 1174.284 | 19.4268 | -111.402 | 1.6757 | 1.6757 | 119.6611 | 299.6611 | 109.214 | 0 | 0 | 35.3286 | 35.3286 | -2.5382 | 0% | 15.9756 | 0 | 0 | 149.733 | 149.733 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4749 | 21 | 16.8 | 0 | 7.64 | 7.64 | 7.64 | 3.82 | 198 | 4749 | 1260 | 195.2877 | 21.1041 | -8.6761 | 1234.284 | 20.4268 | -126.402 | -6.7056 | 0 | 121.7204 | 301.7204 | 111.8253 | 0 | 0 | 6.5211 | 6.5211 | -17.8843 | 0% | 2.9489 | 0 | 0 | -6.0655 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4750 | 22 | 15.8 | 0 | 0 | 0 | 0 | 0 | 198 | 4750 | 1320 | 195.2877 | 21.1041 | -8.6761 | 1294.284 | 21.4268 | -141.402 | -13.7061 | 0 | 121.7204 | 301.7204 | 111.8253 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6528 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4751 | 23 | 14.2 | 0 | 0 | 0 | 0 | 0 | 198 | 4751 | 1380 | 195.2877 | 21.1041 | -8.6761 | 1354.284 | 22.4268 | -156.402 | -18.8497 | 0 | 121.7204 | 301.7204 | 111.8253 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4922 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
7 | 198 | 17 | 4752 | 24 | 15.1 | 0 | 0 | 0 | 0 | 0 | 198 | 4752 | 1440 | 195.2877 | 21.1041 | -8.6761 | 1414.284 | 23.4268 | -171.402 | -21.6745 | 0 | 121.7204 | 301.7204 | 111.8253 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5217 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4753 | 1 | 14.3 | 0 | 0 | 0 | 0 | 0 | 199 | 4753 | 60 | 196.274 | 20.9396 | -9.0097 | 34.284 | 0.42124 | 173.6814 | -22.042 | 0 | 121.4571 | 58.5429 | 111.6546 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2794 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4754 | 2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 199 | 4754 | 120 | 196.274 | 20.9396 | -9.0097 | 94.284 | 1.4212 | 158.6814 | -19.5972 | 0 | 121.4571 | 58.5429 | 111.6546 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5785 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4755 | 3 | 12.4 | 0 | 0 | 0 | 0 | 0 | 199 | 4755 | 180 | 196.274 | 20.9396 | -9.0097 | 154.284 | 2.4212 | 143.6814 | -14.7689 | 0 | 121.4571 | 58.5429 | 111.6546 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6396 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4756 | 4 | 12.2 | 0 | 0 | 0 | 0 | 0 | 199 | 4756 | 240 | 196.274 | 20.9396 | -9.0097 | 214.284 | 3.4212 | 128.6814 | -8.0082 | 0 | 121.4571 | 58.5429 | 111.6546 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9444 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4757 | 5 | 11.4 | 0 | 0 | 0 | 0 | 0 | 199 | 4757 | 300 | 196.274 | 20.9396 | -9.0097 | 274.284 | 4.4212 | 113.6814 | 0.20237 | 0.20237 | 121.2052 | 58.7948 | 111.3372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.1033 | 4.1033 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4758 | 6 | 11.1 | 2.28 | 11.06 | 13.34 | 11.06 | 5.53 | 199 | 4758 | 360 | 196.274 | 20.9396 | -9.0097 | 334.284 | 5.4212 | 98.6814 | 9.4325 | 9.4325 | 110.6241 | 69.3759 | 97.4589 | 0 | 0 | 9.4403 | 9.4403 | -13.4834 | 0% | 4.2689 | 0 | 0 | 18.3263 | 18.3263 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4759 | 7 | 12.2 | 58.61 | 48.67 | 107.28 | 48.67 | 24.34 | 199 | 4759 | 420 | 196.274 | 20.9396 | -9.0097 | 394.284 | 6.4212 | 83.6814 | 19.3185 | 19.3185 | 100.3685 | 79.6315 | 83.464 | 20.1663 | 20.1663 | 41.5424 | 61.7087 | -1.3405 | 0% | 27.9047 | 0 | 0 | 196.6514 | 196.6514 | 0% | 11.67% | 11.67% | 80% | 9.335% | 2.6049 | 6.6941 | 6 | 15.6294 | 5.7605 | 7.948% | 7.948%
7 | 199 | 18 | 4760 | 8 | 14.2 | 182.72 | 78.19 | 260.91 | 78.19 | 39.1 | 199 | 4760 | 480 | 196.274 | 20.9396 | -9.0097 | 454.284 | 7.4212 | 68.6814 | 29.5351 | 29.5351 | 89.8235 | 90.1765 | 69.484 | 129.9052 | 129.9052 | 66.7393 | 196.6446 | 0.15436 | 15.44% | 88.9227 | 13.7259 | 9.6081 | 175.6728 | 175.6728 | 5.469% | 11.54% | 11.54% | 80% | 9.236% | 8.2125 | 6.2045 | 6 | 49.2751 | 18.1613 | 28.05% | 28.05%
7 | 199 | 18 | 4761 | 9 | 16.2 | 325.06 | 96.61 | 421.67 | 96.61 | 48.31 | 199 | 4761 | 540 | 196.274 | 20.9396 | -9.0097 | 514.284 | 8.4212 | 53.6814 | 39.7356 | 39.7356 | 78.1173 | 101.8827 | 55.6684 | 286.7875 | 286.7875 | 82.4618 | 369.2493 | 0.4703 | 47.03% | 166.9745 | 78.5283 | 54.9698 | 186.4336 | 186.4336 | 29.48% | 11.44% | 11.44% | 85% | 9.726% | 16.2395 | 5.7429 | 5.7429 | 93.2617 | 35.9122 | 50.02% | 50.02%
7 | 199 | 18 | 4762 | 10 | 19 | 473.89 | 106.25 | 580.14 | 106.25 | 53.13 | 199 | 4762 | 600 | 196.274 | 20.9396 | -9.0097 | 574.284 | 9.4212 | 38.6814 | 49.4395 | 49.4395 | 63.8542 | 116.1458 | 42.2843 | 461.4742 | 461.4742 | 90.69 | 552.1643 | 0.59217 | 59.22% | 249.6887 | 147.858 | 103.5006 | 192.8324 | 192.8324 | 53.67% | 11.37% | 11.37% | 90% | 10.23% | 25.5408 | 5.1437 | 5.1437 | 131.3743 | 56.4813 | 68.13% | 68.13%
7 | 199 | 18 | 4763 | 11 | 20.7 | 590.61 | 135.61 | 726.22 | 135.61 | 67.81 | 199 | 4763 | 660 | 196.274 | 20.9396 | -9.0097 | 634.284 | 10.4212 | 23.6814 | 57.7973 | 57.7973 | 44.7416 | 135.2584 | 30.0042 | 604.4441 | 604.4441 | 115.7504 | 720.1945 | 0.64679 | 64.68% | 325.672 | 210.6421 | 147.4495 | 189.9025 | 189.9025 | 77.64% | 11.35% | 11.35% | 90% | 10.21% | 33.2642 | 4.8067 | 4.8067 | 159.8904 | 73.5609 | 84.2% | 84.2%
7 | 199 | 18 | 4764 | 12 | 21.5 | 658 | 143.19 | 801.19 | 143.19 | 71.6 | 199 | 4764 | 720 | 196.274 | 20.9396 | -9.0097 | 694.284 | 11.4212 | 8.6814 | 63.2144 | 63.2144 | 18.2291 | 161.7709 | 20.9487 | 688.3696 | 688.3696 | 122.2203 | 810.5899 | 0.66648 | 66.65% | 366.5488 | 244.298 | 171.0086 | 177.2864 | 177.2864 | 96.46% | 11.35% | 11.35% | 95% | 10.79% | 39.5331 | 4.6551 | 4.6551 | 184.0297 | 87.424 | 103.8% | 103.8%
7 | 199 | 18 | 4765 | 13 | 22.4 | 727.78 | 125.83 | 853.61 | 125.83 | 62.92 | 199 | 4765 | 780 | 196.274 | 20.9396 | -9.0097 | 754.284 | 12.4212 | -6.3186 | 63.6555 | 63.6555 | 13.3928 | 193.3928 | 20.1281 | 762.526 | 762.526 | 107.4026 | 869.9286 | 0.67811 | 67.81% | 393.3817 | 266.7568 | 186.7298 | 176.2627 | 176.2627 | 105.9% | 11.36% | 11.36% | 95% | 10.79% | 42.4584 | 4.4899 | 4.4899 | 190.6329 | 93.8929 | 108.2% | 108.2%
7 | 199 | 18 | 4766 | 14 | 22.4 | 535.36 | 137.86 | 673.22 | 137.86 | 68.93 | 199 | 4766 | 840 | 196.274 | 20.9396 | -9.0097 | 814.284 | 13.4212 | -21.3186 | 58.8994 | 58.8994 | 41.0972 | 221.0972 | 28.2707 | 550.652 | 550.652 | 117.6709 | 668.3229 | 0.64014 | 64.01% | 302.2156 | 193.4593 | 135.4215 | 166.9932 | 166.9932 | 81.09% | 11.33% | 11.33% | 90% | 10.2% | 30.8295 | 4.4899 | 4.4899 | 138.4207 | 68.1767 | 82.89% | 82.89%
7 | 199 | 18 | 4767 | 15 | 22.5 | 528.28 | 140.61 | 668.89 | 140.61 | 70.31 | 199 | 4767 | 900 | 196.274 | 20.9396 | -9.0097 | 874.284 | 14.4212 | -36.3186 | 50.8755 | 50.8755 | 61.2382 | 241.2382 | 40.2485 | 519.7499 | 519.7499 | 120.0181 | 639.7681 | 0.63316 | 63.32% | 289.3031 | 183.1757 | 128.223 | 163.8229 | 163.8229 | 78.27% | 11.33% | 11.33% | 90% | 10.2% | 29.5002 | 4.4719 | 4.4719 | 131.921 | 65.237 | 80.53% | 80.53%
7 | 199 | 18 | 4768 | 16 | 23 | 449.22 | 160.28 | 609.5 | 160.28 | 80.14 | 199 | 4768 | 960 | 196.274 | 20.9396 | -9.0097 | 934.284 | 15.4212 | -51.3186 | 41.3129 | 41.3129 | 76.0866 | 256.0866 | 53.5215 | 404.5482 | 404.5482 | 136.8075 | 541.3557 | 0.6041 | 60.41% | 244.8011 | 147.8853 | 103.5197 | 159.7588 | 159.7588 | 64.8% | 11.31% | 11.31% | 90% | 10.18% | 24.9168 | 4.3829 | 4.3829 | 109.2079 | 55.1013 | 68.36% | 68.36%
7 | 199 | 18 | 4769 | 17 | 23.1 | 352.78 | 151.39 | 504.17 | 151.39 | 75.7 | 199 | 4769 | 1020 | 196.274 | 20.9396 | -9.0097 | 994.284 | 16.4212 | -66.3186 | 31.1529 | 31.1529 | 88.0842 | 268.0842 | 67.2921 | 263.2486 | 263.2486 | 129.2194 | 392.4681 | 0.52882 | 52.88% | 177.4741 | 93.8521 | 65.6965 | 153.7877 | 153.7877 | 42.72% | 11.28% | 11.28% | 85% | 9.59% | 17.02 | 4.3653 | 4.3653 | 74.2977 | 37.6382 | 48.31% | 48.31%
7 | 199 | 18 | 4770 | 18 | 23.1 | 222.56 | 89.86 | 312.42 | 89.86 | 44.93 | 199 | 4770 | 1080 | 196.274 | 20.9396 | -9.0097 | 1054.284 | 17.4212 | -81.3186 | 20.9142 | 20.9142 | 98.7449 | 278.7449 | 81.2576 | 94.763 | 94.763 | 76.7003 | 171.4633 | 0.17413 | 17.41% | 77.5357 | 13.5017 | 9.4512 | 236.3463 | 236.3463 | 3.999% | 11.24% | 11.24% | 80% | 8.996% | 6.975 | 4.3653 | 4.3653 | 30.4481 | 15.4246 | 12.88% | 12.88%
7 | 199 | 18 | 4771 | 19 | 22.7 | 141.61 | 75.14 | 216.75 | 75.14 | 37.57 | 199 | 4771 | 1140 | 196.274 | 20.9396 | -9.0097 | 1114.284 | 18.4212 | -96.3186 | 10.9549 | 10.9549 | 109.0008 | 289.0008 | 95.2585 | -68.2954 | 0 | 64.136 | 64.136 | -0.89339 | 0% | 29.0023 | 0 | 0 | 127.7139 | 127.7139 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4361 | 4.4361 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4772 | 20 | 22.2 | 48.67 | 42.72 | 91.39 | 42.72 | 21.36 | 199 | 4772 | 1200 | 196.274 | 20.9396 | -9.0097 | 1174.284 | 19.4212 | -111.3186 | 1.5987 | 1.5987 | 119.4961 | 299.4961 | 109.1651 | 0 | 0 | 36.4638 | 36.4638 | -2.2113 | 0% | 16.4889 | 0 | 0 | 153.7415 | 153.7415 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.5261 | 4.5261 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4773 | 21 | 19.9 | 0 | 7.17 | 7.17 | 7.17 | 3.59 | 199 | 4773 | 1260 | 196.274 | 20.9396 | -9.0097 | 1234.284 | 20.4212 | -126.3186 | -6.7992 | 0 | 121.4571 | 301.4571 | 111.6546 | 0 | 0 | 6.12 | 6.12 | -17.9833 | 0% | 2.7675 | 0 | 0 | -3.7327 | 0 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4774 | 22 | 17.2 | 0 | 0 | 0 | 0 | 0 | 199 | 4774 | 1320 | 196.274 | 20.9396 | -9.0097 | 1294.284 | 21.4212 | -141.3186 | -13.8195 | 0 | 121.4571 | 301.4571 | 111.6546 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.163 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4775 | 23 | 16.5 | 0 | 0 | 0 | 0 | 0 | 199 | 4775 | 1380 | 196.274 | 20.9396 | -9.0097 | 1354.284 | 22.4212 | -156.3186 | -18.9845 | 0 | 121.4571 | 301.4571 | 111.6546 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4621 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
7 | 199 | 18 | 4776 | 24 | 15.5 | 0 | 0 | 0 | 0 | 0 | 199 | 4776 | 1440 | 196.274 | 20.9396 | -9.0097 | 1414.284 | 23.4212 | -171.3186 | -21.8294 | 0 | 121.4571 | 301.4571 | 111.6546 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2184 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4777 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 200 | 4777 | 60 | 197.2603 | 20.7697 | -9.3345 | 34.284 | 0.41583 | 173.7626 | -22.2175 | 0 | 121.1856 | 58.8144 | 111.4783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2664 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4778 | 2 | 16.1 | 0 | 0 | 0 | 0 | 0 | 200 | 4778 | 120 | 197.2603 | 20.7697 | -9.3345 | 94.284 | 1.4158 | 158.7626 | -19.7812 | 0 | 121.1856 | 58.8144 | 111.4783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4511 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4779 | 3 | 15 | 0 | 0 | 0 | 0 | 0 | 200 | 4779 | 180 | 197.2603 | 20.7697 | -9.3345 | 154.284 | 2.4158 | 143.7626 | -14.955 | 0 | 121.1856 | 58.8144 | 111.4783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4646 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4780 | 4 | 14.7 | 0 | 0 | 0 | 0 | 0 | 200 | 4780 | 240 | 197.2603 | 20.7697 | -9.3345 | 214.284 | 3.4158 | 128.7626 | -8.1923 | 0 | 121.1856 | 58.8144 | 111.4783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9218 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4781 | 5 | 13.8 | 0 | 0 | 0 | 0 | 0 | 200 | 4781 | 300 | 197.2603 | 20.7697 | -9.3345 | 274.284 | 4.4158 | 113.7626 | 0.022393 | 0.022393 | 121.1578 | 58.8422 | 111.4432 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.5972 | 4.5972 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4782 | 6 | 13.9 | 1.81 | 7 | 8.81 | 7 | 3.5 | 200 | 4782 | 360 | 197.2603 | 20.7697 | -9.3345 | 334.284 | 5.4158 | 98.7626 | 9.2568 | 9.2568 | 110.5619 | 69.4381 | 97.5488 | 0 | 0 | 5.9749 | 5.9749 | -20.6915 | 0% | 2.7018 | 0 | 0 | 18.3973 | 18.3973 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4783 | 7 | 14.7 | 58.75 | 33.33 | 92.08 | 33.33 | 16.67 | 200 | 4783 | 420 | 197.2603 | 20.7697 | -9.3345 | 394.284 | 6.4158 | 83.7626 | 19.1461 | 19.1461 | 100.2944 | 79.7056 | 83.5382 | 20.1592 | 20.1592 | 28.4489 | 48.6082 | -1.8007 | 0% | 21.9806 | 0 | 0 | 193.584 | 193.584 | 0% | 11.57% | 11.57% | 80% | 9.257% | 2.0347 | 6.0865 | 6 | 12.2082 | 4.4996 | 6.306% | 6.306%
7 | 200 | 19 | 4784 | 8 | 17.8 | 158.19 | 62.56 | 220.75 | 62.56 | 31.28 | 200 | 4784 | 480 | 197.2603 | 20.7697 | -9.3345 | 454.284 | 7.4158 | 68.7626 | 29.3638 | 29.3638 | 89.7397 | 90.2603 | 69.5413 | 112.7604 | 112.7604 | 53.3983 | 166.1587 | 0.084013 | 8.401% | 75.137 | 6.3125 | 4.4187 | 172.2226 | 172.2226 | 2.566% | 11.43% | 11.43% | 80% | 9.143% | 6.8697 | 5.3938 | 5.3938 | 37.0539 | 15.1918 | 21.52% | 21.52%
7 | 200 | 19 | 4785 | 9 | 19.6 | 275.28 | 94.44 | 369.72 | 94.44 | 47.22 | 200 | 4785 | 540 | 197.2603 | 20.7697 | -9.3345 | 514.284 | 8.4158 | 53.7626 | 39.5627 | 39.5627 | 78.0277 | 101.9723 | 55.7051 | 243.526 | 243.526 | 80.6096 | 324.1356 | 0.44724 | 44.72% | 146.5741 | 65.5537 | 45.8876 | 182.2242 | 182.2242 | 25.18% | 11.36% | 11.36% | 85% | 9.658% | 14.1563 | 5.0224 | 5.0224 | 71.099 | 31.3053 | 39.02% | 39.02%
7 | 200 | 19 | 4786 | 10 | 21.5 | 326.33 | 95.14 | 421.47 | 95.14 | 47.57 | 200 | 4786 | 600 | 197.2603 | 20.7697 | -9.3345 | 574.284 | 9.4158 | 38.7626 | 49.2616 | 49.2616 | 63.7704 | 116.2296 | 42.292 | 318.5898 | 318.5898 | 81.2071 | 399.7968 | 0.52518 | 52.52% | 180.7881 | 94.9464 | 66.4625 | 182.8855 | 182.8855 | 36.34% | 11.32% | 11.32% | 85% | 9.621% | 17.3939 | 4.6551 | 4.6551 | 80.9698 | 38.465 | 44.27% | 44.27%
7 | 200 | 19 | 4787 | 11 | 23.6 | 435.89 | 95.83 | 531.72 | 95.83 | 47.92 | 200 | 4787 | 660 | 197.2603 | 20.7697 | -9.3345 | 634.284 | 10.4158 | 23.7626 | 57.6126 | 57.6126 | 44.6992 | 135.3008 | 29.9644 | 447.1897 | 447.1897 | 81.796 | 528.9857 | 0.60188 | 60.19% | 239.2073 | 143.9731 | 100.7812 | 190.5281 | 190.5281 | 52.9% | 11.3% | 11.3% | 90% | 10.17% | 24.3238 | 4.2784 | 4.2784 | 104.068 | 53.7899 | 54.62% | 54.62%
7 | 200 | 19 | 4788 | 12 | 25.8 | 451.33 | 127.22 | 578.55 | 127.22 | 63.61 | 200 | 4788 | 720 | 197.2603 | 20.7697 | -9.3345 | 694.284 | 11.4158 | 8.7626 | 63.0315 | 63.0315 | 18.3061 | 161.6939 | 20.8271 | 473.3083 | 473.3083 | 108.5891 | 581.8974 | 0.62834 | 62.83% | 263.134 | 165.3372 | 115.736 | 218.4466 | 218.4466 | 52.98% | 11.28% | 11.28% | 90% | 10.15% | 26.7191 | 3.917 | 3.917 | 104.6582 | 59.0869 | 47.91% | 47.91%
7 | 200 | 19 | 4789 | 13 | 26.4 | 518.83 | 161.17 | 680 | 161.17 | 80.59 | 200 | 4789 | 780 | 197.2603 | 20.7697 | -9.3345 | 754.284 | 12.4158 | -6.2374 | 63.5007 | 63.5007 | 13.1604 | 193.1604 | 19.9428 | 544.9726 | 544.9726 | 137.5672 | 682.5398 | 0.6561 | 65.61% | 308.6445 | 202.5026 | 141.7518 | 230.9723 | 230.9723 | 61.37% | 11.31% | 11.31% | 90% | 10.18% | 31.4187 | 3.8243 | 3.8243 | 120.1541 | 69.4797 | 52.02% | 52.02%
7 | 200 | 19 | 4790 | 14 | 26.4 | 510.89 | 219.03 | 729.92 | 219.03 | 109.52 | 200 | 4790 | 840 | 197.2603 | 20.7697 | -9.3345 | 814.284 | 13.4158 | -21.2374 | 58.7868 | 58.7868 | 40.8108 | 220.8108 | 28.1036 | 526.931 | 526.931 | 186.9538 | 713.8848 | 0.6626 | 66.26% | 322.8187 | 213.8987 | 149.7291 | 272.3889 | 272.3889 | 54.97% | 11.32% | 11.32% | 90% | 10.19% | 32.8937 | 3.8243 | 3.8243 | 125.7946 | 72.7414 | 46.18% | 46.18%
7 | 200 | 19 | 4791 | 15 | 27.1 | 410.56 | 176.53 | 587.09 | 176.53 | 88.27 | 200 | 4791 | 900 | 197.2603 | 20.7697 | -9.3345 | 874.284 | 14.4158 | -36.2374 | 50.7938 | 50.7938 | 60.9734 | 240.9734 | 40.111 | 405.2203 | 405.2203 | 150.6778 | 555.8981 | 0.62507 | 62.51% | 251.3771 | 157.1277 | 109.9894 | 270.9003 | 270.9003 | 40.6% | 11.26% | 11.26% | 90% | 10.13% | 25.467 | 3.7193 | 3.7193 | 94.72 | 56.3181 | 34.96% | 34.96%
7 | 200 | 19 | 4792 | 16 | 26.8 | 447.5 | 185.69 | 633.19 | 185.69 | 92.85 | 200 | 4792 | 960 | 197.2603 | 20.7697 | -9.3345 | 934.284 | 15.4158 | -51.2374 | 41.2473 | 41.2473 | 75.8548 | 255.8548 | 53.4069 | 404.6157 | 404.6157 | 158.4963 | 563.112 | 0.62624 | 62.62% | 254.6392 | 159.4645 | 111.6252 | 265.4803 | 265.4803 | 42.05% | 11.26% | 11.26% | 90% | 10.14% | 25.8129 | 3.7639 | 3.7639 | 97.1568 | 57.083 | 36.6% | 36.6%
7 | 200 | 19 | 4793 | 17 | 27 | 336.72 | 147.64 | 484.36 | 147.64 | 73.82 | 200 | 4793 | 1020 | 197.2603 | 20.7697 | -9.3345 | 994.284 | 16.4158 | -66.2374 | 31.0927 | 31.0927 | 87.8785 | 267.8785 | 67.1958 | 252.7127 | 252.7127 | 126.0186 | 378.7313 | 0.54081 | 54.08% | 171.2623 | 92.6201 | 64.8341 | 254.4249 | 254.4249 | 25.48% | 11.19% | 11.19% | 85% | 9.511% | 16.2893 | 3.7341 | 3.7341 | 60.826 | 36.0224 | 23.91% | 23.91%
7 | 200 | 19 | 4794 | 18 | 26.7 | 263.67 | 116.61 | 380.28 | 116.61 | 58.31 | 200 | 4794 | 1080 | 197.2603 | 20.7697 | -9.3345 | 1054.284 | 17.4158 | -81.2374 | 20.852 | 20.852 | 98.5572 | 278.5572 | 81.1774 | 113.6109 | 113.6109 | 99.5329 | 213.1437 | 0.33337 | 33.34% | 96.3836 | 32.1315 | 22.4921 | 245.9661 | 245.9661 | 9.144% | 11.14% | 11.14% | 80% | 8.909% | 8.5864 | 3.7789 | 3.7789 | 32.447 | 18.9881 | 13.19% | 13.19%
7 | 200 | 19 | 4795 | 19 | 26.2 | 180.56 | 73.19 | 253.75 | 73.19 | 36.6 | 200 | 4795 | 1140 | 197.2603 | 20.7697 | -9.3345 | 1114.284 | 18.4158 | -96.2374 | 10.885 | 10.885 | 108.8251 | 288.8251 | 95.1944 | -86.567 | 0 | 62.4716 | 62.4716 | -0.81864 | 0% | 28.2496 | 0 | 0 | 189.4975 | 189.4975 | 0% | 11.1% | 0% | 80% | 0% | 0 | 3.8549 | 3.8549 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4796 | 20 | 25.1 | 44.39 | 42.28 | 86.67 | 42.28 | 21.14 | 200 | 4796 | 1200 | 197.2603 | 20.7697 | -9.3345 | 1174.284 | 19.4158 | -111.2374 | 1.5163 | 1.5163 | 119.3292 | 299.3292 | 109.1187 | 0 | 0 | 36.0882 | 36.0882 | -2.0697 | 0% | 16.3191 | 0 | 0 | 192.6944 | 192.6944 | 0% | 11.14% | 0% | 80% | 0% | 0 | 4.0283 | 4.0283 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4797 | 21 | 24.1 | 0 | 8.56 | 8.56 | 8.56 | 4.28 | 200 | 4797 | 1260 | 197.2603 | 20.7697 | -9.3345 | 1234.284 | 20.4158 | -126.2374 | -6.8983 | 0 | 121.1856 | 301.1856 | 111.4783 | 0 | 0 | 7.3064 | 7.3064 | -13.6827 | 0% | 3.304 | 0 | 0 | 1.5532 | 1.5532 | 0% | 11.17% | 0% | 80% | 0% | 0 | 4.1933 | 4.1933 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4798 | 22 | 21.3 | 0 | 0 | 0 | 0 | 0 | 200 | 4798 | 1320 | 197.2603 | 20.7697 | -9.3345 | 1294.284 | 21.4158 | -141.2374 | -13.9386 | 0 | 121.1856 | 301.1856 | 111.4783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.1779 | 0 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6926 | 4.6926 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4799 | 23 | 19.9 | 0 | 0 | 0 | 0 | 0 | 200 | 4799 | 1380 | 197.2603 | 20.7697 | -9.3345 | 1354.284 | 22.4158 | -156.2374 | -19.125 | 0 | 121.1856 | 301.1856 | 111.4783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.6486 | 0 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
7 | 200 | 19 | 4800 | 24 | 17.9 | 0 | 0 | 0 | 0 | 0 | 200 | 4800 | 1440 | 197.2603 | 20.7697 | -9.3345 | 1414.284 | 23.4158 | -171.2374 | -21.9898 | 0 | 121.1856 | 301.1856 | 111.4783 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0337 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4801 | 1 | 17.5 | 0 | 0 | 0 | 0 | 0 | 201 | 4801 | 60 | 198.2466 | 20.5943 | -9.6501 | 34.284 | 0.41056 | 173.8415 | -22.3982 | 0 | 120.906 | 59.094 | 111.2964 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9598 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4802 | 2 | 16.7 | 0 | 0 | 0 | 0 | 0 | 201 | 4802 | 120 | 198.2466 | 20.5943 | -9.6501 | 94.284 | 1.4106 | 158.8415 | -19.9698 | 0 | 120.906 | 59.094 | 111.2964 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.352 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4803 | 3 | 15.7 | 0 | 0 | 0 | 0 | 0 | 201 | 4803 | 180 | 198.2466 | 20.5943 | -9.6501 | 154.284 | 2.4106 | 143.8415 | -15.1451 | 0 | 120.906 | 59.094 | 111.2964 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0491 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4804 | 4 | 15.3 | 0 | 0 | 0 | 0 | 0 | 201 | 4804 | 240 | 198.2466 | 20.5943 | -9.6501 | 214.284 | 3.4106 | 128.8415 | -8.3797 | 0 | 120.906 | 59.094 | 111.2964 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6587 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4805 | 5 | 15.1 | 0 | 0 | 0 | 0 | 0 | 201 | 4805 | 300 | 198.2466 | 20.5943 | -9.6501 | 274.284 | 4.4106 | 113.8415 | -0.16052 | 0 | 120.906 | 59.094 | 111.2964 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.0848 | 9.0848 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4806 | 6 | 14.8 | 2 | 8.39 | 10.39 | 8.39 | 4.2 | 201 | 4806 | 360 | 198.2466 | 20.5943 | -9.6501 | 334.284 | 5.4106 | 98.8415 | 9.0786 | 9.0786 | 110.4946 | 69.5054 | 97.637 | 0 | 0 | 7.1613 | 7.1613 | -16.8441 | 0% | 3.2383 | 0 | 0 | 24.3622 | 24.3622 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4807 | 7 | 15.9 | 62.56 | 42.36 | 104.92 | 42.36 | 21.18 | 201 | 4807 | 420 | 198.2466 | 20.5943 | -9.6501 | 394.284 | 6.4106 | 83.8415 | 18.9712 | 18.9712 | 100.2149 | 79.7851 | 83.6104 | 21.416 | 21.416 | 36.1565 | 57.5725 | -1.348 | 0% | 26.0343 | 0 | 0 | 205.3074 | 205.3074 | 0% | 11.52% | 11.52% | 80% | 9.216% | 2.3992 | 5.8104 | 5.8104 | 13.9402 | 5.3056 | 6.79% | 6.79%
7 | 201 | 20 | 4808 | 8 | 18 | 199.39 | 65.69 | 265.08 | 65.69 | 32.85 | 201 | 4808 | 480 | 198.2466 | 20.5943 | -9.6501 | 454.284 | 7.4106 | 68.8415 | 29.1903 | 29.1903 | 89.6502 | 90.3498 | 69.5963 | 142.5307 | 142.5307 | 56.0699 | 198.6006 | 0.20387 | 20.39% | 89.8072 | 18.3089 | 12.8163 | 185.6965 | 185.6965 | 6.902% | 11.42% | 11.42% | 80% | 9.135% | 8.2035 | 5.3514 | 5.3514 | 43.9 | 18.1412 | 23.64% | 23.64%
7 | 201 | 20 | 4809 | 9 | 21.3 | 356.53 | 76.61 | 433.14 | 76.61 | 38.31 | 201 | 4809 | 540 | 198.2466 | 20.5943 | -9.6501 | 514.284 | 8.4106 | 53.8415 | 39.3875 | 39.3875 | 77.9319 | 102.0681 | 55.7391 | 316.302 | 316.302 | 65.3907 | 381.6928 | 0.51081 | 51.08% | 172.6015 | 88.167 | 61.7169 | 198.7421 | 198.7421 | 31.05% | 11.32% | 11.32% | 85% | 9.624% | 16.6108 | 4.6926 | 4.6926 | 77.947 | 36.7333 | 39.22% | 39.22%
7 | 201 | 20 | 4810 | 10 | 23 | 477.64 | 97.44 | 575.08 | 97.44 | 48.72 | 201 | 4810 | 600 | 198.2466 | 20.5943 | -9.6501 | 574.284 | 9.4106 | 38.8415 | 49.0808 | 49.0808 | 63.6795 | 116.3205 | 42.2966 | 467.5495 | 467.5495 | 83.1702 | 550.7198 | 0.6075 | 60.75% | 249.0355 | 151.2898 | 105.9029 | 202.0524 | 202.0524 | 52.41% | 11.31% | 11.31% | 90% | 10.18% | 25.3513 | 4.3829 | 4.3829 | 111.1121 | 56.0621 | 54.99% | 54.99%
7 | 201 | 20 | 4811 | 11 | 24.9 | 603.94 | 104.72 | 708.66 | 104.72 | 52.36 | 201 | 4811 | 660 | 198.2466 | 20.5943 | -9.6501 | 634.284 | 10.4106 | 23.8415 | 57.4242 | 57.4242 | 44.649 | 135.351 | 29.9208 | 621.1663 | 621.1663 | 89.3841 | 710.5504 | 0.65745 | 65.74% | 321.3109 | 211.2448 | 147.8714 | 230.2306 | 230.2306 | 64.23% | 11.33% | 11.33% | 90% | 10.2% | 32.758 | 4.0608 | 4.0608 | 133.0221 | 72.4414 | 57.78% | 57.78%
7 | 201 | 20 | 4812 | 12 | 26.5 | 668.11 | 125.14 | 793.25 | 125.14 | 62.57 | 201 | 4812 | 720 | 198.2466 | 20.5943 | -9.6501 | 694.284 | 11.4106 | 8.8415 | 62.8439 | 62.8439 | 18.3752 | 161.6248 | 20.7007 | 702.405 | 702.405 | 106.8137 | 809.2187 | 0.67952 | 67.95% | 365.9287 | 248.6547 | 174.0583 | 245.1589 | 245.1589 | 71% | 11.36% | 11.36% | 95% | 10.79% | 39.4747 | 3.8091 | 3.8091 | 150.362 | 87.2947 | 61.33% | 61.33%
7 | 201 | 20 | 4813 | 13 | 27.8 | 721.39 | 125.69 | 847.08 | 125.69 | 62.85 | 201 | 4813 | 780 | 198.2466 | 20.5943 | -9.6501 | 754.284 | 12.4106 | -6.1585 | 63.34 | 63.34 | 12.9329 | 192.9329 | 19.7531 | 759.7109 | 759.7109 | 107.2831 | 866.9941 | 0.69097 | 69.1% | 392.0547 | 270.8976 | 189.6283 | 286.2208 | 286.2208 | 66.25% | 11.38% | 11.38% | 95% | 10.81% | 42.3878 | 3.6178 | 3.6178 | 153.3497 | 93.7368 | 53.58% | 53.58%
7 | 201 | 20 | 4814 | 14 | 28.8 | 681.94 | 150 | 831.94 | 150 | 75 | 201 | 4814 | 840 | 198.2466 | 20.5943 | -9.6501 | 814.284 | 13.4106 | -21.1585 | 58.6679 | 58.6679 | 40.5246 | 220.5246 | 27.9347 | 705.3437 | 705.3437 | 128.033 | 833.3767 | 0.68892 | 68.89% | 376.853 | 259.6204 | 181.7343 | 300.3979 | 300.3979 | 60.5% | 11.37% | 11.37% | 95% | 10.8% | 40.6992 | 3.4787 | 3.4787 | 141.5794 | 90.0026 | 47.13% | 47.13%
7 | 201 | 20 | 4815 | 15 | 29.4 | 498.33 | 159.03 | 657.36 | 159.03 | 79.52 | 201 | 4815 | 900 | 198.2466 | 20.5943 | -9.6501 | 874.284 | 14.4106 | -36.1585 | 50.7061 | 50.7061 | 60.7065 | 240.7065 | 39.9735 | 493.4579 | 493.4579 | 135.7406 | 629.1985 | 0.65355 | 65.36% | 284.5236 | 185.9516 | 130.1662 | 301.1416 | 301.1416 | 43.22% | 11.26% | 11.26% | 90% | 10.14% | 28.8431 | 3.3986 | 3.3986 | 98.0255 | 63.7839 | 32.55% | 32.55%
7 | 201 | 20 | 4816 | 16 | 29.5 | 451.19 | 149.17 | 600.36 | 149.17 | 74.59 | 201 | 4816 | 960 | 198.2466 | 20.5943 | -9.6501 | 934.284 | 15.4106 | -51.1585 | 41.1761 | 41.1761 | 75.6203 | 255.6203 | 53.2932 | 409.6222 | 409.6222 | 127.3246 | 536.9468 | 0.62809 | 62.81% | 242.8073 | 152.5056 | 106.7539 | 299.2495 | 299.2495 | 35.67% | 11.21% | 11.21% | 90% | 10.09% | 24.5068 | 3.3855 | 3.3855 | 82.9671 | 54.1946 | 27.73% | 27.73%
7 | 201 | 20 | 4817 | 17 | 29.5 | 421.72 | 134.11 | 555.83 | 134.11 | 67.06 | 201 | 4817 | 1020 | 198.2466 | 20.5943 | -9.6501 | 994.284 | 16.4106 | -66.1585 | 31.0272 | 31.0272 | 87.67 | 267.67 | 67.1009 | 318.3564 | 318.3564 | 114.47 | 432.8264 | 0.58578 | 58.58% | 195.7241 | 114.6507 | 80.2555 | 291.4581 | 291.4581 | 27.54% | 11.16% | 11.16% | 85% | 9.486% | 18.5666 | 3.3855 | 3.3855 | 62.8569 | 41.0585 | 21.57% | 21.57%
7 | 201 | 20 | 4818 | 18 | 29.1 | 266.94 | 112.64 | 379.58 | 112.64 | 56.32 | 201 | 4818 | 1080 | 198.2466 | 20.5943 | -9.6501 | 1054.284 | 17.4106 | -81.1585 | 20.7845 | 20.7845 | 98.3668 | 278.3668 | 81.0992 | 116.3917 | 116.3917 | 96.1443 | 212.536 | 0.35568 | 35.57% | 96.1088 | 34.1844 | 23.9291 | 267.8338 | 267.8338 | 8.934% | 11.06% | 11.06% | 80% | 8.846% | 8.5021 | 3.4383 | 3.4383 | 29.2331 | 18.8017 | 10.91% | 10.91%
7 | 201 | 20 | 4819 | 19 | 28.5 | 182.78 | 77.08 | 259.86 | 77.08 | 38.54 | 201 | 4819 | 1140 | 198.2466 | 20.5943 | -9.6501 | 1114.284 | 18.4106 | -96.1585 | 10.8098 | 10.8098 | 108.6472 | 288.6472 | 95.1326 | -87.186 | 0 | 65.7919 | 65.7919 | -0.66325 | 0% | 29.7511 | 0 | 0 | 250.9458 | 250.9458 | 0% | 11.01% | 0% | 80% | 0% | 0 | 3.5197 | 3.5197 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4820 | 20 | 27.5 | 62.08 | 40.06 | 102.14 | 40.06 | 20.03 | 201 | 4820 | 1200 | 198.2466 | 20.5943 | -9.6501 | 1174.284 | 19.4106 | -111.1585 | 1.4286 | 1.4286 | 119.1603 | 299.1603 | 109.075 | 0 | 0 | 34.1933 | 34.1933 | -2.0804 | 0% | 15.4622 | 0 | 0 | 256.846 | 256.846 | 0% | 11.04% | 0% | 80% | 0% | 0 | 3.6609 | 3.6609 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4821 | 21 | 24.8 | 0 | 7.22 | 7.22 | 7.22 | 3.61 | 201 | 4821 | 1260 | 198.2466 | 20.5943 | -9.6501 | 1234.284 | 20.4106 | -126.1585 | -7.0029 | 0 | 120.906 | 300.906 | 111.2964 | 0 | 0 | 6.1627 | 6.1627 | -16.1282 | 0% | 2.7868 | 0 | 0 | 1.2222 | 1.2222 | 0% | 11.14% | 0% | 80% | 0% | 0 | 4.0771 | 4.0771 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4822 | 22 | 21.2 | 0 | 0 | 0 | 0 | 0 | 201 | 4822 | 1320 | 198.2466 | 20.5943 | -9.6501 | 1294.284 | 21.4106 | -141.1585 | -14.0632 | 0 | 120.906 | 300.906 | 111.2964 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.8019 | 0 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.7114 | 4.7114 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4823 | 23 | 19.5 | 0 | 0 | 0 | 0 | 0 | 201 | 4823 | 1380 | 198.2466 | 20.5943 | -9.6501 | 1354.284 | 22.4106 | -156.1585 | -19.2711 | 0 | 120.906 | 300.906 | 111.2964 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5657 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0425 | 5.0425 | 0 | 0 | 0% | 0%
7 | 201 | 20 | 4824 | 24 | 18.5 | 0 | 0 | 0 | 0 | 0 | 201 | 4824 | 1440 | 198.2466 | 20.5943 | -9.6501 | 1414.284 | 23.4106 | -171.1585 | -22.1556 | 0 | 120.906 | 300.906 | 111.2964 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2628 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4825 | 1 | 18.1 | 0 | 0 | 0 | 0 | 0 | 202 | 4825 | 60 | 199.2329 | 20.4136 | -9.9564 | 34.284 | 0.40546 | 173.9181 | -22.584 | 0 | 120.6184 | 59.3816 | 111.109 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3234 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4826 | 2 | 17.4 | 0 | 0 | 0 | 0 | 0 | 202 | 4826 | 120 | 199.2329 | 20.4136 | -9.9564 | 94.284 | 1.4055 | 158.9181 | -20.163 | 0 | 120.6184 | 59.3816 | 111.109 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5832 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4827 | 3 | 16.8 | 0 | 0 | 0 | 0 | 0 | 202 | 4827 | 180 | 199.2329 | 20.4136 | -9.9564 | 154.284 | 2.4055 | 143.9181 | -15.3393 | 0 | 120.6184 | 59.3816 | 111.109 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6906 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4828 | 4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 202 | 4828 | 240 | 199.2329 | 20.4136 | -9.9564 | 214.284 | 3.4055 | 128.9181 | -8.5706 | 0 | 120.6184 | 59.3816 | 111.109 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4526 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4829 | 5 | 15.7 | 0 | 0 | 0 | 0 | 0 | 202 | 4829 | 300 | 199.2329 | 20.4136 | -9.9564 | 274.284 | 4.4055 | 113.9181 | -0.3463 | 0 | 120.6184 | 59.3816 | 111.109 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.6062 | 8.6062 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4830 | 6 | 15.5 | 0.61 | 7.5 | 8.11 | 7.5 | 3.75 | 202 | 4830 | 360 | 199.2329 | 20.4136 | -9.9564 | 334.284 | 5.4055 | 98.9181 | 8.8978 | 8.8978 | 110.4222 | 69.5778 | 97.7236 | 0 | 0 | 6.4017 | 6.4017 | -18.6906 | 0% | 2.8948 | 0 | 0 | 23.0412 | 23.0412 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4831 | 7 | 16.5 | 47.5 | 40.42 | 87.92 | 40.42 | 20.21 | 202 | 4831 | 420 | 199.2329 | 20.4136 | -9.9564 | 394.284 | 6.4055 | 83.9181 | 18.7942 | 18.7942 | 100.1301 | 79.8699 | 83.6806 | 16.2285 | 16.2285 | 34.5006 | 50.7292 | -1.6116 | 0% | 22.9397 | 0 | 0 | 201.32 | 201.32 | 0% | 11.5% | 11.5% | 80% | 9.197% | 2.1098 | 5.6761 | 5.6761 | 11.9752 | 4.6656 | 5.948% | 5.948%
7 | 202 | 21 | 4832 | 8 | 18.5 | 184.78 | 78.06 | 262.84 | 78.06 | 39.03 | 202 | 4832 | 480 | 199.2329 | 20.4136 | -9.9564 | 454.284 | 7.4055 | 68.9181 | 29.0146 | 29.0146 | 89.555 | 90.445 | 69.6489 | 132.4887 | 132.4887 | 66.6284 | 199.1171 | 0.21101 | 21.1% | 90.0407 | 18.9997 | 13.2998 | 181.9548 | 181.9548 | 7.309% | 11.4% | 11.4% | 80% | 9.121% | 8.2128 | 5.2467 | 5.2467 | 43.0901 | 18.162 | 23.68% | 23.68%
7 | 202 | 21 | 4833 | 9 | 21.5 | 313.47 | 114.94 | 428.41 | 114.94 | 57.47 | 202 | 4833 | 540 | 199.2329 | 20.4136 | -9.9564 | 514.284 | 8.4055 | 53.9181 | 39.2099 | 39.2099 | 77.8298 | 102.1702 | 55.7704 | 278.932 | 278.932 | 98.1074 | 377.0395 | 0.50835 | 50.84% | 170.4973 | 86.6726 | 60.6708 | 194.3397 | 194.3397 | 31.22% | 11.32% | 11.32% | 85% | 9.62% | 16.4011 | 4.6551 | 4.6551 | 76.3481 | 36.2695 | 39.29% | 39.29%
7 | 202 | 21 | 4834 | 10 | 24.2 | 383.61 | 130.33 | 513.94 | 130.33 | 65.17 | 202 | 4834 | 600 | 199.2329 | 20.4136 | -9.9564 | 574.284 | 9.4055 | 38.9181 | 48.8973 | 48.8973 | 63.5817 | 116.4183 | 42.2981 | 376.5443 | 376.5443 | 111.2436 | 487.7879 | 0.58745 | 58.74% | 220.5777 | 129.5779 | 90.7045 | 217.2894 | 217.2894 | 41.74% | 11.28% | 11.28% | 85% | 9.588% | 21.1488 | 4.1765 | 4.1765 | 88.3278 | 46.7686 | 40.65% | 40.65%
7 | 202 | 21 | 4835 | 11 | 26 | 479.78 | 169.31 | 649.09 | 169.31 | 84.66 | 202 | 4835 | 660 | 199.2329 | 20.4136 | -9.9564 | 634.284 | 10.4055 | 23.9181 | 57.2324 | 57.2324 | 44.5911 | 135.4089 | 29.8735 | 494.7604 | 494.7604 | 144.5151 | 639.2756 | 0.64477 | 64.48% | 289.0804 | 186.39 | 130.473 | 244.5026 | 244.5026 | 53.36% | 11.3% | 11.3% | 90% | 10.17% | 29.3968 | 3.8858 | 3.8858 | 114.23 | 65.0083 | 46.72% | 46.72%
7 | 202 | 21 | 4836 | 12 | 27.7 | 456.25 | 233.39 | 689.64 | 233.39 | 116.7 | 202 | 4836 | 720 | 199.2329 | 20.4136 | -9.9564 | 694.284 | 11.4055 | 8.9181 | 62.6516 | 62.6516 | 18.4365 | 161.5635 | 20.5697 | 480.9142 | 480.9142 | 199.2108 | 680.125 | 0.6596 | 65.96% | 307.5525 | 202.863 | 142.0041 | 281.3869 | 281.3869 | 50.47% | 11.3% | 11.3% | 90% | 10.17% | 31.2815 | 3.6321 | 3.6321 | 113.6168 | 69.1763 | 40.38% | 40.38%
7 | 202 | 21 | 4837 | 13 | 28.8 | 543.56 | 227.28 | 770.84 | 227.28 | 113.64 | 202 | 4837 | 780 | 199.2329 | 20.4136 | -9.9564 | 754.284 | 12.4055 | -6.0819 | 63.1733 | 63.1733 | 12.7105 | 192.7105 | 19.559 | 573.9681 | 573.9681 | 193.9956 | 767.9637 | 0.67911 | 67.91% | 347.2732 | 235.8383 | 165.0868 | 304.9131 | 304.9131 | 54.14% | 11.34% | 11.34% | 90% | 10.2% | 35.4317 | 3.4787 | 3.4787 | 123.2557 | 78.3541 | 40.42% | 40.42%
7 | 202 | 21 | 4838 | 14 | 29.4 | 524.53 | 232.5 | 757.03 | 232.5 | 116.25 | 202 | 4838 | 840 | 199.2329 | 20.4136 | -9.9564 | 814.284 | 13.4055 | -21.0819 | 58.5427 | 58.5427 | 40.2391 | 220.2391 | 27.7644 | 544.1093 | 544.1093 | 198.4512 | 742.5605 | 0.67652 | 67.65% | 335.7859 | 227.1665 | 159.0166 | 305.3967 | 305.3967 | 52.07% | 11.32% | 11.32% | 90% | 10.19% | 34.2168 | 3.3986 | 3.3986 | 116.2886 | 75.6675 | 38.08% | 38.08%
7 | 202 | 21 | 4839 | 15 | 30 | 432.08 | 191.94 | 624.02 | 191.94 | 95.97 | 202 | 4839 | 900 | 199.2329 | 20.4136 | -9.9564 | 874.284 | 14.4055 | -36.0819 | 50.6125 | 50.6125 | 60.4377 | 240.4377 | 39.8362 | 429.2888 | 429.2888 | 163.831 | 593.1199 | 0.6465 | 64.65% | 268.2088 | 173.3965 | 121.3775 | 307.8177 | 307.8177 | 39.43% | 11.24% | 11.24% | 90% | 10.11% | 27.1277 | 3.321 | 3.321 | 90.0911 | 59.9905 | 29.27% | 29.27%
7 | 202 | 21 | 4840 | 16 | 30 | 386.72 | 207.5 | 594.22 | 207.5 | 103.75 | 202 | 4840 | 960 | 199.2329 | 20.4136 | -9.9564 | 934.284 | 15.4055 | -51.0819 | 41.0993 | 41.0993 | 75.3832 | 255.3832 | 53.1805 | 352.5581 | 352.5581 | 177.1123 | 529.6704 | 0.62763 | 62.76% | 239.517 | 150.3282 | 105.2298 | 309.4079 | 309.4079 | 34.01% | 11.2% | 11.2% | 90% | 10.08% | 24.1505 | 3.321 | 3.321 | 80.2037 | 53.4066 | 25.92% | 25.92%
7 | 202 | 21 | 4841 | 17 | 29.9 | 275.78 | 172.92 | 448.7 | 172.92 | 86.46 | 202 | 4841 | 1020 | 199.2329 | 20.4136 | -9.9564 | 994.284 | 16.4055 | -66.0819 | 30.9562 | 30.9562 | 87.4589 | 267.4589 | 67.0077 | 209.4201 | 209.4201 | 147.5965 | 357.0165 | 0.54176 | 54.18% | 161.4429 | 87.4632 | 61.2242 | 296.1708 | 296.1708 | 20.67% | 11.11% | 11.11% | 85% | 9.444% | 15.247 | 3.3338 | 3.3338 | 50.8296 | 33.7173 | 17.16% | 17.16%
7 | 202 | 21 | 4842 | 18 | 30.1 | 203.61 | 143.39 | 347 | 143.39 | 71.7 | 202 | 4842 | 1080 | 199.2329 | 20.4136 | -9.9564 | 1054.284 | 17.4055 | -81.0819 | 20.7117 | 20.7117 | 98.1741 | 278.1741 | 81.0229 | 89.8339 | 89.8339 | 122.391 | 212.2249 | 0.36479 | 36.48% | 95.9681 | 35.0084 | 24.5059 | 282.1036 | 282.1036 | 8.687% | 11.03% | 11.03% | 80% | 8.82% | 8.4648 | 3.3083 | 3.3083 | 28.0041 | 18.7191 | 9.927% | 9.927%
7 | 202 | 21 | 4843 | 19 | 29.5 | 107.17 | 93.19 | 200.36 | 93.19 | 46.6 | 202 | 4843 | 1140 | 199.2329 | 20.4136 | -9.9564 | 1114.284 | 18.4055 | -96.0819 | 10.7293 | 10.7293 | 108.4671 | 288.4671 | 95.0731 | -50.9036 | 0 | 79.5426 | 79.5426 | -0.38345 | 0% | 35.9692 | 0 | 0 | 260.9787 | 260.9787 | 0% | 10.98% | 0% | 80% | 0% | 0 | 3.3855 | 3.3855 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4844 | 20 | 28.2 | 30.28 | 47.22 | 77.5 | 47.22 | 23.61 | 202 | 4844 | 1200 | 199.2329 | 20.4136 | -9.9564 | 1174.284 | 19.4055 | -111.0819 | 1.3354 | 1.3354 | 118.9896 | 298.9896 | 109.0339 | 0 | 0 | 40.3048 | 40.3048 | -1.6066 | 0% | 18.2258 | 0 | 0 | 268.0778 | 268.0778 | 0% | 11.01% | 0% | 80% | 0% | 0 | 3.5613 | 3.5613 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4845 | 21 | 26.9 | 0 | 7.44 | 7.44 | 7.44 | 3.72 | 202 | 4845 | 1260 | 199.2329 | 20.4136 | -9.9564 | 1234.284 | 20.4055 | -126.0819 | -7.1129 | 0 | 120.6184 | 300.6184 | 111.109 | 0 | 0 | 6.3504 | 6.3504 | -14.9256 | 0% | 2.8717 | 0 | 0 | 4.0118 | 4.0118 | 0% | 11.05% | 0% | 80% | 0% | 0 | 3.749 | 3.749 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4846 | 22 | 22.9 | 0 | 0 | 0 | 0 | 0 | 202 | 4846 | 1320 | 199.2329 | 20.4136 | -9.9564 | 1294.284 | 21.4055 | -141.0819 | -14.1934 | 0 | 120.6184 | 300.6184 | 111.109 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.4294 | 0 | 0% | 11.22% | 0% | 80% | 0% | 0 | 4.4006 | 4.4006 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4847 | 23 | 20.3 | 0 | 0 | 0 | 0 | 0 | 202 | 4847 | 1380 | 199.2329 | 20.4136 | -9.9564 | 1354.284 | 22.4055 | -156.0819 | -19.4227 | 0 | 120.6184 | 300.6184 | 111.109 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5847 | 0 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.8842 | 4.8842 | 0 | 0 | 0% | 0%
7 | 202 | 21 | 4848 | 24 | 18.3 | 0 | 0 | 0 | 0 | 0 | 202 | 4848 | 1440 | 199.2329 | 20.4136 | -9.9564 | 1414.284 | 23.4055 | -171.0819 | -22.3269 | 0 | 120.6184 | 300.6184 | 111.109 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8257 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4849 | 1 | 18 | 0 | 0 | 0 | 0 | 0 | 203 | 4849 | 60 | 200.2192 | 20.2277 | -10.2531 | 34.284 | 0.40052 | 173.9923 | -22.7748 | 0 | 120.323 | 59.677 | 110.9161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1905 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4850 | 2 | 17.2 | 0 | 0 | 0 | 0 | 0 | 203 | 4850 | 120 | 200.2192 | 20.2277 | -10.2531 | 94.284 | 1.4005 | 158.9923 | -20.3607 | 0 | 120.323 | 59.677 | 110.9161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8412 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4851 | 3 | 16.4 | 0 | 0 | 0 | 0 | 0 | 203 | 4851 | 180 | 200.2192 | 20.2277 | -10.2531 | 154.284 | 2.4005 | 143.9923 | -15.5373 | 0 | 120.323 | 59.677 | 110.9161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4919 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4852 | 4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 203 | 4852 | 240 | 200.2192 | 20.2277 | -10.2531 | 214.284 | 3.4005 | 128.9923 | -8.7647 | 0 | 120.323 | 59.677 | 110.9161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6443 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4853 | 5 | 15.6 | 0 | 0 | 0 | 0 | 0 | 203 | 4853 | 300 | 200.2192 | 20.2277 | -10.2531 | 274.284 | 4.4005 | 113.9923 | -0.53487 | 0 | 120.323 | 59.677 | 110.9161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.6563 | 1.6563 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4854 | 6 | 15.6 | 0.69 | 7.64 | 8.33 | 7.64 | 3.82 | 203 | 4854 | 360 | 200.2192 | 20.2277 | -10.2531 | 334.284 | 5.4005 | 98.9923 | 8.7146 | 8.7146 | 110.3447 | 69.6553 | 97.8085 | 0 | 0 | 6.5211 | 6.5211 | -18.2987 | 0% | 2.9489 | 0 | 0 | 12.4371 | 12.4371 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4855 | 7 | 16.6 | 27.17 | 48.28 | 75.45 | 48.28 | 24.14 | 203 | 4855 | 420 | 200.2192 | 20.2277 | -10.2531 | 394.284 | 6.4005 | 83.9923 | 18.6149 | 18.6149 | 100.04 | 79.96 | 83.7488 | 9.2683 | 9.2683 | 41.2096 | 50.4778 | -1.6192 | 0% | 22.8261 | 0 | 0 | 182.2853 | 182.2853 | 0% | 11.49% | 11.49% | 80% | 9.194% | 2.0986 | 5.6539 | 5.6539 | 11.8652 | 4.6408 | 6.509% | 6.509%
7 | 203 | 22 | 4856 | 8 | 18.8 | 84.94 | 60 | 144.94 | 60 | 30 | 203 | 4856 | 480 | 200.2192 | 20.2277 | -10.2531 | 454.284 | 7.4005 | 68.9923 | 28.8368 | 28.8368 | 89.4542 | 90.5458 | 69.6991 | 61.1009 | 61.1009 | 51.2132 | 112.3141 | -0.24136 | 0% | 50.7884 | 0 | 0 | 196.9055 | 196.9055 | 0% | 11.4% | 11.4% | 80% | 9.118% | 4.6308 | 5.1847 | 5.1847 | 24.0094 | 10.2407 | 12.19% | 12.19%
7 | 203 | 22 | 4857 | 9 | 22.3 | 215 | 109.92 | 324.92 | 109.92 | 54.96 | 203 | 4857 | 540 | 200.2192 | 20.2277 | -10.2531 | 514.284 | 8.4005 | 53.9923 | 39.03 | 39.03 | 77.7215 | 102.2785 | 55.7989 | 191.9106 | 191.9106 | 93.8226 | 285.7332 | 0.41997 | 42% | 129.2085 | 54.2635 | 37.9844 | 169.2749 | 169.2749 | 22.44% | 11.29% | 11.29% | 80% | 9.03% | 11.667 | 4.508 | 4.508 | 52.5941 | 25.8004 | 31.07% | 31.07%
7 | 203 | 22 | 4858 | 10 | 24.5 | 267.17 | 168.94 | 436.11 | 168.94 | 84.47 | 203 | 4858 | 600 | 200.2192 | 20.2277 | -10.2531 | 574.284 | 9.4005 | 38.9923 | 48.7112 | 48.7112 | 63.4771 | 116.5229 | 42.2965 | 263.0027 | 263.0027 | 144.1993 | 407.202 | 0.54617 | 54.62% | 184.1368 | 100.5701 | 70.3991 | 199.7012 | 199.7012 | 35.25% | 11.25% | 11.25% | 85% | 9.567% | 17.6156 | 4.1265 | 4.1265 | 72.6902 | 38.9552 | 36.4% | 36.4%
7 | 203 | 22 | 4859 | 11 | 26.4 | 414.94 | 164.11 | 579.05 | 164.11 | 82.06 | 203 | 4859 | 660 | 200.2192 | 20.2277 | -10.2531 | 634.284 | 10.4005 | 23.9923 | 57.037 | 57.037 | 44.5256 | 135.4744 | 29.8225 | 429.0583 | 429.0583 | 140.0766 | 569.1349 | 0.62663 | 62.66% | 257.3628 | 161.2721 | 112.8905 | 232.5956 | 232.5956 | 48.54% | 11.27% | 11.27% | 90% | 10.14% | 26.106 | 3.8243 | 3.8243 | 99.8367 | 57.7311 | 42.92% | 42.92%
7 | 203 | 22 | 4860 | 12 | 27.1 | 454.03 | 159.5 | 613.53 | 159.5 | 79.75 | 203 | 4860 | 720 | 200.2192 | 20.2277 | -10.2531 | 694.284 | 11.4005 | 8.9923 | 62.4545 | 62.4545 | 18.49 | 161.51 | 20.434 | 479.8544 | 479.8544 | 136.1418 | 615.9962 | 0.64252 | 64.25% | 278.5535 | 178.9775 | 125.2843 | 234.4486 | 234.4486 | 53.44% | 11.28% | 11.28% | 90% | 10.15% | 28.2791 | 3.7193 | 3.7193 | 105.1789 | 62.5367 | 44.86% | 44.86%
7 | 203 | 22 | 4861 | 13 | 29.9 | 389.92 | 196.19 | 586.11 | 196.19 | 98.1 | 203 | 4861 | 780 | 200.2192 | 20.2277 | -10.2531 | 754.284 | 12.4005 | -6.0077 | 63.0008 | 63.0008 | 12.4934 | 192.4934 | 19.3606 | 412.8677 | 412.8677 | 167.4586 | 580.3264 | 0.64267 | 64.27% | 262.4236 | 168.6517 | 118.0562 | 298.4474 | 298.4474 | 39.56% | 11.23% | 11.23% | 90% | 10.11% | 26.5288 | 3.3338 | 3.3338 | 88.4405 | 58.6661 | 29.63% | 29.63%
7 | 203 | 22 | 4862 | 14 | 30.4 | 394.44 | 191.31 | 585.75 | 191.31 | 95.66 | 203 | 4862 | 840 | 200.2192 | 20.2277 | -10.2531 | 814.284 | 13.4005 | -21.0077 | 58.4113 | 58.4113 | 39.9544 | 219.9544 | 27.5926 | 410.3842 | 410.3842 | 163.2933 | 573.6775 | 0.6426 | 64.26% | 259.417 | 166.7013 | 116.6909 | 305.1117 | 305.1117 | 38.25% | 11.22% | 11.22% | 90% | 10.1% | 26.2019 | 3.2707 | 3.2707 | 85.6979 | 57.9431 | 28.09% | 28.09%
7 | 203 | 22 | 4863 | 15 | 30.7 | 433.28 | 157.64 | 590.92 | 157.64 | 78.82 | 203 | 4863 | 900 | 200.2192 | 20.2277 | -10.2531 | 874.284 | 14.4005 | -36.0077 | 50.5128 | 50.5128 | 60.1674 | 240.1674 | 39.6991 | 431.9564 | 431.9564 | 134.5542 | 566.5106 | 0.64165 | 64.16% | 256.1761 | 164.375 | 115.0625 | 301.9053 | 301.9053 | 38.11% | 11.21% | 11.21% | 90% | 10.09% | 25.8562 | 3.2337 | 3.2337 | 83.6105 | 57.1787 | 27.69% | 27.69%
7 | 203 | 22 | 4864 | 16 | 31 | 275.56 | 148.28 | 423.84 | 148.28 | 74.14 | 203 | 4864 | 960 | 200.2192 | 20.2277 | -10.2531 | 934.284 | 15.4005 | -51.0077 | 41.0167 | 41.0167 | 75.1437 | 255.1437 | 53.069 | 252.2874 | 252.2874 | 126.5649 | 378.8523 | 0.56286 | 56.29% | 171.317 | 96.4271 | 67.499 | 294.6745 | 294.6745 | 22.91% | 11.1% | 11.1% | 85% | 9.433% | 16.1597 | 3.1973 | 3.1973 | 51.6674 | 35.7357 | 17.53% | 17.53%
7 | 203 | 22 | 4865 | 17 | 31 | 224.44 | 123.19 | 347.63 | 123.19 | 61.6 | 203 | 4865 | 1020 | 200.2192 | 20.2277 | -10.2531 | 994.284 | 16.4005 | -66.0077 | 30.8797 | 30.8797 | 87.2453 | 267.2453 | 66.916 | 171.4576 | 171.4576 | 105.1492 | 276.6069 | 0.47372 | 47.37% | 125.0816 | 59.2539 | 41.4777 | 288.8034 | 288.8034 | 14.36% | 11.04% | 11.04% | 80% | 8.828% | 11.0426 | 3.1973 | 3.1973 | 35.3064 | 24.4196 | 12.23% | 12.23%
7 | 203 | 22 | 4866 | 18 | 30.8 | 156.72 | 101.94 | 258.66 | 101.94 | 50.97 | 203 | 4866 | 1080 | 200.2192 | 20.2277 | -10.2531 | 1054.284 | 17.4005 | -81.0077 | 20.6335 | 20.6335 | 97.979 | 277.979 | 80.9487 | 69.9652 | 69.9652 | 87.0112 | 156.9765 | 0.2194 | 21.94% | 70.9848 | 15.5742 | 10.9019 | 282.4281 | 282.4281 | 3.86% | 10.97% | 10.97% | 80% | 8.776% | 6.2296 | 3.2215 | 3.2215 | 20.0687 | 13.7763 | 7.106% | 7.106%
7 | 203 | 22 | 4867 | 19 | 30 | 92.22 | 77.44 | 169.66 | 77.44 | 38.72 | 203 | 4867 | 1140 | 200.2192 | 20.2277 | -10.2531 | 1114.284 | 18.4005 | -96.0077 | 10.6434 | 10.6434 | 108.2849 | 288.2849 | 95.0159 | -43.6558 | 0 | 66.0992 | 66.0992 | -0.60929 | 0% | 29.89 | 0 | 0 | 269.4209 | 269.4209 | 0% | 10.95% | 0% | 80% | 0% | 0 | 3.321 | 3.321 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4868 | 20 | 28.4 | 28.19 | 36.72 | 64.91 | 36.72 | 18.36 | 203 | 4868 | 1200 | 200.2192 | 20.2277 | -10.2531 | 1174.284 | 19.4005 | -111.0077 | 1.2369 | 1.2369 | 118.8172 | 298.8172 | 108.9955 | 0 | 0 | 31.3425 | 31.3425 | -2.2826 | 0% | 14.1731 | 0 | 0 | 274.6877 | 274.6877 | 0% | 11% | 0% | 80% | 0% | 0 | 3.5335 | 3.5335 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4869 | 21 | 25.8 | 0 | 5.69 | 5.69 | 5.69 | 2.85 | 203 | 4869 | 1260 | 200.2192 | 20.2277 | -10.2531 | 1234.284 | 20.4005 | -126.0077 | -7.2284 | 0 | 120.323 | 300.323 | 110.9161 | 0 | 0 | 4.8567 | 4.8567 | -20.2425 | 0% | 2.1962 | 0 | 0 | 1.7524 | 1.7524 | 0% | 11.1% | 0% | 80% | 0% | 0 | 3.917 | 3.917 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4870 | 22 | 22.4 | 0 | 0 | 0 | 0 | 0 | 203 | 4870 | 1320 | 200.2192 | 20.2277 | -10.2531 | 1294.284 | 21.4005 | -141.0077 | -14.3291 | 0 | 120.323 | 300.323 | 110.9161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.1904 | 0 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.4899 | 4.4899 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4871 | 23 | 20.1 | 0 | 0 | 0 | 0 | 0 | 203 | 4871 | 1380 | 200.2192 | 20.2277 | -10.2531 | 1354.284 | 22.4005 | -156.0077 | -19.5799 | 0 | 120.323 | 300.323 | 110.9161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1271 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
7 | 203 | 22 | 4872 | 24 | 19.2 | 0 | 0 | 0 | 0 | 0 | 203 | 4872 | 1440 | 200.2192 | 20.2277 | -10.2531 | 1414.284 | 23.4005 | -171.0077 | -22.5036 | 0 | 120.323 | 300.323 | 110.9161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.9302 | 0 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4873 | 1 | 18.1 | 0 | 0 | 0 | 0 | 0 | 204 | 4873 | 60 | 201.2055 | 20.0365 | -10.5399 | 34.284 | 0.39574 | 174.064 | -22.9707 | 0 | 120.0198 | 59.9802 | 110.7178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.197 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4874 | 2 | 17.7 | 0 | 0 | 0 | 0 | 0 | 204 | 4874 | 120 | 201.2055 | 20.0365 | -10.5399 | 94.284 | 1.3957 | 159.064 | -20.5628 | 0 | 120.0198 | 59.9802 | 110.7178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3336 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4875 | 3 | 16.9 | 0 | 0 | 0 | 0 | 0 | 204 | 4875 | 180 | 201.2055 | 20.0365 | -10.5399 | 154.284 | 2.3957 | 144.064 | -15.7391 | 0 | 120.0198 | 59.9802 | 110.7178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0797 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4876 | 4 | 16.9 | 0 | 0 | 0 | 0 | 0 | 204 | 4876 | 240 | 201.2055 | 20.0365 | -10.5399 | 214.284 | 3.3957 | 129.064 | -8.9621 | 0 | 120.0198 | 59.9802 | 110.7178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0797 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4877 | 5 | 16.1 | 0 | 0 | 0 | 0 | 0 | 204 | 4877 | 300 | 201.2055 | 20.0365 | -10.5399 | 274.284 | 4.3957 | 114.064 | -0.72615 | 0 | 120.0198 | 59.9802 | 110.7178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.81748 | 0.81748 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4878 | 6 | 16.1 | 0.61 | 6.17 | 6.78 | 6.17 | 3.09 | 204 | 4878 | 360 | 201.2055 | 20.0365 | -10.5399 | 334.284 | 5.3957 | 99.064 | 8.5291 | 8.5291 | 110.262 | 69.738 | 97.8917 | 0 | 0 | 5.2664 | 5.2664 | -22.6357 | 0% | 2.3815 | 0 | 0 | 11.5053 | 11.5053 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4879 | 7 | 17.1 | 28.67 | 37 | 65.67 | 37 | 18.5 | 204 | 4879 | 420 | 201.2055 | 20.0365 | -10.5399 | 394.284 | 6.3957 | 84.064 | 18.4336 | 18.4336 | 99.9446 | 80.0554 | 83.8148 | 9.7689 | 9.7689 | 31.5815 | 41.3504 | -2.127 | 0% | 18.6986 | 0 | 0 | 180.3857 | 180.3857 | 0% | 11.47% | 11.47% | 80% | 9.178% | 1.7162 | 5.5443 | 5.5443 | 9.5154 | 3.7953 | 5.275% | 5.275%
7 | 204 | 23 | 4880 | 8 | 19.3 | 113.89 | 76.53 | 190.42 | 76.53 | 38.27 | 204 | 4880 | 480 | 201.2055 | 20.0365 | -10.5399 | 454.284 | 7.3957 | 69.064 | 28.6569 | 28.6569 | 89.3476 | 90.6524 | 69.747 | 82.2101 | 82.2101 | 65.3224 | 147.5326 | 0.01569 | 1.569% | 66.7142 | 1.0467 | 0.7327 | 156.1202 | 156.1202 | 0.4693% | 11.38% | 11.38% | 80% | 9.102% | 6.0721 | 5.0828 | 5.0828 | 30.8631 | 13.428 | 19.77% | 19.77%
7 | 204 | 23 | 4881 | 9 | 22.8 | 172.64 | 139.11 | 311.75 | 139.11 | 69.56 | 204 | 4881 | 540 | 201.2055 | 20.0365 | -10.5399 | 514.284 | 8.3957 | 54.064 | 38.8478 | 38.8478 | 77.6071 | 102.3929 | 55.8248 | 154.6044 | 154.6044 | 118.7378 | 273.3422 | 0.40652 | 40.65% | 123.6053 | 50.2484 | 35.1739 | 167.5985 | 167.5985 | 20.99% | 11.27% | 11.27% | 80% | 9.017% | 11.1451 | 4.4183 | 4.4183 | 49.2424 | 24.6465 | 29.38% | 29.38%
7 | 204 | 23 | 4882 | 10 | 24.6 | 236.67 | 175.69 | 412.36 | 175.69 | 87.85 | 204 | 4882 | 600 | 201.2055 | 20.0365 | -10.5399 | 574.284 | 9.3957 | 39.064 | 48.5223 | 48.5223 | 63.3656 | 116.6344 | 42.2918 | 233.6734 | 233.6734 | 149.9608 | 383.6342 | 0.53089 | 53.09% | 173.4794 | 92.0983 | 64.4688 | 199.6428 | 199.6428 | 32.29% | 11.25% | 11.25% | 85% | 9.56% | 16.584 | 4.1099 | 4.1099 | 68.1594 | 36.6741 | 34.14% | 34.14%
7 | 204 | 23 | 4883 | 11 | 26.8 | 452.78 | 187.36 | 640.14 | 187.36 | 93.68 | 204 | 4883 | 660 | 201.2055 | 20.0365 | -10.5399 | 634.284 | 10.3957 | 24.064 | 56.8383 | 56.8383 | 44.4525 | 135.5475 | 29.768 | 469.5 | 469.5 | 159.9218 | 629.4217 | 0.64496 | 64.5% | 284.6245 | 183.5727 | 128.5009 | 242.7605 | 242.7605 | 52.93% | 11.29% | 11.29% | 90% | 10.16% | 28.9161 | 3.7639 | 3.7639 | 108.8367 | 63.9454 | 44.83% | 44.83%
7 | 204 | 23 | 4884 | 12 | 28.4 | 557.08 | 175.33 | 732.41 | 175.33 | 87.67 | 204 | 4884 | 720 | 201.2055 | 20.0365 | -10.5399 | 694.284 | 11.3957 | 9.064 | 62.253 | 62.253 | 18.5357 | 161.4643 | 20.2937 | 590.3883 | 590.3883 | 149.6535 | 740.0418 | 0.67328 | 67.33% | 334.6469 | 225.3094 | 157.7166 | 264.537 | 264.537 | 59.62% | 11.32% | 11.32% | 90% | 10.19% | 34.1068 | 3.5335 | 3.5335 | 120.5156 | 75.4241 | 45.56% | 45.56%
7 | 204 | 23 | 4885 | 13 | 29.8 | 481.86 | 218.25 | 700.11 | 218.25 | 109.13 | 204 | 4885 | 780 | 201.2055 | 20.0365 | -10.5399 | 754.284 | 12.3957 | -5.936 | 62.8225 | 62.8225 | 12.2817 | 192.2817 | 19.1579 | 511.6633 | 511.6633 | 186.288 | 697.9513 | 0.66956 | 66.96% | 315.6136 | 211.3229 | 147.926 | 304.7355 | 304.7355 | 48.54% | 11.3% | 11.3% | 90% | 10.17% | 32.0894 | 3.3466 | 3.3466 | 107.3896 | 70.9628 | 35.24% | 35.24%
7 | 204 | 23 | 4886 | 14 | 30.7 | 401.39 | 217.58 | 618.97 | 217.58 | 108.79 | 204 | 4886 | 840 | 201.2055 | 20.0365 | -10.5399 | 814.284 | 13.3957 | -20.936 | 58.2737 | 58.2737 | 39.6709 | 219.6709 | 27.4195 | 418.8925 | 418.8925 | 185.7161 | 604.6086 | 0.65188 | 65.19% | 273.404 | 178.2262 | 124.7584 | 311.6746 | 311.6746 | 40.03% | 11.24% | 11.24% | 90% | 10.11% | 27.6502 | 3.2337 | 3.2337 | 89.4118 | 61.1459 | 28.69% | 28.69%
7 | 204 | 23 | 4887 | 15 | 31.3 | 512.78 | 214.22 | 727 | 214.22 | 107.11 | 204 | 4887 | 900 | 201.2055 | 20.0365 | -10.5399 | 874.284 | 14.3957 | -35.936 | 50.4072 | 50.4072 | 59.8957 | 239.8957 | 39.5624 | 513.0049 | 513.0049 | 182.8482 | 695.8531 | 0.6736 | 67.36% | 314.6648 | 211.9571 | 148.37 | 323.8015 | 323.8015 | 45.82% | 11.29% | 11.29% | 90% | 10.16% | 31.9654 | 3.1616 | 3.1616 | 101.0603 | 70.6886 | 31.21% | 31.21%
7 | 204 | 23 | 4888 | 16 | 31.5 | 510.28 | 167.56 | 677.84 | 167.56 | 83.78 | 204 | 4888 | 960 | 201.2055 | 20.0365 | -10.5399 | 934.284 | 15.3957 | -50.936 | 40.9285 | 40.9285 | 74.902 | 254.902 | 52.9587 | 469.2111 | 469.2111 | 143.0214 | 612.2325 | 0.65645 | 65.65% | 276.8515 | 181.7405 | 127.2183 | 324.8129 | 324.8129 | 39.17% | 11.23% | 11.23% | 90% | 10.11% | 27.9894 | 3.1381 | 3.1381 | 87.833 | 61.8962 | 27.04% | 27.04%
7 | 204 | 23 | 4889 | 17 | 30.7 | 435.5 | 138.56 | 574.06 | 138.56 | 69.28 | 204 | 4889 | 1020 | 201.2055 | 20.0365 | -10.5399 | 994.284 | 16.3957 | -65.936 | 30.7978 | 30.7978 | 87.0294 | 267.0294 | 66.8261 | 334.7189 | 334.7189 | 118.2684 | 452.9872 | 0.60096 | 60.1% | 204.8408 | 123.1014 | 86.171 | 313.2456 | 313.2456 | 27.51% | 11.15% | 11.15% | 85% | 9.476% | 19.4099 | 3.2337 | 3.2337 | 62.7654 | 42.9233 | 20.04% | 20.04%
7 | 204 | 23 | 4890 | 18 | 30.3 | 225.42 | 141.67 | 367.09 | 141.67 | 70.84 | 204 | 4890 | 1080 | 201.2055 | 20.0365 | -10.5399 | 1054.284 | 17.3957 | -80.936 | 20.5499 | 20.5499 | 97.7818 | 277.7818 | 80.8766 | 101.8247 | 101.8247 | 120.9229 | 222.7476 | 0.38739 | 38.74% | 100.7265 | 39.0208 | 27.3146 | 288.1151 | 288.1151 | 9.48% | 11.02% | 11.02% | 80% | 8.82% | 8.8841 | 3.2832 | 3.2832 | 29.1678 | 19.6463 | 10.12% | 10.12%
7 | 204 | 23 | 4891 | 19 | 29.3 | 109.31 | 77.78 | 187.09 | 77.78 | 38.89 | 204 | 4891 | 1140 | 201.2055 | 20.0365 | -10.5399 | 1114.284 | 18.3957 | -95.936 | 10.5522 | 10.5522 | 108.1007 | 288.1007 | 94.9612 | -51.6203 | 0 | 66.3894 | 66.3894 | -0.62496 | 0% | 30.0213 | 0 | 0 | 259.9593 | 259.9593 | 0% | 10.98% | 0% | 80% | 0% | 0 | 3.4118 | 3.4118 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4892 | 20 | 28.2 | 40.28 | 38.89 | 79.17 | 38.89 | 19.45 | 204 | 4892 | 1200 | 201.2055 | 20.0365 | -10.5399 | 1174.284 | 19.3957 | -110.936 | 1.133 | 1.133 | 118.6432 | 298.6432 | 108.9599 | 0 | 0 | 33.1947 | 33.1947 | -2.123 | 0% | 15.0106 | 0 | 0 | 274.7022 | 274.7022 | 0% | 11.01% | 0% | 80% | 0% | 0 | 3.5613 | 3.5613 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4893 | 21 | 26.3 | 0 | 7.22 | 7.22 | 7.22 | 3.61 | 204 | 4893 | 1260 | 201.2055 | 20.0365 | -10.5399 | 1234.284 | 20.3957 | -125.936 | -7.3493 | 0 | 120.0198 | 300.0198 | 110.7178 | 0 | 0 | 6.1627 | 6.1627 | -15.6105 | 0% | 2.7868 | 0 | 0 | 2.0784 | 2.0784 | 0% | 11.08% | 0% | 80% | 0% | 0 | 3.8396 | 3.8396 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4894 | 22 | 23.5 | 0 | 0 | 0 | 0 | 0 | 204 | 4894 | 1320 | 201.2055 | 20.0365 | -10.5399 | 1294.284 | 21.3957 | -140.936 | -14.4703 | 0 | 120.0198 | 300.0198 | 110.7178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.3865 | 0 | 0% | 11.2% | 0% | 80% | 0% | 0 | 4.2957 | 4.2957 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4895 | 23 | 21.3 | 0 | 0 | 0 | 0 | 0 | 204 | 4895 | 1380 | 201.2055 | 20.0365 | -10.5399 | 1354.284 | 22.3957 | -155.936 | -19.7425 | 0 | 120.0198 | 300.0198 | 110.7178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2663 | 0 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6926 | 4.6926 | 0 | 0 | 0% | 0%
7 | 204 | 23 | 4896 | 24 | 20.7 | 0 | 0 | 0 | 0 | 0 | 204 | 4896 | 1440 | 201.2055 | 20.0365 | -10.5399 | 1414.284 | 23.3957 | -170.936 | -22.6857 | 0 | 120.0198 | 300.0198 | 110.7178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7077 | 0 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.8067 | 4.8067 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4897 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 205 | 4897 | 60 | 202.1918 | 19.8401 | -10.8166 | 34.284 | 0.39112 | 174.1331 | -23.1714 | 0 | 119.709 | 60.291 | 110.5141 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.8262 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4898 | 2 | 19.8 | 0 | 0 | 0 | 0 | 0 | 205 | 4898 | 120 | 202.1918 | 19.8401 | -10.8166 | 94.284 | 1.3911 | 159.1331 | -20.7693 | 0 | 119.709 | 60.291 | 110.5141 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5586 | 0 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9826 | 4.9826 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4899 | 3 | 18.4 | 0 | 0 | 0 | 0 | 0 | 205 | 4899 | 180 | 202.1918 | 19.8401 | -10.8166 | 154.284 | 2.3911 | 144.1331 | -15.9447 | 0 | 119.709 | 60.291 | 110.5141 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1198 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4900 | 4 | 17.6 | 0 | 0 | 0 | 0 | 0 | 205 | 4900 | 240 | 202.1918 | 19.8401 | -10.8166 | 214.284 | 3.3911 | 129.1331 | -9.1626 | 0 | 119.709 | 60.291 | 110.5141 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.339 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4901 | 5 | 17.1 | 0 | 0 | 0 | 0 | 0 | 205 | 4901 | 300 | 202.1918 | 19.8401 | -10.8166 | 274.284 | 4.3911 | 114.1331 | -0.92007 | 0 | 119.709 | 60.291 | 110.5141 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.2942 | 5.2942 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4902 | 6 | 16.8 | 0.56 | 5.42 | 5.98 | 5.42 | 2.71 | 205 | 4902 | 360 | 202.1918 | 19.8401 | -10.8166 | 334.284 | 5.3911 | 99.1331 | 8.3413 | 8.3413 | 110.1743 | 69.8257 | 97.9729 | 0 | 0 | 4.6263 | 4.6263 | -25.5389 | 0% | 2.092 | 0 | 0 | 17.074 | 17.074 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4903 | 7 | 18 | 25.89 | 36.17 | 62.06 | 36.17 | 18.09 | 205 | 4903 | 420 | 202.1918 | 19.8401 | -10.8166 | 394.284 | 6.3911 | 84.1331 | 18.2501 | 18.2501 | 99.8438 | 80.1562 | 83.8787 | 8.8156 | 8.8156 | 30.873 | 39.6886 | -2.199 | 0% | 17.9472 | 0 | 0 | 189.0727 | 189.0727 | 0% | 11.44% | 11.44% | 80% | 9.149% | 1.6419 | 5.3514 | 5.3514 | 8.7865 | 3.6309 | 4.647% | 4.647%
7 | 205 | 24 | 4904 | 8 | 21 | 119.78 | 77.17 | 196.95 | 77.17 | 38.59 | 205 | 4904 | 480 | 202.1918 | 19.8401 | -10.8166 | 454.284 | 7.3911 | 69.1331 | 28.475 | 28.475 | 89.2355 | 90.7645 | 69.7923 | 86.7808 | 86.7808 | 65.8687 | 152.6495 | 0.066603 | 6.66% | 69.0281 | 4.5975 | 3.2183 | 167.8952 | 167.8952 | 1.917% | 11.32% | 11.32% | 80% | 9.053% | 6.2492 | 4.7493 | 4.7493 | 29.6793 | 13.8195 | 17.68% | 17.68%
7 | 205 | 24 | 4905 | 9 | 23.6 | 230.14 | 121.89 | 352.03 | 121.89 | 60.95 | 205 | 4905 | 540 | 202.1918 | 19.8401 | -10.8166 | 514.284 | 8.3911 | 54.1331 | 38.6636 | 38.6636 | 77.4865 | 102.5135 | 55.8479 | 206.8017 | 206.8017 | 104.0396 | 310.8414 | 0.46003 | 46% | 140.5625 | 64.6627 | 45.2639 | 190.0754 | 190.0754 | 23.81% | 11.26% | 11.26% | 85% | 9.567% | 13.4474 | 4.2784 | 4.2784 | 57.534 | 29.7378 | 30.27% | 30.27%
7 | 205 | 24 | 4906 | 10 | 26.2 | 337.5 | 130.14 | 467.64 | 130.14 | 65.07 | 205 | 4906 | 600 | 202.1918 | 19.8401 | -10.8166 | 574.284 | 9.3911 | 39.1331 | 48.3309 | 48.3309 | 63.2474 | 116.7526 | 42.284 | 334.2568 | 334.2568 | 111.0814 | 445.3382 | 0.57638 | 57.64% | 201.3819 | 116.0721 | 81.2505 | 240.4047 | 240.4047 | 33.8% | 11.23% | 11.23% | 85% | 9.546% | 19.2247 | 3.8549 | 3.8549 | 74.1094 | 42.5138 | 30.83% | 30.83%
7 | 205 | 24 | 4907 | 11 | 28.4 | 439.03 | 122.22 | 561.25 | 122.22 | 61.11 | 205 | 4907 | 660 | 202.1918 | 19.8401 | -10.8166 | 634.284 | 10.3911 | 24.1331 | 56.6362 | 56.6362 | 44.372 | 135.628 | 29.7099 | 456.5612 | 456.5612 | 104.3213 | 560.8825 | 0.63152 | 63.15% | 253.6311 | 160.1727 | 112.1209 | 276.0511 | 276.0511 | 40.62% | 11.24% | 11.24% | 90% | 10.12% | 25.6608 | 3.5335 | 3.5335 | 90.6719 | 56.7466 | 32.85% | 32.85%
7 | 205 | 24 | 4908 | 12 | 29.4 | 508.28 | 136.33 | 644.61 | 136.33 | 68.17 | 205 | 4908 | 720 | 202.1918 | 19.8401 | -10.8166 | 694.284 | 11.3911 | 9.1331 | 62.0469 | 62.0469 | 18.5737 | 161.4263 | 20.1488 | 540.1982 | 540.1982 | 116.3649 | 656.5631 | 0.65982 | 65.98% | 296.8978 | 195.9006 | 137.1304 | 284.5307 | 284.5307 | 48.2% | 11.28% | 11.28% | 90% | 10.15% | 30.1353 | 3.3986 | 3.3986 | 102.4172 | 66.6415 | 36% | 36%
7 | 205 | 24 | 4909 | 13 | 29.1 | 410.83 | 228.61 | 639.44 | 228.61 | 114.31 | 205 | 4909 | 780 | 202.1918 | 19.8401 | -10.8166 | 754.284 | 12.3911 | -5.8669 | 62.6384 | 62.6384 | 12.0756 | 192.0756 | 18.951 | 437.5082 | 437.5082 | 195.1308 | 632.639 | 0.65339 | 65.34% | 286.0794 | 186.9207 | 130.8445 | 277.1099 | 277.1099 | 47.22% | 11.27% | 11.27% | 90% | 10.14% | 29.0125 | 3.4383 | 3.4383 | 99.7541 | 64.1585 | 36% | 36%
7 | 205 | 24 | 4910 | 14 | 30 | 460.08 | 245.28 | 705.36 | 245.28 | 122.64 | 205 | 4910 | 840 | 202.1918 | 19.8401 | -10.8166 | 814.284 | 13.3911 | -20.8669 | 58.1299 | 58.1299 | 39.3887 | 219.3887 | 27.2453 | 481.6458 | 481.6458 | 209.3596 | 691.0054 | 0.66881 | 66.88% | 312.4726 | 208.9846 | 146.2892 | 295.6461 | 295.6461 | 49.48% | 11.29% | 11.29% | 90% | 10.16% | 31.7561 | 3.321 | 3.321 | 105.4621 | 70.2258 | 35.67% | 35.67%
7 | 205 | 24 | 4911 | 15 | 29.8 | 634.36 | 146.86 | 781.22 | 146.86 | 73.43 | 205 | 4911 | 900 | 202.1918 | 19.8401 | -10.8166 | 874.284 | 14.3911 | -35.8669 | 50.2955 | 50.2955 | 59.6228 | 239.6228 | 39.4262 | 636.9104 | 636.9104 | 125.3529 | 762.2633 | 0.6809 | 68.09% | 344.6955 | 234.7047 | 164.2933 | 292.4291 | 292.4291 | 56.18% | 11.33% | 11.33% | 90% | 10.2% | 35.1537 | 3.3466 | 3.3466 | 117.6448 | 77.7394 | 40.23% | 40.23%
7 | 205 | 24 | 4912 | 16 | 30.6 | 542.5 | 158.33 | 700.83 | 158.33 | 79.17 | 205 | 4912 | 960 | 202.1918 | 19.8401 | -10.8166 | 934.284 | 15.3911 | -50.8669 | 40.8345 | 40.8345 | 74.6583 | 254.6583 | 52.8497 | 501.0425 | 501.0425 | 135.1431 | 636.1856 | 0.65911 | 65.91% | 287.6831 | 189.6136 | 132.7295 | 302.798 | 302.798 | 43.83% | 11.26% | 11.26% | 90% | 10.13% | 29.1447 | 3.2459 | 3.2459 | 94.6021 | 64.451 | 31.24% | 31.24%
7 | 205 | 24 | 4913 | 17 | 30.4 | 449.94 | 124.44 | 574.38 | 124.44 | 62.22 | 205 | 4913 | 1020 | 202.1918 | 19.8401 | -10.8166 | 994.284 | 16.3911 | -65.8669 | 30.7103 | 30.7103 | 86.8112 | 266.8112 | 66.7381 | 347.9498 | 347.9498 | 106.2162 | 454.166 | 0.60013 | 60.01% | 205.3739 | 123.2506 | 86.2754 | 290.9527 | 290.9527 | 29.65% | 11.15% | 11.15% | 85% | 9.481% | 19.4716 | 3.2707 | 3.2707 | 63.6854 | 43.0597 | 21.89% | 21.89%
7 | 205 | 24 | 4914 | 18 | 28.7 | 296.44 | 103.89 | 400.33 | 103.89 | 51.95 | 205 | 4914 | 1080 | 202.1918 | 19.8401 | -10.8166 | 1054.284 | 17.3911 | -80.8669 | 20.461 | 20.461 | 97.5824 | 277.5824 | 80.8067 | 135.4839 | 135.4839 | 88.6757 | 224.1595 | 0.37522 | 37.52% | 101.3649 | 38.0338 | 26.6237 | 246.3194 | 246.3194 | 10.81% | 11.08% | 11.08% | 80% | 8.861% | 8.9821 | 3.4923 | 3.4923 | 31.368 | 19.8632 | 12.73% | 12.73%
7 | 205 | 24 | 4915 | 19 | 27 | 144.17 | 82.22 | 226.39 | 82.22 | 41.11 | 205 | 4915 | 1140 | 202.1918 | 19.8401 | -10.8166 | 1114.284 | 18.3911 | -95.8669 | 10.4556 | 10.4556 | 107.9147 | 287.9147 | 94.909 | -67.9825 | 0 | 70.1792 | 70.1792 | -0.61635 | 0% | 31.735 | 0 | 0 | 200.1741 | 200.1741 | 0% | 11.07% | 0% | 80% | 0% | 0 | 3.7341 | 3.7341 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4916 | 20 | 26.2 | 40.61 | 45.5 | 86.11 | 45.5 | 22.75 | 205 | 4916 | 1200 | 202.1918 | 19.8401 | -10.8166 | 1174.284 | 19.3911 | -110.8669 | 1.0237 | 1.0237 | 118.4675 | 298.4675 | 108.927 | 0 | 0 | 38.8367 | 38.8367 | -1.8061 | 0% | 17.5619 | 0 | 0 | 210.7786 | 210.7786 | 0% | 11.09% | 0% | 80% | 0% | 0 | 3.8549 | 3.8549 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4917 | 21 | 24.9 | 0 | 4.92 | 4.92 | 4.92 | 2.46 | 205 | 4917 | 1260 | 202.1918 | 19.8401 | -10.8166 | 1234.284 | 20.3911 | -125.8669 | -7.4757 | 0 | 119.709 | 299.709 | 110.5141 | 0 | 0 | 4.1995 | 4.1995 | -23.9927 | 0% | 1.899 | 0 | 0 | 0.2082 | 0.2082 | 0% | 11.14% | 0% | 80% | 0% | 0 | 4.0608 | 4.0608 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4918 | 22 | 23.4 | 0 | 0 | 0 | 0 | 0 | 205 | 4918 | 1320 | 202.1918 | 19.8401 | -10.8166 | 1294.284 | 21.3911 | -140.8669 | -14.617 | 0 | 119.709 | 299.709 | 110.5141 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.3618 | 0 | 0% | 11.2% | 0% | 80% | 0% | 0 | 4.313 | 4.313 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4919 | 23 | 22.3 | 0 | 0 | 0 | 0 | 0 | 205 | 4919 | 1380 | 202.1918 | 19.8401 | -10.8166 | 1354.284 | 22.3911 | -155.8669 | -19.9107 | 0 | 119.709 | 299.709 | 110.5141 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.4658 | 0 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.508 | 4.508 | 0 | 0 | 0% | 0%
7 | 205 | 24 | 4920 | 24 | 21.4 | 0 | 0 | 0 | 0 | 0 | 205 | 4920 | 1440 | 202.1918 | 19.8401 | -10.8166 | 1414.284 | 23.3911 | -170.8669 | -22.8731 | 0 | 119.709 | 299.709 | 110.5141 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.265 | 0 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6738 | 4.6738 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4921 | 1 | 20.3 | 0 | 0 | 0 | 0 | 0 | 206 | 4921 | 60 | 203.1781 | 19.6386 | -11.083 | 34.284 | 0.38668 | 174.1998 | -23.3771 | 0 | 119.3906 | 60.6094 | 110.3052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.3003 | 0 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.8842 | 4.8842 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4922 | 2 | 20 | 0 | 0 | 0 | 0 | 0 | 206 | 4922 | 120 | 203.1781 | 19.6386 | -11.083 | 94.284 | 1.3867 | 159.1998 | -20.9802 | 0 | 119.3906 | 60.6094 | 110.3052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.1036 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4923 | 3 | 18.6 | 0 | 0 | 0 | 0 | 0 | 206 | 4923 | 180 | 203.1781 | 19.6386 | -11.083 | 154.284 | 2.3867 | 144.1998 | -16.154 | 0 | 119.3906 | 60.6094 | 110.3052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5832 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4924 | 4 | 18.2 | 0 | 0 | 0 | 0 | 0 | 206 | 4924 | 240 | 203.1781 | 19.6386 | -11.083 | 214.284 | 3.3867 | 129.1998 | -9.3662 | 0 | 119.3906 | 60.6094 | 110.3052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1928 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3093 | 5.3093 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4925 | 5 | 17.7 | 0 | 0 | 0 | 0 | 0 | 206 | 4925 | 300 | 203.1781 | 19.6386 | -11.083 | 274.284 | 4.3867 | 114.1998 | -1.1165 | 0 | 119.3906 | 60.6094 | 110.3052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.6775 | 7.6775 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4926 | 6 | 17.6 | 0.56 | 4.78 | 5.34 | 4.78 | 2.39 | 206 | 4926 | 360 | 203.1781 | 19.6386 | -11.083 | 334.284 | 5.3867 | 99.1998 | 8.1514 | 8.1514 | 110.0815 | 69.9185 | 98.0523 | 0 | 0 | 4.08 | 4.08 | -28.6271 | 0% | 1.845 | 0 | 0 | 19.689 | 19.689 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4927 | 7 | 18.1 | 40.33 | 38 | 78.33 | 38 | 19 | 206 | 4927 | 420 | 203.1781 | 19.6386 | -11.083 | 394.284 | 6.3867 | 84.1998 | 18.0647 | 18.0647 | 99.7377 | 80.2623 | 83.9403 | 13.7295 | 13.7295 | 32.435 | 46.1645 | -1.7729 | 0% | 20.8756 | 0 | 0 | 192.5657 | 192.5657 | 0% | 11.43% | 11.43% | 80% | 9.145% | 1.909 | 5.3303 | 5.3303 | 10.1755 | 4.2216 | 5.284% | 5.284%
7 | 206 | 25 | 4928 | 8 | 20.5 | 140.78 | 55.33 | 196.11 | 55.33 | 27.67 | 206 | 4928 | 480 | 203.1781 | 19.6386 | -11.083 | 454.284 | 7.3867 | 69.1998 | 28.2911 | 28.2911 | 89.1178 | 90.8822 | 69.8352 | 102.3941 | 102.3941 | 47.2271 | 149.6212 | 0.044357 | 4.436% | 67.6587 | 3.0012 | 2.1008 | 169.1112 | 169.1112 | 1.242% | 11.33% | 11.33% | 80% | 9.067% | 6.1348 | 4.8453 | 4.8453 | 29.7249 | 13.5666 | 17.58% | 17.58%
7 | 206 | 25 | 4929 | 9 | 22.4 | 257.22 | 77.78 | 335 | 77.78 | 38.89 | 206 | 4929 | 540 | 203.1781 | 19.6386 | -11.083 | 514.284 | 8.3867 | 54.1998 | 38.4772 | 38.4772 | 77.36 | 102.64 | 55.8683 | 231.9587 | 231.9587 | 66.3894 | 298.3481 | 0.43693 | 43.69% | 134.913 | 58.948 | 41.2636 | 178.7456 | 178.7456 | 23.09% | 11.29% | 11.29% | 80% | 9.029% | 12.1808 | 4.4899 | 4.4899 | 54.6903 | 26.9367 | 30.6% | 30.6%
7 | 206 | 25 | 4930 | 10 | 25.4 | 340.83 | 119.78 | 460.61 | 119.78 | 59.89 | 206 | 4930 | 600 | 203.1781 | 19.6386 | -11.083 | 574.284 | 9.3867 | 39.1998 | 48.137 | 48.137 | 63.1226 | 116.8774 | 42.2732 | 338.6348 | 338.6348 | 102.2386 | 440.8735 | 0.57022 | 57.02% | 199.363 | 113.6807 | 79.5765 | 225.7185 | 225.7185 | 35.25% | 11.25% | 11.25% | 85% | 9.559% | 19.0562 | 3.9802 | 3.9802 | 75.8471 | 42.1411 | 33.6% | 33.6%
7 | 206 | 25 | 4931 | 11 | 27.1 | 428.89 | 114.31 | 543.2 | 114.31 | 57.16 | 206 | 4931 | 660 | 203.1781 | 19.6386 | -11.083 | 634.284 | 10.3867 | 24.1998 | 56.4308 | 56.4308 | 44.2841 | 135.7159 | 29.6482 | 447.3486 | 447.3486 | 97.5697 | 544.9183 | 0.62146 | 62.15% | 246.412 | 153.1358 | 107.1951 | 250.7659 | 250.7659 | 42.75% | 11.25% | 11.25% | 90% | 10.13% | 24.9545 | 3.7193 | 3.7193 | 92.8137 | 55.1847 | 37.01% | 37.01%
7 | 206 | 25 | 4932 | 12 | 28.1 | 521.94 | 122.72 | 644.66 | 122.72 | 61.36 | 206 | 4932 | 720 | 203.1781 | 19.6386 | -11.083 | 694.284 | 11.3867 | 9.1998 | 61.8363 | 61.8363 | 18.604 | 161.396 | 19.9994 | 556.3334 | 556.3334 | 104.7481 | 661.0815 | 0.65671 | 65.67% | 298.9411 | 196.3184 | 137.4228 | 259.1454 | 259.1454 | 53.03% | 11.29% | 11.29% | 90% | 10.16% | 30.3757 | 3.5753 | 3.5753 | 108.6027 | 67.1732 | 41.91% | 41.91%
7 | 206 | 25 | 4933 | 13 | 29.8 | 491.33 | 182.64 | 673.97 | 182.64 | 91.32 | 206 | 4933 | 780 | 203.1781 | 19.6386 | -11.083 | 754.284 | 12.3867 | -5.8002 | 62.4487 | 62.4487 | 11.8752 | 191.8752 | 18.7401 | 524.7958 | 524.7958 | 155.893 | 680.6888 | 0.66615 | 66.62% | 307.8075 | 205.0468 | 143.5327 | 288.9567 | 288.9567 | 49.67% | 11.29% | 11.29% | 90% | 10.16% | 31.2699 | 3.3466 | 3.3466 | 104.6473 | 69.1506 | 36.22% | 36.22%
7 | 206 | 25 | 4934 | 14 | 28.8 | 483.75 | 121.61 | 605.36 | 121.61 | 60.81 | 206 | 4934 | 840 | 203.1781 | 19.6386 | -11.083 | 814.284 | 13.3867 | -20.8002 | 57.9798 | 57.9798 | 39.1082 | 219.1082 | 27.0701 | 508.0491 | 508.0491 | 103.8006 | 611.8498 | 0.64725 | 64.72% | 276.6785 | 179.0801 | 125.3561 | 265.3443 | 265.3443 | 47.24% | 11.26% | 11.26% | 90% | 10.13% | 28.0409 | 3.4787 | 3.4787 | 97.5454 | 62.01 | 36.76% | 36.76%
7 | 206 | 25 | 4935 | 15 | 28.3 | 326.06 | 139.5 | 465.56 | 139.5 | 69.75 | 206 | 4935 | 900 | 203.1781 | 19.6386 | -11.083 | 874.284 | 14.3867 | -35.8002 | 50.1778 | 50.1778 | 59.349 | 239.349 | 39.2907 | 328.5678 | 328.5678 | 119.0707 | 447.6385 | 0.58742 | 58.74% | 202.4221 | 118.9063 | 83.2344 | 259.8566 | 259.8566 | 32.03% | 11.19% | 11.19% | 85% | 9.512% | 19.2554 | 3.5474 | 3.5474 | 68.3056 | 42.5815 | 26.29% | 26.29%
7 | 206 | 25 | 4936 | 16 | 28.5 | 368.56 | 172.44 | 541 | 172.44 | 86.22 | 206 | 4936 | 960 | 203.1781 | 19.6386 | -11.083 | 934.284 | 15.3867 | -50.8002 | 40.7348 | 40.7348 | 74.4126 | 254.4126 | 52.7422 | 341.9264 | 341.9264 | 147.1867 | 489.1132 | 0.60664 | 60.66% | 221.177 | 134.174 | 93.9218 | 252.8804 | 252.8804 | 37.14% | 11.21% | 11.21% | 85% | 9.526% | 21.0686 | 3.5197 | 3.5197 | 74.1545 | 46.5913 | 29.32% | 29.32%
7 | 206 | 25 | 4937 | 17 | 26.2 | 269.86 | 165.69 | 435.55 | 165.69 | 82.85 | 206 | 4937 | 1020 | 203.1781 | 19.6386 | -11.083 | 994.284 | 16.3867 | -65.8002 | 30.6174 | 30.6174 | 86.591 | 266.591 | 66.6519 | 209.993 | 209.993 | 141.4253 | 351.4183 | 0.51554 | 51.55% | 158.9114 | 81.9257 | 57.348 | 202.5657 | 202.5657 | 28.31% | 11.2% | 11.2% | 85% | 9.519% | 15.1271 | 3.8549 | 3.8549 | 58.3133 | 33.4521 | 28.79% | 28.79%
7 | 206 | 25 | 4938 | 18 | 26.2 | 200.69 | 133.11 | 333.8 | 133.11 | 66.56 | 206 | 4938 | 1080 | 203.1781 | 19.6386 | -11.083 | 1054.284 | 17.3867 | -80.8002 | 20.3667 | 20.3667 | 97.3809 | 277.3809 | 80.739 | 92.8016 | 92.8016 | 113.6165 | 206.4181 | 0.31291 | 31.29% | 93.3423 | 29.2082 | 20.4457 | 193.4733 | 193.4733 | 10.57% | 11.15% | 11.15% | 80% | 8.92% | 8.3258 | 3.8549 | 3.8549 | 32.0952 | 18.4118 | 16.59% | 16.59%
7 | 206 | 25 | 4939 | 19 | 26.1 | 79.67 | 89.39 | 169.06 | 89.39 | 44.7 | 206 | 4939 | 1140 | 203.1781 | 19.6386 | -11.083 | 1114.284 | 18.3867 | -95.8002 | 10.3537 | 10.3537 | 107.7268 | 287.7268 | 94.8593 | -37.5503 | 0 | 76.2991 | 76.2991 | -0.52735 | 0% | 34.5025 | 0 | 0 | 178.5399 | 178.5399 | 0% | 11.11% | 0% | 80% | 0% | 0 | 3.8703 | 3.8703 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4940 | 20 | 25.9 | 36.06 | 39.78 | 75.84 | 39.78 | 19.89 | 206 | 4940 | 1200 | 203.1781 | 19.6386 | -11.083 | 1174.284 | 19.3867 | -110.8002 | 0.90901 | 0.90901 | 118.2903 | 298.2903 | 108.8969 | 0 | 0 | 33.9544 | 33.9544 | -2.2002 | 0% | 15.3542 | 0 | 0 | 204.6834 | 204.6834 | 0% | 11.1% | 0% | 80% | 0% | 0 | 3.9014 | 3.9014 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4941 | 21 | 24.5 | 0 | 5.22 | 5.22 | 5.22 | 2.61 | 206 | 4941 | 1260 | 203.1781 | 19.6386 | -11.083 | 1234.284 | 20.3867 | -125.8002 | -7.6075 | 0 | 119.3906 | 299.3906 | 110.3052 | 0 | 0 | 4.4555 | 4.4555 | -22.7596 | 0% | 2.0148 | 0 | 0 | 0.12617 | 0.12617 | 0% | 11.16% | 0% | 80% | 0% | 0 | 4.1265 | 4.1265 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4942 | 22 | 23.7 | 0 | 0 | 0 | 0 | 0 | 206 | 4942 | 1320 | 203.1781 | 19.6386 | -11.083 | 1294.284 | 21.3867 | -140.8002 | -14.7692 | 0 | 119.3906 | 299.3906 | 110.3052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.0805 | 0 | 0% | 11.19% | 0% | 80% | 0% | 0 | 4.2613 | 4.2613 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4943 | 23 | 22.2 | 0 | 0 | 0 | 0 | 0 | 206 | 4943 | 1380 | 203.1781 | 19.6386 | -11.083 | 1354.284 | 22.3867 | -155.8002 | -20.0843 | 0 | 119.3906 | 299.3906 | 110.3052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7126 | 0 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.5261 | 4.5261 | 0 | 0 | 0% | 0%
7 | 206 | 25 | 4944 | 24 | 21.6 | 0 | 0 | 0 | 0 | 0 | 206 | 4944 | 1440 | 203.1781 | 19.6386 | -11.083 | 1414.284 | 23.3867 | -170.8002 | -23.0657 | 0 | 119.3906 | 299.3906 | 110.3052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.973 | 0 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.6364 | 4.6364 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4945 | 1 | 20.9 | 0 | 0 | 0 | 0 | 0 | 207 | 4945 | 60 | 204.1644 | 19.4321 | -11.3389 | 34.284 | 0.38242 | 174.2637 | -23.5876 | 0 | 119.0649 | 60.9351 | 110.091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.1616 | 0 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7684 | 4.7684 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4946 | 2 | 20.1 | 0 | 0 | 0 | 0 | 0 | 207 | 4946 | 120 | 204.1644 | 19.4321 | -11.3389 | 94.284 | 1.3824 | 159.2637 | -21.1953 | 0 | 119.0649 | 60.9351 | 110.091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7542 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4947 | 3 | 19.1 | 0 | 0 | 0 | 0 | 0 | 207 | 4947 | 180 | 204.1644 | 19.4321 | -11.3389 | 154.284 | 2.3824 | 144.2637 | -16.3669 | 0 | 119.0649 | 60.9351 | 110.091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.6516 | 0 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1233 | 5.1233 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4948 | 4 | 18.8 | 0 | 0 | 0 | 0 | 0 | 207 | 4948 | 240 | 204.1644 | 19.4321 | -11.3389 | 214.284 | 3.3824 | 129.2637 | -9.5727 | 0 | 119.0649 | 60.9351 | 110.091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.1088 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4949 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 207 | 4949 | 300 | 204.1644 | 19.4321 | -11.3389 | 274.284 | 4.3824 | 114.2637 | -1.3155 | 0 | 119.0649 | 60.9351 | 110.091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.9813 | 8.9813 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4950 | 6 | 18 | 1.06 | 5.69 | 6.75 | 5.69 | 2.85 | 207 | 4950 | 360 | 204.1644 | 19.4321 | -11.3389 | 334.284 | 5.3824 | 99.2637 | 7.9593 | 7.9593 | 109.9836 | 70.0164 | 98.1297 | 0 | 0 | 4.8567 | 4.8567 | -23.7365 | 0% | 2.1962 | 0 | 0 | 20.9544 | 20.9544 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4951 | 7 | 18.2 | 41.39 | 37.92 | 79.31 | 37.92 | 18.96 | 207 | 4951 | 420 | 204.1644 | 19.4321 | -11.3389 | 394.284 | 6.3824 | 84.2637 | 17.8774 | 17.8774 | 99.6264 | 80.3736 | 83.9997 | 14.0941 | 14.0941 | 32.3667 | 46.4608 | -1.7517 | 0% | 21.0096 | 0 | 0 | 193.0737 | 193.0737 | 0% | 11.43% | 11.43% | 80% | 9.141% | 1.9205 | 5.3093 | 5.3093 | 10.1968 | 4.2471 | 5.281% | 5.281%
7 | 207 | 26 | 4952 | 8 | 20.2 | 139.11 | 64.67 | 203.78 | 64.67 | 32.34 | 207 | 4952 | 480 | 204.1644 | 19.4321 | -11.3389 | 454.284 | 7.3824 | 69.2637 | 28.1054 | 28.1054 | 88.9945 | 91.0055 | 69.8756 | 101.5977 | 101.5977 | 55.1993 | 156.797 | 0.07492 | 7.492% | 70.9036 | 5.3121 | 3.7185 | 169.0606 | 169.0606 | 2.199% | 11.34% | 11.34% | 80% | 9.076% | 6.4352 | 4.9037 | 4.9037 | 31.5561 | 14.2308 | 18.67% | 18.67%
7 | 207 | 26 | 4953 | 9 | 22.5 | 257.08 | 97.22 | 354.3 | 97.22 | 48.61 | 207 | 4953 | 540 | 204.1644 | 19.4321 | -11.3389 | 514.284 | 8.3824 | 54.2637 | 38.2888 | 38.2888 | 77.2274 | 102.7726 | 55.8859 | 232.6914 | 232.6914 | 82.9825 | 315.6739 | 0.45777 | 45.78% | 142.7477 | 65.3451 | 45.7416 | 179.8568 | 179.8568 | 25.43% | 11.29% | 11.29% | 85% | 9.593% | 13.6932 | 4.4719 | 4.4719 | 61.2343 | 30.2813 | 34.05% | 34.05%
7 | 207 | 26 | 4954 | 10 | 24.7 | 362.28 | 113.83 | 476.11 | 113.83 | 56.92 | 207 | 4954 | 600 | 204.1644 | 19.4321 | -11.3389 | 574.284 | 9.3824 | 39.2637 | 47.9406 | 47.9406 | 62.9911 | 117.0089 | 42.2593 | 361.1374 | 361.1374 | 97.16 | 458.2973 | 0.57585 | 57.58% | 207.2421 | 119.3402 | 83.5382 | 213.5045 | 213.5045 | 39.13% | 11.26% | 11.26% | 85% | 9.574% | 19.8416 | 4.0935 | 4.0935 | 81.2211 | 43.8779 | 38.04% | 38.04%
7 | 207 | 26 | 4955 | 11 | 26.2 | 448.28 | 104.67 | 552.95 | 104.67 | 52.34 | 207 | 4955 | 660 | 204.1644 | 19.4321 | -11.3389 | 634.284 | 10.3824 | 24.2637 | 56.2222 | 56.2222 | 44.189 | 135.811 | 29.5831 | 469.0117 | 469.0117 | 89.3414 | 558.3531 | 0.62245 | 62.25% | 252.4873 | 157.1608 | 110.0125 | 234.7071 | 234.7071 | 46.87% | 11.27% | 11.27% | 90% | 10.14% | 25.6089 | 3.8549 | 3.8549 | 98.7196 | 56.6317 | 42.06% | 42.06%
7 | 207 | 26 | 4956 | 12 | 27.4 | 452.5 | 129.39 | 581.89 | 129.39 | 64.7 | 207 | 4956 | 720 | 204.1644 | 19.4321 | -11.3389 | 694.284 | 11.3824 | 9.2637 | 61.6214 | 61.6214 | 18.6266 | 161.3734 | 19.8455 | 483.7623 | 483.7623 | 110.4413 | 594.2035 | 0.63766 | 63.77% | 268.6988 | 171.3398 | 119.9378 | 244.1749 | 244.1749 | 49.12% | 11.27% | 11.27% | 90% | 10.14% | 27.2499 | 3.6754 | 3.6754 | 100.1536 | 60.2607 | 41.02% | 41.02%
7 | 207 | 26 | 4957 | 13 | 25.8 | 488.25 | 122.69 | 610.94 | 122.69 | 61.35 | 207 | 4957 | 780 | 204.1644 | 19.4321 | -11.3389 | 754.284 | 12.3824 | -5.7363 | 62.2534 | 62.2534 | 11.6807 | 191.6807 | 18.525 | 523.0998 | 523.0998 | 104.7225 | 627.8223 | 0.64119 | 64.12% | 283.9012 | 182.034 | 127.4238 | 212.3563 | 212.3563 | 60% | 11.3% | 11.3% | 90% | 10.17% | 28.8653 | 3.917 | 3.917 | 113.0647 | 63.833 | 53.24% | 53.24%
7 | 207 | 26 | 4958 | 14 | 22.6 | 485.97 | 155.28 | 641.25 | 155.28 | 77.64 | 207 | 4958 | 840 | 204.1644 | 19.4321 | -11.3389 | 814.284 | 13.3824 | -20.7363 | 57.8237 | 57.8237 | 38.8297 | 218.8297 | 26.894 | 512.0545 | 512.0545 | 132.5398 | 644.5943 | 0.63478 | 63.48% | 291.4855 | 185.0283 | 129.5198 | 159.4683 | 159.4683 | 81.22% | 11.33% | 11.33% | 90% | 10.2% | 29.7222 | 4.4539 | 4.4539 | 132.3809 | 65.728 | 83.01% | 83.01%
7 | 207 | 26 | 4959 | 15 | 20.9 | 493.33 | 133 | 626.33 | 133 | 66.5 | 207 | 4959 | 900 | 204.1644 | 19.4321 | -11.3389 | 874.284 | 14.3824 | -35.7363 | 50.0541 | 50.0541 | 59.0744 | 239.0744 | 39.156 | 498.9792 | 498.9792 | 113.5226 | 612.5018 | 0.61987 | 61.99% | 276.9733 | 171.6865 | 120.1805 | 154.0253 | 154.0253 | 78.03% | 11.34% | 11.34% | 90% | 10.21% | 28.2747 | 4.7684 | 4.7684 | 134.8237 | 62.5269 | 87.53% | 87.53%
7 | 207 | 26 | 4960 | 16 | 21.3 | 437 | 151.44 | 588.44 | 151.44 | 75.72 | 207 | 4960 | 960 | 204.1644 | 19.4321 | -11.3389 | 934.284 | 15.3824 | -50.7363 | 40.6294 | 40.6294 | 74.1653 | 254.1653 | 52.6362 | 407.277 | 407.277 | 129.2621 | 536.5391 | 0.59543 | 59.54% | 242.623 | 144.4643 | 101.125 | 151.4848 | 151.4848 | 66.76% | 11.33% | 11.33% | 90% | 10.2% | 24.7472 | 4.6926 | 4.6926 | 116.1275 | 54.7262 | 76.66% | 76.66%
7 | 207 | 26 | 4961 | 17 | 21.2 | 348.61 | 142 | 490.61 | 142 | 71 | 207 | 4961 | 1020 | 204.1644 | 19.4321 | -11.3389 | 994.284 | 16.3824 | -65.7363 | 30.5189 | 30.5189 | 86.3688 | 266.3688 | 66.5677 | 272.9889 | 272.9889 | 121.2046 | 394.1935 | 0.51956 | 51.96% | 178.2543 | 92.6131 | 64.8292 | 144.5773 | 144.5773 | 44.84% | 11.33% | 11.33% | 85% | 9.626% | 17.1595 | 4.7114 | 4.7114 | 80.8454 | 37.9468 | 55.92% | 55.92%
7 | 207 | 26 | 4962 | 18 | 21.2 | 221.81 | 108.61 | 330.42 | 108.61 | 54.31 | 207 | 4962 | 1080 | 204.1644 | 19.4321 | -11.3389 | 1054.284 | 17.3824 | -80.7363 | 20.267 | 20.267 | 97.1776 | 277.1776 | 80.6736 | 103.7721 | 103.7721 | 92.7044 | 196.4766 | 0.23332 | 23.33% | 88.8467 | 20.7294 | 14.5106 | 132.6836 | 132.6836 | 10.94% | 11.31% | 11.31% | 80% | 9.05% | 8.0404 | 4.7114 | 4.7114 | 37.8815 | 17.7806 | 28.55% | 28.55%
7 | 207 | 26 | 4963 | 19 | 21.1 | 129.58 | 80.14 | 209.72 | 80.14 | 40.07 | 207 | 4963 | 1140 | 204.1644 | 19.4321 | -11.3389 | 1114.284 | 18.3824 | -95.7363 | 10.2465 | 10.2465 | 107.5372 | 287.5372 | 94.8121 | -61.1091 | 0 | 68.4038 | 68.4038 | -0.83837 | 0% | 30.9322 | 0 | 0 | 122.0217 | 122.0217 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7303 | 4.7303 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4964 | 20 | 20.2 | 42.44 | 44.31 | 86.75 | 44.31 | 22.16 | 207 | 4964 | 1200 | 204.1644 | 19.4321 | -11.3389 | 1174.284 | 19.3824 | -110.7363 | 0.78897 | 0.78897 | 118.1117 | 298.1117 | 108.8696 | 0 | 0 | 37.821 | 37.821 | -2.2186 | 0% | 17.1026 | 0 | 0 | 148.5299 | 148.5299 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.9037 | 4.9037 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4965 | 21 | 20.1 | 0 | 4.78 | 4.78 | 4.78 | 2.39 | 207 | 4965 | 1260 | 204.1644 | 19.4321 | -11.3389 | 1234.284 | 20.3824 | -125.7363 | -7.7448 | 0 | 119.0649 | 299.0649 | 110.091 | 0 | 0 | 4.08 | 4.08 | -27.269 | 0% | 1.845 | 0 | 0 | -5.2709 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4966 | 22 | 20.2 | 0 | 0 | 0 | 0 | 0 | 207 | 4966 | 1320 | 204.1644 | 19.4321 | -11.3389 | 1294.284 | 21.3824 | -140.7363 | -14.9269 | 0 | 119.0649 | 299.0649 | 110.091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.1082 | 0 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.9037 | 4.9037 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4967 | 23 | 18.7 | 0 | 0 | 0 | 0 | 0 | 207 | 4967 | 1380 | 204.1644 | 19.4321 | -11.3389 | 1354.284 | 22.3824 | -155.7363 | -20.2633 | 0 | 119.0649 | 299.0649 | 110.091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7676 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2053 | 5.2053 | 0 | 0 | 0% | 0%
7 | 207 | 26 | 4968 | 24 | 17.7 | 0 | 0 | 0 | 0 | 0 | 207 | 4968 | 1440 | 204.1644 | 19.4321 | -11.3389 | 1414.284 | 23.3824 | -170.7363 | -23.2636 | 0 | 119.0649 | 299.0649 | 110.091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.665 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4969 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 208 | 4969 | 60 | 205.1507 | 19.2205 | -11.5841 | 34.284 | 0.37833 | 174.325 | -23.8029 | 0 | 118.7319 | 61.2681 | 109.8717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0435 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4970 | 2 | 16.5 | 0 | 0 | 0 | 0 | 0 | 208 | 4970 | 120 | 205.1507 | 19.2205 | -11.5841 | 94.284 | 1.3783 | 159.325 | -21.4147 | 0 | 118.7319 | 61.2681 | 109.8717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2508 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4971 | 3 | 15.8 | 0 | 0 | 0 | 0 | 0 | 208 | 4971 | 180 | 205.1507 | 19.2205 | -11.5841 | 154.284 | 2.3783 | 144.325 | -16.5833 | 0 | 118.7319 | 61.2681 | 109.8717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7629 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4972 | 4 | 14.8 | 0 | 0 | 0 | 0 | 0 | 208 | 4972 | 240 | 205.1507 | 19.2205 | -11.5841 | 214.284 | 3.3783 | 129.325 | -9.7822 | 0 | 118.7319 | 61.2681 | 109.8717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2868 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4973 | 5 | 14.9 | 0 | 0 | 0 | 0 | 0 | 208 | 4973 | 300 | 205.1507 | 19.2205 | -11.5841 | 274.284 | 4.3783 | 114.325 | -1.5169 | 0 | 118.7319 | 61.2681 | 109.8717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.578 | 1.578 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4974 | 6 | 14.6 | 1.06 | 5.97 | 7.03 | 5.97 | 2.99 | 208 | 4974 | 360 | 205.1507 | 19.2205 | -11.5841 | 334.284 | 5.3783 | 99.325 | 7.7651 | 7.7651 | 109.8805 | 70.1195 | 98.205 | 0 | 0 | 5.0957 | 5.0957 | -24.0872 | 0% | 2.3043 | 0 | 0 | 12.1653 | 12.1653 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4975 | 7 | 15.9 | 34.08 | 40.19 | 74.27 | 40.19 | 20.1 | 208 | 4975 | 420 | 205.1507 | 19.2205 | -11.5841 | 394.284 | 6.3783 | 84.325 | 17.6882 | 17.6882 | 99.5098 | 80.4902 | 84.0568 | 11.6139 | 11.6139 | 34.3043 | 45.9182 | -1.8942 | 0% | 20.7642 | 0 | 0 | 183.0846 | 183.0846 | 0% | 11.52% | 11.52% | 80% | 9.218% | 1.914 | 5.8104 | 5.8104 | 11.1208 | 4.2326 | 6.074% | 6.074%
7 | 208 | 27 | 4976 | 8 | 17.1 | 104.17 | 88.47 | 192.64 | 88.47 | 44.24 | 208 | 4976 | 480 | 205.1507 | 19.2205 | -11.5841 | 454.284 | 7.3783 | 69.325 | 27.9178 | 27.9178 | 88.8657 | 91.1343 | 69.9134 | 76.4113 | 76.4113 | 75.5139 | 151.9251 | 0.00626 | 0.626% | 68.7005 | 0.43007 | 0.30105 | 156.9296 | 156.9296 | 0.1918% | 11.46% | 11.46% | 80% | 9.164% | 6.2959 | 5.5443 | 5.5443 | 34.9066 | 13.9229 | 22.24% | 22.24%
7 | 208 | 27 | 4977 | 9 | 19.2 | 194.31 | 123.11 | 317.42 | 123.11 | 61.56 | 208 | 4977 | 540 | 205.1507 | 19.2205 | -11.5841 | 514.284 | 8.3783 | 54.325 | 38.0983 | 38.0983 | 77.089 | 102.911 | 55.9008 | 176.5533 | 176.5533 | 105.081 | 281.6343 | 0.39026 | 39.03% | 127.355 | 49.7019 | 34.7913 | 166.5399 | 166.5399 | 20.89% | 11.37% | 11.37% | 80% | 9.1% | 11.5891 | 5.103 | 5.103 | 59.1392 | 25.6283 | 35.51% | 35.51%
7 | 208 | 27 | 4978 | 10 | 21.7 | 311.06 | 168.47 | 479.53 | 168.47 | 84.24 | 208 | 4978 | 600 | 205.1507 | 19.2205 | -11.5841 | 574.284 | 9.3783 | 39.325 | 47.7417 | 47.7417 | 62.8532 | 117.1468 | 42.2425 | 311.1381 | 311.1381 | 143.7981 | 454.9363 | 0.55993 | 55.99% | 205.7222 | 115.1905 | 80.6334 | 174.6853 | 174.6853 | 46.16% | 11.32% | 11.32% | 85% | 9.622% | 19.7941 | 4.6179 | 4.6179 | 91.4068 | 43.7729 | 52.33% | 52.33%
7 | 208 | 27 | 4979 | 11 | 22.7 | 448.28 | 194.86 | 643.14 | 194.86 | 97.43 | 208 | 4979 | 660 | 205.1507 | 19.2205 | -11.5841 | 634.284 | 10.3783 | 24.325 | 56.0104 | 56.0104 | 44.0868 | 135.9132 | 29.5145 | 470.4965 | 470.4965 | 166.3234 | 636.8199 | 0.63305 | 63.31% | 287.97 | 182.2997 | 127.6098 | 174.816 | 174.816 | 73% | 11.33% | 11.33% | 90% | 10.19% | 29.3585 | 4.4361 | 4.4361 | 130.2366 | 64.9237 | 74.5% | 74.5%
7 | 208 | 27 | 4980 | 12 | 24.7 | 590.61 | 168.11 | 758.72 | 168.11 | 84.06 | 208 | 4980 | 720 | 205.1507 | 19.2205 | -11.5841 | 694.284 | 11.3783 | 9.325 | 61.4022 | 61.4022 | 18.6417 | 161.3583 | 19.6872 | 633.355 | 633.355 | 143.4909 | 776.8459 | 0.6694 | 66.94% | 351.2897 | 235.1545 | 164.6082 | 199.0157 | 199.0157 | 82.71% | 11.35% | 11.35% | 90% | 10.21% | 35.8716 | 4.0935 | 4.0935 | 146.8397 | 79.3269 | 73.78% | 73.78%
7 | 208 | 27 | 4981 | 13 | 25.5 | 513.39 | 200.33 | 713.72 | 200.33 | 100.17 | 208 | 4981 | 780 | 205.1507 | 19.2205 | -11.5841 | 754.284 | 12.3783 | -5.675 | 62.0525 | 62.0525 | 11.4921 | 191.4921 | 18.306 | 551.7559 | 551.7559 | 170.9924 | 722.7482 | 0.66169 | 66.17% | 326.8268 | 216.2578 | 151.3805 | 209.3469 | 209.3469 | 72.31% | 11.33% | 11.33% | 90% | 10.2% | 33.3225 | 3.9643 | 3.9643 | 132.0995 | 73.6897 | 63.1% | 63.1%
7 | 208 | 27 | 4982 | 14 | 25.6 | 432.78 | 201.94 | 634.72 | 201.94 | 100.97 | 208 | 4982 | 840 | 205.1507 | 19.2205 | -11.5841 | 814.284 | 13.3783 | -20.675 | 57.6614 | 57.6614 | 38.5532 | 218.5532 | 26.7173 | 457.5382 | 457.5382 | 172.3666 | 629.9048 | 0.64105 | 64.11% | 284.843 | 182.599 | 127.8193 | 206.6112 | 206.6112 | 61.86% | 11.3% | 11.3% | 90% | 10.17% | 28.9675 | 3.9484 | 3.9484 | 114.3766 | 64.0591 | 55.36% | 55.36%
7 | 208 | 27 | 4983 | 15 | 26.8 | 586.11 | 216.25 | 802.36 | 216.25 | 108.13 | 208 | 4983 | 900 | 205.1507 | 19.2205 | -11.5841 | 874.284 | 14.3783 | -35.675 | 49.9243 | 49.9243 | 58.7994 | 238.7994 | 39.0222 | 595.0778 | 595.0778 | 184.5809 | 779.6587 | 0.67561 | 67.56% | 352.5617 | 238.1941 | 166.7359 | 233.6876 | 233.6876 | 71.35% | 11.34% | 11.34% | 90% | 10.21% | 35.9964 | 3.7639 | 3.7639 | 135.4861 | 79.6028 | 57.98% | 57.98%
7 | 208 | 27 | 4984 | 16 | 27.1 | 442.83 | 190.33 | 633.16 | 190.33 | 95.17 | 208 | 4984 | 960 | 205.1507 | 19.2205 | -11.5841 | 934.284 | 15.3783 | -50.675 | 40.5182 | 40.5182 | 73.9164 | 253.9164 | 52.5318 | 414.6328 | 414.6328 | 162.4568 | 577.0896 | 0.63164 | 63.16% | 260.9599 | 164.8323 | 115.3826 | 230.5173 | 230.5173 | 50.05% | 11.26% | 11.26% | 90% | 10.14% | 26.4573 | 3.7193 | 3.7193 | 98.4031 | 58.508 | 42.69% | 42.69%
7 | 208 | 27 | 4985 | 17 | 27.2 | 264.39 | 132.28 | 396.67 | 132.28 | 66.14 | 208 | 4985 | 1020 | 205.1507 | 19.2205 | -11.5841 | 994.284 | 16.3783 | -65.675 | 30.4149 | 30.4149 | 86.1447 | 266.1447 | 66.4856 | 208.3643 | 208.3643 | 112.908 | 321.2723 | 0.49505 | 49.5% | 145.2794 | 71.9203 | 50.3442 | 219.0643 | 219.0643 | 22.98% | 11.16% | 11.16% | 85% | 9.488% | 13.7842 | 3.7046 | 3.7046 | 51.0649 | 30.4825 | 23.31% | 23.31%
7 | 208 | 27 | 4986 | 18 | 27 | 154.39 | 108.19 | 262.58 | 108.19 | 54.1 | 208 | 4986 | 1080 | 205.1507 | 19.2205 | -11.5841 | 1054.284 | 17.3783 | -80.675 | 20.1619 | 20.1619 | 96.9725 | 276.9725 | 80.6106 | 73.077 | 73.077 | 92.3459 | 165.423 | 0.20143 | 20.14% | 74.8043 | 15.0679 | 10.5475 | 204.7444 | 204.7444 | 5.152% | 11.11% | 11.11% | 80% | 8.886% | 6.6472 | 3.7341 | 3.7341 | 24.8214 | 14.6997 | 12.12% | 12.12%
7 | 208 | 27 | 4987 | 19 | 26.5 | 78.47 | 85.06 | 163.53 | 85.06 | 42.53 | 208 | 4987 | 1140 | 205.1507 | 19.2205 | -11.5841 | 1114.284 | 18.3783 | -95.675 | 10.1339 | 10.1339 | 107.346 | 287.346 | 94.7676 | -37.0674 | 0 | 72.6033 | 72.6033 | -0.58346 | 0% | 32.8312 | 0 | 0 | 185.8106 | 185.8106 | 0% | 11.09% | 0% | 80% | 0% | 0 | 3.8091 | 3.8091 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4988 | 20 | 26.1 | 27.44 | 43.61 | 71.05 | 43.61 | 21.81 | 208 | 4988 | 1200 | 205.1507 | 19.2205 | -11.5841 | 1174.284 | 19.3783 | -110.675 | 0.66357 | 0.66357 | 117.9317 | 297.9317 | 108.8451 | 0 | 0 | 37.2235 | 37.2235 | -1.9249 | 0% | 16.8325 | 0 | 0 | 208.3157 | 208.3157 | 0% | 11.1% | 0% | 80% | 0% | 0 | 3.8703 | 3.8703 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4989 | 21 | 23.9 | 0 | 3.89 | 3.89 | 3.89 | 1.95 | 208 | 4989 | 1260 | 205.1507 | 19.2205 | -11.5841 | 1234.284 | 20.3783 | -125.675 | -7.8874 | 0 | 118.7319 | 298.7319 | 109.8717 | 0 | 0 | 3.3203 | 3.3203 | -31.2036 | 0% | 1.5014 | 0 | 0 | -0.33509 | 0 | 0% | 11.18% | 0% | 80% | 0% | 0 | 4.2272 | 4.2272 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4990 | 22 | 21.3 | 0 | 0 | 0 | 0 | 0 | 208 | 4990 | 1320 | 205.1507 | 19.2205 | -11.5841 | 1294.284 | 21.3783 | -140.675 | -15.0899 | 0 | 118.7319 | 298.7319 | 109.8717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.1545 | 0 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6926 | 4.6926 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4991 | 23 | 20.4 | 0 | 0 | 0 | 0 | 0 | 208 | 4991 | 1380 | 205.1507 | 19.2205 | -11.5841 | 1354.284 | 22.3783 | -155.675 | -20.4478 | 0 | 118.7319 | 298.7319 | 109.8717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9714 | 0 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8647 | 4.8647 | 0 | 0 | 0% | 0%
7 | 208 | 27 | 4992 | 24 | 19.4 | 0 | 0 | 0 | 0 | 0 | 208 | 4992 | 1440 | 205.1507 | 19.2205 | -11.5841 | 1414.284 | 23.3783 | -170.675 | -23.4667 | 0 | 118.7319 | 298.7319 | 109.8717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9407 | 0 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0626 | 5.0626 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 4993 | 1 | 18.6 | 0 | 0 | 0 | 0 | 0 | 209 | 4993 | 60 | 206.137 | 19.0039 | -11.8184 | 34.284 | 0.37443 | 174.3836 | -24.0229 | 0 | 118.3917 | 61.6083 | 109.6472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7995 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 4994 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 209 | 4994 | 120 | 206.137 | 19.0039 | -11.8184 | 94.284 | 1.3744 | 159.3836 | -21.6382 | 0 | 118.3917 | 61.6083 | 109.6472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9135 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 4995 | 3 | 17.4 | 0 | 0 | 0 | 0 | 0 | 209 | 4995 | 180 | 206.137 | 19.0039 | -11.8184 | 154.284 | 2.3744 | 144.3836 | -16.8032 | 0 | 118.3917 | 61.6083 | 109.6472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0275 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 4996 | 4 | 17 | 0 | 0 | 0 | 0 | 0 | 209 | 4996 | 240 | 206.137 | 19.0039 | -11.8184 | 214.284 | 3.3744 | 129.3836 | -9.9946 | 0 | 118.3917 | 61.6083 | 109.6472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6371 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 4997 | 5 | 16.9 | 0 | 0 | 0 | 0 | 0 | 209 | 4997 | 300 | 206.137 | 19.0039 | -11.8184 | 274.284 | 4.3744 | 114.3836 | -1.7206 | 0 | 118.3917 | 61.6083 | 109.6472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 12.1539 | 12.1539 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 4998 | 6 | 16.7 | 0.89 | 5.69 | 6.58 | 5.69 | 2.85 | 209 | 4998 | 360 | 206.137 | 19.0039 | -11.8184 | 334.284 | 5.3744 | 99.3836 | 7.569 | 7.569 | 109.7724 | 70.2276 | 98.2782 | 0 | 0 | 4.8567 | 4.8567 | -24.3351 | 0% | 2.1962 | 0 | 0 | 26.9855 | 26.9855 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 4999 | 7 | 16.3 | 49.94 | 38.06 | 88 | 38.06 | 19.03 | 209 | 4999 | 420 | 206.137 | 19.0039 | -11.8184 | 394.284 | 6.3744 | 84.3836 | 17.4973 | 17.4973 | 99.388 | 80.612 | 84.1115 | 17.0407 | 17.0407 | 32.4862 | 49.527 | -1.6794 | 0% | 22.3961 | 0 | 0 | 205.2069 | 205.2069 | 0% | 11.5% | 11.5% | 80% | 9.204% | 2.0613 | 5.7206 | 5.7206 | 11.7917 | 4.5584 | 5.746% | 5.746%
7 | 209 | 28 | 5000 | 8 | 18 | 175 | 62.64 | 237.64 | 62.64 | 31.32 | 209 | 5000 | 480 | 206.137 | 19.0039 | -11.8184 | 454.284 | 7.3744 | 69.3836 | 27.7285 | 27.7285 | 88.7314 | 91.2686 | 69.9487 | 128.9556 | 128.9556 | 53.4666 | 182.4222 | 0.15065 | 15.06% | 82.4913 | 12.427 | 8.6989 | 184.4755 | 184.4755 | 4.715% | 11.42% | 11.42% | 80% | 9.136% | 7.5364 | 5.3514 | 5.3514 | 40.3301 | 16.666 | 21.86% | 21.86%
7 | 209 | 28 | 5001 | 9 | 21.4 | 336.25 | 75.97 | 412.22 | 75.97 | 37.99 | 209 | 5001 | 540 | 206.137 | 19.0039 | -11.8184 | 514.284 | 8.3744 | 54.3836 | 37.9059 | 37.9059 | 76.9446 | 103.0554 | 55.9128 | 306.7426 | 306.7426 | 64.8445 | 371.5871 | 0.50343 | 50.34% | 168.0317 | 84.5916 | 59.2141 | 198.1785 | 198.1785 | 29.88% | 11.32% | 11.32% | 85% | 9.621% | 16.1666 | 4.6738 | 4.6738 | 75.5591 | 35.751 | 38.13% | 38.13%
7 | 209 | 28 | 5002 | 10 | 23.7 | 481.25 | 85.69 | 566.94 | 85.69 | 42.85 | 209 | 5002 | 600 | 206.137 | 19.0039 | -11.8184 | 574.284 | 9.3744 | 39.3836 | 47.5405 | 47.5405 | 62.7089 | 117.2911 | 42.2226 | 483.0672 | 483.0672 | 73.141 | 556.2082 | 0.61216 | 61.22% | 251.5173 | 153.9677 | 107.7774 | 215.0457 | 215.0457 | 50.12% | 11.3% | 11.3% | 90% | 10.17% | 25.5847 | 4.2613 | 4.2613 | 109.0235 | 56.5783 | 50.7% | 50.7%
7 | 209 | 28 | 5003 | 11 | 25.6 | 600.61 | 97.28 | 697.89 | 97.28 | 48.64 | 209 | 5003 | 660 | 206.137 | 19.0039 | -11.8184 | 634.284 | 10.3744 | 24.3836 | 55.7955 | 55.7955 | 43.9775 | 136.0225 | 29.4426 | 632.4275 | 632.4275 | 83.0337 | 715.4612 | 0.66054 | 66.05% | 323.5315 | 213.7046 | 149.5932 | 243.1806 | 243.1806 | 61.52% | 11.33% | 11.33% | 90% | 10.19% | 32.9788 | 3.9484 | 3.9484 | 130.2146 | 72.9296 | 53.55% | 53.55%
7 | 209 | 28 | 5004 | 12 | 27.2 | 679.86 | 111.67 | 791.53 | 111.67 | 55.84 | 209 | 5004 | 720 | 206.137 | 19.0039 | -11.8184 | 694.284 | 11.3744 | 9.3836 | 61.1787 | 61.1787 | 18.6494 | 161.3506 | 19.5245 | 731.3628 | 731.3628 | 95.3163 | 826.6791 | 0.68393 | 68.39% | 373.8243 | 255.6704 | 178.9693 | 258.5598 | 258.5598 | 69.22% | 11.36% | 11.36% | 95% | 10.79% | 40.3522 | 3.7046 | 3.7046 | 149.4889 | 89.2354 | 57.82% | 57.82%
7 | 209 | 28 | 5005 | 13 | 27.9 | 517.86 | 143.25 | 661.11 | 143.25 | 71.63 | 209 | 5005 | 780 | 206.137 | 19.0039 | -11.8184 | 754.284 | 12.3744 | -5.6164 | 61.8461 | 61.8461 | 11.3097 | 191.3097 | 18.083 | 558.3428 | 558.3428 | 122.2715 | 680.6144 | 0.66032 | 66.03% | 307.7738 | 203.2305 | 142.2614 | 262.6634 | 262.6634 | 54.16% | 11.3% | 11.3% | 90% | 10.17% | 31.3009 | 3.6036 | 3.6036 | 112.7947 | 69.2193 | 42.94% | 42.94%
7 | 209 | 28 | 5006 | 14 | 27.6 | 642.69 | 166.11 | 808.8 | 166.11 | 83.06 | 209 | 5006 | 840 | 206.137 | 19.0039 | -11.8184 | 814.284 | 13.3744 | -20.6164 | 57.4929 | 57.4929 | 38.2792 | 218.2792 | 26.54 | 681.7835 | 681.7835 | 141.7838 | 823.5672 | 0.6845 | 68.45% | 372.4171 | 254.9192 | 178.4435 | 283.3656 | 283.3656 | 62.97% | 11.36% | 11.36% | 95% | 10.79% | 40.1978 | 3.6464 | 3.6464 | 146.5789 | 88.8939 | 51.73% | 51.73%
7 | 209 | 28 | 5007 | 15 | 24.9 | 611.17 | 134.17 | 745.34 | 134.17 | 67.09 | 209 | 5007 | 900 | 206.137 | 19.0039 | -11.8184 | 874.284 | 14.3744 | -35.6164 | 49.7885 | 49.7885 | 58.524 | 238.524 | 38.8894 | 622.9289 | 622.9289 | 114.5213 | 737.4502 | 0.66279 | 66.28% | 333.475 | 221.0247 | 154.7173 | 205.492 | 205.492 | 75.29% | 11.34% | 11.34% | 90% | 10.2% | 34.0199 | 4.0608 | 4.0608 | 138.1464 | 75.2319 | 67.23% | 67.23%
7 | 209 | 28 | 5008 | 16 | 24.9 | 610.69 | 108.89 | 719.58 | 108.89 | 54.45 | 209 | 5008 | 960 | 206.137 | 19.0039 | -11.8184 | 934.284 | 15.3744 | -50.6164 | 40.4012 | 40.4012 | 73.6661 | 253.6661 | 52.4292 | 574.5128 | 574.5128 | 92.9434 | 667.4562 | 0.64798 | 64.8% | 301.8237 | 195.5771 | 136.904 | 202.3742 | 202.3742 | 67.65% | 11.32% | 11.32% | 90% | 10.18% | 30.7397 | 4.0608 | 4.0608 | 124.8264 | 67.9781 | 61.68% | 61.68%
7 | 209 | 28 | 5009 | 17 | 24.1 | 476.61 | 101.89 | 578.5 | 101.89 | 50.95 | 209 | 5009 | 1020 | 206.137 | 19.0039 | -11.8184 | 994.284 | 16.3744 | -65.6164 | 30.3053 | 30.3053 | 85.919 | 265.919 | 66.4057 | 378.0499 | 378.0499 | 86.9686 | 465.0185 | 0.57638 | 57.64% | 210.2814 | 121.2026 | 84.8418 | 178.1957 | 178.1957 | 47.61% | 11.28% | 11.28% | 85% | 9.585% | 20.1555 | 4.1933 | 4.1933 | 84.5182 | 44.572 | 47.43% | 47.43%
7 | 209 | 28 | 5010 | 18 | 26.2 | 309.11 | 83.47 | 392.58 | 83.47 | 41.74 | 209 | 5010 | 1080 | 206.137 | 19.0039 | -11.8184 | 1054.284 | 17.3744 | -80.6164 | 20.0513 | 20.0513 | 96.7656 | 276.7656 | 80.55 | 148.0237 | 148.0237 | 71.2461 | 219.2698 | 0.3417 | 34.17% | 99.1538 | 33.8807 | 23.7165 | 203.0059 | 203.0059 | 11.68% | 11.15% | 11.15% | 80% | 8.923% | 8.8477 | 3.8549 | 3.8549 | 34.1069 | 19.5658 | 16.8% | 16.8%
7 | 209 | 28 | 5011 | 19 | 26.5 | 178.75 | 65.78 | 244.53 | 65.78 | 32.89 | 209 | 5011 | 1140 | 206.137 | 19.0039 | -11.8184 | 1114.284 | 18.3744 | -95.6164 | 10.0159 | 10.0159 | 107.1531 | 287.1531 | 94.7257 | -84.6729 | 0 | 56.1467 | 56.1467 | -0.99012 | 0% | 25.3896 | 0 | 0 | 236.5023 | 236.5023 | 0% | 11.09% | 0% | 80% | 0% | 0 | 3.8091 | 3.8091 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 5012 | 20 | 26.1 | 54.31 | 36.81 | 91.12 | 36.81 | 18.41 | 209 | 5012 | 1200 | 206.137 | 19.0039 | -11.8184 | 1174.284 | 19.3744 | -110.6164 | 0.53282 | 0.53282 | 117.7505 | 297.7505 | 108.8235 | 0 | 0 | 31.4193 | 31.4193 | -2.4291 | 0% | 14.2078 | 0 | 0 | 263.4264 | 263.4264 | 0% | 11.09% | 0% | 80% | 0% | 0 | 3.8703 | 3.8703 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 5013 | 21 | 25.1 | 0 | 4.5 | 4.5 | 4.5 | 2.25 | 209 | 5013 | 1260 | 206.137 | 19.0039 | -11.8184 | 1234.284 | 20.3744 | -125.6164 | -8.0354 | 0 | 118.3917 | 298.3917 | 109.6472 | 0 | 0 | 3.841 | 3.841 | -26.196 | 0% | 1.7369 | 0 | 0 | 2.1905 | 2.1905 | 0% | 11.13% | 0% | 80% | 0% | 0 | 4.0283 | 4.0283 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 5014 | 22 | 18.7 | 0 | 0 | 0 | 0 | 0 | 209 | 5014 | 1320 | 206.137 | 19.0039 | -11.8184 | 1294.284 | 21.3744 | -140.6164 | -15.2584 | 0 | 118.3917 | 298.3917 | 109.6472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0482 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2053 | 5.2053 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 5015 | 23 | 17.3 | 0 | 0 | 0 | 0 | 0 | 209 | 5015 | 1380 | 206.137 | 19.0039 | -11.8184 | 1354.284 | 22.3744 | -155.6164 | -20.6375 | 0 | 118.3917 | 298.3917 | 109.6472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3814 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
7 | 209 | 28 | 5016 | 24 | 17.8 | 0 | 0 | 0 | 0 | 0 | 209 | 5016 | 1440 | 206.137 | 19.0039 | -11.8184 | 1414.284 | 23.3744 | -170.6164 | -23.6749 | 0 | 118.3917 | 298.3917 | 109.6472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8191 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5017 | 1 | 18 | 0 | 0 | 0 | 0 | 0 | 210 | 5017 | 60 | 207.1233 | 18.7825 | -12.0417 | 34.284 | 0.37071 | 174.4394 | -24.2477 | 0 | 118.0445 | 61.9555 | 109.4176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.373 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5018 | 2 | 17.8 | 0 | 0 | 0 | 0 | 0 | 210 | 5018 | 120 | 207.1233 | 18.7825 | -12.0417 | 94.284 | 1.3707 | 159.4394 | -21.8657 | 0 | 118.0445 | 61.9555 | 109.4176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9754 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5019 | 3 | 17.2 | 0 | 0 | 0 | 0 | 0 | 210 | 5019 | 180 | 207.1233 | 18.7825 | -12.0417 | 154.284 | 2.3707 | 144.4394 | -17.0265 | 0 | 118.0445 | 61.9555 | 109.4176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.1873 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5020 | 4 | 16.2 | 0 | 0 | 0 | 0 | 0 | 210 | 5020 | 240 | 207.1233 | 18.7825 | -12.0417 | 214.284 | 3.3707 | 129.4394 | -10.2097 | 0 | 118.0445 | 61.9555 | 109.4176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7113 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5021 | 5 | 15.5 | 0 | 0 | 0 | 0 | 0 | 210 | 5021 | 300 | 207.1233 | 18.7825 | -12.0417 | 274.284 | 4.3707 | 114.4394 | -1.9266 | 0 | 118.0445 | 61.9555 | 109.4176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.2855 | 8.2855 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5022 | 6 | 14.9 | 0.69 | 5.56 | 6.25 | 5.56 | 2.78 | 210 | 5022 | 360 | 207.1233 | 18.7825 | -12.0417 | 334.284 | 5.3707 | 99.4394 | 7.3709 | 7.3709 | 109.6592 | 70.3408 | 98.3492 | 0 | 0 | 4.7458 | 4.7458 | -25.7791 | 0% | 2.146 | 0 | 0 | 20.6047 | 20.6047 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5023 | 7 | 15.8 | 39.03 | 49.72 | 88.75 | 49.72 | 24.86 | 210 | 5023 | 420 | 207.1233 | 18.7825 | -12.0417 | 394.284 | 6.3707 | 84.4394 | 17.3045 | 17.3045 | 99.261 | 80.739 | 84.1639 | 13.3425 | 13.3425 | 42.4387 | 55.7811 | -1.4211 | 0% | 25.2242 | 0 | 0 | 196.4522 | 196.4522 | 0% | 11.52% | 11.52% | 80% | 9.219% | 2.3255 | 5.833 | 5.833 | 13.5643 | 5.1425 | 6.905% | 6.905%
7 | 210 | 29 | 5024 | 8 | 17.4 | 127.22 | 80.61 | 207.83 | 80.61 | 40.31 | 210 | 5024 | 480 | 207.1233 | 18.7825 | -12.0417 | 454.284 | 7.3707 | 69.4394 | 27.5374 | 27.5374 | 88.5916 | 91.4084 | 69.9814 | 94.1986 | 94.1986 | 68.8049 | 163.0036 | 0.064597 | 6.46% | 73.7102 | 4.7614 | 3.333 | 172.6536 | 172.6536 | 1.93% | 11.44% | 11.44% | 80% | 9.154% | 6.7478 | 5.4794 | 5.4794 | 36.9737 | 14.9221 | 21.41% | 21.41%
7 | 210 | 29 | 5025 | 9 | 19.7 | 268 | 114.11 | 382.11 | 114.11 | 57.06 | 210 | 5025 | 540 | 207.1233 | 18.7825 | -12.0417 | 514.284 | 8.3707 | 54.4394 | 37.7116 | 37.7116 | 76.7944 | 103.2056 | 55.9222 | 245.4937 | 245.4937 | 97.399 | 342.8927 | 0.4674 | 46.74% | 155.0561 | 72.4729 | 50.731 | 184.9474 | 184.9474 | 27.43% | 11.36% | 11.36% | 85% | 9.656% | 14.9716 | 5.0025 | 5.0025 | 74.8951 | 33.1084 | 40.5% | 40.5%
7 | 210 | 29 | 5026 | 10 | 21.3 | 345.78 | 118.19 | 463.97 | 118.19 | 59.1 | 210 | 5026 | 600 | 207.1233 | 18.7825 | -12.0417 | 574.284 | 9.3707 | 39.4394 | 47.3369 | 47.3369 | 62.5582 | 117.4418 | 42.1997 | 348.3461 | 348.3461 | 100.8815 | 449.2276 | 0.55489 | 55.49% | 203.1407 | 112.7206 | 78.9044 | 186.6331 | 186.6331 | 42.28% | 11.33% | 11.33% | 85% | 9.628% | 19.5581 | 4.6926 | 4.6926 | 91.7777 | 43.2511 | 49.18% | 49.18%
7 | 210 | 29 | 5027 | 11 | 22.5 | 480.97 | 148.67 | 629.64 | 148.67 | 74.34 | 210 | 5027 | 660 | 207.1233 | 18.7825 | -12.0417 | 634.284 | 10.3707 | 24.4394 | 55.5774 | 55.5774 | 43.8612 | 136.1388 | 29.3673 | 508.1426 | 508.1426 | 126.8978 | 635.0404 | 0.63189 | 63.19% | 287.1653 | 181.4568 | 127.0198 | 184.9503 | 184.9503 | 68.68% | 11.33% | 11.33% | 90% | 10.2% | 29.2805 | 4.4719 | 4.4719 | 130.9386 | 64.7512 | 70.8% | 70.8%
7 | 210 | 29 | 5028 | 12 | 22.9 | 598.06 | 171.89 | 769.95 | 171.89 | 85.95 | 210 | 5028 | 720 | 207.1233 | 18.7825 | -12.0417 | 694.284 | 11.3707 | 9.4394 | 60.9511 | 60.9511 | 18.6496 | 161.3504 | 19.3575 | 645.4445 | 645.4445 | 146.7173 | 792.1617 | 0.66712 | 66.71% | 358.2155 | 238.9728 | 167.281 | 175.8704 | 175.8704 | 95.12% | 11.35% | 11.35% | 90% | 10.22% | 36.5941 | 4.4006 | 4.4006 | 161.0345 | 80.9247 | 91.56% | 91.56%
7 | 210 | 29 | 5029 | 13 | 22.9 | 570.64 | 168.69 | 739.33 | 168.69 | 84.35 | 210 | 5029 | 780 | 207.1233 | 18.7825 | -12.0417 | 754.284 | 12.3707 | -5.5606 | 61.6343 | 61.6343 | 11.1334 | 191.1334 | 17.8562 | 617.2646 | 617.2646 | 143.9859 | 761.2505 | 0.66156 | 66.16% | 344.2375 | 227.7345 | 159.4141 | 170.8345 | 170.8345 | 93.31% | 11.35% | 11.35% | 90% | 10.21% | 35.1509 | 4.4006 | 4.4006 | 154.6835 | 77.7331 | 90.55% | 90.55%
7 | 210 | 29 | 5030 | 14 | 23.9 | 606.47 | 176.67 | 783.14 | 176.67 | 88.34 | 210 | 5030 | 840 | 207.1233 | 18.7825 | -12.0417 | 814.284 | 13.3707 | -20.5606 | 57.3185 | 57.3185 | 38.0077 | 218.0077 | 26.3623 | 645.6097 | 645.6097 | 150.7973 | 796.407 | 0.67056 | 67.06% | 360.1352 | 241.4909 | 169.0437 | 187.6008 | 187.6008 | 90.11% | 11.35% | 11.35% | 90% | 10.22% | 36.7918 | 4.2272 | 4.2272 | 155.5246 | 81.3618 | 82.9% | 82.9%
7 | 210 | 29 | 5031 | 15 | 23.4 | 565.89 | 197.83 | 763.72 | 197.83 | 98.92 | 210 | 5031 | 900 | 207.1233 | 18.7825 | -12.0417 | 874.284 | 14.3707 | -35.5606 | 49.6467 | 49.6467 | 58.2486 | 238.2486 | 38.7578 | 579.0583 | 579.0583 | 168.8585 | 747.9168 | 0.66047 | 66.05% | 338.208 | 223.3748 | 156.3624 | 174.9547 | 174.9547 | 89.37% | 11.34% | 11.34% | 90% | 10.21% | 34.5244 | 4.313 | 4.313 | 148.903 | 76.3476 | 85.11% | 85.11%
7 | 210 | 29 | 5032 | 16 | 22.5 | 373.56 | 209.67 | 583.23 | 209.67 | 104.84 | 210 | 5032 | 960 | 207.1233 | 18.7825 | -12.0417 | 934.284 | 15.3707 | -50.5606 | 40.2785 | 40.2785 | 73.4145 | 253.4145 | 52.3285 | 353.1226 | 353.1226 | 178.9645 | 532.0872 | 0.59859 | 59.86% | 240.6098 | 144.0262 | 100.8184 | 156.8767 | 156.8767 | 64.27% | 11.32% | 11.32% | 90% | 10.18% | 24.5029 | 4.4719 | 4.4719 | 109.5737 | 54.1859 | 69.85% | 69.85%
7 | 210 | 29 | 5033 | 17 | 21.1 | 191.53 | 138.56 | 330.09 | 138.56 | 69.28 | 210 | 5033 | 1020 | 207.1233 | 18.7825 | -12.0417 | 994.284 | 16.3707 | -65.5606 | 30.1902 | 30.1902 | 85.6916 | 265.6916 | 66.328 | 152.9204 | 152.9204 | 118.2684 | 271.1887 | 0.38973 | 38.97% | 122.6315 | 47.7936 | 33.4555 | 139.7847 | 139.7847 | 23.93% | 11.32% | 11.32% | 80% | 9.056% | 11.1055 | 4.7303 | 4.7303 | 52.5326 | 24.5589 | 37.58% | 37.58%
7 | 210 | 29 | 5034 | 18 | 20.9 | 151.39 | 101.58 | 252.97 | 101.58 | 50.79 | 210 | 5034 | 1080 | 207.1233 | 18.7825 | -12.0417 | 1054.284 | 17.3707 | -80.5606 | 19.9354 | 19.9354 | 96.5571 | 276.5571 | 80.4919 | 73.3446 | 73.3446 | 86.704 | 160.0485 | 0.099326 | 9.933% | 72.374 | 7.1886 | 5.032 | 130.7697 | 130.7697 | 3.848% | 11.32% | 11.32% | 80% | 9.056% | 6.5544 | 4.7684 | 4.7684 | 31.2536 | 14.4944 | 23.9% | 23.9%
7 | 210 | 29 | 5035 | 19 | 21.4 | 135.08 | 83.14 | 218.22 | 83.14 | 41.57 | 210 | 5035 | 1140 | 207.1233 | 18.7825 | -12.0417 | 1114.284 | 18.3707 | -95.5606 | 9.8926 | 9.8926 | 106.9589 | 286.9589 | 94.6865 | 0 | 0 | 70.9644 | 70.9644 | -0.76988 | 0% | 32.0901 | 0 | 0 | 125.1672 | 125.1672 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.6738 | 4.6738 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5036 | 20 | 21 | 47.69 | 39.17 | 86.86 | 39.17 | 19.59 | 210 | 5036 | 1200 | 207.1233 | 18.7825 | -12.0417 | 1174.284 | 19.3707 | -110.5606 | 0.39672 | 0.39672 | 117.568 | 297.568 | 108.8048 | 0 | 0 | 33.4337 | 33.4337 | -2.5628 | 0% | 15.1187 | 0 | 0 | 151.4653 | 151.4653 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7493 | 4.7493 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5037 | 21 | 18.9 | 0 | 4.11 | 4.11 | 4.11 | 2.06 | 210 | 5037 | 1260 | 207.1233 | 18.7825 | -12.0417 | 1234.284 | 20.3707 | -125.5606 | -8.1888 | 0 | 118.0445 | 298.0445 | 109.4176 | 0 | 0 | 3.5081 | 3.5081 | -32.6006 | 0% | 1.5864 | 0 | 0 | -5.9765 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5038 | 22 | 17.2 | 0 | 0 | 0 | 0 | 0 | 210 | 5038 | 1320 | 207.1233 | 18.7825 | -12.0417 | 1294.284 | 21.3707 | -140.5606 | -15.4323 | 0 | 118.0445 | 298.0445 | 109.4176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6996 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5039 | 23 | 16.8 | 0 | 0 | 0 | 0 | 0 | 210 | 5039 | 1380 | 207.1233 | 18.7825 | -12.0417 | 1354.284 | 22.3707 | -155.5606 | -20.8326 | 0 | 118.0445 | 298.0445 | 109.4176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6067 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
7 | 210 | 29 | 5040 | 24 | 15.6 | 0 | 0 | 0 | 0 | 0 | 210 | 5040 | 1440 | 207.1233 | 18.7825 | -12.0417 | 1414.284 | 23.3707 | -170.5606 | -23.8882 | 0 | 118.0445 | 298.0445 | 109.4176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.733 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5041 | 1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 211 | 5041 | 60 | 208.1096 | 18.5562 | -12.2537 | 34.284 | 0.36717 | 174.4924 | -24.477 | 0 | 117.6903 | 62.3097 | 109.1831 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6144 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5042 | 2 | 14.6 | 0 | 0 | 0 | 0 | 0 | 211 | 5042 | 120 | 208.1096 | 18.5562 | -12.2537 | 94.284 | 1.3672 | 159.4924 | -22.0973 | 0 | 117.6903 | 62.3097 | 109.1831 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4142 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5043 | 3 | 14.3 | 0 | 0 | 0 | 0 | 0 | 211 | 5043 | 180 | 208.1096 | 18.5562 | -12.2537 | 154.284 | 2.3672 | 144.4924 | -17.2532 | 0 | 117.6903 | 62.3097 | 109.1831 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2141 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5044 | 4 | 13.9 | 0 | 0 | 0 | 0 | 0 | 211 | 5044 | 240 | 208.1096 | 18.5562 | -12.2537 | 214.284 | 3.3672 | 129.4924 | -10.4276 | 0 | 117.6903 | 62.3097 | 109.1831 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8237 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5045 | 5 | 13.6 | 0 | 0 | 0 | 0 | 0 | 211 | 5045 | 300 | 208.1096 | 18.5562 | -12.2537 | 274.284 | 4.3672 | 114.4924 | -2.1349 | 0 | 117.6903 | 62.3097 | 109.1831 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.1448 | 4.1448 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5046 | 6 | 12.8 | 0.47 | 4.44 | 4.91 | 4.44 | 2.22 | 211 | 5046 | 360 | 208.1096 | 18.5562 | -12.2537 | 334.284 | 5.3672 | 99.4924 | 7.171 | 7.171 | 109.5409 | 70.4591 | 98.418 | 0 | 0 | 3.7898 | 3.7898 | -33.75 | 0% | 1.7137 | 0 | 0 | 14.9269 | 14.9269 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5047 | 7 | 13.8 | 27.78 | 40.5 | 68.28 | 40.5 | 20.25 | 211 | 5047 | 420 | 208.1096 | 18.5562 | -12.2537 | 394.284 | 6.3672 | 84.4924 | 17.1102 | 17.1102 | 99.1288 | 80.8712 | 84.2137 | 9.5195 | 9.5195 | 34.5689 | 44.0884 | -2.1143 | 0% | 19.9368 | 0 | 0 | 187.484 | 187.484 | 0% | 11.61% | 11.61% | 80% | 9.288% | 1.8517 | 6.3002 | 6 | 11.1101 | 4.0948 | 5.926% | 5.926%
7 | 211 | 30 | 5048 | 8 | 16 | 80.5 | 82.44 | 162.94 | 82.44 | 41.22 | 211 | 5048 | 480 | 208.1096 | 18.5562 | -12.2537 | 454.284 | 7.3672 | 69.4924 | 27.3447 | 27.3447 | 88.4465 | 91.5535 | 70.0115 | 59.9063 | 59.9063 | 70.3669 | 130.2732 | -0.1453 | 0% | 58.9095 | 0 | 0 | 162.3481 | 162.3481 | 0% | 11.5% | 11.5% | 80% | 9.199% | 5.4194 | 5.7878 | 5.7878 | 31.3662 | 11.9844 | 19.32% | 19.32%
7 | 211 | 30 | 5049 | 9 | 18.3 | 204.72 | 93.39 | 298.11 | 93.39 | 46.7 | 211 | 5049 | 540 | 208.1096 | 18.5562 | -12.2537 | 514.284 | 8.3672 | 54.4924 | 37.5154 | 37.5154 | 76.6385 | 103.3615 | 55.9287 | 188.3313 | 188.3313 | 79.7134 | 268.0446 | 0.36184 | 36.18% | 121.2098 | 43.8586 | 30.701 | 172.9739 | 172.9739 | 17.75% | 11.4% | 11.4% | 80% | 9.121% | 11.056 | 5.2884 | 5.2884 | 58.4681 | 24.4494 | 33.8% | 33.8%
7 | 211 | 30 | 5050 | 10 | 20.7 | 347.36 | 157.83 | 505.19 | 157.83 | 78.92 | 211 | 5050 | 600 | 208.1096 | 18.5562 | -12.2537 | 574.284 | 9.3672 | 39.4924 | 47.131 | 47.131 | 62.4013 | 117.5987 | 42.1739 | 351.2463 | 351.2463 | 134.7163 | 485.9626 | 0.57102 | 57.1% | 219.7523 | 125.4827 | 87.8379 | 182.0806 | 182.0806 | 48.24% | 11.34% | 11.34% | 85% | 9.639% | 21.1818 | 4.8067 | 4.8067 | 101.8138 | 46.8416 | 55.92% | 55.92%
7 | 211 | 30 | 5051 | 11 | 22.4 | 427.83 | 222.5 | 650.33 | 222.5 | 111.25 | 211 | 5051 | 660 | 208.1096 | 18.5562 | -12.2537 | 634.284 | 10.3672 | 24.4924 | 55.3564 | 55.3564 | 43.7382 | 136.2618 | 29.2888 | 453.5513 | 453.5513 | 189.9156 | 643.4669 | 0.63381 | 63.38% | 290.9758 | 184.4224 | 129.0957 | 181.1431 | 181.1431 | 71.27% | 11.33% | 11.33% | 90% | 10.2% | 29.6743 | 4.4899 | 4.4899 | 133.234 | 65.6221 | 73.55% | 73.55%
7 | 211 | 30 | 5052 | 12 | 23.5 | 482.44 | 223.33 | 705.77 | 223.33 | 111.67 | 211 | 5052 | 720 | 208.1096 | 18.5562 | -12.2537 | 694.284 | 11.3672 | 9.4924 | 60.7193 | 60.7193 | 18.6425 | 161.3575 | 19.1863 | 522.3863 | 522.3863 | 190.6241 | 713.0103 | 0.65374 | 65.37% | 322.4233 | 210.7814 | 147.547 | 276.3109 | 276.3109 | 53.4% | 11.34% | 11.34% | 90% | 10.2% | 32.8927 | 4.2957 | 4.2957 | 141.2966 | 72.7394 | 51.14% | 51.14%
7 | 211 | 30 | 5053 | 13 | 24.2 | 238.81 | 244.64 | 483.45 | 244.64 | 122.32 | 211 | 5053 | 780 | 208.1096 | 18.5562 | -12.2537 | 754.284 | 12.3672 | -5.5076 | 61.4171 | 61.4171 | 10.9633 | 190.9633 | 17.6256 | 259.1873 | 259.1873 | 208.8133 | 468.0006 | 0.57829 | 57.83% | 211.6299 | 122.3838 | 85.6687 | 266.7417 | 266.7417 | 32.12% | 11.28% | 11.28% | 85% | 9.584% | 20.2826 | 4.1765 | 4.1765 | 84.7104 | 44.8532 | 31.76% | 31.76%
7 | 211 | 30 | 5054 | 14 | 24.4 | 226.11 | 151.39 | 377.5 | 151.39 | 75.7 | 211 | 5054 | 840 | 208.1096 | 18.5562 | -12.2537 | 814.284 | 13.3672 | -20.5076 | 57.1379 | 57.1379 | 37.739 | 217.739 | 26.1843 | 241.5612 | 241.5612 | 129.2194 | 370.7806 | 0.52027 | 52.03% | 167.667 | 87.2316 | 61.0621 | 260.5617 | 260.5617 | 23.43% | 11.25% | 11.25% | 85% | 9.561% | 16.0305 | 4.1431 | 4.1431 | 66.4156 | 35.45 | 25.49% | 25.49%
7 | 211 | 30 | 5055 | 15 | 25.4 | 294.31 | 214.17 | 508.48 | 214.17 | 107.09 | 211 | 5055 | 900 | 208.1096 | 18.5562 | -12.2537 | 874.284 | 14.3672 | -35.5076 | 49.4988 | 49.4988 | 57.9732 | 237.9732 | 38.6275 | 302.3716 | 302.3716 | 182.8055 | 485.1771 | 0.59157 | 59.16% | 219.3971 | 129.7881 | 90.8517 | 264.6639 | 264.6639 | 34.33% | 11.26% | 11.26% | 85% | 9.57% | 20.9957 | 3.9802 | 3.9802 | 83.5666 | 46.4301 | 31.57% | 31.57%
7 | 211 | 30 | 5056 | 16 | 25.5 | 352.44 | 212.83 | 565.27 | 212.83 | 106.42 | 211 | 5056 | 960 | 208.1096 | 18.5562 | -12.2537 | 934.284 | 15.3672 | -50.5076 | 40.1499 | 40.1499 | 73.1619 | 253.1619 | 52.2297 | 334.7885 | 334.7885 | 181.6618 | 516.4503 | 0.60484 | 60.48% | 233.5388 | 141.2543 | 98.878 | 267.5162 | 267.5162 | 36.96% | 11.27% | 11.27% | 90% | 10.14% | 23.6799 | 3.9643 | 3.9643 | 93.8737 | 52.366 | 35.09% | 35.09%
7 | 211 | 30 | 5057 | 17 | 25.6 | 221.53 | 143.67 | 365.2 | 143.67 | 71.84 | 211 | 5057 | 1020 | 208.1096 | 18.5562 | -12.2537 | 994.284 | 16.3672 | -65.5076 | 30.0695 | 30.0695 | 85.4628 | 265.4628 | 66.2526 | 178.0486 | 178.0486 | 122.63 | 300.6786 | 0.46263 | 46.26% | 135.9669 | 62.9026 | 44.0318 | 253.6455 | 253.6455 | 17.36% | 11.2% | 11.2% | 85% | 9.518% | 12.942 | 3.9484 | 3.9484 | 51.1006 | 28.62 | 20.15% | 20.15%
7 | 211 | 30 | 5058 | 18 | 24.9 | 115.33 | 101.06 | 216.39 | 101.06 | 50.53 | 211 | 5058 | 1080 | 208.1096 | 18.5562 | -12.2537 | 1054.284 | 17.3672 | -80.5076 | 19.814 | 19.814 | 96.3471 | 276.3471 | 80.4364 | 56.5281 | 56.5281 | 86.2601 | 142.7882 | 0.074714 | 7.471% | 64.5688 | 4.8242 | 3.3769 | 235.0867 | 235.0867 | 1.436% | 11.17% | 11.17% | 80% | 8.94% | 5.7724 | 4.0608 | 4.0608 | 23.4403 | 12.7651 | 9.971% | 9.971%
7 | 211 | 30 | 5059 | 19 | 24.4 | 61.44 | 79.22 | 140.66 | 79.22 | 39.61 | 211 | 5059 | 1140 | 208.1096 | 18.5562 | -12.2537 | 1114.284 | 18.3672 | -95.5076 | 9.7639 | 9.7639 | 106.7632 | 286.7632 | 94.6501 | 0 | 0 | 67.6185 | 67.6185 | -0.75183 | 0% | 30.5771 | 0 | 0 | 262.6668 | 262.6668 | 0% | 11.17% | 0% | 80% | 0% | 0 | 4.1431 | 4.1431 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5060 | 20 | 23.2 | 15.69 | 40.5 | 56.19 | 40.5 | 20.25 | 211 | 5060 | 1200 | 208.1096 | 18.5562 | -12.2537 | 1174.284 | 19.3672 | -110.5076 | 0.25528 | 0.25528 | 117.3843 | 297.3843 | 108.789 | 0 | 0 | 34.5689 | 34.5689 | -2.3139 | 0% | 15.6321 | 0 | 0 | 155.3927 | 155.3927 | 0% | 11.22% | 0% | 80% | 0% | 0 | 4.3478 | 4.3478 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5061 | 21 | 21.3 | 0 | 4.39 | 4.39 | 4.39 | 2.2 | 211 | 5061 | 1260 | 208.1096 | 18.5562 | -12.2537 | 1234.284 | 20.3672 | -125.5076 | -8.3475 | 0 | 117.6903 | 297.6903 | 109.1831 | 0 | 0 | 3.7471 | 3.7471 | -29.0611 | 0% | 1.6944 | 0 | 0 | -1.9433 | 0 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.6926 | 4.6926 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5062 | 22 | 18.4 | 0 | 0 | 0 | 0 | 0 | 211 | 5062 | 1320 | 208.1096 | 18.5562 | -12.2537 | 1294.284 | 21.3672 | -140.5076 | -15.6115 | 0 | 117.6903 | 297.6903 | 109.1831 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2524 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5063 | 23 | 16.7 | 0 | 0 | 0 | 0 | 0 | 211 | 5063 | 1380 | 208.1096 | 18.5562 | -12.2537 | 1354.284 | 22.3672 | -155.5076 | -21.033 | 0 | 117.6903 | 297.6903 | 109.1831 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1858 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
7 | 211 | 30 | 5064 | 24 | 15.8 | 0 | 0 | 0 | 0 | 0 | 211 | 5064 | 1440 | 208.1096 | 18.5562 | -12.2537 | 1414.284 | 23.3672 | -170.5076 | -24.1066 | 0 | 117.6903 | 297.6903 | 109.1831 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9001 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5065 | 1 | 15.5 | 0 | 0 | 0 | 0 | 0 | 212 | 5065 | 60 | 209.0959 | 18.325 | -12.4543 | 34.284 | 0.36383 | 174.5426 | -24.711 | 0 | 117.3294 | 62.6706 | 108.9435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9455 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5066 | 2 | 14.8 | 0 | 0 | 0 | 0 | 0 | 212 | 5066 | 120 | 209.0959 | 18.325 | -12.4543 | 94.284 | 1.3638 | 159.5426 | -22.3329 | 0 | 117.3294 | 62.6706 | 108.9435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3107 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5067 | 3 | 14.7 | 0 | 0 | 0 | 0 | 0 | 212 | 5067 | 180 | 209.0959 | 18.325 | -12.4543 | 154.284 | 2.3638 | 144.5426 | -17.4831 | 0 | 117.3294 | 62.6706 | 108.9435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7616 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5068 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 212 | 5068 | 240 | 209.0959 | 18.325 | -12.4543 | 214.284 | 3.3638 | 129.5426 | -10.648 | 0 | 117.3294 | 62.6706 | 108.9435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8283 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5069 | 5 | 13.9 | 0 | 0 | 0 | 0 | 0 | 212 | 5069 | 300 | 209.0959 | 18.325 | -12.4543 | 274.284 | 4.3638 | 114.5426 | -2.3452 | 0 | 117.3294 | 62.6706 | 108.9435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.203 | 5.203 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5070 | 6 | 13.6 | 0.33 | 3.75 | 4.08 | 3.75 | 1.88 | 212 | 5070 | 360 | 209.0959 | 18.325 | -12.4543 | 334.284 | 5.3638 | 99.5426 | 6.9693 | 6.9693 | 109.4176 | 70.5824 | 98.4846 | 0 | 0 | 3.2008 | 3.2008 | -39.5351 | 0% | 1.4474 | 0 | 0 | 17.9081 | 17.9081 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5071 | 7 | 14.1 | 29.58 | 38.33 | 67.91 | 38.33 | 19.17 | 212 | 5071 | 420 | 209.0959 | 18.325 | -12.4543 | 394.284 | 6.3638 | 84.5426 | 16.9142 | 16.9142 | 98.9914 | 81.0086 | 84.2611 | 10.1665 | 10.1665 | 32.7167 | 42.8832 | -2.1803 | 0% | 19.3918 | 0 | 0 | 192.2335 | 192.2335 | 0% | 11.6% | 11.6% | 80% | 9.278% | 1.7992 | 6.2283 | 6 | 10.7952 | 3.9788 | 5.616% | 5.616%
7 | 212 | 31 | 5072 | 8 | 16 | 160.22 | 82.28 | 242.5 | 82.28 | 41.14 | 212 | 5072 | 480 | 209.0959 | 18.325 | -12.4543 | 454.284 | 7.3638 | 69.5426 | 27.1503 | 27.1503 | 88.296 | 91.704 | 70.0389 | 119.8619 | 119.8619 | 70.2304 | 190.0923 | 0.15343 | 15.34% | 85.9597 | 13.1886 | 9.2321 | 172.1688 | 172.1688 | 5.362% | 11.49% | 11.49% | 80% | 9.189% | 7.8988 | 5.7878 | 5.7878 | 45.7166 | 17.4675 | 26.55% | 26.55%
7 | 212 | 31 | 5073 | 9 | 18.5 | 221.61 | 129.5 | 351.11 | 129.5 | 64.75 | 212 | 5073 | 540 | 209.0959 | 18.325 | -12.4543 | 514.284 | 8.3638 | 54.5426 | 37.3175 | 37.3175 | 76.4769 | 103.5231 | 55.9325 | 204.7722 | 204.7722 | 110.5352 | 315.3074 | 0.42953 | 42.95% | 142.582 | 61.2428 | 42.87 | 181.07 | 181.07 | 23.68% | 11.39% | 11.39% | 85% | 9.683% | 13.8065 | 5.2467 | 5.2467 | 72.4381 | 30.5318 | 40.01% | 40.01%
7 | 212 | 31 | 5074 | 10 | 20.4 | 387.5 | 153.19 | 540.69 | 153.19 | 76.6 | 212 | 5074 | 600 | 209.0959 | 18.325 | -12.4543 | 574.284 | 9.3638 | 39.5426 | 46.9228 | 46.9228 | 62.2382 | 117.7618 | 42.1451 | 393.3425 | 393.3425 | 130.7558 | 524.0983 | 0.58672 | 58.67% | 236.9973 | 139.0501 | 97.3351 | 188.1123 | 188.1123 | 51.74% | 11.35% | 11.35% | 90% | 10.21% | 24.2006 | 4.8647 | 4.8647 | 117.7281 | 53.5174 | 62.58% | 62.58%
7 | 212 | 31 | 5075 | 11 | 22.7 | 473.94 | 174.67 | 648.61 | 174.67 | 87.34 | 212 | 5075 | 660 | 209.0959 | 18.325 | -12.4543 | 634.284 | 10.3638 | 24.5426 | 55.1323 | 55.1323 | 43.6084 | 136.3916 | 29.2071 | 504.2014 | 504.2014 | 149.0902 | 653.2916 | 0.63736 | 63.74% | 295.4185 | 188.2883 | 131.8018 | 185.2243 | 185.2243 | 71.16% | 11.33% | 11.33% | 90% | 10.2% | 30.1244 | 4.4361 | 4.4361 | 133.6341 | 66.6174 | 72.15% | 72.15%
7 | 212 | 31 | 5076 | 12 | 24.8 | 510.22 | 192.22 | 702.44 | 192.22 | 96.11 | 212 | 5076 | 720 | 209.0959 | 18.325 | -12.4543 | 694.284 | 11.3638 | 9.5426 | 60.4834 | 60.4834 | 18.6282 | 161.3718 | 19.0109 | 554.3367 | 554.3367 | 164.07 | 718.4068 | 0.65875 | 65.88% | 324.8635 | 214.0045 | 149.8032 | 205.744 | 205.744 | 72.81% | 11.33% | 11.33% | 90% | 10.2% | 33.1277 | 4.0771 | 4.0771 | 135.0642 | 73.2589 | 65.65% | 65.65%
7 | 212 | 31 | 5077 | 13 | 25.8 | 501.89 | 217.17 | 719.06 | 217.17 | 108.59 | 212 | 5077 | 780 | 209.0959 | 18.325 | -12.4543 | 754.284 | 12.3638 | -5.4574 | 61.1947 | 61.1947 | 10.7995 | 190.7995 | 17.3914 | 546.5789 | 546.5789 | 185.3662 | 731.9451 | 0.66435 | 66.43% | 330.9856 | 219.8898 | 153.9229 | 271.2195 | 271.2195 | 56.75% | 11.33% | 11.33% | 90% | 10.2% | 33.7515 | 3.917 | 3.917 | 132.2038 | 74.6384 | 48.74% | 48.74%
7 | 212 | 31 | 5078 | 14 | 27 | 465.47 | 229.44 | 694.91 | 229.44 | 114.72 | 212 | 5078 | 840 | 209.0959 | 18.325 | -12.4543 | 814.284 | 13.3638 | -20.4574 | 56.9514 | 56.9514 | 37.4733 | 217.4733 | 26.0063 | 499.0872 | 499.0872 | 195.8393 | 694.9265 | 0.66056 | 66.06% | 314.2458 | 207.5788 | 145.3052 | 272.716 | 272.716 | 53.28% | 11.31% | 11.31% | 90% | 10.18% | 31.9915 | 3.7341 | 3.7341 | 119.4593 | 70.7462 | 43.8% | 43.8%
7 | 212 | 31 | 5079 | 15 | 27.8 | 417.36 | 195.14 | 612.5 | 195.14 | 97.57 | 212 | 5079 | 900 | 209.0959 | 18.325 | -12.4543 | 874.284 | 14.3638 | -35.4574 | 49.345 | 49.345 | 57.6982 | 237.6982 | 38.4987 | 430.5505 | 430.5505 | 166.5624 | 597.1129 | 0.63988 | 63.99% | 270.0144 | 172.7772 | 120.9441 | 276.1073 | 276.1073 | 43.8% | 11.26% | 11.26% | 90% | 10.14% | 27.3753 | 3.6178 | 3.6178 | 99.0379 | 60.5381 | 35.87% | 35.87%
7 | 212 | 31 | 5080 | 16 | 28.2 | 347.56 | 174.11 | 521.67 | 174.11 | 87.06 | 212 | 5080 | 960 | 209.0959 | 18.325 | -12.4543 | 934.284 | 15.3638 | -50.4574 | 40.0156 | 40.0156 | 72.9083 | 252.9083 | 52.1331 | 331.7945 | 331.7945 | 148.6122 | 480.4067 | 0.60176 | 60.18% | 217.2399 | 130.7252 | 91.5077 | 274.078 | 274.078 | 33.39% | 11.21% | 11.21% | 85% | 9.527% | 20.6958 | 3.5613 | 3.5613 | 73.7038 | 45.7668 | 26.89% | 26.89%
7 | 212 | 31 | 5081 | 17 | 27.7 | 345.14 | 129.78 | 474.92 | 129.78 | 64.89 | 212 | 5081 | 1020 | 209.0959 | 18.325 | -12.4543 | 994.284 | 16.3638 | -65.4574 | 29.9432 | 29.9432 | 85.2326 | 265.2326 | 66.1796 | 279.2633 | 279.2633 | 110.7742 | 390.0375 | 0.55221 | 55.22% | 176.375 | 97.3962 | 68.1774 | 262.9338 | 262.9338 | 25.93% | 11.18% | 11.18% | 85% | 9.502% | 16.7585 | 3.6321 | 3.6321 | 60.8681 | 37.0599 | 23.15% | 23.15%
7 | 212 | 31 | 5082 | 18 | 27.33 | 223.39 | 93.83 | 317.22 | 93.83 | 46.92 | 212 | 5082 | 1080 | 209.0959 | 18.325 | -12.4543 | 1054.284 | 17.3638 | -80.4574 | 19.6872 | 19.6872 | 96.1357 | 276.1357 | 80.3835 | 110.7738 | 110.7738 | 80.0889 | 190.8628 | 0.28539 | 28.54% | 86.3081 | 24.6311 | 17.2418 | 244.9238 | 244.9238 | 7.04% | 11.11% | 11.11% | 80% | 8.885% | 7.6686 | 3.6856 | 3.6856 | 28.2632 | 16.9584 | 11.54% | 11.54%
7 | 212 | 31 | 5083 | 19 | 26.93 | 112.36 | 76.53 | 188.89 | 76.53 | 38.27 | 212 | 5083 | 1140 | 209.0959 | 18.325 | -12.4543 | 1114.284 | 18.3638 | -95.4574 | 9.6298 | 9.6298 | 106.5661 | 286.5661 | 94.6164 | 0 | 0 | 65.3224 | 65.3224 | -0.72421 | 0% | 29.5388 | 0 | 0 | 198.5809 | 198.5809 | 0% | 11.07% | 0% | 80% | 0% | 0 | 3.7445 | 3.7445 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5084 | 20 | 25.55 | 19.31 | 29.22 | 48.53 | 29.22 | 14.61 | 212 | 5084 | 1200 | 209.0959 | 18.325 | -12.4543 | 1174.284 | 19.3638 | -110.4574 | 0.10852 | 0.10852 | 117.1995 | 297.1995 | 108.7762 | 0 | 0 | 24.9408 | 24.9408 | -3.3157 | 0% | 11.2782 | 0 | 0 | 198.2584 | 198.2584 | 0% | 11.12% | 0% | 80% | 0% | 0 | 3.9563 | 3.9563 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5085 | 21 | 23.32 | 0 | 2.78 | 2.78 | 2.78 | 1.39 | 212 | 5085 | 1260 | 209.0959 | 18.325 | -12.4543 | 1234.284 | 20.3638 | -125.4574 | -8.5116 | 0 | 117.3294 | 297.3294 | 108.9435 | 0 | 0 | 2.3729 | 2.3729 | -44.5098 | 0% | 1.073 | 0 | 0 | -0.043097 | 0 | 0% | 11.21% | 0% | 80% | 0% | 0 | 4.3269 | 4.3269 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5086 | 22 | 20.98 | 0 | 0 | 0 | 0 | 0 | 212 | 5086 | 1320 | 209.0959 | 18.325 | -12.4543 | 1294.284 | 21.3638 | -140.4574 | -15.796 | 0 | 117.3294 | 297.3294 | 108.9435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.6989 | 0 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7531 | 4.7531 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5087 | 23 | 19.31 | 0 | 0 | 0 | 0 | 0 | 212 | 5087 | 1380 | 209.0959 | 18.325 | -12.4543 | 1354.284 | 22.3638 | -155.4574 | -21.2386 | 0 | 117.3294 | 297.3294 | 108.9435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5423 | 0 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0807 | 5.0807 | 0 | 0 | 0% | 0%
7 | 212 | 31 | 5088 | 24 | 18.33 | 0 | 0 | 0 | 0 | 0 | 212 | 5088 | 1440 | 209.0959 | 18.325 | -12.4543 | 1414.284 | 23.3638 | -170.4574 | -24.33 | 0 | 117.3294 | 297.3294 | 108.9435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3343 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2821 | 5.2821 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5089 | 1 | 17.7 | 0 | 0 | 0 | 0 | 0 | 213 | 5089 | 60 | 210.0822 | 18.0892 | -12.6435 | 34.284 | 0.36068 | 174.5899 | -24.9494 | 0 | 116.9617 | 63.0383 | 108.6991 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5446 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5090 | 2 | 17.34 | 0 | 0 | 0 | 0 | 0 | 213 | 5090 | 120 | 210.0822 | 18.0892 | -12.6435 | 94.284 | 1.3607 | 159.5899 | -22.5724 | 0 | 116.9617 | 63.0383 | 108.6991 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5374 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4923 | 5.4923 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5091 | 3 | 16.87 | 0 | 0 | 0 | 0 | 0 | 213 | 5091 | 180 | 210.0822 | 18.0892 | -12.6435 | 154.284 | 2.3607 | 144.5899 | -17.7163 | 0 | 116.9617 | 63.0383 | 108.6991 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6979 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.5945 | 5.5945 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5092 | 4 | 16.42 | 0 | 0 | 0 | 0 | 0 | 213 | 5092 | 240 | 210.0822 | 18.0892 | -12.6435 | 214.284 | 3.3607 | 129.5899 | -10.8711 | 0 | 116.9617 | 63.0383 | 108.6991 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3837 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6938 | 5.6938 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5093 | 5 | 16.19 | 0 | 0 | 0 | 0 | 0 | 213 | 5093 | 300 | 210.0822 | 18.0892 | -12.6435 | 274.284 | 4.3607 | 114.5899 | -2.5576 | 0 | 116.9617 | 63.0383 | 108.6991 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.5451 | 5.5451 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7451 | 5.7451 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5094 | 6 | 16.35 | 0.08 | 2.22 | 2.3 | 2.22 | 1.11 | 213 | 5094 | 360 | 210.0822 | 18.0892 | -12.6435 | 334.284 | 5.3607 | 99.5899 | 6.7658 | 6.7658 | 109.2891 | 70.7109 | 98.5487 | 0 | 0 | 1.8949 | 1.8949 | -64.0444 | 0% | 0.85687 | 0 | 0 | 17.2222 | 17.2222 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7094 | 5.7094 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5095 | 7 | 17.46 | 17.08 | 35.5 | 52.58 | 35.5 | 17.75 | 213 | 5095 | 420 | 210.0822 | 18.0892 | -12.6435 | 394.284 | 6.3607 | 84.5899 | 16.7166 | 16.7166 | 98.8488 | 81.1512 | 84.306 | 5.8914 | 5.8914 | 30.3011 | 36.1925 | -2.5224 | 0% | 16.3663 | 0 | 0 | 186.7657 | 186.7657 | 0% | 11.46% | 11.46% | 80% | 9.167% | 1.5003 | 5.4665 | 5.4665 | 8.2013 | 3.3178 | 4.391% | 4.391%
8 | 213 | 1 | 5096 | 8 | 19.6 | 91.72 | 81.67 | 173.39 | 81.67 | 40.84 | 213 | 5096 | 480 | 210.0822 | 18.0892 | -12.6435 | 454.284 | 7.3607 | 69.5899 | 26.9544 | 26.9544 | 88.1401 | 91.8599 | 70.0637 | 68.9952 | 68.9952 | 69.7097 | 138.7049 | -0.029705 | 0% | 62.7223 | 0 | 0 | 163.1486 | 163.1486 | 0% | 11.37% | 11.37% | 80% | 9.093% | 5.7035 | 5.0224 | 5.0224 | 28.6455 | 12.6128 | 17.56% | 17.56%
8 | 213 | 1 | 5097 | 9 | 22.1 | 165.78 | 130.28 | 296.06 | 130.28 | 65.14 | 213 | 5097 | 540 | 210.0822 | 18.0892 | -12.6435 | 514.284 | 8.3607 | 54.5899 | 37.1177 | 37.1177 | 76.3096 | 103.6904 | 55.9335 | 153.8849 | 153.8849 | 111.2009 | 265.0859 | 0.38842 | 38.84% | 119.8718 | 46.5604 | 32.5923 | 173.4263 | 173.4263 | 18.79% | 11.29% | 11.29% | 80% | 9.032% | 10.827 | 4.5443 | 4.5443 | 49.2014 | 23.943 | 28.37% | 28.37%
8 | 213 | 1 | 5098 | 10 | 24.9 | 268 | 147.44 | 415.44 | 147.44 | 73.72 | 213 | 5098 | 600 | 210.0822 | 18.0892 | -12.6435 | 574.284 | 9.3607 | 39.5899 | 46.7125 | 46.7125 | 62.0691 | 117.9309 | 42.1135 | 273.1162 | 273.1162 | 125.8479 | 398.9641 | 0.54299 | 54.3% | 180.4116 | 97.9617 | 68.5732 | 212.7009 | 212.7009 | 32.24% | 11.24% | 11.24% | 85% | 9.557% | 17.2425 | 4.0608 | 4.0608 | 70.0177 | 38.1303 | 32.92% | 32.92%
8 | 213 | 1 | 5099 | 11 | 25.5 | 342.92 | 194.58 | 537.5 | 194.58 | 97.29 | 213 | 5099 | 660 | 210.0822 | 18.0892 | -12.6435 | 634.284 | 10.3607 | 24.5899 | 54.9052 | 54.9052 | 43.4721 | 136.5279 | 29.1222 | 366.1313 | 366.1313 | 166.0844 | 532.2157 | 0.61074 | 61.07% | 240.6679 | 146.9861 | 102.8903 | 220.7543 | 220.7543 | 46.61% | 11.27% | 11.27% | 90% | 10.14% | 24.4131 | 3.9643 | 3.9643 | 96.7803 | 53.9874 | 43.84% | 43.84%
8 | 213 | 1 | 5100 | 12 | 26.1 | 402.44 | 203.56 | 606 | 203.56 | 101.78 | 213 | 5100 | 720 | 210.0822 | 18.0892 | -12.6435 | 694.284 | 11.3607 | 9.5899 | 60.2435 | 60.2435 | 18.6068 | 161.3932 | 18.8313 | 438.7512 | 438.7512 | 173.7493 | 612.5005 | 0.63815 | 63.82% | 276.9727 | 176.7513 | 123.7259 | 222.2448 | 222.2448 | 55.67% | 11.29% | 11.29% | 90% | 10.16% | 28.1409 | 3.8703 | 3.8703 | 108.9143 | 62.2312 | 49.01% | 49.01%
8 | 213 | 1 | 5101 | 13 | 26.6 | 445.33 | 203.75 | 649.08 | 203.75 | 101.88 | 213 | 5101 | 780 | 210.0822 | 18.0892 | -12.6435 | 754.284 | 12.3607 | -5.4101 | 60.967 | 60.967 | 10.6421 | 190.6421 | 17.1535 | 486.6767 | 486.6767 | 173.9115 | 660.5882 | 0.65183 | 65.18% | 298.718 | 194.7129 | 136.299 | 230.7645 | 230.7645 | 59.06% | 11.3% | 11.3% | 90% | 10.17% | 30.3834 | 3.7939 | 3.7939 | 115.2727 | 67.1901 | 49.95% | 49.95%
8 | 213 | 1 | 5102 | 14 | 27.3 | 208.47 | 328.19 | 536.66 | 328.19 | 164.1 | 213 | 5102 | 840 | 210.0822 | 18.0892 | -12.6435 | 814.284 | 13.3607 | -20.4101 | 56.7589 | 56.7589 | 37.2108 | 217.2108 | 25.8285 | 224.3553 | 224.3553 | 280.1277 | 504.4829 | 0.60767 | 60.77% | 228.1272 | 138.6251 | 97.0376 | 267.9551 | 267.9551 | 36.21% | 11.23% | 11.23% | 90% | 10.11% | 23.0637 | 3.69 | 3.69 | 85.104 | 51.0033 | 31.76% | 31.76%
8 | 213 | 1 | 5103 | 15 | 20.3 | 372.92 | 219.11 | 592.03 | 219.11 | 109.56 | 213 | 5103 | 900 | 210.0822 | 18.0892 | -12.6435 | 874.284 | 14.3607 | -35.4101 | 49.1851 | 49.1851 | 57.4237 | 237.4237 | 38.3714 | 386.3116 | 386.3116 | 187.0221 | 573.3337 | 0.60499 | 60.5% | 259.2615 | 156.8512 | 109.7959 | 153.5305 | 153.5305 | 71.51% | 11.35% | 11.35% | 90% | 10.21% | 26.4795 | 4.8842 | 4.8842 | 129.33 | 58.5571 | 84.24% | 84.24%
8 | 213 | 1 | 5104 | 16 | 21.4 | 381.94 | 159.03 | 540.97 | 159.03 | 79.52 | 213 | 5104 | 960 | 210.0822 | 18.0892 | -12.6435 | 934.284 | 15.3607 | -50.4101 | 39.8755 | 39.8755 | 72.654 | 252.654 | 52.0385 | 366.4566 | 366.4566 | 135.7406 | 502.1972 | 0.5816 | 58.16% | 227.0936 | 132.0774 | 92.4542 | 151.0678 | 151.0678 | 61.2% | 11.33% | 11.33% | 90% | 10.2% | 23.1548 | 4.6738 | 4.6738 | 108.2206 | 51.2048 | 71.64% | 71.64%
8 | 213 | 1 | 5105 | 17 | 23.3 | 249.39 | 153.11 | 402.5 | 153.11 | 76.56 | 213 | 5105 | 1020 | 210.0822 | 18.0892 | -12.6435 | 994.284 | 16.3607 | -65.4101 | 29.8114 | 29.8114 | 85.0011 | 265.0011 | 66.1091 | 203.1636 | 203.1636 | 130.6876 | 333.8512 | 0.4818 | 48.18% | 150.9675 | 72.736 | 50.9152 | 150.1401 | 150.1401 | 33.91% | 11.27% | 11.27% | 85% | 9.577% | 14.4586 | 4.3304 | 4.3304 | 62.6108 | 31.9739 | 41.7% | 41.7%
8 | 213 | 1 | 5106 | 18 | 23.3 | 186.67 | 122.36 | 309.03 | 122.36 | 61.18 | 213 | 5106 | 1080 | 210.0822 | 18.0892 | -12.6435 | 1054.284 | 17.3607 | -80.4101 | 19.5549 | 19.5549 | 95.9229 | 275.9229 | 80.3332 | 93.6489 | 93.6489 | 104.4408 | 198.0896 | 0.26098 | 26.1% | 89.5761 | 23.3773 | 16.3641 | 141.458 | 141.458 | 11.57% | 11.24% | 11.24% | 80% | 8.994% | 8.0567 | 4.3304 | 4.3304 | 34.8882 | 17.8166 | 24.66% | 24.66%
8 | 213 | 1 | 5107 | 19 | 22.2 | 110.06 | 77.22 | 187.28 | 77.22 | 38.61 | 213 | 5107 | 1140 | 210.0822 | 18.0892 | -12.6435 | 1114.284 | 18.3607 | -95.4101 | 9.4905 | 9.4905 | 106.3679 | 286.3679 | 94.5855 | 0 | 0 | 65.9114 | 65.9114 | -0.86411 | 0% | 29.8051 | 0 | 0 | 123.6827 | 123.6827 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.5261 | 4.5261 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5108 | 20 | 20.9 | 34.58 | 38 | 72.58 | 38 | 19 | 213 | 5108 | 1200 | 210.0822 | 18.0892 | -12.6435 | 1174.284 | 19.3607 | -110.4101 | -0.043549 | 0 | 116.9617 | 296.9617 | 108.6991 | 0 | 0 | 32.435 | 32.435 | -2.6732 | 0% | 14.6671 | 0 | 0 | 149.7009 | 149.7009 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7684 | 4.7684 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5109 | 21 | 20 | 0 | 2.78 | 2.78 | 2.78 | 1.39 | 213 | 5109 | 1260 | 210.0822 | 18.0892 | -12.6435 | 1234.284 | 20.3607 | -125.4101 | -8.681 | 0 | 116.9617 | 296.9617 | 108.6991 | 0 | 0 | 2.3729 | 2.3729 | -47.5581 | 0% | 1.073 | 0 | 0 | -4.7586 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5110 | 22 | 19 | 0 | 0 | 0 | 0 | 0 | 213 | 5110 | 1320 | 210.0822 | 18.0892 | -12.6435 | 1294.284 | 21.3607 | -140.4101 | -15.9859 | 0 | 116.9617 | 296.9617 | 108.6991 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2309 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5111 | 23 | 18.5 | 0 | 0 | 0 | 0 | 0 | 213 | 5111 | 1380 | 210.0822 | 18.0892 | -12.6435 | 1354.284 | 22.3607 | -155.4101 | -21.4495 | 0 | 116.9617 | 296.9617 | 108.6991 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4371 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
8 | 213 | 1 | 5112 | 24 | 17.6 | 0 | 0 | 0 | 0 | 0 | 213 | 5112 | 1440 | 210.0822 | 18.0892 | -12.6435 | 1414.284 | 23.3607 | -170.4101 | -24.5584 | 0 | 116.9617 | 296.9617 | 108.6991 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2528 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5113 | 1 | 17.3 | 0 | 0 | 0 | 0 | 0 | 214 | 5113 | 60 | 211.0685 | 17.8486 | -12.821 | 34.284 | 0.35772 | 174.6342 | -25.1924 | 0 | 116.5874 | 63.4126 | 108.4499 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5299 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5114 | 2 | 16.8 | 0 | 0 | 0 | 0 | 0 | 214 | 5114 | 120 | 211.0685 | 17.8486 | -12.821 | 94.284 | 1.3577 | 159.6342 | -22.8157 | 0 | 116.5874 | 63.4126 | 108.4499 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.664 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5115 | 3 | 16.7 | 0 | 0 | 0 | 0 | 0 | 214 | 5115 | 180 | 211.0685 | 17.8486 | -12.821 | 154.284 | 2.3577 | 144.6342 | -17.9525 | 0 | 116.5874 | 63.4126 | 108.4499 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1886 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5116 | 4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 214 | 5116 | 240 | 211.0685 | 17.8486 | -12.821 | 214.284 | 3.3577 | 129.6342 | -11.0966 | 0 | 116.5874 | 63.4126 | 108.4499 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.7982 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5117 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 214 | 5117 | 300 | 211.0685 | 17.8486 | -12.821 | 274.284 | 4.3577 | 114.6342 | -2.7721 | 0 | 116.5874 | 63.4126 | 108.4499 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.5726 | 5.5726 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5118 | 6 | 15.8 | 0.28 | 3.67 | 3.95 | 3.67 | 1.84 | 214 | 5118 | 360 | 211.0685 | 17.8486 | -12.821 | 334.284 | 5.3577 | 99.6342 | 6.5607 | 6.5607 | 109.1556 | 70.8444 | 98.6105 | 0 | 0 | 3.1325 | 3.1325 | -38.8188 | 0% | 1.4165 | 0 | 0 | 16.7576 | 16.7576 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5119 | 7 | 17.3 | 30.97 | 39.58 | 70.55 | 39.58 | 19.79 | 214 | 5119 | 420 | 211.0685 | 17.8486 | -12.821 | 394.284 | 6.3577 | 84.6342 | 16.5175 | 16.5175 | 98.7011 | 81.2989 | 84.3484 | 10.7275 | 10.7275 | 33.7836 | 44.5111 | -1.9088 | 0% | 20.1279 | 0 | 0 | 189.833 | 189.833 | 0% | 11.46% | 11.46% | 80% | 9.171% | 1.846 | 5.501 | 5.501 | 10.1548 | 4.0823 | 5.349% | 5.349%
8 | 214 | 2 | 5120 | 8 | 19.1 | 116.53 | 59.11 | 175.64 | 59.11 | 29.56 | 214 | 5120 | 480 | 211.0685 | 17.8486 | -12.821 | 454.284 | 7.3577 | 69.6342 | 26.757 | 26.757 | 87.9789 | 92.0211 | 70.0858 | 88.1628 | 88.1628 | 50.4535 | 138.6163 | -0.038208 | 0% | 62.6823 | 0 | 0 | 164.5348 | 164.5348 | 0% | 11.38% | 11.38% | 80% | 9.108% | 5.709 | 5.1233 | 5.1233 | 29.2489 | 12.6249 | 17.78% | 17.78%
8 | 214 | 2 | 5121 | 9 | 21.2 | 230.33 | 77.78 | 308.11 | 77.78 | 38.89 | 214 | 5121 | 540 | 211.0685 | 17.8486 | -12.821 | 514.284 | 8.3577 | 54.6342 | 36.9162 | 36.9162 | 76.1367 | 103.8633 | 55.9317 | 214.8126 | 214.8126 | 66.3894 | 281.202 | 0.40526 | 40.53% | 127.1596 | 51.5329 | 36.0731 | 174.3948 | 174.3948 | 20.68% | 11.32% | 11.32% | 80% | 9.054% | 11.5133 | 4.7114 | 4.7114 | 54.2437 | 25.4606 | 31.1% | 31.1%
8 | 214 | 2 | 5122 | 10 | 24.2 | 338.94 | 103.06 | 442 | 103.06 | 51.53 | 214 | 5122 | 600 | 211.0685 | 17.8486 | -12.821 | 574.284 | 9.3577 | 39.6342 | 46.4999 | 46.4999 | 61.894 | 118.106 | 42.0789 | 346.8128 | 346.8128 | 87.9672 | 434.7801 | 0.56105 | 56.1% | 196.6075 | 110.3059 | 77.2141 | 201.7335 | 201.7335 | 38.28% | 11.27% | 11.27% | 85% | 9.577% | 18.8301 | 4.1765 | 4.1765 | 78.6438 | 41.641 | 38.98% | 38.98%
8 | 214 | 2 | 5123 | 11 | 25.1 | 443.47 | 145.83 | 589.3 | 145.83 | 72.92 | 214 | 5123 | 660 | 211.0685 | 17.8486 | -12.821 | 634.284 | 10.3577 | 24.6342 | 54.6753 | 54.6753 | 43.3294 | 136.6706 | 29.0341 | 475.2358 | 475.2358 | 124.4737 | 599.7095 | 0.63107 | 63.11% | 271.1886 | 171.1395 | 119.7977 | 215.4301 | 215.4301 | 55.61% | 11.3% | 11.3% | 90% | 10.17% | 27.5697 | 4.0283 | 4.0283 | 111.0594 | 60.9679 | 51.55% | 51.55%
8 | 214 | 2 | 5124 | 12 | 27.1 | 521.39 | 157.08 | 678.47 | 157.08 | 78.54 | 214 | 5124 | 720 | 211.0685 | 17.8486 | -12.821 | 694.284 | 11.3577 | 9.6342 | 59.9997 | 59.9997 | 18.5785 | 161.4215 | 18.6477 | 570.4451 | 570.4451 | 134.0762 | 704.5213 | 0.66281 | 66.28% | 318.5845 | 211.1625 | 147.8137 | 274.6469 | 274.6469 | 53.82% | 11.31% | 11.31% | 90% | 10.18% | 32.4422 | 3.7193 | 3.7193 | 120.6629 | 71.7431 | 43.93% | 43.93%
8 | 214 | 2 | 5125 | 13 | 27.2 | 488.14 | 135.92 | 624.06 | 135.92 | 67.96 | 214 | 5125 | 780 | 211.0685 | 17.8486 | -12.821 | 754.284 | 12.3577 | -5.3658 | 60.7341 | 60.7341 | 10.491 | 190.491 | 16.9121 | 535.3627 | 535.3627 | 116.015 | 651.3776 | 0.65162 | 65.16% | 294.553 | 191.9363 | 134.3554 | 238.6594 | 238.6594 | 56.3% | 11.29% | 11.29% | 90% | 10.16% | 29.9379 | 3.7046 | 3.7046 | 110.9078 | 66.2049 | 46.47% | 46.47%
8 | 214 | 2 | 5126 | 14 | 21.9 | 529.5 | 168.56 | 698.06 | 168.56 | 84.28 | 214 | 5126 | 840 | 211.0685 | 17.8486 | -12.821 | 814.284 | 13.3577 | -20.3658 | 56.5605 | 56.5605 | 36.9516 | 216.9516 | 25.6509 | 572.0013 | 572.0013 | 143.875 | 715.8763 | 0.6495 | 64.95% | 323.7192 | 210.257 | 147.1799 | 159.9518 | 159.9518 | 92.02% | 11.34% | 11.34% | 90% | 10.21% | 33.0481 | 4.581 | 4.581 | 151.392 | 73.083 | 94.65% | 94.65%
8 | 214 | 2 | 5127 | 15 | 24 | 505.22 | 181.72 | 686.94 | 181.72 | 90.86 | 214 | 5127 | 900 | 211.0685 | 17.8486 | -12.821 | 874.284 | 14.3577 | -35.3658 | 49.0193 | 49.0193 | 57.1498 | 237.1498 | 38.2459 | 525.5851 | 525.5851 | 155.1077 | 680.6928 | 0.64819 | 64.82% | 307.8093 | 199.518 | 139.6626 | 177.4287 | 177.4287 | 78.71% | 11.33% | 11.33% | 90% | 10.19% | 31.3755 | 4.2102 | 4.2102 | 132.0973 | 69.3842 | 74.45% | 74.45%
8 | 214 | 2 | 5128 | 16 | 26.6 | 324.5 | 160.42 | 484.92 | 160.42 | 80.21 | 214 | 5128 | 960 | 211.0685 | 17.8486 | -12.821 | 934.284 | 15.3577 | -50.3658 | 39.7296 | 39.7296 | 72.399 | 252.399 | 51.9463 | 312.9422 | 312.9422 | 136.927 | 449.8692 | 0.58055 | 58.06% | 203.4309 | 118.102 | 82.6714 | 215.1696 | 215.1696 | 38.42% | 11.22% | 11.22% | 85% | 9.541% | 19.4097 | 3.7939 | 3.7939 | 73.6392 | 42.9228 | 34.22% | 34.22%
8 | 214 | 2 | 5129 | 17 | 27 | 253.11 | 153.11 | 406.22 | 153.11 | 76.56 | 214 | 5129 | 1020 | 211.0685 | 17.8486 | -12.821 | 994.284 | 16.3577 | -65.3658 | 29.674 | 29.674 | 84.7686 | 264.7686 | 66.0411 | 207.6159 | 207.6159 | 130.6876 | 338.3035 | 0.50936 | 50.94% | 152.9808 | 77.9218 | 54.5453 | 216.3698 | 216.3698 | 25.21% | 11.17% | 11.17% | 85% | 9.498% | 14.5303 | 3.7341 | 3.7341 | 54.2575 | 32.1324 | 25.08% | 25.08%
8 | 214 | 2 | 5130 | 18 | 21.3 | 165.69 | 105.22 | 270.91 | 105.22 | 52.61 | 214 | 5130 | 1080 | 211.0685 | 17.8486 | -12.821 | 1054.284 | 17.3577 | -80.3658 | 19.4173 | 19.4173 | 95.7089 | 275.7089 | 80.2857 | 84.0977 | 84.0977 | 89.8109 | 173.9085 | 0.16052 | 16.05% | 78.6414 | 12.6231 | 8.8362 | 128.5719 | 128.5719 | 6.873% | 11.31% | 11.31% | 80% | 9.046% | 7.1137 | 4.6926 | 4.6926 | 33.3816 | 15.7314 | 25.96% | 25.96%
8 | 214 | 2 | 5131 | 19 | 21.1 | 101.61 | 73 | 174.61 | 73 | 36.5 | 214 | 5131 | 1140 | 211.0685 | 17.8486 | -12.821 | 1114.284 | 18.3577 | -95.3658 | 9.3458 | 9.3458 | 106.1684 | 286.1684 | 94.5575 | 0 | 0 | 62.3094 | 62.3094 | -0.99901 | 0% | 28.1763 | 0 | 0 | 119.3678 | 119.3678 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7303 | 4.7303 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5132 | 20 | 20.6 | 22.78 | 34.44 | 57.22 | 34.44 | 17.22 | 214 | 5132 | 1200 | 211.0685 | 17.8486 | -12.821 | 1174.284 | 19.3577 | -110.3658 | -0.20091 | 0 | 116.5874 | 296.5874 | 108.4499 | 0 | 0 | 29.3964 | 29.3964 | -3.055 | 0% | 13.293 | 0 | 0 | 146.9213 | 146.9213 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8259 | 4.8259 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5133 | 21 | 20.5 | 0 | 2.5 | 2.5 | 2.5 | 1.25 | 214 | 5133 | 1260 | 211.0685 | 17.8486 | -12.821 | 1234.284 | 20.3577 | -125.3658 | -8.8556 | 0 | 116.5874 | 296.5874 | 108.4499 | 0 | 0 | 2.1339 | 2.1339 | -52.4598 | 0% | 0.96494 | 0 | 0 | -4.7992 | 0 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8453 | 4.8453 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5134 | 22 | 19.4 | 0 | 0 | 0 | 0 | 0 | 214 | 5134 | 1320 | 211.0685 | 17.8486 | -12.821 | 1294.284 | 21.3577 | -140.3658 | -16.181 | 0 | 116.5874 | 296.5874 | 108.4499 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.213 | 0 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0626 | 5.0626 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5135 | 23 | 18.8 | 0 | 0 | 0 | 0 | 0 | 214 | 5135 | 1380 | 211.0685 | 17.8486 | -12.821 | 1354.284 | 22.3577 | -155.3658 | -21.6655 | 0 | 116.5874 | 296.5874 | 108.4499 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4996 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
8 | 214 | 2 | 5136 | 24 | 18.5 | 0 | 0 | 0 | 0 | 0 | 214 | 5136 | 1440 | 211.0685 | 17.8486 | -12.821 | 1414.284 | 23.3577 | -170.3658 | -24.7918 | 0 | 116.5874 | 296.5874 | 108.4499 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3289 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5137 | 1 | 18.1 | 0 | 0 | 0 | 0 | 0 | 215 | 5137 | 60 | 212.0548 | 17.6034 | -12.9867 | 34.284 | 0.35496 | 174.6757 | -25.4398 | 0 | 116.2067 | 63.7933 | 108.1958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7314 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5138 | 2 | 18.5 | 0 | 0 | 0 | 0 | 0 | 215 | 5138 | 120 | 212.0548 | 17.6034 | -12.9867 | 94.284 | 1.355 | 159.6757 | -23.0627 | 0 | 116.2067 | 63.7933 | 108.1958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.491 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5139 | 3 | 18.6 | 0 | 0 | 0 | 0 | 0 | 215 | 5139 | 180 | 212.0548 | 17.6034 | -12.9867 | 154.284 | 2.355 | 144.6757 | -18.1919 | 0 | 116.2067 | 63.7933 | 108.1958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.7078 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5140 | 4 | 18.4 | 0 | 0 | 0 | 0 | 0 | 215 | 5140 | 240 | 212.0548 | 17.6034 | -12.9867 | 214.284 | 3.355 | 129.6757 | -11.3246 | 0 | 116.2067 | 63.7933 | 108.1958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.0125 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5141 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 215 | 5141 | 300 | 212.0548 | 17.6034 | -12.9867 | 274.284 | 4.355 | 114.6757 | -2.9884 | 0 | 116.2067 | 63.7933 | 108.1958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.3295 | 9.3295 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5142 | 6 | 18.2 | 0.19 | 3.06 | 3.25 | 3.06 | 1.53 | 215 | 5142 | 360 | 212.0548 | 17.6034 | -12.9867 | 334.284 | 5.355 | 99.6757 | 6.354 | 6.354 | 109.0171 | 70.9829 | 98.6698 | 0 | 0 | 2.6119 | 2.6119 | -44.658 | 0% | 1.1811 | 0 | 0 | 21.2062 | 21.2062 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3093 | 5.3093 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5143 | 7 | 18.5 | 25.22 | 36.39 | 61.61 | 36.39 | 18.2 | 215 | 5143 | 420 | 212.0548 | 17.6034 | -12.9867 | 394.284 | 6.355 | 84.6757 | 16.317 | 16.317 | 98.5484 | 81.4516 | 84.3881 | 8.7782 | 8.7782 | 31.0608 | 39.839 | -2.1598 | 0% | 18.0152 | 0 | 0 | 191.9122 | 191.9122 | 0% | 11.41% | 11.41% | 80% | 9.132% | 1.6451 | 5.2467 | 5.2467 | 8.6313 | 3.638 | 4.498% | 4.498%
8 | 215 | 3 | 5144 | 8 | 19 | 106.61 | 83.75 | 190.36 | 83.75 | 41.88 | 215 | 5144 | 480 | 212.0548 | 17.6034 | -12.9867 | 454.284 | 7.355 | 69.6757 | 26.5581 | 26.5581 | 87.8125 | 92.1875 | 70.1053 | 81.1412 | 81.1412 | 71.4851 | 152.6263 | 0.03765 | 3.765% | 69.0176 | 2.5985 | 1.819 | 165.8633 | 165.8633 | 1.097% | 11.39% | 11.39% | 80% | 9.11% | 6.2876 | 5.1437 | 5.1437 | 32.3413 | 13.9044 | 19.5% | 19.5%
8 | 215 | 3 | 5145 | 9 | 20 | 191.89 | 127.22 | 319.11 | 127.22 | 63.61 | 215 | 5145 | 540 | 212.0548 | 17.6034 | -12.9867 | 514.284 | 8.355 | 54.6757 | 36.713 | 36.713 | 75.9583 | 104.0417 | 55.9272 | 179.8333 | 179.8333 | 108.5891 | 288.4223 | 0.40612 | 40.61% | 130.4246 | 52.968 | 37.0776 | 173.8091 | 173.8091 | 21.33% | 11.35% | 11.35% | 80% | 9.082% | 11.8446 | 4.943 | 4.943 | 58.548 | 26.1934 | 33.69% | 33.69%
8 | 215 | 3 | 5146 | 10 | 22.3 | 335.14 | 152.36 | 487.5 | 152.36 | 76.18 | 215 | 5146 | 600 | 212.0548 | 17.6034 | -12.9867 | 574.284 | 9.355 | 39.6757 | 46.2852 | 46.2852 | 61.713 | 118.287 | 42.0416 | 344.3534 | 344.3534 | 130.0474 | 474.4008 | 0.5727 | 57.27% | 214.524 | 122.8571 | 86 | 181.0411 | 181.0411 | 47.5% | 11.31% | 11.31% | 85% | 9.614% | 20.6247 | 4.508 | 4.508 | 92.9754 | 45.6098 | 51.36% | 51.36%
8 | 215 | 3 | 5147 | 11 | 24.8 | 390.5 | 175.33 | 565.83 | 175.33 | 87.67 | 215 | 5147 | 660 | 212.0548 | 17.6034 | -12.9867 | 634.284 | 10.355 | 24.6757 | 54.4425 | 54.4425 | 43.1803 | 136.8197 | 28.9431 | 420.0532 | 420.0532 | 149.6535 | 569.7068 | 0.62084 | 62.08% | 257.6214 | 159.9419 | 111.9593 | 209.3405 | 209.3405 | 53.48% | 11.29% | 11.29% | 90% | 10.16% | 26.1797 | 4.0771 | 4.0771 | 106.7367 | 57.8941 | 50.99% | 50.99%
8 | 215 | 3 | 5148 | 12 | 25.5 | 435.89 | 226.81 | 662.7 | 226.81 | 113.41 | 215 | 5148 | 720 | 212.0548 | 17.6034 | -12.9867 | 694.284 | 11.355 | 9.6757 | 59.752 | 59.752 | 18.5432 | 161.4568 | 18.46 | 478.6245 | 478.6245 | 193.5944 | 672.219 | 0.65099 | 65.1% | 303.9774 | 197.887 | 138.5209 | 212.8252 | 212.8252 | 65.09% | 11.31% | 11.31% | 90% | 10.18% | 30.951 | 3.9643 | 3.9643 | 122.6983 | 68.4454 | 57.65% | 57.65%
8 | 215 | 3 | 5149 | 13 | 24.2 | 369.44 | 227.22 | 596.66 | 227.22 | 113.61 | 215 | 5149 | 780 | 212.0548 | 17.6034 | -12.9867 | 754.284 | 12.355 | -5.3243 | 60.4961 | 60.4961 | 10.3462 | 190.3462 | 16.6673 | 406.6524 | 406.6524 | 193.9444 | 600.5969 | 0.62812 | 62.81% | 271.5899 | 170.5917 | 119.4142 | 182.6344 | 182.6344 | 65.38% | 11.31% | 11.31% | 90% | 10.18% | 27.6352 | 4.1765 | 4.1765 | 115.4184 | 61.1128 | 63.2% | 63.2%
8 | 215 | 3 | 5150 | 14 | 23.8 | 191.39 | 124.67 | 316.06 | 124.67 | 62.34 | 215 | 5150 | 840 | 212.0548 | 17.6034 | -12.9867 | 814.284 | 13.355 | -20.3243 | 56.3563 | 56.3563 | 36.696 | 216.696 | 25.4737 | 207.5482 | 207.5482 | 106.4125 | 313.9607 | 0.46482 | 46.48% | 141.973 | 65.9913 | 46.1939 | 161.4734 | 161.4734 | 28.61% | 11.25% | 11.25% | 85% | 9.563% | 13.5767 | 4.2442 | 4.2442 | 57.6218 | 30.0236 | 35.69% | 35.69%
8 | 215 | 3 | 5151 | 15 | 24.3 | 212.22 | 169.11 | 381.33 | 169.11 | 84.56 | 215 | 5151 | 900 | 212.0548 | 17.6034 | -12.9867 | 874.284 | 14.355 | -35.3243 | 48.8475 | 48.8475 | 56.8768 | 236.8768 | 38.1223 | 221.728 | 221.728 | 144.3444 | 366.0724 | 0.51603 | 51.6% | 165.538 | 85.4229 | 59.796 | 170.6585 | 170.6585 | 35.04% | 11.25% | 11.25% | 85% | 9.562% | 15.8287 | 4.1598 | 4.1598 | 65.8435 | 35.0037 | 38.58% | 38.58%
8 | 215 | 3 | 5152 | 16 | 24.3 | 286.89 | 188.19 | 475.08 | 188.19 | 94.1 | 215 | 5152 | 960 | 212.0548 | 17.6034 | -12.9867 | 934.284 | 15.355 | -50.3243 | 39.578 | 39.578 | 72.1436 | 252.1436 | 51.8564 | 278.1127 | 278.1127 | 160.6302 | 438.7429 | 0.56373 | 56.37% | 198.3995 | 111.8436 | 78.2905 | 172.5574 | 172.5574 | 45.37% | 11.27% | 11.27% | 85% | 9.577% | 18.9999 | 4.1598 | 4.1598 | 79.0349 | 42.0166 | 45.8% | 45.8%
8 | 215 | 3 | 5153 | 17 | 24.4 | 242.36 | 173 | 415.36 | 173 | 86.5 | 215 | 5153 | 1020 | 212.0548 | 17.6034 | -12.9867 | 994.284 | 16.355 | -65.3243 | 29.531 | 29.531 | 84.535 | 264.535 | 65.9757 | 200.1858 | 200.1858 | 147.6647 | 347.8505 | 0.50156 | 50.16% | 157.298 | 78.8949 | 55.2264 | 169.0724 | 169.0724 | 32.66% | 11.24% | 11.24% | 85% | 9.556% | 15.0317 | 4.1431 | 4.1431 | 62.2775 | 33.2413 | 36.83% | 36.83%
8 | 215 | 3 | 5154 | 18 | 22.7 | 143 | 153.61 | 296.61 | 153.61 | 76.81 | 215 | 5154 | 1080 | 212.0548 | 17.6034 | -12.9867 | 1054.284 | 17.355 | -80.3243 | 19.2742 | 19.2742 | 95.4937 | 275.4937 | 80.2409 | 73.433 | 73.433 | 131.1143 | 204.5473 | 0.27178 | 27.18% | 92.4963 | 25.1389 | 17.5972 | 132.5614 | 132.5614 | 13.27% | 11.26% | 11.26% | 80% | 9.011% | 8.3347 | 4.4361 | 4.4361 | 36.9734 | 18.4315 | 27.89% | 27.89%
8 | 215 | 3 | 5155 | 19 | 22.7 | 77.28 | 87.08 | 164.36 | 87.08 | 43.54 | 215 | 5155 | 1140 | 212.0548 | 17.6034 | -12.9867 | 1114.284 | 18.355 | -95.3243 | 9.1958 | 9.1958 | 105.9679 | 285.9679 | 94.5324 | 0 | 0 | 74.3274 | 74.3274 | -0.66065 | 0% | 33.6109 | 0 | 0 | 121.6317 | 121.6317 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4361 | 4.4361 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5156 | 20 | 21.4 | 15.33 | 29.67 | 45 | 29.67 | 14.84 | 215 | 5156 | 1200 | 212.0548 | 17.6034 | -12.9867 | 1174.284 | 19.355 | -110.3243 | -0.36355 | 0 | 116.2067 | 296.2067 | 108.1958 | 0 | 0 | 25.3249 | 25.3249 | -3.6062 | 0% | 11.4519 | 0 | 0 | 147.8084 | 147.8084 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6738 | 4.6738 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5157 | 21 | 20.4 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 215 | 5157 | 1260 | 212.0548 | 17.6034 | -12.9867 | 1234.284 | 20.355 | -125.3243 | -9.0356 | 0 | 116.2067 | 296.2067 | 108.1958 | 0 | 0 | 1.6559 | 1.6559 | -67.9674 | 0% | 0.7488 | 0 | 0 | -4.3861 | 0 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8647 | 4.8647 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5158 | 22 | 19.7 | 0 | 0 | 0 | 0 | 0 | 215 | 5158 | 1320 | 212.0548 | 17.6034 | -12.9867 | 1294.284 | 21.355 | -140.3243 | -16.3813 | 0 | 116.2067 | 296.2067 | 108.1958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.1855 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5159 | 23 | 18.9 | 0 | 0 | 0 | 0 | 0 | 215 | 5159 | 1380 | 212.0548 | 17.6034 | -12.9867 | 1354.284 | 22.355 | -155.3243 | -21.8867 | 0 | 116.2067 | 296.2067 | 108.1958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7739 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
8 | 215 | 3 | 5160 | 24 | 18.6 | 0 | 0 | 0 | 0 | 0 | 215 | 5160 | 1440 | 212.0548 | 17.6034 | -12.9867 | 1414.284 | 23.355 | -170.3243 | -25.03 | 0 | 116.2067 | 296.2067 | 108.1958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.6002 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5161 | 1 | 18.5 | 0 | 0 | 0 | 0 | 0 | 216 | 5161 | 60 | 213.0411 | 17.3536 | -13.1405 | 34.284 | 0.35239 | 174.7141 | -25.6915 | 0 | 115.8195 | 64.1805 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5546 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5162 | 2 | 18.1 | 0 | 0 | 0 | 0 | 0 | 216 | 5162 | 120 | 213.0411 | 17.3536 | -13.1405 | 94.284 | 1.3524 | 159.7141 | -23.3135 | 0 | 115.8195 | 64.1805 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5349 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5163 | 3 | 17.4 | 0 | 0 | 0 | 0 | 0 | 216 | 5163 | 180 | 213.0411 | 17.3536 | -13.1405 | 154.284 | 2.3524 | 144.7141 | -18.4342 | 0 | 115.8195 | 64.1805 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9724 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5164 | 4 | 17.2 | 0 | 0 | 0 | 0 | 0 | 216 | 5164 | 240 | 213.0411 | 17.3536 | -13.1405 | 214.284 | 3.3524 | 129.7141 | -11.555 | 0 | 115.8195 | 64.1805 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2772 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5165 | 5 | 16.8 | 0 | 0 | 0 | 0 | 0 | 216 | 5165 | 300 | 213.0411 | 17.3536 | -13.1405 | 274.284 | 4.3524 | 114.7141 | -3.2067 | 0 | 115.8195 | 64.1805 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.0382 | 6.0382 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5166 | 6 | 16.5 | 0.08 | 1.67 | 1.75 | 1.67 | 0.84 | 216 | 5166 | 360 | 213.0411 | 17.3536 | -13.1405 | 334.284 | 5.3524 | 99.7141 | 6.1457 | 6.1457 | 108.8736 | 71.1264 | 98.7266 | 0 | 0 | 1.4254 | 1.4254 | -85.1649 | 0% | 0.64458 | 0 | 0 | 16.218 | 16.218 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5167 | 7 | 17.4 | 17.17 | 31.89 | 49.06 | 31.89 | 15.95 | 216 | 5167 | 420 | 213.0411 | 17.3536 | -13.1405 | 394.284 | 6.3524 | 84.7141 | 16.1151 | 16.1151 | 98.3905 | 81.6095 | 84.4253 | 6.0092 | 6.0092 | 27.2198 | 33.229 | -2.8231 | 0% | 15.0262 | 0 | 0 | 185.9742 | 185.9742 | 0% | 11.46% | 11.46% | 80% | 9.169% | 1.3778 | 5.4794 | 5.4794 | 7.5495 | 3.0469 | 4.059% | 4.059%
8 | 216 | 4 | 5168 | 8 | 19.6 | 88.67 | 72.28 | 160.95 | 72.28 | 36.14 | 216 | 5168 | 480 | 213.0411 | 17.3536 | -13.1405 | 454.284 | 7.3524 | 69.7141 | 26.3578 | 26.3578 | 87.6409 | 92.3591 | 70.122 | 67.9079 | 67.9079 | 61.6948 | 129.6028 | -0.088257 | 0% | 58.6064 | 0 | 0 | 161.175 | 161.175 | 0% | 11.37% | 11.37% | 80% | 9.093% | 5.3293 | 5.0224 | 5.0224 | 26.7661 | 11.7853 | 16.61% | 16.61%
8 | 216 | 4 | 5169 | 9 | 21.9 | 212.56 | 110.28 | 322.84 | 110.28 | 55.14 | 216 | 5169 | 540 | 213.0411 | 17.3536 | -13.1405 | 514.284 | 8.3524 | 54.7141 | 36.5082 | 36.5082 | 75.7744 | 104.2256 | 55.9199 | 200.203 | 200.203 | 94.1299 | 294.3329 | 0.42824 | 42.82% | 133.0973 | 56.997 | 39.8979 | 172.8418 | 172.8418 | 23.08% | 11.3% | 11.3% | 80% | 9.039% | 12.0311 | 4.581 | 4.581 | 55.1139 | 26.6057 | 31.89% | 31.89%
8 | 216 | 4 | 5170 | 10 | 24.8 | 326.44 | 123.89 | 450.33 | 123.89 | 61.95 | 216 | 5170 | 600 | 213.0411 | 17.3536 | -13.1405 | 574.284 | 9.3524 | 39.7141 | 46.0684 | 46.0684 | 61.5262 | 118.4738 | 42.0014 | 336.8473 | 336.8473 | 105.7467 | 442.5941 | 0.56824 | 56.82% | 200.141 | 113.7276 | 79.6094 | 209.9313 | 209.9313 | 37.92% | 11.26% | 11.26% | 85% | 9.569% | 19.1515 | 4.0771 | 4.0771 | 78.0822 | 42.3518 | 37.19% | 37.19%
8 | 216 | 4 | 5171 | 11 | 25.1 | 407.92 | 112.83 | 520.75 | 112.83 | 56.42 | 216 | 5171 | 660 | 213.0411 | 17.3536 | -13.1405 | 634.284 | 10.3524 | 24.7141 | 54.2068 | 54.2068 | 43.0249 | 136.9751 | 28.8491 | 440.4879 | 440.4879 | 96.3064 | 536.7943 | 0.6108 | 61.08% | 242.7384 | 148.2655 | 103.7859 | 209.1496 | 209.1496 | 49.62% | 11.28% | 11.28% | 90% | 10.15% | 24.6388 | 4.0283 | 4.0283 | 99.2529 | 54.4865 | 47.46% | 47.46%
8 | 216 | 4 | 5172 | 12 | 27.8 | 411.11 | 156.67 | 567.78 | 156.67 | 78.34 | 216 | 5172 | 720 | 213.0411 | 17.3536 | -13.1405 | 694.284 | 11.3524 | 9.7141 | 59.5004 | 59.5004 | 18.5012 | 161.4988 | 18.2685 | 453.0809 | 453.0809 | 133.7262 | 586.8071 | 0.637 | 63.7% | 265.3542 | 169.0303 | 118.3212 | 267.4782 | 267.4782 | 44.24% | 11.26% | 11.26% | 90% | 10.13% | 26.8923 | 3.6178 | 3.6178 | 97.2904 | 59.4699 | 36.37% | 36.37%
8 | 216 | 4 | 5173 | 13 | 27.9 | 441.72 | 154.86 | 596.58 | 154.86 | 77.43 | 216 | 5173 | 780 | 213.0411 | 17.3536 | -13.1405 | 754.284 | 12.3524 | -5.2859 | 60.253 | 60.253 | 10.2079 | 190.2079 | 16.4191 | 488.0147 | 488.0147 | 132.1813 | 620.196 | 0.64633 | 64.63% | 280.4526 | 181.2643 | 126.885 | 272.1379 | 272.1379 | 46.63% | 11.27% | 11.27% | 90% | 10.15% | 28.4561 | 3.6036 | 3.6036 | 102.5431 | 62.9281 | 37.68% | 37.68%
8 | 216 | 4 | 5174 | 14 | 26.8 | 387.36 | 181.44 | 568.8 | 181.44 | 90.72 | 216 | 5174 | 840 | 213.0411 | 17.3536 | -13.1405 | 814.284 | 13.3524 | -20.2859 | 56.1462 | 56.1462 | 36.4439 | 216.4439 | 25.2972 | 421.7094 | 421.7094 | 154.8687 | 576.5781 | 0.63039 | 63.04% | 260.7286 | 164.3604 | 115.0523 | 223.9348 | 223.9348 | 51.38% | 11.27% | 11.27% | 90% | 10.14% | 26.442 | 3.7639 | 3.7639 | 99.5247 | 58.4742 | 44.44% | 44.44%
8 | 216 | 4 | 5175 | 15 | 28.2 | 287.44 | 188.19 | 475.63 | 188.19 | 94.1 | 216 | 5175 | 900 | 213.0411 | 17.3536 | -13.1405 | 874.284 | 14.3524 | -35.2859 | 48.6697 | 48.6697 | 56.6048 | 236.6048 | 38.0006 | 301.637 | 301.637 | 160.6302 | 462.2672 | 0.59382 | 59.38% | 209.0372 | 124.1303 | 86.8912 | 256.6438 | 256.6438 | 33.86% | 11.2% | 11.2% | 85% | 9.52% | 19.8998 | 3.5613 | 3.5613 | 70.8691 | 44.0066 | 27.61% | 27.61%
8 | 216 | 4 | 5176 | 16 | 26.1 | 160 | 60.56 | 220.56 | 60.56 | 30.28 | 216 | 5176 | 960 | 213.0411 | 17.3536 | -13.1405 | 934.284 | 15.3524 | -50.2859 | 39.4205 | 39.4205 | 71.8878 | 251.8878 | 51.7689 | 155.9249 | 155.9249 | 51.6912 | 207.6161 | 0.31473 | 31.47% | 93.884 | 29.5479 | 20.6836 | 190.1251 | 190.1251 | 10.88% | 11.15% | 11.15% | 80% | 8.923% | 8.3769 | 3.8703 | 3.8703 | 32.4212 | 18.5248 | 17.05% | 17.05%
8 | 216 | 4 | 5177 | 17 | 25.2 | 134.78 | 98.33 | 233.11 | 98.33 | 49.17 | 216 | 5177 | 1020 | 213.0411 | 17.3536 | -13.1405 | 994.284 | 16.3524 | -65.2859 | 29.3825 | 29.3825 | 84.3005 | 264.3005 | 65.913 | 112.113 | 112.113 | 83.9299 | 196.0429 | 0.27609 | 27.61% | 88.6506 | 24.4753 | 17.1327 | 171.1665 | 171.1665 | 10.01% | 11.18% | 11.18% | 80% | 8.943% | 7.9284 | 4.0122 | 4.0122 | 31.8103 | 17.5329 | 18.58% | 18.58%
8 | 216 | 4 | 5178 | 18 | 25.1 | 91.81 | 76.81 | 168.62 | 76.81 | 38.41 | 216 | 5178 | 1080 | 213.0411 | 17.3536 | -13.1405 | 1054.284 | 17.3524 | -80.2859 | 19.1258 | 19.1258 | 95.2775 | 275.2775 | 80.1989 | 47.7005 | 47.7005 | 65.5614 | 113.262 | -0.11164 | 0% | 51.2171 | 0 | 0 | 162.3811 | 162.3811 | 0% | 11.16% | 11.16% | 80% | 8.927% | 4.5724 | 4.0283 | 4.0283 | 18.4191 | 10.1115 | 11.34% | 11.34%
8 | 216 | 4 | 5179 | 19 | 23.7 | 54.86 | 63.61 | 118.47 | 63.61 | 31.81 | 216 | 5179 | 1140 | 213.0411 | 17.3536 | -13.1405 | 1114.284 | 18.3524 | -95.2859 | 9.0405 | 9.0405 | 105.7663 | 285.7663 | 94.5101 | 0 | 0 | 54.2945 | 54.2945 | -1.1613 | 0% | 24.552 | 0 | 0 | 172.2774 | 172.2774 | 0% | 11.2% | 0% | 80% | 0% | 0 | 4.2613 | 4.2613 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5180 | 20 | 22.3 | 15 | 24.5 | 39.5 | 24.5 | 12.25 | 216 | 5180 | 1200 | 213.0411 | 17.3536 | -13.1405 | 1174.284 | 19.3524 | -110.2859 | -0.53144 | 0 | 115.8195 | 295.8195 | 107.9371 | 0 | 0 | 20.9121 | 20.9121 | -4.4432 | 0% | 9.4564 | 0 | 0 | 147.894 | 147.894 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.508 | 4.508 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5181 | 21 | 20.7 | 0 | 0 | 0 | 0 | 0 | 216 | 5181 | 1260 | 213.0411 | 17.3536 | -13.1405 | 1234.284 | 20.3524 | -125.2859 | -9.2207 | 0 | 115.8195 | 295.8195 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7097 | 0 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.8067 | 4.8067 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5182 | 22 | 19.7 | 0 | 0 | 0 | 0 | 0 | 216 | 5182 | 1320 | 213.0411 | 17.3536 | -13.1405 | 1294.284 | 21.3524 | -140.2859 | -16.5869 | 0 | 115.8195 | 295.8195 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.6137 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5183 | 23 | 18.9 | 0 | 0 | 0 | 0 | 0 | 216 | 5183 | 1380 | 213.0411 | 17.3536 | -13.1405 | 1354.284 | 22.3524 | -155.2859 | -22.113 | 0 | 115.8195 | 295.8195 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2036 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
8 | 216 | 4 | 5184 | 24 | 18.3 | 0 | 0 | 0 | 0 | 0 | 216 | 5184 | 1440 | 213.0411 | 17.3536 | -13.1405 | 1414.284 | 23.3524 | -170.2859 | -25.2731 | 0 | 115.8195 | 295.8195 | 107.9371 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4887 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5185 | 1 | 17.7 | 0 | 0 | 0 | 0 | 0 | 217 | 5185 | 60 | 214.0274 | 17.0993 | -13.2824 | 34.284 | 0.35003 | 174.7496 | -25.9476 | 0 | 115.4261 | 64.5739 | 107.6736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7794 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5186 | 2 | 17.5 | 0 | 0 | 0 | 0 | 0 | 217 | 5186 | 120 | 214.0274 | 17.0993 | -13.2824 | 94.284 | 1.35 | 159.7496 | -23.5679 | 0 | 115.4261 | 64.5739 | 107.6736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7442 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5187 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 217 | 5187 | 180 | 214.0274 | 17.0993 | -13.2824 | 154.284 | 2.35 | 144.7496 | -18.6795 | 0 | 115.4261 | 64.5739 | 107.6736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1663 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5188 | 4 | 16.9 | 0 | 0 | 0 | 0 | 0 | 217 | 5188 | 240 | 214.0274 | 17.0993 | -13.2824 | 214.284 | 3.35 | 129.7496 | -11.7876 | 0 | 115.4261 | 64.5739 | 107.6736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3187 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5189 | 5 | 16.2 | 0 | 0 | 0 | 0 | 0 | 217 | 5189 | 300 | 214.0274 | 17.0993 | -13.2824 | 274.284 | 4.35 | 114.7496 | -3.4267 | 0 | 115.4261 | 64.5739 | 107.6736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.1758 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5190 | 6 | 16 | 0 | 1.39 | 1.39 | 1.39 | 0.7 | 217 | 5190 | 360 | 214.0274 | 17.0993 | -13.2824 | 334.284 | 5.35 | 99.7496 | 5.9359 | 5.9359 | 108.725 | 71.275 | 98.7809 | 0 | 0 | 1.1864 | 1.1864 | -103.4312 | 0% | 0.53651 | 0 | 0 | 5.4546 | 5.4546 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5191 | 7 | 16.8 | 2.5 | 23 | 25.5 | 23 | 11.5 | 217 | 5191 | 420 | 214.0274 | 17.0993 | -13.2824 | 394.284 | 6.35 | 84.7496 | 15.9118 | 15.9118 | 98.2277 | 81.7723 | 84.4598 | 0.88037 | 0.88037 | 19.6317 | 20.5121 | -5.1373 | 0% | 9.2756 | 0 | 0 | 165.2231 | 165.2231 | 0% | 11.49% | 11.49% | 80% | 9.191% | 0.85255 | 5.6099 | 5.6099 | 4.7827 | 1.8853 | 2.895% | 2.895%
8 | 217 | 5 | 5192 | 8 | 19.2 | 6.25 | 60.33 | 66.58 | 60.33 | 30.17 | 217 | 5192 | 480 | 214.0274 | 17.0993 | -13.2824 | 454.284 | 7.35 | 69.7496 | 26.156 | 26.156 | 87.4641 | 92.5359 | 70.1361 | 4.8176 | 4.8176 | 51.4949 | 56.3125 | -1.2652 | 0% | 25.4645 | 0 | 0 | 176.4233 | 176.4233 | 0% | 11.38% | 11.38% | 80% | 9.108% | 2.3192 | 5.103 | 5.103 | 11.8351 | 5.1288 | 6.708% | 6.708%
8 | 217 | 5 | 5193 | 9 | 20.4 | 58.06 | 119.44 | 177.5 | 119.44 | 59.72 | 217 | 5193 | 540 | 214.0274 | 17.0993 | -13.2824 | 514.284 | 8.35 | 54.7496 | 36.3017 | 36.3017 | 75.5852 | 104.4148 | 55.9099 | 54.9668 | 54.9668 | 101.9484 | 156.9152 | 0.078269 | 7.827% | 70.9571 | 5.5538 | 3.8876 | 163.5017 | 163.5017 | 2.378% | 11.34% | 11.34% | 80% | 9.07% | 6.436 | 4.8647 | 4.8647 | 31.3091 | 14.2327 | 19.15% | 19.15%
8 | 217 | 5 | 5194 | 10 | 22.1 | 110.78 | 196.44 | 307.22 | 196.44 | 98.22 | 217 | 5194 | 600 | 214.0274 | 17.0993 | -13.2824 | 574.284 | 9.35 | 39.7496 | 45.8495 | 45.8495 | 61.3337 | 118.6663 | 41.9585 | 114.8123 | 114.8123 | 167.672 | 282.4844 | 0.41401 | 41.4% | 127.7394 | 52.8859 | 37.0201 | 149.9325 | 149.9325 | 24.69% | 11.29% | 11.29% | 80% | 9.034% | 11.5397 | 4.5443 | 4.5443 | 52.44 | 25.519 | 34.98% | 34.98%
8 | 217 | 5 | 5195 | 11 | 24 | 126.67 | 268.11 | 394.78 | 268.11 | 134.06 | 217 | 5195 | 660 | 214.0274 | 17.0993 | -13.2824 | 634.284 | 10.35 | 24.7496 | 53.9683 | 53.9683 | 42.8635 | 137.1365 | 28.7522 | 137.3237 | 137.3237 | 228.8462 | 366.1699 | 0.51435 | 51.44% | 165.582 | 85.1673 | 59.6171 | 169.1928 | 169.1928 | 35.24% | 11.26% | 11.26% | 85% | 9.568% | 15.843 | 4.2102 | 4.2102 | 66.7022 | 35.0354 | 39.42% | 39.42%
8 | 217 | 5 | 5196 | 12 | 24 | 353.06 | 204.5 | 557.56 | 204.5 | 102.25 | 217 | 5196 | 720 | 214.0274 | 17.0993 | -13.2824 | 694.284 | 11.35 | 9.7496 | 59.245 | 59.245 | 18.4525 | 161.5475 | 18.0731 | 390.5695 | 390.5695 | 174.5517 | 565.1212 | 0.61632 | 61.63% | 255.5478 | 157.4998 | 110.2498 | 168.3309 | 168.3309 | 65.5% | 11.3% | 11.3% | 90% | 10.17% | 25.99 | 4.2102 | 4.2102 | 109.4229 | 57.4745 | 65% | 65%
8 | 217 | 5 | 5197 | 13 | 23.2 | 277.42 | 228.61 | 506.03 | 228.61 | 114.31 | 217 | 5197 | 780 | 214.0274 | 17.0993 | -13.2824 | 754.284 | 12.35 | -5.2504 | 60.005 | 60.005 | 10.076 | 190.076 | 16.1677 | 307.6524 | 307.6524 | 195.1308 | 502.7833 | 0.58963 | 58.96% | 227.3586 | 134.0569 | 93.8398 | 149.6848 | 149.6848 | 62.69% | 11.3% | 11.3% | 90% | 10.17% | 23.1217 | 4.3478 | 4.3478 | 100.5287 | 51.1317 | 67.16% | 67.16%
8 | 217 | 5 | 5198 | 14 | 22.7 | 318.94 | 248.56 | 567.5 | 248.56 | 124.28 | 217 | 5198 | 840 | 214.0274 | 17.0993 | -13.2824 | 814.284 | 13.35 | -20.2504 | 55.9303 | 55.9303 | 36.1957 | 216.1957 | 25.1216 | 348.6072 | 348.6072 | 212.1592 | 560.7664 | 0.60987 | 60.99% | 253.5786 | 154.649 | 108.2543 | 147.0373 | 147.0373 | 73.62% | 11.32% | 11.32% | 90% | 10.18% | 25.8265 | 4.4361 | 4.4361 | 114.5685 | 57.1131 | 77.92% | 77.92%
8 | 217 | 5 | 5199 | 15 | 21.8 | 186.94 | 237.28 | 424.22 | 237.28 | 118.64 | 217 | 5199 | 900 | 214.0274 | 17.0993 | -13.2824 | 874.284 | 14.35 | -35.2504 | 48.4861 | 48.4861 | 56.334 | 236.334 | 37.8811 | 197.049 | 197.049 | 202.5311 | 399.5801 | 0.52667 | 52.67% | 180.6901 | 95.1632 | 66.6143 | 137.7839 | 137.7839 | 48.35% | 11.31% | 11.31% | 85% | 9.616% | 17.3743 | 4.5994 | 4.5994 | 79.9109 | 38.4216 | 58% | 58%
8 | 217 | 5 | 5200 | 16 | 23.5 | 180.78 | 192.92 | 373.7 | 192.92 | 96.46 | 217 | 5200 | 960 | 214.0274 | 17.0993 | -13.2824 | 934.284 | 15.35 | -50.2504 | 39.2574 | 39.2574 | 71.6317 | 251.6317 | 51.6841 | 177.1211 | 177.1211 | 164.6675 | 341.7886 | 0.49054 | 49.05% | 154.5568 | 75.8167 | 53.0717 | 145.2454 | 145.2454 | 36.54% | 11.26% | 11.26% | 85% | 9.574% | 14.7976 | 4.2957 | 4.2957 | 63.5657 | 32.7236 | 43.76% | 43.76%
8 | 217 | 5 | 5201 | 17 | 25.3 | 70.89 | 162.36 | 233.25 | 162.36 | 81.18 | 217 | 5201 | 1020 | 214.0274 | 17.0993 | -13.2824 | 994.284 | 16.35 | -65.2504 | 29.2284 | 29.2284 | 84.0653 | 264.0653 | 65.8531 | 59.3897 | 59.3897 | 138.5829 | 197.9726 | 0.28231 | 28.23% | 89.5232 | 25.2733 | 17.6913 | 170.2521 | 170.2521 | 10.39% | 11.18% | 11.18% | 80% | 8.941% | 8.0045 | 3.9962 | 3.9962 | 31.9871 | 17.7011 | 18.79% | 18.79%
8 | 217 | 5 | 5202 | 18 | 23.8 | 11.94 | 86.67 | 98.61 | 86.67 | 43.34 | 217 | 5202 | 1080 | 214.0274 | 17.0993 | -13.2824 | 1054.284 | 17.35 | -80.2504 | 18.9719 | 18.9719 | 95.0603 | 275.0603 | 80.1597 | 6.2767 | 6.2767 | 73.9775 | 80.2541 | -0.52292 | 0% | 36.2909 | 0 | 0 | 174.7471 | 174.7471 | 0% | 11.2% | 11.2% | 80% | 8.961% | 3.2521 | 4.2442 | 4.2442 | 13.8026 | 7.1918 | 7.899% | 7.899%
8 | 217 | 5 | 5203 | 19 | 22.5 | 9.58 | 59.44 | 69.02 | 59.44 | 29.72 | 217 | 5203 | 1140 | 214.0274 | 17.0993 | -13.2824 | 1114.284 | 18.35 | -95.2504 | 8.8798 | 8.8798 | 105.5637 | 285.5637 | 94.4908 | 0 | 0 | 50.7352 | 50.7352 | -1.3503 | 0% | 22.9425 | 0 | 0 | 154.2861 | 154.2861 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.4719 | 4.4719 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5204 | 20 | 21 | 3.81 | 29.53 | 33.34 | 29.53 | 14.77 | 217 | 5204 | 1200 | 214.0274 | 17.0993 | -13.2824 | 1174.284 | 19.35 | -110.2504 | -0.70457 | 0 | 115.4261 | 295.4261 | 107.6736 | 0 | 0 | 25.2054 | 25.2054 | -3.6618 | 0% | 11.3979 | 0 | 0 | 145.3374 | 145.3374 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7493 | 4.7493 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5205 | 21 | 19.7 | 0 | 2.08 | 2.08 | 2.08 | 1.04 | 217 | 5205 | 1260 | 214.0274 | 17.0993 | -13.2824 | 1234.284 | 20.35 | -125.2504 | -9.4111 | 0 | 115.4261 | 295.4261 | 107.6736 | 0 | 0 | 1.7754 | 1.7754 | -64.2061 | 0% | 0.80283 | 0 | 0 | -5.5642 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5206 | 22 | 19.1 | 0 | 0 | 0 | 0 | 0 | 217 | 5206 | 1320 | 214.0274 | 17.0993 | -13.2824 | 1294.284 | 21.35 | -140.2504 | -16.7976 | 0 | 115.4261 | 295.4261 | 107.6736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.6656 | 0 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1233 | 5.1233 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5207 | 23 | 18.3 | 0 | 0 | 0 | 0 | 0 | 217 | 5207 | 1380 | 214.0274 | 17.0993 | -13.2824 | 1354.284 | 22.35 | -155.2504 | -22.3443 | 0 | 115.4261 | 295.4261 | 107.6736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5449 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
8 | 217 | 5 | 5208 | 24 | 17.6 | 0 | 0 | 0 | 0 | 0 | 217 | 5208 | 1440 | 214.0274 | 17.0993 | -13.2824 | 1414.284 | 23.35 | -170.2504 | -25.521 | 0 | 115.4261 | 295.4261 | 107.6736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2717 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5209 | 1 | 17.4 | 0 | 0 | 0 | 0 | 0 | 218 | 5209 | 60 | 215.0137 | 16.8405 | -13.4123 | 34.284 | 0.34786 | 174.7821 | -26.2079 | 0 | 115.0266 | 64.9734 | 107.4056 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5725 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5210 | 2 | 17.1 | 0 | 0 | 0 | 0 | 0 | 218 | 5210 | 120 | 215.0137 | 16.8405 | -13.4123 | 94.284 | 1.3479 | 159.7821 | -23.826 | 0 | 115.0266 | 64.9734 | 107.4056 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.3117 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5211 | 3 | 17.1 | 0 | 0 | 0 | 0 | 0 | 218 | 5211 | 180 | 215.0137 | 16.8405 | -13.4123 | 154.284 | 2.3479 | 144.7821 | -18.9277 | 0 | 115.0266 | 64.9734 | 107.4056 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.5938 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5212 | 4 | 16.7 | 0 | 0 | 0 | 0 | 0 | 218 | 5212 | 240 | 215.0137 | 16.8405 | -13.4123 | 214.284 | 3.3479 | 129.7821 | -12.0225 | 0 | 115.0266 | 64.9734 | 107.4056 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2034 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5213 | 5 | 16.2 | 0 | 0 | 0 | 0 | 0 | 218 | 5213 | 300 | 215.0137 | 16.8405 | -13.4123 | 274.284 | 4.3479 | 114.7821 | -3.6485 | 0 | 115.0266 | 64.9734 | 107.4056 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.8243 | 9.8243 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5214 | 6 | 16 | 0 | 1.58 | 1.58 | 1.58 | 0.79 | 218 | 5214 | 360 | 215.0137 | 16.8405 | -13.4123 | 334.284 | 5.3479 | 99.7821 | 5.7247 | 5.7247 | 108.5714 | 71.4286 | 98.8326 | 0 | 0 | 1.3486 | 1.3486 | -90.8966 | 0% | 0.60984 | 0 | 0 | 22.2774 | 22.2774 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5215 | 7 | 17 | 18.67 | 31.06 | 49.73 | 31.06 | 15.53 | 218 | 5215 | 420 | 215.0137 | 16.8405 | -13.4123 | 394.284 | 6.3479 | 84.7821 | 15.7072 | 15.7072 | 98.0598 | 81.9402 | 84.4916 | 6.6199 | 6.6199 | 26.5114 | 33.1313 | -2.8608 | 0% | 14.982 | 0 | 0 | 195.8073 | 195.8073 | 0% | 11.48% | 11.48% | 80% | 9.183% | 1.3758 | 5.5661 | 5.5661 | 7.6577 | 3.0424 | 3.911% | 3.911%
8 | 218 | 6 | 5216 | 8 | 19.6 | 109.67 | 70.97 | 180.64 | 70.97 | 35.49 | 218 | 5216 | 480 | 215.0137 | 16.8405 | -13.4123 | 454.284 | 7.3479 | 69.7821 | 25.953 | 25.953 | 87.2822 | 92.7178 | 70.1474 | 85.1033 | 85.1033 | 60.5767 | 145.68 | 0.010212 | 1.021% | 65.8765 | 0.67275 | 0.47093 | 174.2781 | 174.2781 | 0.2702% | 11.37% | 11.37% | 80% | 9.093% | 5.9902 | 5.0224 | 5.0224 | 30.0855 | 13.2468 | 17.26% | 17.26%
8 | 218 | 6 | 5217 | 9 | 22 | 235.5 | 100.69 | 336.19 | 100.69 | 50.35 | 218 | 5217 | 540 | 215.0137 | 16.8405 | -13.4123 | 514.284 | 8.3479 | 54.7821 | 36.0937 | 36.0937 | 75.3906 | 104.6094 | 55.8972 | 224.1361 | 224.1361 | 85.9443 | 310.0804 | 0.44802 | 44.8% | 140.2183 | 62.8207 | 43.9745 | 185.7667 | 185.7667 | 23.67% | 11.3% | 11.3% | 85% | 9.603% | 13.4657 | 4.5626 | 4.5626 | 61.4387 | 29.7782 | 33.07% | 33.07%
8 | 218 | 6 | 5218 | 10 | 23.8 | 354.03 | 145.83 | 499.86 | 145.83 | 72.92 | 218 | 5218 | 600 | 215.0137 | 16.8405 | -13.4123 | 574.284 | 9.3479 | 39.7821 | 45.6285 | 45.6285 | 61.1355 | 118.8645 | 41.9128 | 368.5618 | 368.5618 | 124.4737 | 493.0355 | 0.58801 | 58.8% | 222.9506 | 131.0973 | 91.7681 | 204.9016 | 204.9016 | 44.79% | 11.29% | 11.29% | 85% | 9.595% | 21.3914 | 4.2442 | 4.2442 | 90.7888 | 47.3051 | 44.31% | 44.31%
8 | 218 | 6 | 5219 | 11 | 22.9 | 373 | 201.33 | 574.33 | 201.33 | 100.67 | 218 | 5219 | 660 | 215.0137 | 16.8405 | -13.4123 | 634.284 | 10.3479 | 24.7821 | 53.7271 | 53.7271 | 42.6962 | 137.3038 | 28.6526 | 406.004 | 406.004 | 171.8459 | 577.8499 | 0.61635 | 61.64% | 261.3037 | 161.0557 | 112.739 | 182.1649 | 182.1649 | 61.89% | 11.32% | 11.32% | 90% | 10.18% | 26.6135 | 4.4006 | 4.4006 | 117.1144 | 58.8535 | 64.29% | 64.29%
8 | 218 | 6 | 5220 | 12 | 25.8 | 396.33 | 207.56 | 603.89 | 207.56 | 103.78 | 218 | 5220 | 720 | 215.0137 | 16.8405 | -13.4123 | 694.284 | 11.3479 | 9.7821 | 58.9859 | 58.9859 | 18.3973 | 161.6027 | 17.8739 | 440.1202 | 440.1202 | 177.1635 | 617.2838 | 0.63841 | 63.84% | 279.1357 | 178.2025 | 124.7418 | 220.269 | 220.269 | 56.63% | 11.29% | 11.29% | 90% | 10.16% | 28.3723 | 3.917 | 3.917 | 111.1338 | 62.7428 | 50.45% | 50.45%
8 | 218 | 6 | 5221 | 13 | 27.1 | 339.53 | 221.47 | 561 | 221.47 | 110.74 | 218 | 5221 | 780 | 215.0137 | 16.8405 | -13.4123 | 754.284 | 12.3479 | -5.2179 | 59.7521 | 59.7521 | 9.9504 | 189.9504 | 15.9131 | 377.9791 | 377.9791 | 189.0365 | 567.0156 | 0.62858 | 62.86% | 256.4044 | 161.1697 | 112.8188 | 275.7118 | 275.7118 | 40.92% | 11.26% | 11.26% | 90% | 10.13% | 25.9864 | 3.7193 | 3.7193 | 96.6515 | 57.4666 | 35.06% | 35.06%
8 | 218 | 6 | 5222 | 14 | 23.9 | 211.39 | 274.25 | 485.64 | 274.25 | 137.13 | 218 | 5222 | 840 | 215.0137 | 16.8405 | -13.4123 | 814.284 | 13.3479 | -20.2179 | 55.7087 | 55.7087 | 35.9513 | 215.9513 | 24.947 | 231.9907 | 231.9907 | 234.087 | 466.0777 | 0.57598 | 57.6% | 210.7604 | 121.3935 | 84.9755 | 174.7382 | 174.7382 | 48.63% | 11.28% | 11.28% | 85% | 9.588% | 20.2084 | 4.2272 | 4.2272 | 85.4239 | 44.689 | 48.89% | 48.89%
8 | 218 | 6 | 5223 | 15 | 26.8 | 233.56 | 168.89 | 402.45 | 168.89 | 84.45 | 218 | 5223 | 900 | 215.0137 | 16.8405 | -13.4123 | 874.284 | 14.3479 | -35.2179 | 48.2965 | 48.2965 | 56.0645 | 236.0645 | 37.7639 | 247.3069 | 247.3069 | 144.1566 | 391.4635 | 0.54829 | 54.83% | 177.0198 | 97.0585 | 67.9409 | 257.8773 | 257.8773 | 26.35% | 11.2% | 11.2% | 85% | 9.519% | 16.8511 | 3.7639 | 3.7639 | 63.4255 | 37.2647 | 24.6% | 24.6%
8 | 218 | 6 | 5224 | 16 | 18.6 | 312.08 | 207.56 | 519.64 | 207.56 | 103.78 | 218 | 5224 | 960 | 215.0137 | 16.8405 | -13.4123 | 934.284 | 15.3479 | -50.2179 | 39.0885 | 39.0885 | 71.3757 | 251.3757 | 51.6019 | 307.4288 | 307.4288 | 177.1635 | 484.5924 | 0.5608 | 56.08% | 219.1327 | 122.89 | 86.023 | 146.4898 | 146.4898 | 58.72% | 11.38% | 11.38% | 85% | 9.67% | 21.1898 | 5.2259 | 5.2259 | 110.7366 | 46.8593 | 75.59% | 75.59%
8 | 218 | 6 | 5225 | 17 | 17.5 | 188.94 | 165.06 | 354 | 165.06 | 82.53 | 218 | 5225 | 1020 | 215.0137 | 16.8405 | -13.4123 | 994.284 | 16.3479 | -65.2179 | 29.0688 | 29.0688 | 83.8293 | 263.8293 | 65.7959 | 159.4352 | 159.4352 | 140.8875 | 300.3228 | 0.40342 | 40.34% | 135.806 | 54.7875 | 38.3512 | 134.1238 | 134.1238 | 28.59% | 11.42% | 11.42% | 85% | 9.708% | 13.1835 | 5.4579 | 5.4579 | 71.9539 | 29.1541 | 53.65% | 53.65%
8 | 218 | 6 | 5226 | 18 | 19.8 | 130 | 93.89 | 223.89 | 93.89 | 46.95 | 218 | 5226 | 1080 | 215.0137 | 16.8405 | -13.4123 | 1054.284 | 17.3479 | -80.2179 | 18.8127 | 18.8127 | 94.8422 | 274.8422 | 80.1235 | 69.1474 | 69.1474 | 80.1401 | 149.2875 | 0.032348 | 3.235% | 67.5078 | 2.1838 | 1.5286 | 126.7551 | 126.7551 | 1.206% | 11.36% | 11.36% | 80% | 9.087% | 6.1347 | 4.9826 | 4.9826 | 30.5664 | 13.5662 | 24.11% | 24.11%
8 | 218 | 6 | 5227 | 19 | 22 | 88.75 | 60.06 | 148.81 | 60.06 | 30.03 | 218 | 5227 | 1140 | 215.0137 | 16.8405 | -13.4123 | 1114.284 | 18.3479 | -95.2179 | 8.714 | 8.714 | 105.3602 | 285.3602 | 94.4744 | 0 | 0 | 51.2644 | 51.2644 | -1.3492 | 0% | 23.1818 | 0 | 0 | 163.9127 | 163.9127 | 0% | 11.27% | 0% | 80% | 0% | 0 | 4.5626 | 4.5626 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5228 | 20 | 20.4 | 19.72 | 27.56 | 47.28 | 27.56 | 13.78 | 218 | 5228 | 1200 | 215.0137 | 16.8405 | -13.4123 | 1174.284 | 19.3479 | -110.2179 | -0.88291 | 0 | 115.0266 | 295.0266 | 107.4056 | 0 | 0 | 23.5239 | 23.5239 | -4.0369 | 0% | 10.6375 | 0 | 0 | 147.9398 | 147.9398 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8647 | 4.8647 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5229 | 21 | 19 | 0 | 1.31 | 1.31 | 1.31 | 0.66 | 218 | 5229 | 1260 | 215.0137 | 16.8405 | -13.4123 | 1234.284 | 20.3479 | -125.2179 | -9.6066 | 0 | 115.0266 | 295.0266 | 107.4056 | 0 | 0 | 1.1182 | 1.1182 | -103.8015 | 0% | 0.50563 | 0 | 0 | -5.4593 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5230 | 22 | 17.8 | 0 | 0 | 0 | 0 | 0 | 218 | 5230 | 1320 | 215.0137 | 16.8405 | -13.4123 | 1294.284 | 21.3479 | -140.2179 | -17.0135 | 0 | 115.0266 | 295.0266 | 107.4056 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1166 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5231 | 23 | 17.7 | 0 | 0 | 0 | 0 | 0 | 218 | 5231 | 1380 | 215.0137 | 16.8405 | -13.4123 | 1354.284 | 22.3479 | -155.2179 | -22.5807 | 0 | 115.0266 | 295.0266 | 107.4056 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5511 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
8 | 218 | 6 | 5232 | 24 | 17.6 | 0 | 0 | 0 | 0 | 0 | 218 | 5232 | 1440 | 215.0137 | 16.8405 | -13.4123 | 1414.284 | 23.3479 | -170.2179 | -25.7736 | 0 | 115.0266 | 295.0266 | 107.4056 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9856 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5233 | 1 | 17.6 | 0 | 0 | 0 | 0 | 0 | 219 | 5233 | 60 | 216 | 16.5773 | -13.53 | 34.284 | 0.3459 | 174.8115 | -26.4725 | 0 | 114.6209 | 65.3791 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5553 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5234 | 2 | 17 | 0 | 0 | 0 | 0 | 0 | 219 | 5234 | 120 | 216 | 16.5773 | -13.53 | 94.284 | 1.3459 | 159.8115 | -24.0875 | 0 | 114.6209 | 65.3791 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.902 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5235 | 3 | 16.3 | 0 | 0 | 0 | 0 | 0 | 219 | 5235 | 180 | 216 | 16.5773 | -13.53 | 154.284 | 2.3459 | 144.8115 | -19.1786 | 0 | 114.6209 | 65.3791 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4011 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5236 | 4 | 16.7 | 0 | 0 | 0 | 0 | 0 | 219 | 5236 | 240 | 216 | 16.5773 | -13.53 | 214.284 | 3.3459 | 129.8115 | -12.2595 | 0 | 114.6209 | 65.3791 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7915 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5237 | 5 | 16.8 | 0 | 0 | 0 | 0 | 0 | 219 | 5237 | 300 | 216 | 16.5773 | -13.53 | 274.284 | 4.3459 | 114.8115 | -3.872 | 0 | 114.6209 | 65.3791 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.6374 | 6.6374 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5238 | 6 | 16.6 | 0.28 | 2.5 | 2.78 | 2.5 | 1.25 | 219 | 5238 | 360 | 216 | 16.5773 | -13.53 | 334.284 | 5.3459 | 99.8115 | 5.5121 | 5.5121 | 108.4129 | 71.5871 | 98.8816 | 0 | 0 | 2.1339 | 2.1339 | -56.5179 | 0% | 0.96494 | 0 | 0 | 16.8619 | 16.8619 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5239 | 7 | 16.7 | 17 | 23.47 | 40.47 | 23.47 | 11.74 | 219 | 5239 | 420 | 216 | 16.5773 | -13.53 | 394.284 | 6.3459 | 84.8115 | 15.5014 | 15.5014 | 97.8869 | 82.1131 | 84.5208 | 6.0736 | 6.0736 | 20.0329 | 26.1065 | -3.8728 | 0% | 11.8053 | 0 | 0 | 183.5031 | 183.5031 | 0% | 11.49% | 11.49% | 80% | 9.194% | 1.0854 | 5.6319 | 5.6319 | 6.1127 | 2.4002 | 3.331% | 3.331%
8 | 219 | 7 | 5240 | 8 | 18.6 | 54.39 | 50.22 | 104.61 | 50.22 | 25.11 | 219 | 5240 | 480 | 216 | 16.5773 | -13.53 | 454.284 | 7.3459 | 69.8115 | 25.7486 | 25.7486 | 87.0952 | 92.9048 | 70.1561 | 42.5004 | 42.5004 | 42.8655 | 85.3659 | -0.57655 | 0% | 38.6025 | 0 | 0 | 197.4881 | 197.4881 | 0% | 11.41% | 11.41% | 80% | 9.126% | 3.5227 | 5.2259 | 5.2259 | 18.4095 | 7.7902 | 9.322% | 9.322%
8 | 219 | 7 | 5241 | 9 | 19.8 | 119.67 | 73 | 192.67 | 73 | 36.5 | 219 | 5241 | 540 | 216 | 16.5773 | -13.53 | 514.284 | 8.3459 | 54.8115 | 35.884 | 35.884 | 75.1908 | 104.8092 | 55.8818 | 114.5161 | 114.5161 | 62.3094 | 176.8255 | 0.15252 | 15.25% | 79.9605 | 12.1957 | 8.537 | 183.2065 | 183.2065 | 4.66% | 11.36% | 11.36% | 80% | 9.087% | 7.2661 | 4.9826 | 4.9826 | 36.2038 | 16.0683 | 19.76% | 19.76%
8 | 219 | 7 | 5242 | 10 | 21.3 | 228.28 | 157.08 | 385.36 | 157.08 | 78.54 | 219 | 5242 | 600 | 216 | 16.5773 | -13.53 | 574.284 | 9.3459 | 39.8115 | 45.4055 | 45.4055 | 60.9319 | 119.0681 | 41.8645 | 238.7408 | 238.7408 | 134.0762 | 372.817 | 0.50383 | 50.38% | 168.5878 | 84.94 | 59.458 | 170.2888 | 170.2888 | 34.92% | 11.32% | 11.32% | 85% | 9.623% | 16.2236 | 4.6926 | 4.6926 | 76.1302 | 35.8771 | 44.71% | 44.71%
8 | 219 | 7 | 5243 | 11 | 21.5 | 393.94 | 151.17 | 545.11 | 151.17 | 75.59 | 219 | 5243 | 660 | 216 | 16.5773 | -13.53 | 634.284 | 10.3459 | 24.8115 | 53.4831 | 53.4831 | 42.523 | 137.477 | 28.5501 | 430.5643 | 430.5643 | 129.0317 | 559.596 | 0.6048 | 60.48% | 253.0493 | 153.0444 | 107.1311 | 169.1489 | 169.1489 | 63.34% | 11.33% | 11.33% | 90% | 10.2% | 25.8084 | 4.6551 | 4.6551 | 120.1399 | 57.0729 | 71.03% | 71.03%
8 | 219 | 7 | 5244 | 12 | 22.6 | 339.94 | 192.5 | 532.44 | 192.5 | 96.25 | 219 | 5244 | 720 | 216 | 16.5773 | -13.53 | 694.284 | 11.3459 | 9.8115 | 58.7231 | 58.7231 | 18.3357 | 161.6643 | 17.671 | 378.9775 | 378.9775 | 164.309 | 543.2865 | 0.60322 | 60.32% | 245.6742 | 148.196 | 103.7372 | 158.1699 | 158.1699 | 65.59% | 11.32% | 11.32% | 90% | 10.18% | 25.0189 | 4.4539 | 4.4539 | 111.4325 | 55.327 | 70.45% | 70.45%
8 | 219 | 7 | 5245 | 13 | 23.3 | 195.64 | 298.89 | 494.53 | 298.89 | 149.45 | 219 | 5245 | 780 | 216 | 16.5773 | -13.53 | 754.284 | 12.3459 | -5.1885 | 59.4943 | 59.4943 | 9.8311 | 189.8311 | 15.6555 | 218.6475 | 218.6475 | 255.1186 | 473.7661 | 0.57695 | 57.7% | 214.237 | 123.6047 | 86.5233 | 160.6611 | 160.6611 | 53.85% | 11.29% | 11.29% | 85% | 9.599% | 20.5643 | 4.3304 | 4.3304 | 89.0509 | 45.4762 | 55.43% | 55.43%
8 | 219 | 7 | 5246 | 14 | 23.9 | 223.89 | 276.61 | 500.5 | 276.61 | 138.31 | 219 | 5246 | 840 | 216 | 16.5773 | -13.53 | 814.284 | 13.3459 | -20.1885 | 55.4815 | 55.4815 | 35.711 | 215.711 | 24.7736 | 246.723 | 246.723 | 236.1014 | 482.8244 | 0.58389 | 58.39% | 218.3332 | 127.4821 | 89.2375 | 170.0919 | 170.0919 | 52.46% | 11.28% | 11.28% | 85% | 9.591% | 20.9411 | 4.2272 | 4.2272 | 88.5215 | 46.3095 | 52.04% | 52.04%
8 | 219 | 7 | 5247 | 15 | 23.4 | 249.11 | 182.28 | 431.39 | 182.28 | 91.14 | 219 | 5247 | 900 | 216 | 16.5773 | -13.53 | 874.284 | 14.3459 | -35.1885 | 48.1011 | 48.1011 | 55.7965 | 235.7965 | 37.649 | 264.9879 | 264.9879 | 155.5857 | 420.5736 | 0.54875 | 54.87% | 190.1834 | 104.3631 | 73.0541 | 154.446 | 154.446 | 47.3% | 11.28% | 11.28% | 85% | 9.589% | 18.2365 | 4.313 | 4.313 | 78.6536 | 40.3283 | 50.93% | 50.93%
8 | 219 | 7 | 5248 | 16 | 25 | 206.61 | 194.31 | 400.92 | 194.31 | 97.16 | 219 | 5248 | 960 | 216 | 16.5773 | -13.53 | 934.284 | 15.3459 | -50.1885 | 38.9138 | 38.9138 | 71.1196 | 251.1196 | 51.5224 | 204.6555 | 204.6555 | 165.854 | 370.5095 | 0.52352 | 52.35% | 167.5444 | 87.7131 | 61.3991 | 180.8449 | 180.8449 | 33.95% | 11.23% | 11.23% | 85% | 9.549% | 15.9985 | 4.0445 | 4.0445 | 64.7059 | 35.3792 | 35.78% | 35.78%
8 | 219 | 7 | 5249 | 17 | 22.8 | 145.22 | 158.83 | 304.05 | 158.83 | 79.42 | 219 | 5249 | 1020 | 216 | 16.5773 | -13.53 | 994.284 | 16.3459 | -65.1885 | 28.9036 | 28.9036 | 83.5928 | 263.5928 | 65.7417 | 123.4412 | 123.4412 | 135.5699 | 259.0111 | 0.38453 | 38.45% | 117.1248 | 45.0381 | 31.5267 | 136.1255 | 136.1255 | 23.16% | 11.27% | 11.27% | 80% | 9.015% | 10.5587 | 4.4183 | 4.4183 | 46.6515 | 23.3497 | 34.27% | 34.27%
8 | 219 | 7 | 5250 | 18 | 23 | 96.61 | 101.53 | 198.14 | 101.53 | 50.77 | 219 | 5250 | 1080 | 216 | 16.5773 | -13.53 | 1054.284 | 17.3459 | -80.1885 | 18.6481 | 18.6481 | 94.6232 | 274.6232 | 80.0902 | 51.9974 | 51.9974 | 86.6613 | 138.6587 | 0.02356 | 2.356% | 62.7014 | 1.4772 | 1.0341 | 127.584 | 127.584 | 0.8105% | 11.24% | 11.24% | 80% | 8.994% | 5.6396 | 4.3829 | 4.3829 | 24.7176 | 12.4714 | 19.37% | 19.37%
8 | 219 | 7 | 5251 | 19 | 21 | 46.89 | 80.22 | 127.11 | 80.22 | 40.11 | 219 | 5251 | 1140 | 216 | 16.5773 | -13.53 | 1114.284 | 18.3459 | -95.1885 | 8.5428 | 8.5428 | 105.1559 | 285.1559 | 94.461 | 0 | 0 | 68.4721 | 68.4721 | -0.83993 | 0% | 30.9631 | 0 | 0 | 158.843 | 158.843 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7493 | 4.7493 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5252 | 20 | 20.1 | 3.06 | 25.14 | 28.2 | 25.14 | 12.57 | 219 | 5252 | 1200 | 216 | 16.5773 | -13.53 | 1174.284 | 19.3459 | -110.1885 | -1.0664 | 0 | 114.6209 | 294.6209 | 107.1329 | 0 | 0 | 21.4583 | 21.4583 | -4.5337 | 0% | 9.7035 | 0 | 0 | 145.1892 | 145.1892 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5253 | 21 | 19.8 | 0 | 0 | 0 | 0 | 0 | 219 | 5253 | 1260 | 216 | 16.5773 | -13.53 | 1234.284 | 20.3459 | -125.1885 | -9.8073 | 0 | 114.6209 | 294.6209 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.4071 | 0 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9826 | 4.9826 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5254 | 22 | 18.5 | 0 | 0 | 0 | 0 | 0 | 219 | 5254 | 1320 | 216 | 16.5773 | -13.53 | 1294.284 | 21.3459 | -140.1885 | -17.2345 | 0 | 114.6209 | 294.6209 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.8868 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5255 | 23 | 17.2 | 0 | 0 | 0 | 0 | 0 | 219 | 5255 | 1380 | 216 | 16.5773 | -13.53 | 1354.284 | 22.3459 | -155.1885 | -22.8221 | 0 | 114.6209 | 294.6209 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3003 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 219 | 7 | 5256 | 24 | 17.1 | 0 | 0 | 0 | 0 | 0 | 219 | 5256 | 1440 | 216 | 16.5773 | -13.53 | 1414.284 | 23.3459 | -170.1885 | -26.031 | 0 | 114.6209 | 294.6209 | 107.1329 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.885 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5257 | 1 | 16.4 | 0 | 0 | 0 | 0 | 0 | 220 | 5257 | 60 | 216.9863 | 16.3097 | -13.6356 | 34.284 | 0.34414 | 174.8379 | -26.7412 | 0 | 114.2094 | 65.7906 | 106.8558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.451 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5258 | 2 | 16.3 | 0 | 0 | 0 | 0 | 0 | 220 | 5258 | 120 | 216.9863 | 16.3097 | -13.6356 | 94.284 | 1.3441 | 159.8379 | -24.3526 | 0 | 114.2094 | 65.7906 | 106.8558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.16 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5259 | 3 | 16.4 | 0 | 0 | 0 | 0 | 0 | 220 | 5259 | 180 | 216.9863 | 16.3097 | -13.6356 | 154.284 | 2.3441 | 144.8379 | -19.4323 | 0 | 114.2094 | 65.7906 | 106.8558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5641 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5260 | 4 | 16.5 | 0 | 0 | 0 | 0 | 0 | 220 | 5260 | 240 | 216.9863 | 16.3097 | -13.6356 | 214.284 | 3.3441 | 129.8379 | -12.4986 | 0 | 114.2094 | 65.7906 | 106.8558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4117 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5261 | 5 | 16.2 | 0 | 0 | 0 | 0 | 0 | 220 | 5261 | 300 | 216.9863 | 16.3097 | -13.6356 | 274.284 | 4.3441 | 114.8379 | -4.097 | 0 | 114.2094 | 65.7906 | 106.8558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.2415 | 4.2415 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5262 | 6 | 16.3 | 0 | 1.25 | 1.25 | 1.25 | 0.63 | 220 | 5262 | 360 | 216.9863 | 16.3097 | -13.6356 | 334.284 | 5.3441 | 99.8379 | 5.2982 | 5.2982 | 108.2494 | 71.7506 | 98.928 | 0 | 0 | 1.0669 | 1.0669 | -114.4721 | 0% | 0.48247 | 0 | 0 | 14.1634 | 14.1634 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5263 | 7 | 16.9 | 10.14 | 33.11 | 43.25 | 33.11 | 16.56 | 220 | 5263 | 420 | 216.9863 | 16.3097 | -13.6356 | 394.284 | 6.3441 | 84.8379 | 15.2944 | 15.2944 | 97.7091 | 82.2909 | 84.5472 | 3.6529 | 3.6529 | 28.2612 | 31.914 | -3.0076 | 0% | 14.4315 | 0 | 0 | 179.7708 | 179.7708 | 0% | 11.48% | 11.48% | 80% | 9.186% | 1.3257 | 5.588 | 5.588 | 7.4081 | 2.9317 | 4.121% | 4.121%
8 | 220 | 8 | 5264 | 8 | 17.3 | 57.64 | 77.08 | 134.72 | 77.08 | 38.54 | 220 | 5264 | 480 | 216.9863 | 16.3097 | -13.6356 | 454.284 | 7.3441 | 69.8379 | 25.5429 | 25.5429 | 86.9033 | 93.0967 | 70.1621 | 45.3649 | 45.3649 | 65.7919 | 111.1568 | -0.28229 | 0% | 50.2651 | 0 | 0 | 192.7595 | 192.7595 | 0% | 11.45% | 11.45% | 80% | 9.163% | 4.606 | 5.501 | 5.501 | 25.3375 | 10.1858 | 13.14% | 13.14%
8 | 220 | 8 | 5265 | 9 | 18.2 | 126.53 | 105.22 | 231.75 | 105.22 | 52.61 | 220 | 5265 | 540 | 216.9863 | 16.3097 | -13.6356 | 514.284 | 8.3441 | 54.8379 | 35.6729 | 35.6729 | 74.9858 | 105.0142 | 55.8637 | 121.7582 | 121.7582 | 89.8109 | 211.569 | 0.24276 | 24.28% | 95.6715 | 23.2252 | 16.2577 | 157.5841 | 157.5841 | 10.32% | 11.41% | 11.41% | 80% | 9.128% | 8.7331 | 5.3093 | 5.3093 | 46.3666 | 19.3125 | 29.42% | 29.42%
8 | 220 | 8 | 5266 | 10 | 19 | 216.06 | 128.61 | 344.67 | 128.61 | 64.31 | 220 | 5266 | 600 | 216.9863 | 16.3097 | -13.6356 | 574.284 | 9.3441 | 39.8379 | 45.1805 | 45.1805 | 60.7229 | 119.2771 | 41.8136 | 227.0215 | 227.0215 | 109.7755 | 336.797 | 0.45671 | 45.67% | 152.2996 | 69.5572 | 48.6901 | 161.7288 | 161.7288 | 30.11% | 11.38% | 11.38% | 85% | 9.671% | 14.7287 | 5.1437 | 5.1437 | 75.7599 | 32.5712 | 46.84% | 46.84%
8 | 220 | 8 | 5267 | 11 | 21.1 | 300.22 | 168.94 | 469.16 | 168.94 | 84.47 | 220 | 5267 | 660 | 216.9863 | 16.3097 | -13.6356 | 634.284 | 10.3441 | 24.8379 | 53.2364 | 53.2364 | 42.3441 | 137.6559 | 28.4451 | 329.5116 | 329.5116 | 144.1993 | 473.7109 | 0.56684 | 56.68% | 214.2121 | 121.4243 | 84.997 | 163.3078 | 163.3078 | 52.05% | 11.33% | 11.33% | 85% | 9.632% | 20.6338 | 4.7303 | 4.7303 | 97.6044 | 45.6298 | 59.77% | 59.77%
8 | 220 | 8 | 5268 | 12 | 22.9 | 344.5 | 212.92 | 557.42 | 212.92 | 106.46 | 220 | 5268 | 720 | 216.9863 | 16.3097 | -13.6356 | 694.284 | 11.3441 | 9.8379 | 58.4566 | 58.4566 | 18.2679 | 161.7321 | 17.4645 | 385.5931 | 385.5931 | 181.7386 | 567.3317 | 0.61288 | 61.29% | 256.5474 | 157.2316 | 110.0621 | 159.3031 | 159.3031 | 69.09% | 11.31% | 11.31% | 90% | 10.18% | 26.1252 | 4.4006 | 4.4006 | 114.9656 | 57.7737 | 72.17% | 72.17%
8 | 220 | 8 | 5269 | 13 | 23.8 | 380.47 | 236.67 | 617.14 | 236.67 | 118.34 | 220 | 5269 | 780 | 216.9863 | 16.3097 | -13.6356 | 754.284 | 12.3441 | -5.1621 | 59.2318 | 59.2318 | 9.7181 | 189.7181 | 15.395 | 426.9082 | 426.9082 | 202.0105 | 628.9187 | 0.63468 | 63.47% | 284.397 | 180.5002 | 126.3502 | 175.2944 | 175.2944 | 72.08% | 11.32% | 11.32% | 90% | 10.18% | 28.9648 | 4.2442 | 4.2442 | 122.9316 | 64.053 | 70.13% | 70.13%
8 | 220 | 8 | 5270 | 14 | 22.9 | 104.64 | 277.86 | 382.5 | 277.86 | 138.93 | 220 | 5270 | 840 | 216.9863 | 16.3097 | -13.6356 | 814.284 | 13.3441 | -20.1621 | 55.2486 | 55.2486 | 35.4749 | 215.4749 | 24.6016 | 115.7954 | 115.7954 | 237.1683 | 352.9637 | 0.4968 | 49.68% | 159.6102 | 79.2941 | 55.5059 | 150.5538 | 150.5538 | 36.87% | 11.28% | 11.28% | 85% | 9.589% | 15.3044 | 4.4006 | 4.4006 | 67.3477 | 33.8443 | 44.73% | 44.73%
8 | 220 | 8 | 5271 | 15 | 20 | 168.61 | 291.61 | 460.22 | 291.61 | 145.81 | 220 | 5271 | 900 | 216.9863 | 16.3097 | -13.6356 | 874.284 | 14.3441 | -35.1621 | 47.8999 | 47.8999 | 55.5302 | 235.5302 | 37.5368 | 180.1967 | 180.1967 | 248.9047 | 429.1014 | 0.53656 | 53.66% | 194.0396 | 104.1145 | 72.8802 | 147.0521 | 147.0521 | 49.56% | 11.35% | 11.35% | 85% | 9.649% | 18.7233 | 4.943 | 4.943 | 92.5491 | 41.4048 | 62.94% | 62.94%
8 | 220 | 8 | 5272 | 16 | 21.2 | 177.5 | 245.28 | 422.78 | 245.28 | 122.64 | 220 | 5272 | 960 | 216.9863 | 16.3097 | -13.6356 | 934.284 | 15.3441 | -50.1621 | 38.7335 | 38.7335 | 70.8638 | 250.8638 | 51.4458 | 176.8068 | 176.8068 | 209.3596 | 386.1663 | 0.51364 | 51.36% | 174.6244 | 89.6947 | 62.7863 | 145.4113 | 145.4113 | 43.18% | 11.32% | 11.32% | 85% | 9.626% | 16.8093 | 4.7114 | 4.7114 | 79.1954 | 37.1723 | 54.46% | 54.46%
8 | 220 | 8 | 5273 | 17 | 22.4 | 166.53 | 212.92 | 379.45 | 212.92 | 106.46 | 220 | 5273 | 1020 | 216.9863 | 16.3097 | -13.6356 | 994.284 | 16.3441 | -65.1621 | 28.733 | 28.733 | 83.3557 | 263.3557 | 65.6904 | 142.6066 | 142.6066 | 181.7386 | 324.3452 | 0.46635 | 46.64% | 146.6689 | 68.3997 | 47.8798 | 142.6422 | 142.6422 | 33.57% | 11.29% | 11.29% | 85% | 9.596% | 14.0741 | 4.4899 | 4.4899 | 63.191 | 31.1236 | 44.3% | 44.3%
8 | 220 | 8 | 5274 | 18 | 21.9 | 182.44 | 156.72 | 339.16 | 156.72 | 78.36 | 220 | 5274 | 1080 | 216.9863 | 16.3097 | -13.6356 | 1054.284 | 17.3441 | -80.1621 | 18.4781 | 18.4781 | 94.4035 | 274.4035 | 80.0598 | 99.3641 | 99.3641 | 133.7689 | 233.133 | 0.32959 | 32.96% | 105.4227 | 34.7466 | 24.3227 | 136.1642 | 136.1642 | 17.86% | 11.29% | 11.29% | 80% | 9.034% | 9.5241 | 4.581 | 4.581 | 43.6295 | 21.0617 | 32.04% | 32.04%
8 | 220 | 8 | 5275 | 19 | 21.1 | 121.94 | 99.39 | 221.33 | 99.39 | 49.7 | 220 | 5275 | 1140 | 216.9863 | 16.3097 | -13.6356 | 1114.284 | 18.3441 | -95.1621 | 8.3665 | 8.3665 | 104.9509 | 284.9509 | 94.4505 | 0 | 0 | 84.8347 | 84.8347 | -0.52028 | 0% | 38.3622 | 0 | 0 | 124.6645 | 124.6645 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7303 | 4.7303 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5276 | 20 | 19.6 | 18.47 | 28.39 | 46.86 | 28.39 | 14.2 | 220 | 5276 | 1200 | 216.9863 | 16.3097 | -13.6356 | 1174.284 | 19.3441 | -110.1621 | -1.2551 | 0 | 114.2094 | 294.2094 | 106.8558 | 0 | 0 | 24.2324 | 24.2324 | -3.9681 | 0% | 10.9579 | 0 | 0 | 147.0964 | 147.0964 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0224 | 5.0224 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5277 | 21 | 19 | 0 | 1.25 | 1.25 | 1.25 | 0.63 | 220 | 5277 | 1260 | 216.9863 | 16.3097 | -13.6356 | 1234.284 | 20.3441 | -125.1621 | -10.0131 | 0 | 114.2094 | 294.2094 | 106.8558 | 0 | 0 | 1.0669 | 1.0669 | -108.8226 | 0% | 0.48247 | 0 | 0 | -5.0501 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5278 | 22 | 18.4 | 0 | 0 | 0 | 0 | 0 | 220 | 5278 | 1320 | 216.9863 | 16.3097 | -13.6356 | 1294.284 | 21.3441 | -140.1621 | -17.4605 | 0 | 114.2094 | 294.2094 | 106.8558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7333 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5279 | 23 | 17.3 | 0 | 0 | 0 | 0 | 0 | 220 | 5279 | 1380 | 216.9863 | 16.3097 | -13.6356 | 1354.284 | 22.3441 | -155.1621 | -23.0684 | 0 | 114.2094 | 294.2094 | 106.8558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.9663 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
8 | 220 | 8 | 5280 | 24 | 17.3 | 0 | 0 | 0 | 0 | 0 | 220 | 5280 | 1440 | 216.9863 | 16.3097 | -13.6356 | 1414.284 | 23.3441 | -170.1621 | -26.293 | 0 | 114.2094 | 294.2094 | 106.8558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5228 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5281 | 1 | 17.3 | 0 | 0 | 0 | 0 | 0 | 221 | 5281 | 60 | 217.9726 | 16.0377 | -13.7289 | 34.284 | 0.34258 | 174.8612 | -27.014 | 0 | 113.7919 | 66.2081 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.6966 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5282 | 2 | 17.3 | 0 | 0 | 0 | 0 | 0 | 221 | 5282 | 120 | 217.9726 | 16.0377 | -13.7289 | 94.284 | 1.3426 | 159.8612 | -24.621 | 0 | 113.7919 | 66.2081 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2149 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5283 | 3 | 17.2 | 0 | 0 | 0 | 0 | 0 | 221 | 5283 | 180 | 217.9726 | 16.0377 | -13.7289 | 154.284 | 2.3426 | 144.8612 | -19.6886 | 0 | 113.7919 | 66.2081 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.8855 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5284 | 4 | 17.1 | 0 | 0 | 0 | 0 | 0 | 221 | 5284 | 240 | 217.9726 | 16.0377 | -13.7289 | 214.284 | 3.3426 | 129.8612 | -12.7398 | 0 | 113.7919 | 66.2081 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.0379 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5285 | 5 | 17.2 | 0 | 0 | 0 | 0 | 0 | 221 | 5285 | 300 | 217.9726 | 16.0377 | -13.7289 | 274.284 | 4.3426 | 114.8612 | -4.3237 | 0 | 113.7919 | 66.2081 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.0307 | 6.0307 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5286 | 6 | 17.2 | 0.08 | 1.11 | 1.19 | 1.11 | 0.56 | 221 | 5286 | 360 | 217.9726 | 16.0377 | -13.7289 | 334.284 | 5.3426 | 99.8612 | 5.083 | 5.083 | 108.081 | 71.919 | 98.9717 | 0 | 0 | 0.94744 | 0.94744 | -126.8793 | 0% | 0.42843 | 0 | 0 | 15.433 | 15.433 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5287 | 7 | 17.1 | 10.69 | 25.69 | 36.38 | 25.69 | 12.85 | 221 | 5287 | 420 | 217.9726 | 16.0377 | -13.7289 | 394.284 | 6.3426 | 84.8612 | 15.0862 | 15.0862 | 97.5264 | 82.4736 | 84.571 | 3.886 | 3.886 | 21.9278 | 25.8138 | -3.891 | 0% | 11.673 | 0 | 0 | 179.9375 | 179.9375 | 0% | 11.48% | 11.48% | 80% | 9.18% | 1.0716 | 5.5443 | 5.5443 | 5.9414 | 2.3698 | 3.302% | 3.302%
8 | 221 | 9 | 5288 | 8 | 17.1 | 32.56 | 76.67 | 109.23 | 76.67 | 38.34 | 221 | 5288 | 480 | 217.9726 | 16.0377 | -13.7289 | 454.284 | 7.3426 | 69.8612 | 25.336 | 25.336 | 86.7063 | 93.2937 | 70.1653 | 25.8172 | 25.8172 | 65.4419 | 91.2592 | -0.52405 | 0% | 41.2674 | 0 | 0 | 190.75 | 190.75 | 0% | 11.47% | 11.47% | 80% | 9.172% | 3.7851 | 5.5443 | 5.5443 | 20.9856 | 8.3703 | 11% | 11%
8 | 221 | 9 | 5289 | 9 | 17.2 | 119.67 | 132 | 251.67 | 132 | 66 | 221 | 5289 | 540 | 217.9726 | 16.0377 | -13.7289 | 514.284 | 8.3426 | 54.8612 | 35.4602 | 35.4602 | 74.7757 | 105.2243 | 55.8429 | 115.818 | 115.818 | 112.669 | 228.487 | 0.27455 | 27.45% | 103.3218 | 28.3668 | 19.8568 | 156.7035 | 156.7035 | 12.67% | 11.44% | 11.44% | 80% | 9.152% | 9.456 | 5.5226 | 5.5226 | 52.2218 | 20.9112 | 33.33% | 33.33%
8 | 221 | 9 | 5290 | 10 | 17.4 | 216.33 | 160.06 | 376.39 | 160.06 | 80.03 | 221 | 5290 | 600 | 217.9726 | 16.0377 | -13.7289 | 574.284 | 9.3426 | 39.8612 | 44.9535 | 44.9535 | 60.5086 | 119.4914 | 41.76 | 228.396 | 228.396 | 136.6198 | 365.0158 | 0.47381 | 47.38% | 165.0601 | 78.2068 | 54.7447 | 160.3294 | 160.3294 | 34.15% | 11.41% | 11.41% | 85% | 9.702% | 16.0143 | 5.4794 | 5.4794 | 87.7482 | 35.4141 | 54.73% | 54.73%
8 | 221 | 9 | 5291 | 11 | 17.5 | 376.17 | 163.39 | 539.56 | 163.39 | 81.7 | 221 | 5291 | 660 | 217.9726 | 16.0377 | -13.7289 | 634.284 | 10.3426 | 24.8612 | 52.9871 | 52.9871 | 42.1597 | 137.8403 | 28.3374 | 414.6434 | 414.6434 | 139.4621 | 554.1055 | 0.58689 | 58.69% | 250.5665 | 147.055 | 102.9385 | 160.2562 | 160.2562 | 64.23% | 11.39% | 11.39% | 90% | 10.25% | 25.6761 | 5.4579 | 5.4579 | 140.1371 | 56.7805 | 87.45% | 87.45%
8 | 221 | 9 | 5292 | 12 | 17.9 | 455.06 | 182.22 | 637.28 | 182.22 | 91.11 | 221 | 5292 | 720 | 217.9726 | 16.0377 | -13.7289 | 694.284 | 11.3426 | 9.8612 | 58.1866 | 58.1866 | 18.194 | 161.806 | 17.2546 | 511.4103 | 511.4103 | 155.5345 | 666.9448 | 0.62496 | 62.5% | 301.5924 | 188.4835 | 131.9385 | 154.003 | 154.003 | 85.67% | 11.37% | 11.37% | 90% | 10.23% | 30.8548 | 5.3726 | 5.3726 | 165.7692 | 68.2327 | 107.6% | 107.6%
8 | 221 | 9 | 5293 | 13 | 17.6 | 401.19 | 230.19 | 631.38 | 230.19 | 115.1 | 221 | 5293 | 780 | 217.9726 | 16.0377 | -13.7289 | 754.284 | 12.3426 | -5.1388 | 58.9645 | 58.9645 | 9.6114 | 189.6114 | 15.1318 | 451.9822 | 451.9822 | 196.4795 | 648.4616 | 0.61883 | 61.88% | 293.2343 | 181.4609 | 127.0226 | 151.145 | 151.145 | 84.04% | 11.37% | 11.37% | 90% | 10.23% | 30.012 | 5.4364 | 5.4364 | 163.1582 | 66.3688 | 107.9% | 107.9%
8 | 221 | 9 | 5294 | 14 | 17.8 | 383.83 | 212.56 | 596.39 | 212.56 | 106.28 | 221 | 5294 | 840 | 217.9726 | 16.0377 | -13.7289 | 814.284 | 13.3426 | -20.1388 | 55.0101 | 55.0101 | 35.2429 | 215.2429 | 24.4312 | 426.5605 | 426.5605 | 181.4313 | 607.9918 | 0.60723 | 60.72% | 274.9339 | 166.9492 | 116.8645 | 148.6915 | 148.6915 | 78.6% | 11.38% | 11.38% | 90% | 10.24% | 28.1469 | 5.3938 | 5.3938 | 151.8184 | 62.2444 | 102.1% | 102.1%
8 | 221 | 9 | 5295 | 15 | 18.2 | 317.72 | 178.61 | 496.33 | 178.61 | 89.31 | 221 | 5295 | 900 | 217.9726 | 16.0377 | -13.7289 | 874.284 | 14.3426 | -35.1388 | 47.6929 | 47.6929 | 55.2656 | 235.2656 | 37.4272 | 341.1677 | 341.1677 | 152.4532 | 493.6209 | 0.56345 | 56.34% | 223.2154 | 125.7705 | 88.0393 | 142.7848 | 142.7848 | 61.66% | 11.38% | 11.38% | 85% | 9.675% | 21.596 | 5.3093 | 5.3093 | 114.6599 | 47.7577 | 80.3% | 80.3%
8 | 221 | 9 | 5296 | 16 | 19.3 | 311.06 | 160.97 | 472.03 | 160.97 | 80.49 | 221 | 5296 | 960 | 217.9726 | 16.0377 | -13.7289 | 934.284 | 15.3426 | -50.1388 | 38.5475 | 38.5475 | 70.6082 | 250.6082 | 51.3721 | 311.6078 | 311.6078 | 137.3965 | 449.0043 | 0.54498 | 54.5% | 203.0397 | 110.6524 | 77.4567 | 141.8715 | 141.8715 | 54.6% | 11.37% | 11.37% | 85% | 9.661% | 19.615 | 5.0828 | 5.0828 | 99.6984 | 43.3769 | 70.27% | 70.27%
8 | 221 | 9 | 5297 | 17 | 19.5 | 231.06 | 133.47 | 364.53 | 133.47 | 66.74 | 221 | 5297 | 1020 | 217.9726 | 16.0377 | -13.7289 | 994.284 | 16.3426 | -65.1388 | 28.5568 | 28.5568 | 83.1183 | 263.1183 | 65.642 | 199.3546 | 199.3546 | 113.9238 | 313.2784 | 0.43417 | 43.42% | 141.6645 | 61.5065 | 43.0545 | 134.9681 | 134.9681 | 31.9% | 11.37% | 11.37% | 85% | 9.661% | 13.6856 | 5.0425 | 5.0425 | 69.0093 | 30.2645 | 51.13% | 51.13%
8 | 221 | 9 | 5298 | 18 | 19.1 | 81.61 | 111.67 | 193.28 | 111.67 | 55.84 | 221 | 5298 | 1080 | 217.9726 | 16.0377 | -13.7289 | 1054.284 | 17.3426 | -80.1388 | 18.3029 | 18.3029 | 94.1832 | 274.1832 | 80.0325 | 44.981 | 44.981 | 95.3163 | 140.2973 | -0.028118 | 0% | 63.4424 | 0 | 0 | 121.9665 | 121.9665 | 0% | 11.38% | 11.38% | 80% | 9.108% | 5.7782 | 5.1233 | 5.1233 | 29.6033 | 12.7779 | 24.27% | 24.27%
8 | 221 | 9 | 5299 | 19 | 19 | 76.89 | 73.61 | 150.5 | 73.61 | 36.81 | 221 | 5299 | 1140 | 217.9726 | 16.0377 | -13.7289 | 1114.284 | 18.3426 | -95.1388 | 8.1849 | 8.1849 | 104.7451 | 284.7451 | 94.4431 | 0 | 0 | 62.8301 | 62.8301 | -1.0576 | 0% | 28.4118 | 0 | 0 | 115.967 | 115.967 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5300 | 20 | 18.6 | 11.72 | 25.42 | 37.14 | 25.42 | 12.71 | 221 | 5300 | 1200 | 217.9726 | 16.0377 | -13.7289 | 1174.284 | 19.3426 | -110.1388 | -1.4489 | 0 | 113.7919 | 293.7919 | 106.5743 | 0 | 0 | 21.6973 | 21.6973 | -4.6276 | 0% | 9.8115 | 0 | 0 | 144.4734 | 144.4734 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5301 | 21 | 17.8 | 0 | 0 | 0 | 0 | 0 | 221 | 5301 | 1260 | 217.9726 | 16.0377 | -13.7289 | 1234.284 | 20.3426 | -125.1388 | -10.224 | 0 | 113.7919 | 293.7919 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.8911 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5302 | 22 | 17.8 | 0 | 0 | 0 | 0 | 0 | 221 | 5302 | 1320 | 217.9726 | 16.0377 | -13.7289 | 1294.284 | 21.3426 | -140.1388 | -17.6916 | 0 | 113.7919 | 293.7919 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3799 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5303 | 23 | 17.9 | 0 | 0 | 0 | 0 | 0 | 221 | 5303 | 1380 | 217.9726 | 16.0377 | -13.7289 | 1354.284 | 22.3426 | -155.1388 | -23.3196 | 0 | 113.7919 | 293.7919 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7457 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
8 | 221 | 9 | 5304 | 24 | 17.5 | 0 | 0 | 0 | 0 | 0 | 221 | 5304 | 1440 | 217.9726 | 16.0377 | -13.7289 | 1414.284 | 23.3426 | -170.1388 | -26.5597 | 0 | 113.7919 | 293.7919 | 106.5743 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.8736 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5305 | 1 | 17.4 | 0 | 0 | 0 | 0 | 0 | 222 | 5305 | 60 | 218.9589 | 15.7616 | -13.81 | 34.284 | 0.34123 | 174.8815 | -27.2909 | 0 | 113.3687 | 66.6313 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4269 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5306 | 2 | 17.3 | 0 | 0 | 0 | 0 | 0 | 222 | 5306 | 120 | 218.9589 | 15.7616 | -13.81 | 94.284 | 1.3412 | 159.8815 | -24.8928 | 0 | 113.3687 | 66.6313 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0666 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5307 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 222 | 5307 | 180 | 218.9589 | 15.7616 | -13.81 | 154.284 | 2.3412 | 144.8815 | -19.9476 | 0 | 113.3687 | 66.6313 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5351 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5308 | 4 | 15.2 | 0 | 0 | 0 | 0 | 0 | 222 | 5308 | 240 | 218.9589 | 15.7616 | -13.81 | 214.284 | 3.3412 | 129.8815 | -12.9829 | 0 | 113.3687 | 66.6313 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7543 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5309 | 5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 222 | 5309 | 300 | 218.9589 | 15.7616 | -13.81 | 274.284 | 4.3412 | 114.8815 | -4.5518 | 0 | 113.3687 | 66.6313 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.3405 | 1.3405 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5310 | 6 | 14 | 0.06 | 1.44 | 1.5 | 1.44 | 0.72 | 222 | 5310 | 360 | 218.9589 | 15.7616 | -13.81 | 334.284 | 5.3412 | 99.8815 | 4.8666 | 4.8666 | 107.9076 | 72.0924 | 99.0126 | 0 | 0 | 1.2291 | 1.2291 | -103.5024 | 0% | 0.55581 | 0 | 0 | 10.2973 | 10.2973 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5311 | 7 | 14.3 | 10.22 | 33.28 | 43.5 | 33.28 | 16.64 | 222 | 5311 | 420 | 218.9589 | 15.7616 | -13.81 | 394.284 | 6.3412 | 84.8815 | 14.8768 | 14.8768 | 97.3388 | 82.6612 | 84.592 | 3.7517 | 3.7517 | 28.4063 | 32.1579 | -3.1615 | 0% | 14.5418 | 0 | 0 | 175.7445 | 175.7445 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5312 | 8 | 16.7 | 40.83 | 81.94 | 122.77 | 81.94 | 40.97 | 222 | 5312 | 480 | 218.9589 | 15.7616 | -13.81 | 454.284 | 7.3412 | 69.8815 | 25.1279 | 25.1279 | 86.5045 | 93.4955 | 70.1659 | 32.6243 | 32.6243 | 69.9402 | 102.5644 | -0.38641 | 0% | 46.3796 | 0 | 0 | 190.9257 | 190.9257 | 0% | 11.48% | 11.48% | 80% | 9.183% | 4.259 | 5.6319 | 5.6319 | 23.986 | 9.4184 | 12.56% | 12.56%
8 | 222 | 10 | 5313 | 9 | 18.6 | 135.42 | 122.83 | 258.25 | 122.83 | 61.42 | 222 | 5313 | 540 | 218.9589 | 15.7616 | -13.81 | 514.284 | 8.3412 | 54.8815 | 35.2461 | 35.2461 | 74.5605 | 105.4395 | 55.8196 | 131.8325 | 131.8325 | 104.842 | 236.6745 | 0.30605 | 30.61% | 107.0242 | 32.7548 | 22.9283 | 159.2944 | 159.2944 | 14.39% | 11.4% | 11.4% | 80% | 9.116% | 9.7566 | 5.2259 | 5.2259 | 50.9877 | 21.576 | 32.01% | 32.01%
8 | 222 | 10 | 5314 | 10 | 20.5 | 217.28 | 145 | 362.28 | 145 | 72.5 | 222 | 5314 | 600 | 218.9589 | 15.7616 | -13.81 | 574.284 | 9.3412 | 39.8815 | 44.7246 | 44.7246 | 60.289 | 119.711 | 41.704 | 230.5237 | 230.5237 | 123.7652 | 354.2889 | 0.48319 | 48.32% | 160.2095 | 77.412 | 54.1884 | 164.5105 | 164.5105 | 32.94% | 11.34% | 11.34% | 85% | 9.639% | 15.4422 | 4.8453 | 4.8453 | 74.8219 | 34.1491 | 45.48% | 45.48%
8 | 222 | 10 | 5315 | 11 | 21.6 | 235.33 | 199.5 | 434.83 | 199.5 | 99.75 | 222 | 5315 | 660 | 218.9589 | 15.7616 | -13.81 | 634.284 | 10.3412 | 24.8815 | 52.735 | 52.735 | 41.9699 | 138.0301 | 28.2273 | 260.5336 | 260.5336 | 170.2839 | 430.8175 | 0.54576 | 54.58% | 194.8157 | 106.3232 | 74.4262 | 162.0659 | 162.0659 | 45.92% | 11.32% | 11.32% | 85% | 9.622% | 18.7444 | 4.6364 | 4.6364 | 86.9071 | 41.4515 | 53.62% | 53.62%
8 | 222 | 10 | 5316 | 12 | 21.9 | 333.11 | 255.69 | 588.8 | 255.69 | 127.85 | 222 | 5316 | 720 | 218.9589 | 15.7616 | -13.81 | 694.284 | 11.3412 | 9.8815 | 57.9129 | 57.9129 | 18.1142 | 161.8858 | 17.0411 | 375.9076 | 375.9076 | 218.2451 | 594.1526 | 0.61785 | 61.79% | 268.6758 | 166.0021 | 116.2015 | 158.3727 | 158.3727 | 73.37% | 11.33% | 11.33% | 90% | 10.2% | 27.3981 | 4.581 | 4.581 | 125.5093 | 60.5884 | 79.25% | 79.25%
8 | 222 | 10 | 5317 | 13 | 22.3 | 420.22 | 285.33 | 705.55 | 285.33 | 142.67 | 222 | 5317 | 780 | 218.9589 | 15.7616 | -13.81 | 754.284 | 12.3412 | -5.1185 | 58.6926 | 58.6926 | 9.5109 | 189.5109 | 14.8658 | 475.3734 | 475.3734 | 243.5444 | 718.9178 | 0.65137 | 65.14% | 325.0946 | 211.7559 | 148.2291 | 161.1003 | 161.1003 | 92.01% | 11.34% | 11.34% | 90% | 10.21% | 33.1843 | 4.508 | 4.508 | 149.5931 | 73.384 | 92.86% | 92.86%
8 | 222 | 10 | 5318 | 14 | 22.5 | 337.92 | 299.22 | 637.14 | 299.22 | 149.61 | 222 | 5318 | 840 | 218.9589 | 15.7616 | -13.81 | 814.284 | 13.3412 | -20.1185 | 54.7662 | 54.7662 | 35.0152 | 215.0152 | 24.2627 | 377.167 | 377.167 | 255.4002 | 632.5673 | 0.63122 | 63.12% | 286.0469 | 180.5577 | 126.3904 | 157.1171 | 157.1171 | 80.44% | 11.33% | 11.33% | 90% | 10.2% | 29.1656 | 4.4719 | 4.4719 | 130.4248 | 64.4971 | 83.01% | 83.01%
8 | 222 | 10 | 5319 | 15 | 23.4 | 224.94 | 264.44 | 489.38 | 264.44 | 132.22 | 222 | 5319 | 900 | 218.9589 | 15.7616 | -13.81 | 874.284 | 14.3412 | -35.1185 | 47.4802 | 47.4802 | 55.0029 | 235.0029 | 37.3204 | 242.7065 | 242.7065 | 225.7137 | 468.4202 | 0.57482 | 57.48% | 211.8196 | 121.7586 | 85.231 | 156.1886 | 156.1886 | 54.57% | 11.29% | 11.29% | 85% | 9.596% | 20.3273 | 4.313 | 4.313 | 87.6711 | 44.9519 | 56.13% | 56.13%
8 | 222 | 10 | 5320 | 16 | 24.2 | 222.5 | 220.42 | 442.92 | 220.42 | 110.21 | 222 | 5320 | 960 | 218.9589 | 15.7616 | -13.81 | 934.284 | 15.3412 | -50.1185 | 38.3558 | 38.3558 | 70.3531 | 250.3531 | 51.3014 | 224.1781 | 224.1781 | 188.1402 | 412.3184 | 0.54781 | 54.78% | 186.4504 | 102.1395 | 71.4977 | 166.9102 | 166.9102 | 42.84% | 11.26% | 11.26% | 85% | 9.573% | 17.849 | 4.1765 | 4.1765 | 74.5465 | 39.4716 | 44.66% | 44.66%
8 | 222 | 10 | 5321 | 17 | 25.3 | 117.72 | 188 | 305.72 | 188 | 94 | 222 | 5321 | 1020 | 218.9589 | 15.7616 | -13.81 | 994.284 | 16.3412 | -65.1185 | 28.3752 | 28.3752 | 82.8806 | 262.8806 | 65.5967 | 102.3406 | 102.3406 | 160.468 | 262.8086 | 0.41101 | 41.1% | 118.8421 | 48.8456 | 34.1919 | 178.3424 | 178.3424 | 19.17% | 11.2% | 11.2% | 80% | 8.956% | 10.6439 | 3.9962 | 3.9962 | 42.5346 | 23.538 | 23.85% | 23.85%
8 | 222 | 10 | 5322 | 18 | 23.5 | 45.83 | 130.61 | 176.44 | 130.61 | 65.31 | 222 | 5322 | 1080 | 218.9589 | 15.7616 | -13.81 | 1054.284 | 17.3412 | -80.1185 | 18.1223 | 18.1223 | 93.9622 | 273.9622 | 80.0082 | 25.5647 | 25.5647 | 111.4826 | 137.0473 | 0.022255 | 2.226% | 61.9728 | 1.3792 | 0.96544 | 134.5858 | 134.5858 | 0.7173% | 11.22% | 11.22% | 80% | 8.98% | 5.5649 | 4.2957 | 4.2957 | 23.9048 | 12.3062 | 17.76% | 17.76%
8 | 222 | 10 | 5323 | 19 | 22.9 | 41.33 | 55.22 | 96.55 | 55.22 | 27.61 | 222 | 5323 | 1140 | 218.9589 | 15.7616 | -13.81 | 1114.284 | 18.3412 | -95.1185 | 7.9982 | 7.9982 | 104.5386 | 284.5386 | 94.4387 | 0 | 0 | 47.1332 | 47.1332 | -1.4965 | 0% | 21.3136 | 0 | 0 | 159.4116 | 159.4116 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.4006 | 4.4006 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5324 | 20 | 22 | 5 | 22.64 | 27.64 | 22.64 | 11.32 | 222 | 5324 | 1200 | 218.9589 | 15.7616 | -13.81 | 1174.284 | 19.3412 | -110.1185 | -1.6479 | 0 | 113.3687 | 293.3687 | 106.2884 | 0 | 0 | 19.3244 | 19.3244 | -4.9081 | 0% | 8.7385 | 0 | 0 | 147.7016 | 147.7016 | 0% | 11.27% | 0% | 80% | 0% | 0 | 4.5626 | 4.5626 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5325 | 21 | 20.8 | 0 | 0 | 0 | 0 | 0 | 222 | 5325 | 1260 | 218.9589 | 15.7616 | -13.81 | 1234.284 | 20.3412 | -125.1185 | -10.44 | 0 | 113.3687 | 293.3687 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.338 | 0 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.7875 | 4.7875 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5326 | 22 | 19.6 | 0 | 0 | 0 | 0 | 0 | 222 | 5326 | 1320 | 218.9589 | 15.7616 | -13.81 | 1294.284 | 21.3412 | -140.1185 | -17.9277 | 0 | 113.3687 | 293.3687 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.6121 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0224 | 5.0224 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5327 | 23 | 18.8 | 0 | 0 | 0 | 0 | 0 | 222 | 5327 | 1380 | 218.9589 | 15.7616 | -13.81 | 1354.284 | 22.3412 | -155.1185 | -23.5757 | 0 | 113.3687 | 293.3687 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.3186 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
8 | 222 | 10 | 5328 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 222 | 5328 | 1440 | 218.9589 | 15.7616 | -13.81 | 1414.284 | 23.3412 | -170.1185 | -26.8309 | 0 | 113.3687 | 293.3687 | 106.2884 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5491 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5329 | 1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 223 | 5329 | 60 | 219.9452 | 15.4812 | -13.8788 | 34.284 | 0.34009 | 174.8987 | -27.5717 | 0 | 112.9399 | 67.0601 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7286 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5330 | 2 | 15.3 | 0 | 0 | 0 | 0 | 0 | 223 | 5330 | 120 | 219.9452 | 15.4812 | -13.8788 | 94.284 | 1.3401 | 159.8987 | -25.1678 | 0 | 112.9399 | 67.0601 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7447 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5331 | 3 | 14.9 | 0 | 0 | 0 | 0 | 0 | 223 | 5331 | 180 | 219.9452 | 15.4812 | -13.8788 | 154.284 | 2.3401 | 144.8987 | -20.2091 | 0 | 112.9399 | 67.0601 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7608 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5332 | 4 | 14.6 | 0 | 0 | 0 | 0 | 0 | 223 | 5332 | 240 | 219.9452 | 15.4812 | -13.8788 | 214.284 | 3.3401 | 129.8987 | -13.2279 | 0 | 112.9399 | 67.0601 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.218 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5333 | 5 | 14.9 | 0 | 0 | 0 | 0 | 0 | 223 | 5333 | 300 | 219.9452 | 15.4812 | -13.8788 | 274.284 | 4.3401 | 114.8987 | -4.7814 | 0 | 112.9399 | 67.0601 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.04 | 4.04 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5334 | 6 | 13.4 | 0 | 0 | 0 | 0 | 0 | 223 | 5334 | 360 | 219.9452 | 15.4812 | -13.8788 | 334.284 | 5.3401 | 99.8987 | 4.6491 | 4.6491 | 107.7294 | 72.2706 | 99.0507 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 12.4454 | 12.4454 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5335 | 7 | 15.6 | 18.06 | 23.61 | 41.67 | 23.61 | 11.81 | 223 | 5335 | 420 | 219.9452 | 15.4812 | -13.8788 | 394.284 | 6.3401 | 84.8987 | 14.6664 | 14.6664 | 97.1464 | 82.8536 | 84.6102 | 6.7001 | 6.7001 | 20.1524 | 26.8525 | -3.8351 | 0% | 12.1427 | 0 | 0 | 183.5219 | 183.5219 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5336 | 8 | 18.5 | 85.61 | 58.19 | 143.8 | 58.19 | 29.1 | 223 | 5336 | 480 | 219.9452 | 15.4812 | -13.8788 | 454.284 | 7.3401 | 69.8987 | 24.9186 | 24.9186 | 86.2978 | 93.7022 | 70.1637 | 68.9492 | 68.9492 | 49.6683 | 118.6174 | -0.19142 | 0% | 53.6388 | 0 | 0 | 201.2765 | 201.2765 | 0% | 11.41% | 11.41% | 80% | 9.127% | 4.8954 | 5.2467 | 5.2467 | 25.6845 | 10.8257 | 12.76% | 12.76%
8 | 223 | 11 | 5337 | 9 | 19.8 | 176.44 | 90.06 | 266.5 | 90.06 | 45.03 | 223 | 5337 | 540 | 219.9452 | 15.4812 | -13.8788 | 514.284 | 8.3401 | 54.8987 | 35.0305 | 35.0305 | 74.3404 | 105.6596 | 55.7936 | 172.8018 | 172.8018 | 76.871 | 249.6728 | 0.3426 | 34.26% | 112.9021 | 38.6807 | 27.0765 | 167.5326 | 167.5326 | 16.16% | 11.36% | 11.36% | 80% | 9.086% | 10.2588 | 4.9826 | 4.9826 | 51.1152 | 22.6864 | 30.51% | 30.51%
8 | 223 | 11 | 5338 | 10 | 22.1 | 279.31 | 141.89 | 421.2 | 141.89 | 70.95 | 223 | 5338 | 600 | 219.9452 | 15.4812 | -13.8788 | 574.284 | 9.3401 | 39.8987 | 44.4937 | 44.4937 | 60.0644 | 119.9356 | 41.6455 | 297.8182 | 297.8182 | 121.1107 | 418.9289 | 0.54103 | 54.1% | 189.4396 | 102.4929 | 71.745 | 174.4513 | 174.4513 | 41.13% | 11.31% | 11.31% | 85% | 9.612% | 18.2085 | 4.5443 | 4.5443 | 82.7453 | 40.2666 | 47.43% | 47.43%
8 | 223 | 11 | 5339 | 11 | 21.6 | 291.11 | 123.67 | 414.78 | 123.67 | 61.84 | 223 | 5339 | 660 | 219.9452 | 15.4812 | -13.8788 | 634.284 | 10.3401 | 24.8987 | 52.4804 | 52.4804 | 41.7748 | 138.2252 | 28.1148 | 323.7245 | 323.7245 | 105.5589 | 429.2834 | 0.54484 | 54.48% | 194.122 | 105.7654 | 74.0358 | 164.2864 | 164.2864 | 45.07% | 11.32% | 11.32% | 85% | 9.621% | 18.6774 | 4.6364 | 4.6364 | 86.5966 | 41.3034 | 52.71% | 52.71%
8 | 223 | 11 | 5340 | 12 | 24.3 | 331.11 | 130.56 | 461.67 | 130.56 | 65.28 | 223 | 5340 | 720 | 219.9452 | 15.4812 | -13.8788 | 694.284 | 11.3401 | 9.8987 | 57.6358 | 57.6358 | 18.0285 | 161.9715 | 16.8244 | 375.2234 | 375.2234 | 111.4399 | 486.6633 | 0.58739 | 58.74% | 220.0692 | 129.266 | 90.4862 | 179.9238 | 179.9238 | 50.29% | 11.28% | 11.28% | 85% | 9.586% | 21.0963 | 4.1598 | 4.1598 | 87.7554 | 46.6526 | 48.77% | 48.77%
8 | 223 | 11 | 5341 | 13 | 23.9 | 245.19 | 231.31 | 476.5 | 231.31 | 115.66 | 223 | 5341 | 780 | 219.9452 | 15.4812 | -13.8788 | 754.284 | 12.3401 | -5.1013 | 58.416 | 58.416 | 9.4165 | 189.4165 | 14.5974 | 278.5336 | 278.5336 | 197.4354 | 475.969 | 0.58072 | 58.07% | 215.2332 | 124.9897 | 87.4928 | 170.6738 | 170.6738 | 51.26% | 11.28% | 11.28% | 85% | 9.59% | 20.6411 | 4.2272 | 4.2272 | 87.2532 | 45.646 | 51.12% | 51.12%
8 | 223 | 11 | 5342 | 14 | 24.8 | 321.89 | 156.72 | 478.61 | 156.72 | 78.36 | 223 | 5342 | 840 | 219.9452 | 15.4812 | -13.8788 | 814.284 | 13.3401 | -20.1013 | 54.5168 | 54.5168 | 34.7919 | 214.7919 | 24.0963 | 360.8569 | 360.8569 | 133.7689 | 494.6258 | 0.59304 | 59.3% | 223.6698 | 132.6448 | 92.8513 | 185.1518 | 185.1518 | 50.15% | 11.27% | 11.27% | 85% | 9.581% | 21.4291 | 4.0771 | 4.0771 | 87.368 | 47.3885 | 47.19% | 47.19%
8 | 223 | 11 | 5343 | 15 | 25.5 | 144.31 | 257.64 | 401.95 | 257.64 | 128.82 | 223 | 5343 | 900 | 219.9452 | 15.4812 | -13.8788 | 874.284 | 14.3401 | -35.1013 | 47.2617 | 47.2617 | 54.7422 | 234.7422 | 37.2165 | 156.4712 | 156.4712 | 219.9095 | 376.3806 | 0.53073 | 53.07% | 170.1993 | 90.3294 | 63.2306 | 192.7806 | 192.7806 | 32.8% | 11.22% | 11.22% | 85% | 9.54% | 16.2375 | 3.9643 | 3.9643 | 64.3699 | 35.9078 | 33.39% | 33.39%
8 | 223 | 11 | 5344 | 16 | 25.1 | 166.89 | 217.83 | 384.72 | 217.83 | 108.92 | 223 | 5344 | 960 | 219.9452 | 15.4812 | -13.8788 | 934.284 | 15.3401 | -50.1013 | 38.1586 | 38.1586 | 70.0985 | 250.0985 | 51.2338 | 169.1331 | 169.1331 | 185.9295 | 355.0626 | 0.51192 | 51.19% | 160.5593 | 82.1935 | 57.5355 | 182.0522 | 182.0522 | 31.6% | 11.23% | 11.23% | 85% | 9.543% | 15.3224 | 4.0283 | 4.0283 | 61.7233 | 33.884 | 33.9% | 33.9%
8 | 223 | 11 | 5345 | 17 | 25.3 | 168.47 | 163.19 | 331.66 | 163.19 | 81.6 | 223 | 5345 | 1020 | 219.9452 | 15.4812 | -13.8788 | 994.284 | 16.3401 | -65.1013 | 28.1882 | 28.1882 | 82.6426 | 262.6426 | 65.5546 | 147.5908 | 147.5908 | 139.2914 | 286.8822 | 0.44399 | 44.4% | 129.7281 | 57.598 | 40.3186 | 180.6899 | 180.6899 | 22.31% | 11.2% | 11.2% | 80% | 8.962% | 11.6262 | 3.9962 | 3.9962 | 46.4599 | 25.7102 | 25.71% | 25.71%
8 | 223 | 11 | 5346 | 18 | 25 | 79.17 | 116.61 | 195.78 | 116.61 | 58.31 | 223 | 5346 | 1080 | 219.9452 | 15.4812 | -13.8788 | 1054.284 | 17.3401 | -80.1013 | 17.9365 | 17.9365 | 93.7407 | 273.7407 | 79.987 | 44.6984 | 44.6984 | 99.5329 | 144.2312 | 0.08349 | 8.349% | 65.2214 | 5.4454 | 3.8117 | 164.5073 | 164.5073 | 2.317% | 11.17% | 11.17% | 80% | 8.937% | 5.829 | 4.0445 | 4.0445 | 23.5756 | 12.8904 | 14.33% | 14.33%
8 | 223 | 11 | 5347 | 19 | 24.3 | 56.67 | 84.94 | 141.61 | 84.94 | 42.47 | 223 | 5347 | 1140 | 219.9452 | 15.4812 | -13.8788 | 1114.284 | 18.3401 | -95.1013 | 7.8063 | 7.8063 | 104.3315 | 284.3315 | 94.4373 | 0 | 0 | 72.5008 | 72.5008 | -0.65001 | 0% | 32.7849 | 0 | 0 | 186.8664 | 186.8664 | 0% | 11.18% | 0% | 80% | 0% | 0 | 4.1598 | 4.1598 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5348 | 20 | 23.3 | 3.67 | 18.75 | 22.42 | 18.75 | 9.38 | 223 | 5348 | 1200 | 219.9452 | 15.4812 | -13.8788 | 1174.284 | 19.3401 | -110.1013 | -1.8518 | 0 | 112.9399 | 292.9399 | 105.9981 | 0 | 0 | 16.0041 | 16.0041 | -5.9172 | 0% | 7.2371 | 0 | 0 | 154.6837 | 154.6837 | 0% | 11.21% | 0% | 80% | 0% | 0 | 4.3304 | 4.3304 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5349 | 21 | 22.4 | 0 | 0 | 0 | 0 | 0 | 223 | 5349 | 1260 | 219.9452 | 15.4812 | -13.8788 | 1234.284 | 20.3401 | -125.1013 | -10.6609 | 0 | 112.9399 | 292.9399 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.78319 | 0 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.4899 | 4.4899 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5350 | 22 | 22.1 | 0 | 0 | 0 | 0 | 0 | 223 | 5350 | 1320 | 219.9452 | 15.4812 | -13.8788 | 1294.284 | 21.3401 | -140.1013 | -18.1687 | 0 | 112.9399 | 292.9399 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.7555 | 0 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.5443 | 4.5443 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5351 | 23 | 22.3 | 0 | 0 | 0 | 0 | 0 | 223 | 5351 | 1380 | 219.9452 | 15.4812 | -13.8788 | 1354.284 | 22.3401 | -155.1013 | -23.8366 | 0 | 112.9399 | 292.9399 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.8572 | 0 | 0% | 11.25% | 0% | 80% | 0% | 0 | 4.508 | 4.508 | 0 | 0 | 0% | 0%
8 | 223 | 11 | 5352 | 24 | 21.6 | 0 | 0 | 0 | 0 | 0 | 223 | 5352 | 1440 | 219.9452 | 15.4812 | -13.8788 | 1414.284 | 23.3401 | -170.1013 | -27.1066 | 0 | 112.9399 | 292.9399 | 105.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.3305 | 0 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.6364 | 4.6364 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5353 | 1 | 19.2 | 0 | 0 | 0 | 0 | 0 | 224 | 5353 | 60 | 220.9315 | 15.1967 | -13.9354 | 34.284 | 0.33914 | 174.9129 | -27.8565 | 0 | 112.5055 | 67.4945 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.124 | 0 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5354 | 2 | 18.9 | 0 | 0 | 0 | 0 | 0 | 224 | 5354 | 120 | 220.9315 | 15.1967 | -13.9354 | 94.284 | 1.3391 | 159.9129 | -25.4461 | 0 | 112.5055 | 67.4945 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.0668 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5355 | 3 | 18.9 | 0 | 0 | 0 | 0 | 0 | 224 | 5355 | 180 | 220.9315 | 15.1967 | -13.9354 | 154.284 | 2.3391 | 144.9129 | -20.473 | 0 | 112.5055 | 67.4945 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.5525 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5356 | 4 | 18.1 | 0 | 0 | 0 | 0 | 0 | 224 | 5356 | 240 | 220.9315 | 15.1967 | -13.9354 | 214.284 | 3.3391 | 129.9129 | -13.4748 | 0 | 112.5055 | 67.4945 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.7717 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5357 | 5 | 17.9 | 0 | 0 | 0 | 0 | 0 | 224 | 5357 | 300 | 220.9315 | 15.1967 | -13.9354 | 274.284 | 4.3391 | 114.9129 | -5.0124 | 0 | 112.5055 | 67.4945 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.1653 | 7.1653 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5358 | 6 | 15.3 | 0 | 0 | 0 | 0 | 0 | 224 | 5358 | 360 | 220.9315 | 15.1967 | -13.9354 | 334.284 | 5.3391 | 99.9129 | 4.4304 | 4.4304 | 107.5463 | 72.4537 | 99.086 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 13.6051 | 13.6051 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5359 | 7 | 15.5 | 17.64 | 23.19 | 40.83 | 23.19 | 11.6 | 224 | 5359 | 420 | 220.9315 | 15.1967 | -13.9354 | 394.284 | 6.3391 | 84.9129 | 14.4549 | 14.4549 | 96.9493 | 83.0507 | 84.6257 | 6.6189 | 6.6189 | 19.7939 | 26.4128 | -3.9209 | 0% | 11.9439 | 0 | 0 | 180.781 | 180.781 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5360 | 8 | 15.8 | 96.25 | 64.86 | 161.11 | 64.86 | 32.43 | 224 | 5360 | 480 | 220.9315 | 15.1967 | -13.9354 | 454.284 | 7.3391 | 69.9129 | 24.7082 | 24.7082 | 86.0862 | 93.9138 | 70.1589 | 78.155 | 78.155 | 55.3615 | 133.5164 | -0.12562 | 0% | 60.3761 | 0 | 0 | 153.5759 | 153.5759 | 0% | 11.51% | 11.51% | 80% | 9.205% | 5.5575 | 5.833 | 5.833 | 32.4167 | 12.2899 | 21.11% | 21.11%
8 | 224 | 12 | 5361 | 9 | 16.4 | 152.44 | 121.39 | 273.83 | 121.39 | 60.7 | 224 | 5361 | 540 | 220.9315 | 15.1967 | -13.9354 | 514.284 | 8.3391 | 54.9129 | 34.8134 | 34.8134 | 74.1154 | 105.8846 | 55.7651 | 150.2188 | 150.2188 | 103.6128 | 253.8317 | 0.32034 | 32.03% | 114.7827 | 36.7696 | 25.7387 | 160.2362 | 160.2362 | 16.06% | 11.46% | 11.46% | 80% | 9.168% | 10.5234 | 5.6983 | 5.6983 | 59.9653 | 23.2716 | 37.42% | 37.42%
8 | 224 | 12 | 5362 | 10 | 18 | 248.56 | 170.22 | 418.78 | 170.22 | 85.11 | 224 | 5362 | 600 | 220.9315 | 15.1967 | -13.9354 | 574.284 | 9.3391 | 39.9129 | 44.2609 | 44.2609 | 59.8347 | 120.1653 | 41.5846 | 266.3849 | 266.3849 | 145.2919 | 411.6767 | 0.51449 | 51.45% | 186.1602 | 95.7768 | 67.0437 | 166.5775 | 166.5775 | 40.25% | 11.39% | 11.39% | 85% | 9.686% | 18.0306 | 5.3514 | 5.3514 | 96.4888 | 39.873 | 57.92% | 57.92%
8 | 224 | 12 | 5363 | 11 | 20.7 | 312.36 | 204.94 | 517.3 | 204.94 | 102.47 | 224 | 5363 | 660 | 220.9315 | 15.1967 | -13.9354 | 634.284 | 10.3391 | 24.9129 | 52.2231 | 52.2231 | 41.5745 | 138.4255 | 28.0001 | 348.9328 | 348.9328 | 174.9272 | 523.86 | 0.58787 | 58.79% | 236.8895 | 139.261 | 97.4827 | 166.9856 | 166.9856 | 58.38% | 11.34% | 11.34% | 90% | 10.21% | 24.1799 | 4.8067 | 4.8067 | 116.2247 | 53.4716 | 69.6% | 69.6%
8 | 224 | 12 | 5364 | 12 | 23.3 | 374.94 | 251.72 | 626.66 | 251.72 | 125.86 | 224 | 5364 | 720 | 220.9315 | 15.1967 | -13.9354 | 694.284 | 11.3391 | 9.9129 | 57.3552 | 57.3552 | 17.9372 | 162.0628 | 16.6045 | 426.7123 | 426.7123 | 214.8565 | 641.5687 | 0.63634 | 63.63% | 290.1174 | 184.6125 | 129.2288 | 169.052 | 169.052 | 76.44% | 11.32% | 11.32% | 90% | 10.19% | 29.5656 | 4.3304 | 4.3304 | 128.0297 | 65.3818 | 75.73% | 75.73%
8 | 224 | 12 | 5365 | 13 | 25.3 | 428.28 | 255.28 | 683.56 | 255.28 | 127.64 | 224 | 5365 | 780 | 220.9315 | 15.1967 | -13.9354 | 754.284 | 12.3391 | -5.0871 | 58.135 | 58.135 | 9.3282 | 189.3282 | 14.3266 | 488.5949 | 488.5949 | 217.8951 | 706.49 | 0.65781 | 65.78% | 319.4748 | 210.1543 | 147.108 | 276.6015 | 276.6015 | 53.18% | 11.32% | 11.32% | 90% | 10.19% | 32.5617 | 3.9962 | 3.9962 | 130.1217 | 72.0073 | 47.04% | 47.04%
8 | 224 | 12 | 5366 | 14 | 24.3 | 415.5 | 243.47 | 658.97 | 243.47 | 121.74 | 224 | 5366 | 840 | 220.9315 | 15.1967 | -13.9354 | 814.284 | 13.3391 | -20.0871 | 54.2621 | 54.2621 | 34.5731 | 214.5731 | 23.9321 | 467.8817 | 467.8817 | 207.8146 | 675.6963 | 0.64799 | 64.8% | 305.5499 | 197.9925 | 138.5947 | 279.513 | 279.513 | 49.58% | 11.32% | 11.32% | 90% | 10.19% | 31.1366 | 4.1598 | 4.1598 | 129.5205 | 68.8558 | 46.34% | 46.34%
8 | 224 | 12 | 5367 | 15 | 25.4 | 422 | 222.17 | 644.17 | 222.17 | 111.09 | 224 | 5367 | 900 | 220.9315 | 15.1967 | -13.9354 | 874.284 | 14.3391 | -35.0871 | 47.0376 | 47.0376 | 54.4837 | 234.4837 | 37.1158 | 459.8382 | 459.8382 | 189.634 | 649.4722 | 0.64531 | 64.53% | 293.6913 | 189.5207 | 132.6645 | 285.9441 | 285.9441 | 46.4% | 11.31% | 11.31% | 90% | 10.18% | 29.8877 | 3.9802 | 3.9802 | 118.9584 | 66.094 | 41.6% | 41.6%
8 | 224 | 12 | 5368 | 16 | 24.3 | 387 | 162.56 | 549.56 | 162.56 | 81.28 | 224 | 5368 | 960 | 220.9315 | 15.1967 | -13.9354 | 934.284 | 15.3391 | -50.0871 | 37.9557 | 37.9557 | 69.8445 | 249.8445 | 51.1694 | 394.5303 | 394.5303 | 138.7536 | 533.2839 | 0.60632 | 60.63% | 241.151 | 146.2158 | 102.3511 | 251.5078 | 251.5078 | 40.69% | 11.29% | 11.29% | 90% | 10.16% | 24.501 | 4.1598 | 4.1598 | 101.9182 | 54.1818 | 40.52% | 40.52%
8 | 224 | 12 | 5369 | 17 | 24.1 | 286.44 | 134.17 | 420.61 | 134.17 | 67.09 | 224 | 5369 | 1020 | 220.9315 | 15.1967 | -13.9354 | 994.284 | 16.3391 | -65.0871 | 27.9958 | 27.9958 | 82.4046 | 262.4046 | 65.5155 | 252.9027 | 252.9027 | 114.5213 | 367.424 | 0.51592 | 51.59% | 166.1491 | 85.7203 | 60.0042 | 259.7951 | 259.7951 | 23.1% | 11.25% | 11.25% | 85% | 9.566% | 15.8943 | 4.1933 | 4.1933 | 66.6498 | 35.1488 | 25.65% | 25.65%
8 | 224 | 12 | 5370 | 18 | 23.9 | 171.72 | 79.39 | 251.11 | 79.39 | 39.7 | 224 | 5370 | 1080 | 220.9315 | 15.1967 | -13.9354 | 1054.284 | 17.3391 | -80.0871 | 17.7454 | 17.7454 | 93.5188 | 273.5188 | 79.9689 | 98.1363 | 98.1363 | 67.7636 | 165.8999 | 0.1634 | 16.34% | 75.0199 | 12.2582 | 8.5808 | 231.6948 | 231.6948 | 3.703% | 11.22% | 11.22% | 80% | 8.973% | 6.7314 | 4.2272 | 4.2272 | 28.4546 | 14.8858 | 12.28% | 12.28%
8 | 224 | 12 | 5371 | 19 | 22.3 | 64.11 | 65.97 | 130.08 | 65.97 | 32.99 | 224 | 5371 | 1140 | 220.9315 | 15.1967 | -13.9354 | 1114.284 | 18.3391 | -95.0871 | 7.6093 | 7.6093 | 104.1239 | 284.1239 | 94.4389 | 0 | 0 | 56.3089 | 56.3089 | -1.1447 | 0% | 25.4629 | 0 | 0 | 161.9766 | 161.9766 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.508 | 4.508 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5372 | 20 | 19.8 | 8.39 | 27.83 | 36.22 | 27.83 | 13.92 | 224 | 5372 | 1200 | 220.9315 | 15.1967 | -13.9354 | 1174.284 | 19.3391 | -110.0871 | -2.0608 | 0 | 112.5055 | 292.5055 | 105.7036 | 0 | 0 | 23.7544 | 23.7544 | -4.0455 | 0% | 10.7417 | 0 | 0 | 145.1804 | 145.1804 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9826 | 4.9826 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5373 | 21 | 18.3 | 0 | 0 | 0 | 0 | 0 | 224 | 5373 | 1260 | 220.9315 | 15.1967 | -13.9354 | 1234.284 | 20.3391 | -125.0871 | -10.8869 | 0 | 112.5055 | 292.5055 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.3217 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5374 | 22 | 17.2 | 0 | 0 | 0 | 0 | 0 | 224 | 5374 | 1320 | 220.9315 | 15.1967 | -13.9354 | 1294.284 | 21.3391 | -140.0871 | -18.4146 | 0 | 112.5055 | 292.5055 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.715 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5375 | 23 | 16.4 | 0 | 0 | 0 | 0 | 0 | 224 | 5375 | 1380 | 220.9315 | 15.1967 | -13.9354 | 1354.284 | 22.3391 | -155.0871 | -24.1023 | 0 | 112.5055 | 292.5055 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4198 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
8 | 224 | 12 | 5376 | 24 | 16.9 | 0 | 0 | 0 | 0 | 0 | 224 | 5376 | 1440 | 220.9315 | 15.1967 | -13.9354 | 1414.284 | 23.3391 | -170.0871 | -27.3868 | 0 | 112.5055 | 292.5055 | 105.7036 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1435 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5377 | 1 | 17.1 | 0 | 0 | 0 | 0 | 0 | 225 | 5377 | 60 | 221.9178 | 14.9081 | -13.9797 | 34.284 | 0.33841 | 174.9239 | -28.1452 | 0 | 112.0657 | 67.9343 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.3702 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5378 | 2 | 17.3 | 0 | 0 | 0 | 0 | 0 | 225 | 5378 | 120 | 221.9178 | 14.9081 | -13.9797 | 94.284 | 1.3384 | 159.9239 | -25.7275 | 0 | 112.0657 | 67.9343 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.2635 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5379 | 3 | 17.4 | 0 | 0 | 0 | 0 | 0 | 225 | 5379 | 180 | 221.9178 | 14.9081 | -13.9797 | 154.284 | 2.3384 | 144.9239 | -20.7394 | 0 | 112.0657 | 67.9343 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.3093 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5380 | 4 | 17.1 | 0 | 0 | 0 | 0 | 0 | 225 | 5380 | 240 | 221.9178 | 14.9081 | -13.9797 | 214.284 | 3.3384 | 129.9239 | -13.7234 | 0 | 112.0657 | 67.9343 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7665 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5381 | 5 | 16.2 | 0 | 0 | 0 | 0 | 0 | 225 | 5381 | 300 | 221.9178 | 14.9081 | -13.9797 | 274.284 | 4.3384 | 114.9239 | -5.2447 | 0 | 112.0657 | 67.9343 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 13.4972 | 13.4972 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5382 | 6 | 15.6 | 0 | 0 | 0 | 0 | 0 | 225 | 5382 | 360 | 221.9178 | 14.9081 | -13.9797 | 334.284 | 5.3384 | 99.9239 | 4.2106 | 4.2106 | 107.3584 | 72.6416 | 99.1185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 26.4362 | 26.4362 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5383 | 7 | 15.9 | 25.69 | 28.39 | 54.08 | 28.39 | 14.2 | 225 | 5383 | 420 | 221.9178 | 14.9081 | -13.9797 | 394.284 | 6.3384 | 84.9239 | 14.2425 | 14.2425 | 96.7473 | 83.2527 | 84.6384 | 9.7571 | 9.7571 | 24.2324 | 33.9895 | -2.8411 | 0% | 15.3701 | 0 | 0 | 202.6047 | 202.6047 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5384 | 8 | 16.2 | 137.08 | 62.22 | 199.3 | 62.22 | 31.11 | 225 | 5384 | 480 | 221.9178 | 14.9081 | -13.9797 | 454.284 | 7.3384 | 69.9239 | 24.4966 | 24.4966 | 85.87 | 94.13 | 70.1514 | 112.2507 | 112.2507 | 53.1081 | 165.3588 | 0.058844 | 5.884% | 74.7753 | 4.4001 | 3.0801 | 179.0839 | 179.0839 | 1.72% | 11.48% | 11.48% | 80% | 9.188% | 6.8701 | 5.7429 | 5.7429 | 39.4545 | 15.1927 | 22.03% | 22.03%
8 | 225 | 13 | 5385 | 9 | 16.5 | 277.22 | 88.47 | 365.69 | 88.47 | 44.24 | 225 | 5385 | 540 | 221.9178 | 14.9081 | -13.9797 | 514.284 | 8.3384 | 54.9239 | 34.595 | 34.595 | 73.8856 | 106.1144 | 55.734 | 274.9075 | 274.9075 | 75.5139 | 350.4214 | 0.4543 | 45.43% | 158.4605 | 71.9883 | 50.3918 | 187.7589 | 187.7589 | 26.84% | 11.44% | 11.44% | 85% | 9.723% | 15.4067 | 5.6761 | 5.6761 | 87.4498 | 34.0706 | 46.58% | 46.58%
8 | 225 | 13 | 5386 | 10 | 18.5 | 385.06 | 105.97 | 491.03 | 105.97 | 52.99 | 225 | 5386 | 600 | 221.9178 | 14.9081 | -13.9797 | 574.284 | 9.3384 | 39.9239 | 44.0262 | 44.0262 | 59.6002 | 120.3998 | 41.5213 | 414.8248 | 414.8248 | 90.4511 | 505.2758 | 0.57032 | 57.03% | 228.4857 | 130.3094 | 91.2166 | 191.0633 | 191.0633 | 47.74% | 11.38% | 11.38% | 90% | 10.24% | 23.3939 | 5.2467 | 5.2467 | 122.7404 | 51.7336 | 64.24% | 64.24%
8 | 225 | 13 | 5387 | 11 | 19.1 | 501.89 | 146.94 | 648.83 | 146.94 | 73.47 | 225 | 5387 | 660 | 221.9178 | 14.9081 | -13.9797 | 634.284 | 10.3384 | 24.9239 | 51.9633 | 51.9633 | 41.3692 | 138.6308 | 27.8831 | 563.2466 | 563.2466 | 125.4211 | 688.6677 | 0.63448 | 63.45% | 311.4155 | 197.5865 | 138.3106 | 186.6602 | 186.6602 | 74.1% | 11.36% | 11.36% | 90% | 10.22% | 31.8321 | 5.1233 | 5.1233 | 163.0861 | 70.394 | 87.37% | 87.37%
8 | 225 | 13 | 5388 | 12 | 18.4 | 412.72 | 187.5 | 600.22 | 187.5 | 93.75 | 225 | 5388 | 720 | 221.9178 | 14.9081 | -13.9797 | 694.284 | 11.3384 | 9.9239 | 57.0712 | 57.0712 | 17.8404 | 162.1596 | 16.3815 | 471.7545 | 471.7545 | 160.0413 | 631.7957 | 0.61676 | 61.68% | 285.698 | 176.2076 | 123.3454 | 166.2844 | 166.2844 | 74.18% | 11.37% | 11.37% | 90% | 10.23% | 29.2273 | 5.2675 | 5.2675 | 153.954 | 64.6335 | 92.58% | 92.58%
8 | 225 | 13 | 5389 | 13 | 19.1 | 508 | 154.39 | 662.39 | 154.39 | 77.2 | 225 | 5389 | 780 | 221.9178 | 14.9081 | -13.9797 | 754.284 | 12.3384 | -5.0761 | 57.8495 | 57.8495 | 9.2458 | 189.2458 | 14.0536 | 582.0505 | 582.0505 | 131.7801 | 713.8306 | 0.64045 | 64.05% | 322.7942 | 206.735 | 144.7145 | 165.2933 | 165.2933 | 87.55% | 11.36% | 11.36% | 90% | 10.22% | 32.9916 | 5.1233 | 5.1233 | 169.0265 | 72.958 | 102.3% | 102.3%
8 | 225 | 13 | 5390 | 14 | 20.2 | 452.31 | 165 | 617.31 | 165 | 82.5 | 225 | 5390 | 840 | 221.9178 | 14.9081 | -13.9797 | 814.284 | 13.3384 | -20.0761 | 54.002 | 54.002 | 34.3587 | 214.3587 | 23.7704 | 511.6445 | 511.6445 | 140.8363 | 652.4808 | 0.6288 | 62.88% | 295.0518 | 185.5273 | 129.8691 | 162.8272 | 162.8272 | 79.76% | 11.35% | 11.35% | 90% | 10.22% | 30.1405 | 4.9037 | 4.9037 | 147.8002 | 66.6531 | 90.77% | 90.77%
8 | 225 | 13 | 5391 | 15 | 19.3 | 474.86 | 151.94 | 626.8 | 151.94 | 75.97 | 225 | 5391 | 900 | 221.9178 | 14.9081 | -13.9797 | 874.284 | 14.3384 | -35.0761 | 46.8079 | 46.8079 | 54.2273 | 234.2273 | 37.0182 | 520.0496 | 520.0496 | 129.6889 | 649.7385 | 0.625 | 62.5% | 293.8118 | 183.6331 | 128.5432 | 158.4854 | 158.4854 | 81.11% | 11.36% | 11.36% | 90% | 10.22% | 30.0335 | 5.0828 | 5.0828 | 152.6527 | 66.4163 | 96.32% | 96.32%
8 | 225 | 13 | 5392 | 16 | 18.9 | 422.64 | 140.69 | 563.33 | 140.69 | 70.35 | 225 | 5392 | 960 | 221.9178 | 14.9081 | -13.9797 | 934.284 | 15.3384 | -50.0761 | 37.7474 | 37.7474 | 69.5912 | 249.5912 | 51.1082 | 433.4589 | 433.4589 | 120.0864 | 553.5453 | 0.5923 | 59.23% | 250.3132 | 148.26 | 103.782 | 152.6826 | 152.6826 | 67.97% | 11.37% | 11.37% | 90% | 10.23% | 25.6076 | 5.1642 | 5.1642 | 132.2415 | 56.6289 | 86.61% | 86.61%
8 | 225 | 13 | 5393 | 17 | 19.1 | 198.61 | 158.28 | 356.89 | 158.28 | 79.14 | 225 | 5393 | 1020 | 221.9178 | 14.9081 | -13.9797 | 994.284 | 16.3384 | -65.0761 | 27.7979 | 27.7979 | 82.1665 | 262.1665 | 65.4797 | 176.7458 | 176.7458 | 135.1004 | 311.8463 | 0.42964 | 42.96% | 141.0169 | 60.586 | 42.4102 | 140.0829 | 140.0829 | 30.28% | 11.38% | 11.38% | 85% | 9.67% | 13.636 | 5.1233 | 5.1233 | 69.8613 | 30.1547 | 49.87% | 49.87%
8 | 225 | 13 | 5394 | 18 | 20.5 | 106.72 | 109.58 | 216.3 | 109.58 | 54.79 | 225 | 5394 | 1080 | 221.9178 | 14.9081 | -13.9797 | 1054.284 | 17.3384 | -80.0761 | 17.5491 | 17.5491 | 93.2965 | 273.2965 | 79.9538 | 61.7411 | 61.7411 | 93.5324 | 155.2734 | 0.07201 | 7.201% | 70.2146 | 5.0561 | 3.5393 | 130.045 | 130.045 | 2.722% | 11.33% | 11.33% | 80% | 9.067% | 6.3667 | 4.8453 | 4.8453 | 30.8482 | 14.0793 | 23.72% | 23.72%
8 | 225 | 13 | 5395 | 19 | 18.8 | 74.44 | 63.11 | 137.55 | 63.11 | 31.56 | 225 | 5395 | 1140 | 221.9178 | 14.9081 | -13.9797 | 1114.284 | 18.3384 | -95.0761 | 7.4072 | 7.4072 | 103.9158 | 283.9158 | 94.4435 | 0 | 0 | 53.8678 | 53.8678 | -1.3756 | 0% | 24.359 | 0 | 0 | 160.7083 | 160.7083 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1847 | 5.1847 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5396 | 20 | 16.5 | 4.39 | 22.17 | 26.56 | 22.17 | 11.09 | 225 | 5396 | 1200 | 221.9178 | 14.9081 | -13.9797 | 1174.284 | 19.3384 | -110.0761 | -2.2748 | 0 | 112.0657 | 292.0657 | 105.4049 | 0 | 0 | 18.9233 | 18.9233 | -5.6718 | 0% | 8.5571 | 0 | 0 | 141.8752 | 141.8752 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5397 | 21 | 15.7 | 0 | 0 | 0 | 0 | 0 | 225 | 5397 | 1260 | 221.9178 | 14.9081 | -13.9797 | 1234.284 | 20.3384 | -125.0761 | -11.1177 | 0 | 112.0657 | 292.0657 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.9989 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5398 | 22 | 15.2 | 0 | 0 | 0 | 0 | 0 | 225 | 5398 | 1320 | 221.9178 | 14.9081 | -13.9797 | 1294.284 | 21.3384 | -140.0761 | -18.6654 | 0 | 112.0657 | 292.0657 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6712 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5399 | 23 | 14.6 | 0 | 0 | 0 | 0 | 0 | 225 | 5399 | 1380 | 221.9178 | 14.9081 | -13.9797 | 1354.284 | 22.3384 | -155.0761 | -24.3727 | 0 | 112.0657 | 292.0657 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7838 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
8 | 225 | 13 | 5400 | 24 | 14.3 | 0 | 0 | 0 | 0 | 0 | 225 | 5400 | 1440 | 221.9178 | 14.9081 | -13.9797 | 1414.284 | 23.3384 | -170.0761 | -27.6714 | 0 | 112.0657 | 292.0657 | 105.4049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4391 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5401 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 226 | 5401 | 60 | 222.9041 | 14.6154 | -14.0117 | 34.284 | 0.33787 | 174.9319 | -28.4377 | 0 | 111.6205 | 68.3795 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6694 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5402 | 2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 226 | 5402 | 120 | 222.9041 | 14.6154 | -14.0117 | 94.284 | 1.3379 | 159.9319 | -26.012 | 0 | 111.6205 | 68.3795 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6581 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5403 | 3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 226 | 5403 | 180 | 222.9041 | 14.6154 | -14.0117 | 154.284 | 2.3379 | 144.9319 | -21.008 | 0 | 111.6205 | 68.3795 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6468 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5404 | 4 | 12.9 | 0 | 0 | 0 | 0 | 0 | 226 | 5404 | 240 | 222.9041 | 14.6154 | -14.0117 | 214.284 | 3.3379 | 129.9319 | -13.9737 | 0 | 111.6205 | 68.3795 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.104 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5405 | 5 | 13.1 | 0 | 0 | 0 | 0 | 0 | 226 | 5405 | 300 | 222.9041 | 14.6154 | -14.0117 | 274.284 | 4.3379 | 114.9319 | -5.4782 | 0 | 111.6205 | 68.3795 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.0092 | 5.0092 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5406 | 6 | 13.4 | 0 | 0 | 0 | 0 | 0 | 226 | 5406 | 360 | 222.9041 | 14.6154 | -14.0117 | 334.284 | 5.3379 | 99.9319 | 3.9898 | 3.9898 | 107.1657 | 72.8343 | 99.1481 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 16.7753 | 16.7753 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5407 | 7 | 13.4 | 15.33 | 23.75 | 39.08 | 23.75 | 11.88 | 226 | 5407 | 420 | 222.9041 | 14.6154 | -14.0117 | 394.284 | 6.3379 | 84.9319 | 14.029 | 14.029 | 96.5407 | 83.4593 | 84.6483 | 5.8982 | 5.8982 | 20.2719 | 26.1701 | -4.1473 | 0% | 11.8341 | 0 | 0 | 185.9177 | 185.9177 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5408 | 8 | 13.7 | 80.83 | 58.94 | 139.77 | 58.94 | 29.47 | 226 | 5408 | 480 | 222.9041 | 14.6154 | -14.0117 | 454.284 | 7.3379 | 69.9319 | 24.284 | 24.284 | 85.6491 | 94.3509 | 70.1413 | 66.766 | 66.766 | 50.3084 | 117.0744 | -0.29692 | 0% | 52.9411 | 0 | 0 | 200.2512 | 200.2512 | 0% | 11.59% | 11.59% | 80% | 9.271% | 4.9081 | 6.3243 | 6 | 29.4487 | 10.8539 | 14.71% | 14.71%
8 | 226 | 14 | 5409 | 9 | 13.9 | 199.94 | 99.58 | 299.52 | 99.58 | 49.79 | 226 | 5409 | 540 | 222.9041 | 14.6154 | -14.0117 | 514.284 | 8.3379 | 54.9319 | 34.3751 | 34.3751 | 73.6511 | 106.3489 | 55.7005 | 199.5541 | 199.5541 | 84.9968 | 284.5509 | 0.35265 | 35.26% | 128.6739 | 45.3765 | 31.7635 | 166.8832 | 166.8832 | 19.03% | 11.52% | 11.52% | 80% | 9.22% | 11.8637 | 6.2762 | 6 | 71.182 | 26.2354 | 42.65% | 42.65%
8 | 226 | 14 | 5410 | 10 | 14.8 | 213 | 162.83 | 375.83 | 162.83 | 81.42 | 226 | 5410 | 600 | 222.9041 | 14.6154 | -14.0117 | 574.284 | 9.3379 | 39.9319 | 43.7896 | 43.7896 | 59.3609 | 120.6391 | 41.4558 | 230.6844 | 230.6844 | 138.9841 | 369.6685 | 0.46212 | 46.21% | 167.1641 | 77.2491 | 54.0744 | 167.8722 | 167.8722 | 32.21% | 11.48% | 11.48% | 85% | 9.754% | 16.3049 | 6.0631 | 6 | 97.8292 | 36.0568 | 58.28% | 58.28%
8 | 226 | 14 | 5411 | 11 | 15.8 | 185.78 | 219.22 | 405 | 219.22 | 109.61 | 226 | 5411 | 660 | 222.9041 | 14.6154 | -14.0117 | 634.284 | 10.3379 | 24.9319 | 51.7009 | 51.7009 | 41.1591 | 138.8409 | 27.7641 | 209.4731 | 209.4731 | 187.116 | 396.5891 | 0.49103 | 49.1% | 179.3376 | 88.0604 | 61.6423 | 161.5087 | 161.5087 | 38.17% | 11.45% | 11.45% | 85% | 9.728% | 17.4467 | 5.833 | 5.833 | 101.7662 | 38.5818 | 63.01% | 63.01%
8 | 226 | 14 | 5412 | 12 | 18.4 | 236.94 | 221.17 | 458.11 | 221.17 | 110.59 | 226 | 5412 | 720 | 222.9041 | 14.6154 | -14.0117 | 694.284 | 11.3379 | 9.9319 | 56.7838 | 56.7838 | 17.7382 | 162.2618 | 16.1556 | 272.0303 | 272.0303 | 188.7804 | 460.8107 | 0.54729 | 54.73% | 208.3786 | 114.0428 | 79.83 | 154.4391 | 154.4391 | 51.69% | 11.38% | 11.38% | 85% | 9.675% | 20.1597 | 5.2675 | 5.2675 | 106.191 | 44.5815 | 68.76% | 68.76%
8 | 226 | 14 | 5413 | 13 | 19.9 | 430.33 | 219.67 | 650 | 219.67 | 109.84 | 226 | 5413 | 780 | 222.9041 | 14.6154 | -14.0117 | 754.284 | 12.3379 | -5.0681 | 57.5596 | 57.5596 | 9.1694 | 189.1694 | 13.7786 | 495.2265 | 495.2265 | 187.5001 | 682.7266 | 0.63559 | 63.56% | 308.729 | 196.2252 | 137.3576 | 161.412 | 161.412 | 85.1% | 11.35% | 11.35% | 90% | 10.22% | 31.544 | 4.9628 | 4.9628 | 156.5452 | 69.7568 | 96.98% | 96.98%
8 | 226 | 14 | 5414 | 14 | 20.4 | 403.11 | 226.81 | 629.92 | 226.81 | 113.41 | 226 | 5414 | 840 | 222.9041 | 14.6154 | -14.0117 | 814.284 | 13.3379 | -20.0681 | 53.7367 | 53.7367 | 34.1488 | 214.1488 | 23.6114 | 458.0918 | 458.0918 | 193.5944 | 651.6863 | 0.62926 | 62.93% | 294.6925 | 185.4371 | 129.806 | 159.6755 | 159.6755 | 81.29% | 11.35% | 11.35% | 90% | 10.21% | 30.0995 | 4.8647 | 4.8647 | 146.4244 | 66.5623 | 91.7% | 91.7%
8 | 226 | 14 | 5415 | 15 | 21 | 378.61 | 149.86 | 528.47 | 149.86 | 74.93 | 226 | 5415 | 900 | 222.9041 | 14.6154 | -14.0117 | 874.284 | 14.3379 | -35.0681 | 46.5727 | 46.5727 | 53.9733 | 233.9733 | 36.924 | 416.7637 | 416.7637 | 127.9135 | 544.6772 | 0.59734 | 59.73% | 246.303 | 147.1266 | 102.9886 | 153.2804 | 153.2804 | 67.19% | 11.34% | 11.34% | 90% | 10.2% | 25.1332 | 4.7493 | 4.7493 | 119.3649 | 55.5797 | 77.87% | 77.87%
8 | 226 | 14 | 5416 | 16 | 21 | 347.64 | 127.92 | 475.56 | 127.92 | 63.96 | 226 | 5416 | 960 | 222.9041 | 14.6154 | -14.0117 | 934.284 | 15.3379 | -50.0681 | 37.5335 | 37.5335 | 69.3388 | 249.3388 | 51.0504 | 358.7171 | 358.7171 | 109.1865 | 467.9036 | 0.56343 | 56.34% | 211.586 | 119.2141 | 83.4499 | 149.0167 | 149.0167 | 56% | 11.33% | 11.33% | 85% | 9.634% | 20.3835 | 4.7493 | 4.7493 | 96.8074 | 45.0763 | 64.96% | 64.96%
8 | 226 | 14 | 5417 | 17 | 18.5 | 231.33 | 139.5 | 370.83 | 139.5 | 69.75 | 226 | 5417 | 1020 | 222.9041 | 14.6154 | -14.0117 | 994.284 | 16.3379 | -65.0681 | 27.5948 | 27.5948 | 81.9284 | 261.9284 | 65.4471 | 207.5176 | 207.5176 | 119.0707 | 326.5883 | 0.44246 | 44.25% | 147.6832 | 65.3442 | 45.7409 | 137.7367 | 137.7367 | 33.21% | 11.39% | 11.39% | 85% | 9.682% | 14.2993 | 5.2467 | 5.2467 | 75.0237 | 31.6216 | 54.47% | 54.47%
8 | 226 | 14 | 5418 | 18 | 17.3 | 139.39 | 109.17 | 248.56 | 109.17 | 54.59 | 226 | 5418 | 1080 | 222.9041 | 14.6154 | -14.0117 | 1054.284 | 17.3379 | -80.0681 | 17.3477 | 17.3477 | 93.0738 | 273.0738 | 79.942 | 81.6443 | 81.6443 | 93.1824 | 174.8268 | 0.11332 | 11.33% | 79.0567 | 8.9588 | 6.2712 | 125.6928 | 125.6928 | 4.989% | 11.44% | 11.44% | 80% | 9.156% | 7.2383 | 5.501 | 5.501 | 39.8177 | 16.0069 | 31.68% | 31.68%
8 | 226 | 14 | 5419 | 19 | 17.2 | 71.94 | 64.5 | 136.44 | 64.5 | 32.25 | 226 | 5419 | 1140 | 222.9041 | 14.6154 | -14.0117 | 1114.284 | 18.3379 | -95.0681 | 7.2001 | 7.2001 | 103.7072 | 283.7072 | 94.4512 | 0 | 0 | 55.0542 | 55.0542 | -1.3933 | 0% | 24.8955 | 0 | 0 | 157.4912 | 157.4912 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5420 | 20 | 16.9 | 9.39 | 21.06 | 30.45 | 21.06 | 10.53 | 226 | 5420 | 1200 | 222.9041 | 14.6154 | -14.0117 | 1174.284 | 19.3379 | -110.0681 | -2.4938 | 0 | 111.6205 | 291.6205 | 105.102 | 0 | 0 | 17.9758 | 17.9758 | -5.9631 | 0% | 8.1287 | 0 | 0 | 143.5656 | 143.5656 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5421 | 21 | 16.3 | 0 | 0 | 0 | 0 | 0 | 226 | 5421 | 1260 | 222.9041 | 14.6154 | -14.0117 | 1234.284 | 20.3379 | -125.0681 | -11.3534 | 0 | 111.6205 | 291.6205 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.3612 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5422 | 22 | 15.6 | 0 | 0 | 0 | 0 | 0 | 226 | 5422 | 1320 | 222.9041 | 14.6154 | -14.0117 | 1294.284 | 21.3379 | -140.0681 | -18.921 | 0 | 111.6205 | 291.6205 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0937 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5423 | 23 | 15.7 | 0 | 0 | 0 | 0 | 0 | 226 | 5423 | 1380 | 222.9041 | 14.6154 | -14.0117 | 1354.284 | 22.3379 | -155.0681 | -24.6478 | 0 | 111.6205 | 291.6205 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3204 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
8 | 226 | 14 | 5424 | 24 | 15.9 | 0 | 0 | 0 | 0 | 0 | 226 | 5424 | 1440 | 222.9041 | 14.6154 | -14.0117 | 1414.284 | 23.3379 | -170.0681 | -27.9604 | 0 | 111.6205 | 291.6205 | 105.102 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3947 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5425 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 227 | 5425 | 60 | 223.8904 | 14.3188 | -14.0315 | 34.284 | 0.33754 | 174.9369 | -28.7339 | 0 | 111.1701 | 68.8299 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1463 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5426 | 2 | 16.3 | 0 | 0 | 0 | 0 | 0 | 227 | 5426 | 120 | 223.8904 | 14.3188 | -14.0315 | 94.284 | 1.3375 | 159.9369 | -26.2995 | 0 | 111.1701 | 68.8299 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9451 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5427 | 3 | 15.9 | 0 | 0 | 0 | 0 | 0 | 227 | 5427 | 180 | 223.8904 | 14.3188 | -14.0315 | 154.284 | 2.3375 | 144.9369 | -21.279 | 0 | 111.1701 | 68.8299 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.8106 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5428 | 4 | 16.1 | 0 | 0 | 0 | 0 | 0 | 227 | 5428 | 240 | 223.8904 | 14.3188 | -14.0315 | 214.284 | 3.3375 | 129.9369 | -14.2257 | 0 | 111.1701 | 68.8299 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5058 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5429 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 227 | 5429 | 300 | 223.8904 | 14.3188 | -14.0315 | 274.284 | 4.3375 | 114.9369 | -5.713 | 0 | 111.1701 | 68.8299 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.7106 | 10.7106 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5430 | 6 | 16 | 0 | 0.92 | 0.92 | 0.92 | 0.46 | 227 | 5430 | 360 | 223.8904 | 14.3188 | -14.0315 | 334.284 | 5.3375 | 99.9369 | 3.768 | 3.768 | 106.9682 | 73.0318 | 99.1749 | 0 | 0 | 0.78527 | 0.78527 | -156.6818 | 0% | 0.3551 | 0 | 0 | 23.6208 | 23.6208 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5431 | 7 | 16 | 10.61 | 29.11 | 39.72 | 29.11 | 14.56 | 227 | 5431 | 420 | 223.8904 | 14.3188 | -14.0315 | 394.284 | 6.3375 | 84.9369 | 13.8146 | 13.8146 | 96.3295 | 83.6705 | 84.6555 | 4.1387 | 4.1387 | 24.8469 | 28.9857 | -3.4625 | 0% | 13.1073 | 0 | 0 | 196.4148 | 196.4148 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5432 | 8 | 15.8 | 101.31 | 96.58 | 197.89 | 96.58 | 48.29 | 227 | 5432 | 480 | 223.8904 | 14.3188 | -14.0315 | 454.284 | 7.3375 | 69.9369 | 24.0702 | 24.0702 | 85.4236 | 94.5764 | 70.1285 | 84.4328 | 84.4328 | 82.4362 | 166.8689 | 0.060183 | 6.018% | 75.4581 | 4.5413 | 3.1789 | 172.5943 | 172.5943 | 1.842% | 11.5% | 11.5% | 80% | 9.199% | 6.9411 | 5.833 | 5.833 | 40.4873 | 15.3496 | 23.46% | 23.46%
8 | 227 | 15 | 5433 | 9 | 15.9 | 220.47 | 122.22 | 342.69 | 122.22 | 61.11 | 227 | 5433 | 540 | 223.8904 | 14.3188 | -14.0315 | 514.284 | 8.3375 | 54.9369 | 34.1539 | 34.1539 | 73.4119 | 106.5881 | 55.6645 | 221.4988 | 221.4988 | 104.3213 | 325.8201 | 0.42375 | 42.37% | 147.3358 | 62.4331 | 43.7031 | 180.3087 | 180.3087 | 24.24% | 11.46% | 11.46% | 85% | 9.74% | 14.3506 | 5.8104 | 5.8104 | 83.3823 | 31.7352 | 46.24% | 46.24%
8 | 227 | 15 | 5434 | 10 | 16.1 | 397.69 | 123.06 | 520.75 | 123.06 | 61.53 | 227 | 5434 | 600 | 223.8904 | 14.3188 | -14.0315 | 574.284 | 9.3375 | 39.9369 | 43.5511 | 43.5511 | 59.117 | 120.883 | 41.3881 | 433.0416 | 433.0416 | 105.0383 | 538.0799 | 0.57459 | 57.46% | 243.3197 | 139.808 | 97.8656 | 184.4638 | 184.4638 | 53.05% | 11.41% | 11.41% | 90% | 10.27% | 24.9825 | 5.7653 | 5.7653 | 144.0321 | 55.2466 | 78.08% | 78.08%
8 | 227 | 15 | 5435 | 11 | 16.3 | 515.56 | 157.78 | 673.34 | 157.78 | 78.89 | 227 | 5435 | 660 | 223.8904 | 14.3188 | -14.0315 | 634.284 | 10.3375 | 24.9369 | 51.436 | 51.436 | 40.9443 | 139.0557 | 27.6432 | 584.0946 | 584.0946 | 134.6737 | 718.7683 | 0.63288 | 63.29% | 325.027 | 205.7043 | 143.993 | 180.1436 | 180.1436 | 79.93% | 11.37% | 11.37% | 90% | 10.23% | 33.2557 | 5.7206 | 5.7206 | 190.2412 | 73.5421 | 105.6% | 105.6%
8 | 227 | 15 | 5436 | 12 | 16.4 | 499.53 | 182.03 | 681.56 | 182.03 | 91.02 | 227 | 5436 | 720 | 223.8904 | 14.3188 | -14.0315 | 694.284 | 11.3375 | 9.9369 | 56.4931 | 56.4931 | 17.6308 | 162.3692 | 15.9268 | 576.0895 | 576.0895 | 155.3723 | 731.4618 | 0.63616 | 63.62% | 330.767 | 210.421 | 147.2947 | 164.4278 | 164.4278 | 89.58% | 11.37% | 11.37% | 90% | 10.23% | 33.8342 | 5.6983 | 5.6983 | 192.7968 | 74.8213 | 117.3% | 117.3%
8 | 227 | 15 | 5437 | 13 | 17.7 | 547.5 | 155.56 | 703.06 | 155.56 | 77.78 | 227 | 5437 | 780 | 223.8904 | 14.3188 | -14.0315 | 754.284 | 12.3375 | -5.0631 | 57.2654 | 57.2654 | 9.0987 | 189.0987 | 13.5017 | 632.8797 | 632.8797 | 132.7788 | 765.6584 | 0.64746 | 64.75% | 346.2307 | 224.171 | 156.9197 | 162.8835 | 162.8835 | 96.34% | 11.36% | 11.36% | 90% | 10.22% | 35.3872 | 5.4151 | 5.4151 | 191.6246 | 78.2557 | 117.6% | 117.6%
8 | 227 | 15 | 5438 | 14 | 19.2 | 617.78 | 153.06 | 770.84 | 153.06 | 76.53 | 227 | 5438 | 840 | 223.8904 | 14.3188 | -14.0315 | 814.284 | 13.3375 | -20.0631 | 53.4662 | 53.4662 | 33.9434 | 213.9434 | 23.4554 | 705.3251 | 705.3251 | 130.6449 | 835.97 | 0.66461 | 66.46% | 378.0256 | 251.2411 | 175.8688 | 165.5318 | 165.5318 | 106.2% | 11.35% | 11.35% | 95% | 10.78% | 40.7621 | 5.103 | 5.103 | 208.0091 | 90.1418 | 125.7% | 125.7%
8 | 227 | 15 | 5439 | 15 | 20.3 | 591.94 | 153.06 | 745 | 153.06 | 76.53 | 227 | 5439 | 900 | 223.8904 | 14.3188 | -14.0315 | 874.284 | 14.3375 | -35.0631 | 46.3319 | 46.3319 | 53.7218 | 233.7218 | 36.8332 | 654.9773 | 654.9773 | 130.6449 | 785.6222 | 0.65877 | 65.88% | 355.2584 | 234.0327 | 163.8229 | 163.1221 | 163.1221 | 100.4% | 11.35% | 11.35% | 90% | 10.22% | 36.2953 | 4.8842 | 4.8842 | 177.2718 | 80.2638 | 108.7% | 108.7%
8 | 227 | 15 | 5440 | 16 | 19.9 | 397.31 | 181.31 | 578.62 | 181.31 | 90.66 | 227 | 5440 | 960 | 223.8904 | 14.3188 | -14.0315 | 934.284 | 15.3375 | -50.0631 | 37.3141 | 37.3141 | 69.0873 | 249.0873 | 50.996 | 412.51 | 412.51 | 154.7578 | 567.2677 | 0.60131 | 60.13% | 256.5185 | 154.2479 | 107.9736 | 153.1671 | 153.1671 | 70.49% | 11.35% | 11.35% | 90% | 10.22% | 26.2109 | 4.9628 | 4.9628 | 130.0784 | 57.9631 | 84.93% | 84.93%
8 | 227 | 15 | 5441 | 17 | 19.5 | 257.69 | 136.67 | 394.36 | 136.67 | 68.34 | 227 | 5441 | 1020 | 223.8904 | 14.3188 | -14.0315 | 994.284 | 16.3375 | -65.0631 | 27.3863 | 27.3863 | 81.6905 | 261.6905 | 65.4178 | 233.0468 | 233.0468 | 116.6551 | 349.7019 | 0.47269 | 47.27% | 158.1352 | 74.749 | 52.3243 | 140.7572 | 140.7572 | 37.17% | 11.36% | 11.36% | 85% | 9.66% | 15.2754 | 5.0425 | 5.0425 | 77.026 | 33.7802 | 54.72% | 54.72%
8 | 227 | 15 | 5442 | 18 | 20.6 | 161.58 | 116.58 | 278.16 | 116.58 | 58.29 | 227 | 5442 | 1080 | 223.8904 | 14.3188 | -14.0315 | 1054.284 | 17.3375 | -80.0631 | 17.1411 | 17.1411 | 92.8509 | 272.8509 | 79.9332 | 95.8296 | 95.8296 | 99.5073 | 195.3368 | 0.22326 | 22.33% | 88.3313 | 19.7211 | 13.8048 | 131.7995 | 131.7995 | 10.47% | 11.33% | 11.33% | 80% | 9.066% | 8.0078 | 4.8259 | 4.8259 | 38.6451 | 17.7085 | 29.32% | 29.32%
8 | 227 | 15 | 5443 | 19 | 21.3 | 87.86 | 71.39 | 159.25 | 71.39 | 35.7 | 227 | 5443 | 1140 | 223.8904 | 14.3188 | -14.0315 | 1114.284 | 18.3375 | -95.0631 | 6.9879 | 6.9879 | 103.4983 | 283.4983 | 94.4619 | 0 | 0 | 60.9352 | 60.9352 | -1.0325 | 0% | 27.5549 | 0 | 0 | 122.2917 | 122.2917 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.6926 | 4.6926 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5444 | 20 | 19.2 | 0 | 19.64 | 19.64 | 19.64 | 9.82 | 227 | 5444 | 1200 | 223.8904 | 14.3188 | -14.0315 | 1174.284 | 19.3375 | -110.0631 | -2.7176 | 0 | 111.1701 | 291.1701 | 104.7951 | 0 | 0 | 16.7638 | 16.7638 | -6.1469 | 0% | 7.5806 | 0 | 0 | 144.2021 | 144.2021 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.103 | 5.103 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5445 | 21 | 19.1 | 0 | 0 | 0 | 0 | 0 | 227 | 5445 | 1260 | 223.8904 | 14.3188 | -14.0315 | 1234.284 | 20.3375 | -125.0631 | -11.594 | 0 | 111.1701 | 291.1701 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.8349 | 0 | 0% | 11.39% | 0% | 80% | 0% | 0 | 5.1233 | 5.1233 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5446 | 22 | 18.3 | 0 | 0 | 0 | 0 | 0 | 227 | 5446 | 1320 | 223.8904 | 14.3188 | -14.0315 | 1294.284 | 21.3375 | -140.0631 | -19.1813 | 0 | 111.1701 | 291.1701 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.8733 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5447 | 23 | 17.7 | 0 | 0 | 0 | 0 | 0 | 227 | 5447 | 1380 | 223.8904 | 14.3188 | -14.0315 | 1354.284 | 22.3375 | -155.0631 | -24.9274 | 0 | 111.1701 | 291.1701 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0436 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
8 | 227 | 15 | 5448 | 24 | 17.8 | 0 | 0 | 0 | 0 | 0 | 227 | 5448 | 1440 | 223.8904 | 14.3188 | -14.0315 | 1414.284 | 23.3375 | -170.0631 | -28.2537 | 0 | 111.1701 | 291.1701 | 104.7951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.1472 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5449 | 1 | 17.4 | 0 | 0 | 0 | 0 | 0 | 228 | 5449 | 60 | 224.8767 | 14.0183 | -14.0392 | 34.284 | 0.33741 | 174.9388 | -29.0338 | 0 | 110.7145 | 69.2855 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.477 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5450 | 2 | 17 | 0 | 0 | 0 | 0 | 0 | 228 | 5450 | 120 | 224.8767 | 14.0183 | -14.0392 | 94.284 | 1.3374 | 159.9388 | -26.59 | 0 | 110.7145 | 69.2855 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.3683 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5451 | 3 | 16.3 | 0 | 0 | 0 | 0 | 0 | 228 | 5451 | 180 | 224.8767 | 14.0183 | -14.0392 | 154.284 | 2.3374 | 144.9388 | -21.5522 | 0 | 110.7145 | 69.2855 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.7169 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5452 | 4 | 16.1 | 0 | 0 | 0 | 0 | 0 | 228 | 5452 | 240 | 224.8767 | 14.0183 | -14.0392 | 214.284 | 3.3374 | 129.9388 | -14.4793 | 0 | 110.7145 | 69.2855 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0217 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5453 | 5 | 16.1 | 0 | 0 | 0 | 0 | 0 | 228 | 5453 | 300 | 224.8767 | 14.0183 | -14.0392 | 274.284 | 4.3374 | 114.9388 | -5.949 | 0 | 110.7145 | 69.2855 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.76 | 10.76 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5454 | 6 | 16.3 | 0 | 0 | 0 | 0 | 0 | 228 | 5454 | 360 | 224.8767 | 14.0183 | -14.0392 | 334.284 | 5.3374 | 99.9388 | 3.5452 | 3.5452 | 106.766 | 73.234 | 99.1987 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 24.3403 | 24.3403 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5455 | 7 | 16.6 | 22.78 | 27.86 | 50.64 | 27.86 | 13.93 | 228 | 5455 | 420 | 224.8767 | 14.0183 | -14.0392 | 394.284 | 6.3374 | 84.9388 | 13.5994 | 13.5994 | 96.1136 | 83.8864 | 84.6599 | 9.0165 | 9.0165 | 23.78 | 32.7965 | -2.9256 | 0% | 14.8306 | 0 | 0 | 199.3611 | 199.3611 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5456 | 8 | 16.7 | 130.36 | 61.75 | 192.11 | 61.75 | 30.88 | 228 | 5456 | 480 | 224.8767 | 14.0183 | -14.0392 | 454.284 | 7.3374 | 69.9388 | 23.8555 | 23.8555 | 85.1935 | 94.8065 | 70.1132 | 109.6447 | 109.6447 | 52.7069 | 162.3516 | 0.051967 | 5.197% | 73.4154 | 3.8152 | 2.6706 | 175.1888 | 175.1888 | 1.524% | 11.47% | 11.47% | 80% | 9.174% | 6.7353 | 5.6319 | 5.6319 | 37.9322 | 14.8944 | 21.65% | 21.65%
8 | 228 | 16 | 5457 | 9 | 17.3 | 252.42 | 90.36 | 342.78 | 90.36 | 45.18 | 228 | 5457 | 540 | 224.8767 | 14.0183 | -14.0392 | 514.284 | 8.3374 | 54.9388 | 33.9313 | 33.9313 | 73.1682 | 106.8318 | 55.6261 | 255.3104 | 255.3104 | 77.1271 | 332.4375 | 0.44078 | 44.08% | 150.3282 | 66.2612 | 46.3828 | 183.7691 | 183.7691 | 25.24% | 11.42% | 11.42% | 85% | 9.708% | 14.5942 | 5.501 | 5.501 | 80.282 | 32.2738 | 43.69% | 43.69%
8 | 228 | 16 | 5458 | 10 | 17.4 | 415.19 | 101.67 | 516.86 | 101.67 | 50.84 | 228 | 5458 | 600 | 224.8767 | 14.0183 | -14.0392 | 574.284 | 9.3374 | 39.9388 | 43.3108 | 43.3108 | 58.8684 | 121.1316 | 41.3182 | 454.5924 | 454.5924 | 86.7808 | 541.3731 | 0.58137 | 58.14% | 244.8089 | 142.3248 | 99.6274 | 187.6172 | 187.6172 | 53.1% | 11.39% | 11.39% | 90% | 10.25% | 25.0931 | 5.4794 | 5.4794 | 137.4948 | 55.4912 | 73.28% | 73.28%
8 | 228 | 16 | 5459 | 11 | 18.4 | 544.72 | 112.58 | 657.3 | 112.58 | 56.29 | 228 | 5459 | 660 | 224.8767 | 14.0183 | -14.0392 | 634.284 | 10.3374 | 24.9388 | 51.1686 | 51.1686 | 40.7249 | 139.2751 | 27.5204 | 620.1365 | 620.1365 | 96.093 | 716.2296 | 0.63883 | 63.88% | 323.879 | 206.9052 | 144.8336 | 183.8728 | 183.8728 | 78.77% | 11.36% | 11.36% | 90% | 10.22% | 33.1116 | 5.2675 | 5.2675 | 174.4145 | 73.2233 | 94.86% | 94.86%
8 | 228 | 16 | 5460 | 12 | 18.5 | 626.47 | 122.14 | 748.61 | 122.14 | 61.07 | 228 | 5460 | 720 | 224.8767 | 14.0183 | -14.0392 | 694.284 | 11.3374 | 9.9388 | 56.1991 | 56.1991 | 17.5184 | 162.4816 | 15.6953 | 725.787 | 725.787 | 104.253 | 830.04 | 0.66175 | 66.17% | 375.3441 | 248.3836 | 173.8685 | 171.4105 | 171.4105 | 101.4% | 11.35% | 11.35% | 95% | 10.78% | 40.4698 | 5.2467 | 5.2467 | 212.3317 | 89.4953 | 123.9% | 123.9%
8 | 228 | 16 | 5461 | 13 | 20.1 | 640.92 | 145.83 | 786.75 | 145.83 | 72.92 | 228 | 5461 | 780 | 224.8767 | 14.0183 | -14.0392 | 754.284 | 12.3374 | -5.0612 | 56.967 | 56.967 | 9.0337 | 189.0337 | 13.2233 | 744.2262 | 744.2262 | 124.4737 | 868.6999 | 0.67215 | 67.22% | 392.8261 | 264.0383 | 184.8268 | 171.6913 | 171.6913 | 107.7% | 11.35% | 11.35% | 95% | 10.78% | 42.3653 | 4.9233 | 4.9233 | 208.5779 | 93.6872 | 121.5% | 121.5%
8 | 228 | 16 | 5462 | 14 | 20.8 | 669.44 | 138.25 | 807.69 | 138.25 | 69.13 | 228 | 5462 | 840 | 224.8767 | 14.0183 | -14.0392 | 814.284 | 13.3374 | -20.0612 | 53.1907 | 53.1907 | 33.7426 | 213.7426 | 23.3025 | 767.9332 | 767.9332 | 118.0038 | 885.937 | 0.67645 | 67.65% | 400.6207 | 271 | 189.7 | 171.7655 | 171.7655 | 110.4% | 11.36% | 11.36% | 95% | 10.79% | 43.2189 | 4.7875 | 4.7875 | 206.9098 | 95.5748 | 120.5% | 120.5%
8 | 228 | 16 | 5463 | 15 | 20.8 | 578.33 | 133.25 | 711.58 | 133.25 | 66.63 | 228 | 5463 | 900 | 224.8767 | 14.0183 | -14.0392 | 874.284 | 14.3374 | -35.0612 | 46.0857 | 46.0857 | 53.4727 | 233.4727 | 36.7461 | 643.291 | 643.291 | 113.736 | 757.027 | 0.65473 | 65.47% | 342.3276 | 224.1323 | 156.8926 | 165.0889 | 165.0889 | 95.04% | 11.35% | 11.35% | 90% | 10.22% | 34.9691 | 4.7875 | 4.7875 | 167.4139 | 77.331 | 101.4% | 101.4%
8 | 228 | 16 | 5464 | 16 | 20.3 | 509.53 | 124.36 | 633.89 | 124.36 | 62.18 | 228 | 5464 | 960 | 224.8767 | 14.0183 | -14.0392 | 934.284 | 15.3374 | -50.0612 | 37.0893 | 37.0893 | 68.8368 | 248.8368 | 50.945 | 532.3478 | 532.3478 | 106.1479 | 638.4957 | 0.6253 | 62.53% | 288.7278 | 180.5421 | 126.3795 | 159.129 | 159.129 | 79.42% | 11.35% | 11.35% | 90% | 10.21% | 29.4918 | 4.8842 | 4.8842 | 144.0426 | 65.2185 | 90.52% | 90.52%
8 | 228 | 16 | 5465 | 17 | 21.2 | 371.67 | 113.81 | 485.48 | 113.81 | 56.91 | 228 | 5465 | 1020 | 224.8767 | 14.0183 | -14.0392 | 994.284 | 16.3374 | -65.0612 | 27.1726 | 27.1726 | 81.4528 | 261.4528 | 65.3918 | 338.9026 | 338.9026 | 97.1429 | 436.0455 | 0.54686 | 54.69% | 197.1798 | 107.8292 | 75.4804 | 150.6943 | 150.6943 | 50.09% | 11.33% | 11.33% | 85% | 9.629% | 18.986 | 4.7114 | 4.7114 | 89.4507 | 41.9859 | 59.36% | 59.36%
8 | 228 | 16 | 5466 | 18 | 21.2 | 201.58 | 100.36 | 301.94 | 100.36 | 50.18 | 228 | 5466 | 1080 | 224.8767 | 14.0183 | -14.0392 | 1054.284 | 17.3374 | -80.0612 | 16.9294 | 16.9294 | 92.6278 | 272.6278 | 79.9277 | 121.0691 | 121.0691 | 85.6626 | 206.7317 | 0.26163 | 26.16% | 93.4841 | 24.4578 | 17.1205 | 136.3467 | 136.3467 | 12.56% | 11.31% | 11.31% | 80% | 9.05% | 8.4606 | 4.7114 | 4.7114 | 39.8611 | 18.7098 | 29.24% | 29.24%
8 | 228 | 16 | 5467 | 19 | 21.3 | 81.67 | 56.94 | 138.61 | 56.94 | 28.47 | 228 | 5467 | 1140 | 224.8767 | 14.0183 | -14.0392 | 1114.284 | 18.3374 | -95.0612 | 6.7709 | 6.7709 | 103.2889 | 283.2889 | 94.4757 | 0 | 0 | 48.6013 | 48.6013 | -1.4986 | 0% | 21.9775 | 0 | 0 | 164.3527 | 164.3527 | 0% | 11.3% | 0% | 80% | 0% | 0 | 4.6926 | 4.6926 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5468 | 20 | 19.4 | 0 | 17.58 | 17.58 | 17.58 | 8.79 | 228 | 5468 | 1200 | 224.8767 | 14.0183 | -14.0392 | 1174.284 | 19.3374 | -110.0612 | -2.9464 | 0 | 110.7145 | 290.7145 | 104.4841 | 0 | 0 | 15.0055 | 15.0055 | -6.9319 | 0% | 6.7855 | 0 | 0 | 144.5228 | 144.5228 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0626 | 5.0626 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5469 | 21 | 18.3 | 0 | 0 | 0 | 0 | 0 | 228 | 5469 | 1260 | 224.8767 | 14.0183 | -14.0392 | 1234.284 | 20.3374 | -125.0612 | -11.8394 | 0 | 110.7145 | 290.7145 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.2114 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5470 | 22 | 18.3 | 0 | 0 | 0 | 0 | 0 | 228 | 5470 | 1320 | 224.8767 | 14.0183 | -14.0392 | 1294.284 | 21.3374 | -140.0612 | -19.4464 | 0 | 110.7145 | 290.7145 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2601 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5471 | 23 | 17.8 | 0 | 0 | 0 | 0 | 0 | 228 | 5471 | 1380 | 224.8767 | 14.0183 | -14.0392 | 1354.284 | 22.3374 | -155.0612 | -25.2117 | 0 | 110.7145 | 290.7145 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3039 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
8 | 228 | 16 | 5472 | 24 | 17.2 | 0 | 0 | 0 | 0 | 0 | 228 | 5472 | 1440 | 224.8767 | 14.0183 | -14.0392 | 1414.284 | 23.3374 | -170.0612 | -28.5513 | 0 | 110.7145 | 290.7145 | 104.4841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5473 | 1 | 17.4 | 0 | 0 | 0 | 0 | 0 | 229 | 5473 | 60 | 225.863 | 13.7139 | -14.0347 | 34.284 | 0.33749 | 174.9377 | -29.3374 | 0 | 110.2538 | 69.7462 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0468 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5474 | 2 | 16.8 | 0 | 0 | 0 | 0 | 0 | 229 | 5474 | 120 | 225.863 | 13.7139 | -14.0347 | 94.284 | 1.3375 | 159.9377 | -26.8834 | 0 | 110.2538 | 69.7462 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2911 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5475 | 3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 229 | 5475 | 180 | 225.863 | 13.7139 | -14.0347 | 154.284 | 2.3375 | 144.9377 | -21.8275 | 0 | 110.2538 | 69.7462 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5354 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5476 | 4 | 15.4 | 0 | 0 | 0 | 0 | 0 | 229 | 5476 | 240 | 225.863 | 13.7139 | -14.0347 | 214.284 | 3.3375 | 129.9377 | -14.7343 | 0 | 110.2538 | 69.7462 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.7546 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5477 | 5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 229 | 5477 | 300 | 225.863 | 13.7139 | -14.0347 | 274.284 | 4.3375 | 114.9377 | -6.186 | 0 | 110.2538 | 69.7462 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.2042 | 8.2042 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5478 | 6 | 15.7 | 0 | 0 | 0 | 0 | 0 | 229 | 5478 | 360 | 225.863 | 13.7139 | -14.0347 | 334.284 | 5.3375 | 99.9377 | 3.3216 | 3.3216 | 106.5592 | 73.4408 | 99.2197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 21.4468 | 21.4468 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5479 | 7 | 15.7 | 16.19 | 21.67 | 37.86 | 21.67 | 10.84 | 229 | 5479 | 420 | 225.863 | 13.7139 | -14.0347 | 394.284 | 6.3375 | 84.9377 | 13.3832 | 13.3832 | 95.8932 | 84.1068 | 84.6616 | 6.5077 | 6.5077 | 18.4965 | 25.0042 | -4.169 | 0% | 11.3069 | 0 | 0 | 193.7609 | 193.7609 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5480 | 8 | 16.8 | 92.5 | 65 | 157.5 | 65 | 32.5 | 229 | 5480 | 480 | 225.863 | 13.7139 | -14.0347 | 454.284 | 7.3375 | 69.9377 | 23.6397 | 23.6397 | 84.9589 | 95.0411 | 70.0952 | 78.5377 | 78.5377 | 55.481 | 134.0187 | -0.10535 | 0% | 60.6033 | 0 | 0 | 169.6101 | 169.6101 | 0% | 11.47% | 11.47% | 80% | 9.175% | 5.5606 | 5.6099 | 5.6099 | 31.1941 | 12.2967 | 18.39% | 18.39%
8 | 229 | 17 | 5481 | 9 | 19.1 | 203.06 | 96.75 | 299.81 | 96.75 | 48.38 | 229 | 5481 | 540 | 225.863 | 13.7139 | -14.0347 | 514.284 | 8.3375 | 54.9377 | 33.7074 | 33.7074 | 72.92 | 107.08 | 55.5854 | 206.8015 | 206.8015 | 82.5813 | 289.3828 | 0.40058 | 40.06% | 130.8589 | 52.419 | 36.6933 | 180.7738 | 180.7738 | 20.3% | 11.38% | 11.38% | 80% | 9.102% | 11.9105 | 5.1233 | 5.1233 | 61.0215 | 26.3391 | 33.76% | 33.76%
8 | 229 | 17 | 5482 | 10 | 21 | 370.08 | 120.75 | 490.83 | 120.75 | 60.38 | 229 | 5482 | 600 | 225.863 | 13.7139 | -14.0347 | 574.284 | 9.3375 | 39.9377 | 43.0686 | 43.0686 | 58.6155 | 121.3845 | 41.2463 | 407.4786 | 407.4786 | 103.0666 | 510.5452 | 0.58352 | 58.35% | 230.8685 | 134.7172 | 94.3021 | 188.8206 | 188.8206 | 49.94% | 11.34% | 11.34% | 90% | 10.2% | 23.5543 | 4.7493 | 4.7493 | 111.8664 | 52.0882 | 59.24% | 59.24%
8 | 229 | 17 | 5483 | 11 | 22.2 | 469.36 | 150.08 | 619.44 | 150.08 | 75.04 | 229 | 5483 | 660 | 225.863 | 13.7139 | -14.0347 | 634.284 | 10.3375 | 24.9377 | 50.8987 | 50.8987 | 40.5011 | 139.4989 | 27.3959 | 536.9887 | 536.9887 | 128.1013 | 665.09 | 0.63869 | 63.87% | 300.7537 | 192.0876 | 134.4613 | 185.7011 | 185.7011 | 72.41% | 11.34% | 11.34% | 90% | 10.2% | 30.6832 | 4.5261 | 4.5261 | 138.8753 | 67.8532 | 74.78% | 74.78%
8 | 229 | 17 | 5484 | 12 | 23.7 | 600.75 | 143.25 | 744 | 143.25 | 71.63 | 229 | 5484 | 720 | 225.863 | 13.7139 | -14.0347 | 694.284 | 11.3375 | 9.9377 | 55.9018 | 55.9018 | 17.4012 | 162.5988 | 15.4613 | 699.2205 | 699.2205 | 122.2715 | 821.492 | 0.67411 | 67.41% | 371.4787 | 250.4166 | 175.2916 | 189.695 | 189.695 | 92.41% | 11.36% | 11.36% | 95% | 10.79% | 40.0772 | 4.2613 | 4.2613 | 170.7799 | 88.6271 | 90.03% | 90.03%
8 | 229 | 17 | 5485 | 13 | 23.9 | 634.25 | 155.47 | 789.72 | 155.47 | 77.74 | 229 | 5485 | 780 | 225.863 | 13.7139 | -14.0347 | 754.284 | 12.3375 | -5.0623 | 56.6643 | 56.6643 | 8.9743 | 188.9743 | 12.9433 | 739.8693 | 739.8693 | 132.7019 | 872.5712 | 0.6822 | 68.22% | 394.5767 | 269.1819 | 188.4273 | 191.8763 | 191.8763 | 98.2% | 11.37% | 11.37% | 95% | 10.8% | 42.6111 | 4.2272 | 4.2272 | 180.1236 | 94.2306 | 93.87% | 93.87%
8 | 229 | 17 | 5486 | 14 | 25 | 515.92 | 195.28 | 711.2 | 195.28 | 97.64 | 229 | 5486 | 840 | 225.863 | 13.7139 | -14.0347 | 814.284 | 13.3375 | -20.0623 | 52.91 | 52.91 | 33.5464 | 213.5464 | 23.153 | 594.6758 | 594.6758 | 166.6819 | 761.3577 | 0.66751 | 66.75% | 344.286 | 229.8133 | 160.8693 | 208.0052 | 208.0052 | 77.34% | 11.34% | 11.34% | 90% | 10.21% | 35.1421 | 4.0445 | 4.0445 | 142.1321 | 77.7136 | 68.33% | 68.33%
8 | 229 | 17 | 5487 | 15 | 25.2 | 502.58 | 197.69 | 700.27 | 197.69 | 98.85 | 229 | 5487 | 900 | 225.863 | 13.7139 | -14.0347 | 874.284 | 14.3375 | -35.0623 | 45.8342 | 45.8342 | 53.2262 | 233.2262 | 36.6626 | 562.0212 | 562.0212 | 168.739 | 730.7601 | 0.66238 | 66.24% | 330.4497 | 218.8818 | 153.2173 | 282.473 | 282.473 | 54.24% | 11.33% | 11.33% | 90% | 10.2% | 33.7025 | 4.0122 | 4.0122 | 135.2211 | 74.5301 | 47.87% | 47.87%
8 | 229 | 17 | 5488 | 16 | 22.9 | 413.53 | 159.36 | 572.89 | 159.36 | 79.68 | 229 | 5488 | 960 | 225.863 | 13.7139 | -14.0347 | 934.284 | 15.3375 | -50.0623 | 36.8592 | 36.8592 | 68.5875 | 248.5875 | 50.8976 | 434.8028 | 434.8028 | 136.0223 | 570.825 | 0.61405 | 61.4% | 258.1271 | 158.5017 | 110.9512 | 159.7451 | 159.7451 | 69.46% | 11.32% | 11.32% | 90% | 10.18% | 26.2874 | 4.4006 | 4.4006 | 115.6792 | 58.1323 | 72.41% | 72.41%
8 | 229 | 17 | 5489 | 17 | 22.3 | 315.47 | 124.44 | 439.91 | 124.44 | 62.22 | 229 | 5489 | 1020 | 225.863 | 13.7139 | -14.0347 | 994.284 | 16.3375 | -65.0623 | 26.9537 | 26.9537 | 81.2153 | 261.2153 | 65.3691 | 290.0669 | 290.0669 | 106.2162 | 396.2831 | 0.5271 | 52.71% | 179.1992 | 94.456 | 66.1192 | 149.5735 | 149.5735 | 44.21% | 11.3% | 11.3% | 85% | 9.606% | 17.2135 | 4.508 | 4.508 | 77.5977 | 38.0661 | 51.88% | 51.88%
8 | 229 | 17 | 5490 | 18 | 22.4 | 230.08 | 100.36 | 330.44 | 100.36 | 50.18 | 229 | 5490 | 1080 | 225.863 | 13.7139 | -14.0347 | 1054.284 | 17.3375 | -80.0623 | 16.7127 | 16.7127 | 92.4045 | 272.4045 | 79.9253 | 139.9588 | 139.9588 | 85.6626 | 225.6214 | 0.31861 | 31.86% | 102.026 | 32.5068 | 22.7548 | 139.4179 | 139.4179 | 16.32% | 11.28% | 11.28% | 80% | 9.021% | 9.2037 | 4.4899 | 4.4899 | 41.3236 | 20.3532 | 29.64% | 29.64%
8 | 229 | 17 | 5491 | 19 | 21 | 114.81 | 61.31 | 176.12 | 61.31 | 30.66 | 229 | 5491 | 1140 | 225.863 | 13.7139 | -14.0347 | 1114.284 | 18.3375 | -95.0623 | 6.5489 | 6.5489 | 103.0792 | 283.0792 | 94.4924 | 0 | 0 | 52.3314 | 52.3314 | -1.347 | 0% | 23.6642 | 0 | 0 | 124.0262 | 124.0262 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7493 | 4.7493 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5492 | 20 | 19.8 | 0 | 22.42 | 22.42 | 22.42 | 11.21 | 229 | 5492 | 1200 | 225.863 | 13.7139 | -14.0347 | 1174.284 | 19.3375 | -110.0623 | -3.1799 | 0 | 110.2538 | 290.2538 | 104.1692 | 0 | 0 | 19.1367 | 19.1367 | -5.2158 | 0% | 8.6536 | 0 | 0 | 144.9299 | 144.9299 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9826 | 4.9826 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5493 | 21 | 18.4 | 0 | 0 | 0 | 0 | 0 | 229 | 5493 | 1260 | 225.863 | 13.7139 | -14.0347 | 1234.284 | 20.3375 | -125.0623 | -12.0895 | 0 | 110.2538 | 290.2538 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.4901 | 0 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5494 | 22 | 17.2 | 0 | 0 | 0 | 0 | 0 | 229 | 5494 | 1320 | 225.863 | 13.7139 | -14.0347 | 1294.284 | 21.3375 | -140.0623 | -19.7162 | 0 | 110.2538 | 290.2538 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3618 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5495 | 23 | 16.2 | 0 | 0 | 0 | 0 | 0 | 229 | 5495 | 1380 | 225.863 | 13.7139 | -14.0347 | 1354.284 | 22.3375 | -155.0623 | -25.5005 | 0 | 110.2538 | 290.2538 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2157 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
8 | 229 | 17 | 5496 | 24 | 15.6 | 0 | 0 | 0 | 0 | 0 | 229 | 5496 | 1440 | 225.863 | 13.7139 | -14.0347 | 1414.284 | 23.3375 | -170.0623 | -28.8531 | 0 | 110.2538 | 290.2538 | 104.1692 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4601 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5497 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 230 | 5497 | 60 | 226.8493 | 13.4057 | -14.0181 | 34.284 | 0.33776 | 174.9335 | -29.6446 | 0 | 109.7882 | 70.2118 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5979 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5498 | 2 | 14.5 | 0 | 0 | 0 | 0 | 0 | 230 | 5498 | 120 | 226.8493 | 13.4057 | -14.0181 | 94.284 | 1.3378 | 159.9335 | -27.1796 | 0 | 109.7882 | 70.2118 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5559 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5499 | 3 | 14.1 | 0 | 0 | 0 | 0 | 0 | 230 | 5499 | 180 | 226.8493 | 13.4057 | -14.0181 | 154.284 | 2.3378 | 144.9335 | -22.1048 | 0 | 109.7882 | 70.2118 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3615 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5500 | 4 | 13.7 | 0 | 0 | 0 | 0 | 0 | 230 | 5500 | 240 | 226.8493 | 13.4057 | -14.0181 | 214.284 | 3.3378 | 129.9335 | -14.9909 | 0 | 109.7882 | 70.2118 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9711 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5501 | 5 | 13.1 | 0 | 0 | 0 | 0 | 0 | 230 | 5501 | 300 | 226.8493 | 13.4057 | -14.0181 | 274.284 | 4.3378 | 114.9335 | -6.4242 | 0 | 109.7882 | 70.2118 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.1074 | 7.1074 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5502 | 6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 230 | 5502 | 360 | 226.8493 | 13.4057 | -14.0181 | 334.284 | 5.3378 | 99.9335 | 3.0971 | 3.0971 | 106.3477 | 73.6523 | 99.2377 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 20.0976 | 20.0976 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5503 | 7 | 13.1 | 15.47 | 26.03 | 41.5 | 26.03 | 13.02 | 230 | 5503 | 420 | 226.8493 | 13.4057 | -14.0181 | 394.284 | 6.3378 | 84.9335 | 13.1662 | 13.1662 | 95.6683 | 84.3317 | 84.6605 | 6.3202 | 6.3202 | 22.218 | 28.5382 | -3.7605 | 0% | 12.905 | 0 | 0 | 194.4044 | 194.4044 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5504 | 8 | 15.2 | 106.89 | 68.39 | 175.28 | 68.39 | 34.2 | 230 | 5504 | 480 | 226.8493 | 13.4057 | -14.0181 | 454.284 | 7.3378 | 69.9335 | 23.4229 | 23.4229 | 84.7199 | 95.2801 | 70.0747 | 91.638 | 91.638 | 58.3745 | 150.0125 | -0.032441 | 0% | 67.8357 | 0 | 0 | 173.0741 | 173.0741 | 0% | 11.52% | 11.52% | 80% | 9.219% | 6.2537 | 5.9702 | 5.9702 | 37.3358 | 13.8295 | 21.57% | 21.57%
8 | 230 | 18 | 5505 | 9 | 17.2 | 245.22 | 105.97 | 351.19 | 105.97 | 52.99 | 230 | 5505 | 540 | 226.8493 | 13.4057 | -14.0181 | 514.284 | 8.3378 | 54.9335 | 33.4821 | 33.4821 | 72.6674 | 107.3326 | 55.5424 | 251.4962 | 251.4962 | 90.4511 | 341.9473 | 0.45022 | 45.02% | 154.6285 | 69.6174 | 48.7322 | 185.1862 | 185.1862 | 26.32% | 11.42% | 11.42% | 85% | 9.709% | 15.0131 | 5.5226 | 5.5226 | 82.9115 | 33.2002 | 44.77% | 44.77%
8 | 230 | 18 | 5506 | 10 | 20.7 | 373.56 | 126.44 | 500 | 126.44 | 63.22 | 230 | 5506 | 600 | 226.8493 | 13.4057 | -14.0181 | 574.284 | 9.3378 | 39.9335 | 42.8246 | 42.8246 | 58.3582 | 121.6418 | 41.1725 | 413.6633 | 413.6633 | 107.9233 | 521.5866 | 0.58693 | 58.69% | 235.8615 | 138.4345 | 96.9041 | 192.6017 | 192.6017 | 50.31% | 11.34% | 11.34% | 90% | 10.21% | 24.0747 | 4.8067 | 4.8067 | 115.7194 | 53.2391 | 60.08% | 60.08%
8 | 230 | 18 | 5507 | 11 | 23.2 | 511.67 | 132.5 | 644.17 | 132.5 | 66.25 | 230 | 5507 | 660 | 226.8493 | 13.4057 | -14.0181 | 634.284 | 10.3378 | 24.9335 | 50.6263 | 50.6263 | 40.2731 | 139.7269 | 27.2698 | 588.341 | 588.341 | 113.0958 | 701.4368 | 0.65034 | 65.03% | 317.1897 | 206.2811 | 144.3968 | 194.3902 | 194.3902 | 74.28% | 11.33% | 11.33% | 90% | 10.2% | 32.3571 | 4.3478 | 4.3478 | 140.6823 | 71.5549 | 72.37% | 72.37%
8 | 230 | 18 | 5508 | 12 | 24.8 | 594.58 | 141.53 | 736.11 | 141.53 | 70.77 | 230 | 5508 | 720 | 226.8493 | 13.4057 | -14.0181 | 694.284 | 11.3378 | 9.9335 | 55.6013 | 55.6013 | 17.2792 | 162.7208 | 15.225 | 695.301 | 695.301 | 120.8034 | 816.1045 | 0.67614 | 67.61% | 369.0424 | 249.5244 | 174.6671 | 211.1727 | 211.1727 | 82.71% | 11.36% | 11.36% | 95% | 10.79% | 39.8139 | 4.0771 | 4.0771 | 162.3245 | 88.0449 | 76.87% | 76.87%
8 | 230 | 18 | 5509 | 13 | 25.9 | 505.42 | 178.06 | 683.48 | 178.06 | 89.03 | 230 | 5509 | 780 | 226.8493 | 13.4057 | -14.0181 | 754.284 | 12.3378 | -5.0665 | 56.3575 | 56.3575 | 8.9203 | 188.9203 | 12.6622 | 592.338 | 592.338 | 151.9837 | 744.3218 | 0.66696 | 66.7% | 336.5823 | 224.4856 | 157.1399 | 293.0624 | 293.0624 | 53.62% | 11.33% | 11.33% | 90% | 10.2% | 34.3332 | 3.9014 | 3.9014 | 133.946 | 75.9248 | 45.71% | 45.71%
8 | 230 | 18 | 5510 | 14 | 26 | 287.64 | 191.61 | 479.25 | 191.61 | 95.81 | 230 | 5510 | 840 | 226.8493 | 13.4057 | -14.0181 | 814.284 | 13.3378 | -20.0665 | 52.6245 | 52.6245 | 33.3547 | 213.3547 | 23.0072 | 333.1679 | 333.1679 | 163.5494 | 496.7173 | 0.59907 | 59.91% | 224.6156 | 134.5602 | 94.1922 | 289.6374 | 289.6374 | 32.52% | 11.25% | 11.25% | 85% | 9.564% | 21.4825 | 3.8858 | 3.8858 | 83.4768 | 47.5067 | 28.82% | 28.82%
8 | 230 | 18 | 5511 | 15 | 27.3 | 216.89 | 186.67 | 403.56 | 186.67 | 93.34 | 230 | 5511 | 900 | 226.8493 | 13.4057 | -14.0181 | 874.284 | 14.3378 | -35.0665 | 45.5773 | 45.5773 | 52.9823 | 232.9823 | 36.583 | 243.8572 | 243.8572 | 159.3328 | 403.19 | 0.55834 | 55.83% | 182.3225 | 101.7981 | 71.2587 | 279.9328 | 279.9328 | 25.46% | 11.19% | 11.19% | 85% | 9.514% | 17.3458 | 3.69 | 3.69 | 64.0051 | 38.3586 | 22.86% | 22.86%
8 | 230 | 18 | 5512 | 16 | 26.2 | 239.5 | 233.39 | 472.89 | 233.39 | 116.7 | 230 | 5512 | 960 | 226.8493 | 13.4057 | -14.0181 | 934.284 | 15.3378 | -50.0665 | 36.6238 | 36.6238 | 68.3392 | 248.3392 | 50.8538 | 253.4484 | 253.4484 | 199.2108 | 452.6593 | 0.58006 | 58.01% | 204.6925 | 118.7338 | 83.1137 | 270.7414 | 270.7414 | 30.7% | 11.23% | 11.23% | 85% | 9.549% | 19.5451 | 3.8549 | 3.8549 | 75.3445 | 43.2223 | 27.83% | 27.83%
8 | 230 | 18 | 5513 | 17 | 25.7 | 117.78 | 202.08 | 319.86 | 202.08 | 101.04 | 230 | 5513 | 1020 | 226.8493 | 13.4057 | -14.0181 | 994.284 | 16.3378 | -65.0665 | 26.7296 | 26.7296 | 80.9781 | 260.9781 | 65.3499 | 109.2161 | 109.2161 | 172.4861 | 281.7022 | 0.44039 | 44.04% | 127.3857 | 56.0995 | 39.2697 | 251.027 | 251.027 | 15.64% | 11.19% | 11.19% | 80% | 8.952% | 11.4031 | 3.9327 | 3.9327 | 44.8446 | 25.2169 | 17.86% | 17.86%
8 | 230 | 18 | 5514 | 18 | 23 | 88.67 | 152.22 | 240.89 | 152.22 | 76.11 | 230 | 5514 | 1080 | 226.8493 | 13.4057 | -14.0181 | 1054.284 | 17.3378 | -80.0665 | 16.4909 | 16.4909 | 92.1811 | 272.1811 | 79.9261 | 54.6388 | 54.6388 | 129.9279 | 184.5667 | 0.21768 | 21.77% | 83.4611 | 18.168 | 12.7176 | 132.0961 | 132.0961 | 9.628% | 11.25% | 11.25% | 80% | 9% | 7.5118 | 4.3829 | 4.3829 | 32.9235 | 16.6117 | 24.92% | 24.92%
8 | 230 | 18 | 5515 | 19 | 21.6 | 31.72 | 86.11 | 117.83 | 86.11 | 43.06 | 230 | 5515 | 1140 | 226.8493 | 13.4057 | -14.0181 | 1114.284 | 18.3378 | -95.0665 | 6.322 | 6.322 | 102.8693 | 282.8693 | 94.5121 | 0 | 0 | 73.4995 | 73.4995 | -0.70966 | 0% | 33.2365 | 0 | 0 | 161.0486 | 161.0486 | 0% | 11.29% | 0% | 80% | 0% | 0 | 4.6364 | 4.6364 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5516 | 20 | 19.7 | 0 | 24.11 | 24.11 | 24.11 | 12.06 | 230 | 5516 | 1200 | 226.8493 | 13.4057 | -14.0181 | 1174.284 | 19.3378 | -110.0665 | -3.4182 | 0 | 109.7882 | 289.7882 | 103.8503 | 0 | 0 | 20.5792 | 20.5792 | -4.8045 | 0% | 9.3059 | 0 | 0 | 144.9111 | 144.9111 | 0% | 11.36% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5517 | 21 | 18.1 | 0 | 0 | 0 | 0 | 0 | 230 | 5517 | 1260 | 226.8493 | 13.4057 | -14.0181 | 1234.284 | 20.3378 | -125.0665 | -12.3442 | 0 | 109.7882 | 289.7882 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.5331 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3303 | 5.3303 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5518 | 22 | 17.1 | 0 | 0 | 0 | 0 | 0 | 230 | 5518 | 1320 | 226.8493 | 13.4057 | -14.0181 | 1294.284 | 21.3378 | -140.0665 | -19.9905 | 0 | 109.7882 | 289.7882 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8095 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5519 | 23 | 16.5 | 0 | 0 | 0 | 0 | 0 | 230 | 5519 | 1380 | 226.8493 | 13.4057 | -14.0181 | 1354.284 | 22.3378 | -155.0665 | -25.7937 | 0 | 109.7882 | 289.7882 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9199 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
8 | 230 | 18 | 5520 | 24 | 16.2 | 0 | 0 | 0 | 0 | 0 | 230 | 5520 | 1440 | 226.8493 | 13.4057 | -14.0181 | 1414.284 | 23.3378 | -170.0665 | -29.159 | 0 | 109.7882 | 289.7882 | 103.8503 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5731 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5521 | 1 | 14.6 | 0 | 0 | 0 | 0 | 0 | 231 | 5521 | 60 | 227.8356 | 13.0937 | -13.9896 | 34.284 | 0.33824 | 174.9264 | -29.9553 | 0 | 109.3177 | 70.6823 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9158 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5522 | 2 | 14.3 | 0 | 0 | 0 | 0 | 0 | 231 | 5522 | 120 | 227.8356 | 13.0937 | -13.9896 | 94.284 | 1.3382 | 159.9264 | -27.4786 | 0 | 109.3177 | 70.6823 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6266 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5523 | 3 | 14.3 | 0 | 0 | 0 | 0 | 0 | 231 | 5523 | 180 | 227.8356 | 13.0937 | -13.9896 | 154.284 | 2.3382 | 144.9264 | -22.3842 | 0 | 109.3177 | 70.6823 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8802 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5524 | 4 | 13.4 | 0 | 0 | 0 | 0 | 0 | 231 | 5524 | 240 | 227.8356 | 13.0937 | -13.9896 | 214.284 | 3.3382 | 129.9264 | -15.2489 | 0 | 109.3177 | 70.6823 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2518 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5525 | 5 | 12.8 | 0 | 0 | 0 | 0 | 0 | 231 | 5525 | 300 | 227.8356 | 13.0937 | -13.9896 | 274.284 | 4.3382 | 114.9264 | -6.6633 | 0 | 109.3177 | 70.6823 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.1617 | 7.1617 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5526 | 6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 231 | 5526 | 360 | 227.8356 | 13.0937 | -13.9896 | 334.284 | 5.3382 | 99.9264 | 2.8718 | 2.8718 | 106.1315 | 73.8685 | 99.2528 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 20.9212 | 20.9212 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5527 | 7 | 12.9 | 16.11 | 23 | 39.11 | 23 | 11.5 | 231 | 5527 | 420 | 227.8356 | 13.0937 | -13.9896 | 394.284 | 6.3382 | 84.9264 | 12.9484 | 12.9484 | 95.439 | 84.561 | 84.6567 | 6.6952 | 6.6952 | 19.6317 | 26.327 | -4.1613 | 0% | 11.9051 | 0 | 0 | 195.2349 | 195.2349 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5528 | 8 | 14.8 | 107.36 | 66.61 | 173.97 | 66.61 | 33.31 | 231 | 5528 | 480 | 227.8356 | 13.0937 | -13.9896 | 454.284 | 7.3382 | 69.9264 | 23.2051 | 23.2051 | 84.4766 | 95.5234 | 70.0517 | 92.9591 | 92.9591 | 56.8552 | 149.8143 | -0.039603 | 0% | 67.746 | 0 | 0 | 173.8355 | 173.8355 | 0% | 11.54% | 11.54% | 80% | 9.23% | 6.2532 | 6.0631 | 6 | 37.5192 | 13.8284 | 21.58% | 21.58%
8 | 231 | 19 | 5529 | 9 | 18.7 | 243.39 | 96.17 | 339.56 | 96.17 | 48.09 | 231 | 5529 | 540 | 227.8356 | 13.0937 | -13.9896 | 514.284 | 8.3382 | 54.9264 | 33.2555 | 33.2555 | 72.4106 | 107.5894 | 55.4971 | 251.4118 | 251.4118 | 82.0862 | 333.4981 | 0.45128 | 45.13% | 150.8078 | 68.0572 | 47.64 | 188.4504 | 188.4504 | 25.28% | 11.39% | 11.39% | 85% | 9.678% | 14.5945 | 5.2053 | 5.2053 | 75.9684 | 32.2744 | 40.31% | 40.31%
8 | 231 | 19 | 5530 | 10 | 20.9 | 371.89 | 120.56 | 492.45 | 120.56 | 60.28 | 231 | 5530 | 600 | 227.8356 | 13.0937 | -13.9896 | 574.284 | 9.3382 | 39.9264 | 42.5788 | 42.5788 | 58.0968 | 121.9032 | 41.0967 | 414.2112 | 414.2112 | 102.9044 | 517.1156 | 0.5859 | 58.59% | 233.8397 | 137.0071 | 95.9049 | 194.214 | 194.214 | 49.38% | 11.34% | 11.34% | 90% | 10.2% | 23.8615 | 4.7684 | 4.7684 | 113.7799 | 52.7675 | 58.58% | 58.58%
8 | 231 | 19 | 5531 | 11 | 22.1 | 471.44 | 159.67 | 631.11 | 159.67 | 79.84 | 231 | 5531 | 660 | 227.8356 | 13.0937 | -13.9896 | 634.284 | 10.3382 | 24.9264 | 50.3515 | 50.3515 | 40.0409 | 139.9591 | 27.1423 | 544.8543 | 544.8543 | 136.2869 | 681.1412 | 0.64226 | 64.23% | 308.012 | 197.8251 | 138.4776 | 190.5192 | 190.5192 | 72.68% | 11.34% | 11.34% | 90% | 10.2% | 31.4309 | 4.5443 | 4.5443 | 142.832 | 69.5067 | 74.97% | 74.97%
8 | 231 | 19 | 5532 | 12 | 23 | 559.17 | 188 | 747.17 | 188 | 94 | 231 | 5532 | 720 | 227.8356 | 13.0937 | -13.9896 | 694.284 | 11.3382 | 9.9264 | 55.2977 | 55.2977 | 17.1527 | 162.8473 | 14.9864 | 657.0212 | 657.0212 | 160.468 | 817.4892 | 0.67163 | 67.16% | 369.6686 | 248.2788 | 173.7952 | 180.0971 | 180.0971 | 96.5% | 11.35% | 11.35% | 95% | 10.79% | 39.8767 | 4.3829 | 4.3829 | 174.7755 | 88.1837 | 97.05% | 97.05%
8 | 231 | 19 | 5533 | 13 | 24.1 | 464.17 | 242.14 | 706.31 | 242.14 | 121.07 | 231 | 5533 | 780 | 227.8356 | 13.0937 | -13.9896 | 754.284 | 12.3382 | -5.0736 | 56.0467 | 56.0467 | 8.8717 | 188.8717 | 12.3802 | 546.5705 | 546.5705 | 206.6794 | 753.2499 | 0.66348 | 66.35% | 340.6196 | 225.9946 | 158.1962 | 272.8959 | 272.8959 | 57.97% | 11.34% | 11.34% | 90% | 10.21% | 34.7681 | 4.1933 | 4.1933 | 145.7936 | 76.8866 | 53.42% | 53.42%
8 | 231 | 19 | 5534 | 14 | 24.6 | 414.5 | 177.36 | 591.86 | 177.36 | 88.68 | 231 | 5534 | 840 | 227.8356 | 13.0937 | -13.9896 | 814.284 | 13.3382 | -20.0736 | 52.334 | 52.334 | 33.1676 | 213.1676 | 22.8653 | 482.4856 | 482.4856 | 151.3862 | 633.8718 | 0.63871 | 63.87% | 286.6368 | 183.0769 | 128.1538 | 197.8258 | 197.8258 | 64.78% | 11.31% | 11.31% | 90% | 10.18% | 29.1767 | 4.1099 | 4.1099 | 119.9144 | 64.5216 | 60.62% | 60.62%
8 | 231 | 19 | 5535 | 15 | 25.1 | 411.33 | 133.06 | 544.39 | 133.06 | 66.53 | 231 | 5535 | 900 | 227.8356 | 13.0937 | -13.9896 | 874.284 | 14.3382 | -35.0736 | 45.3151 | 45.3151 | 52.7411 | 232.7411 | 36.5073 | 465.0161 | 465.0161 | 113.5738 | 578.59 | 0.62476 | 62.48% | 261.6384 | 163.4611 | 114.4228 | 272.6216 | 272.6216 | 41.97% | 11.29% | 11.29% | 90% | 10.16% | 26.5848 | 4.0283 | 4.0283 | 107.0921 | 58.79 | 39.28% | 39.28%
8 | 231 | 19 | 5536 | 16 | 23.9 | 407.92 | 91.72 | 499.64 | 91.72 | 45.86 | 231 | 5536 | 960 | 227.8356 | 13.0937 | -13.9896 | 934.284 | 15.3382 | -50.0736 | 36.3831 | 36.3831 | 68.0922 | 248.0922 | 50.8137 | 434.5082 | 434.5082 | 78.2879 | 512.7961 | 0.59675 | 59.68% | 231.8864 | 138.3789 | 96.8652 | 174.9062 | 174.9062 | 55.38% | 11.29% | 11.29% | 90% | 10.16% | 23.5628 | 4.2272 | 4.2272 | 99.6036 | 52.107 | 56.95% | 56.95%
8 | 231 | 19 | 5537 | 17 | 22.3 | 317.5 | 95.78 | 413.28 | 95.78 | 47.89 | 231 | 5537 | 1020 | 227.8356 | 13.0937 | -13.9896 | 994.284 | 16.3382 | -65.0736 | 26.5004 | 26.5004 | 80.7414 | 260.7414 | 65.334 | 296.9532 | 296.9532 | 81.7533 | 378.7065 | 0.51425 | 51.42% | 171.2511 | 88.0657 | 61.646 | 149.9333 | 149.9333 | 41.12% | 11.3% | 11.3% | 85% | 9.604% | 16.4468 | 4.508 | 4.508 | 74.1414 | 36.3706 | 49.45% | 49.45%
8 | 231 | 19 | 5538 | 18 | 22.3 | 195.33 | 89.17 | 284.5 | 89.17 | 44.59 | 231 | 5538 | 1080 | 227.8356 | 13.0937 | -13.9896 | 1054.284 | 17.3382 | -80.0736 | 16.2642 | 16.2642 | 91.9576 | 271.9576 | 79.9301 | 121.9466 | 121.9466 | 76.1114 | 198.058 | 0.24997 | 25% | 89.5618 | 22.3875 | 15.6712 | 138.3434 | 138.3434 | 11.33% | 11.28% | 11.28% | 80% | 9.021% | 8.0791 | 4.508 | 4.508 | 36.4202 | 17.8662 | 26.33% | 26.33%
8 | 231 | 19 | 5539 | 19 | 21 | 83.19 | 48.75 | 131.94 | 48.75 | 24.38 | 231 | 5539 | 1140 | 227.8356 | 13.0937 | -13.9896 | 1114.284 | 18.3382 | -95.0736 | 6.0903 | 6.0903 | 102.659 | 282.659 | 94.5349 | 0 | 0 | 41.6107 | 41.6107 | -1.9011 | 0% | 18.8164 | 0 | 0 | 164.7894 | 164.7894 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7493 | 4.7493 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5540 | 20 | 18.7 | 0 | 15.06 | 15.06 | 15.06 | 7.53 | 231 | 5540 | 1200 | 227.8356 | 13.0937 | -13.9896 | 1174.284 | 19.3382 | -110.0736 | -3.6611 | 0 | 109.3177 | 289.3177 | 103.5277 | 0 | 0 | 12.8545 | 12.8545 | -8.3469 | 0% | 5.8128 | 0 | 0 | 144.1525 | 144.1525 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2053 | 5.2053 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5541 | 21 | 18.2 | 0 | 0 | 0 | 0 | 0 | 231 | 5541 | 1260 | 227.8356 | 13.0937 | -13.9896 | 1234.284 | 20.3382 | -125.0736 | -12.6036 | 0 | 109.3177 | 289.3177 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.5851 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3093 | 5.3093 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5542 | 22 | 17.1 | 0 | 0 | 0 | 0 | 0 | 231 | 5542 | 1320 | 227.8356 | 13.0937 | -13.9896 | 1294.284 | 21.3382 | -140.0736 | -20.2694 | 0 | 109.3177 | 289.3177 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.345 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5543 | 23 | 17.2 | 0 | 0 | 0 | 0 | 0 | 231 | 5543 | 1380 | 227.8356 | 13.0937 | -13.9896 | 1354.284 | 22.3382 | -155.0736 | -26.0914 | 0 | 109.3177 | 289.3177 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4462 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
8 | 231 | 19 | 5544 | 24 | 16.1 | 0 | 0 | 0 | 0 | 0 | 231 | 5544 | 1440 | 227.8356 | 13.0937 | -13.9896 | 1414.284 | 23.3382 | -170.0736 | -29.469 | 0 | 109.3177 | 289.3177 | 103.5277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3762 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5545 | 1 | 16.1 | 0 | 0 | 0 | 0 | 0 | 232 | 5545 | 60 | 228.8219 | 12.7781 | -13.9492 | 34.284 | 0.33891 | 174.9163 | -30.2694 | 0 | 108.8424 | 71.1576 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.217 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5546 | 2 | 15.9 | 0 | 0 | 0 | 0 | 0 | 232 | 5546 | 120 | 228.8219 | 12.7781 | -13.9492 | 94.284 | 1.3389 | 159.9163 | -27.7803 | 0 | 108.8424 | 71.1576 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8107 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5547 | 3 | 15.6 | 0 | 0 | 0 | 0 | 0 | 232 | 5547 | 180 | 228.8219 | 12.7781 | -13.9492 | 154.284 | 2.3389 | 144.9163 | -22.6656 | 0 | 108.8424 | 71.1576 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5567 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5548 | 4 | 15.5 | 0 | 0 | 0 | 0 | 0 | 232 | 5548 | 240 | 228.8219 | 12.7781 | -13.9492 | 214.284 | 3.3389 | 129.9163 | -15.5082 | 0 | 108.8424 | 71.1576 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7091 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5549 | 5 | 14.8 | 0 | 0 | 0 | 0 | 0 | 232 | 5549 | 300 | 228.8219 | 12.7781 | -13.9492 | 274.284 | 4.3389 | 114.9163 | -6.9034 | 0 | 108.8424 | 71.1576 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.8409 | 8.8409 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5550 | 6 | 13.9 | 0 | 0 | 0 | 0 | 0 | 232 | 5550 | 360 | 228.8219 | 12.7781 | -13.9492 | 334.284 | 5.3389 | 99.9163 | 2.6457 | 2.6457 | 105.9109 | 74.0891 | 99.265 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 20.5452 | 20.5452 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5551 | 7 | 14 | 15.5 | 24.03 | 39.53 | 24.03 | 12.02 | 232 | 5551 | 420 | 228.8219 | 12.7781 | -13.9492 | 394.284 | 6.3389 | 84.9163 | 12.7298 | 12.7298 | 95.2053 | 84.7947 | 84.6501 | 6.5585 | 6.5585 | 20.5109 | 27.0694 | -3.9322 | 0% | 12.2408 | 0 | 0 | 194.438 | 194.438 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5552 | 8 | 16.1 | 104.72 | 62.08 | 166.8 | 62.08 | 31.04 | 232 | 5552 | 480 | 228.8219 | 12.7781 | -13.9492 | 454.284 | 7.3389 | 69.9163 | 22.9864 | 22.9864 | 84.2291 | 95.7709 | 70.0263 | 91.6007 | 91.6007 | 52.9886 | 144.5893 | -0.049751 | 0% | 65.3833 | 0 | 0 | 172.4982 | 172.4982 | 0% | 11.49% | 11.49% | 80% | 9.194% | 6.0114 | 5.7653 | 5.7653 | 34.6575 | 13.2936 | 20.09% | 20.09%
8 | 232 | 20 | 5553 | 9 | 18 | 256.06 | 84.03 | 340.09 | 84.03 | 42.02 | 232 | 5553 | 540 | 228.8219 | 12.7781 | -13.9492 | 514.284 | 8.3389 | 54.9163 | 33.0276 | 33.0276 | 72.1496 | 107.8504 | 55.4496 | 266.4362 | 266.4362 | 71.7241 | 338.1603 | 0.45154 | 45.15% | 152.9161 | 69.0485 | 48.334 | 184.5323 | 184.5323 | 26.19% | 11.4% | 11.4% | 85% | 9.692% | 14.8212 | 5.3514 | 5.3514 | 79.3142 | 32.7758 | 42.98% | 42.98%
8 | 232 | 20 | 5554 | 10 | 19.7 | 396.94 | 102.08 | 499.02 | 102.08 | 51.04 | 232 | 5554 | 600 | 228.8219 | 12.7781 | -13.9492 | 574.284 | 9.3389 | 39.9163 | 42.3311 | 42.3311 | 57.8313 | 122.1687 | 41.0192 | 444.7295 | 444.7295 | 87.1307 | 531.8602 | 0.58699 | 58.7% | 240.5072 | 141.1756 | 98.8229 | 190.0651 | 190.0651 | 51.99% | 11.36% | 11.36% | 90% | 10.22% | 24.5817 | 5.0025 | 5.0025 | 122.9694 | 54.3603 | 64.7% | 64.7%
8 | 232 | 20 | 5555 | 11 | 20.2 | 526.33 | 113.94 | 640.27 | 113.94 | 56.97 | 232 | 5555 | 660 | 228.8219 | 12.7781 | -13.9492 | 634.284 | 10.3389 | 24.9163 | 50.0742 | 50.0742 | 39.8048 | 140.1952 | 27.0135 | 611.4508 | 611.4508 | 97.2539 | 708.7047 | 0.6427 | 64.27% | 320.4763 | 205.9685 | 144.178 | 185.6767 | 185.6767 | 77.65% | 11.35% | 11.35% | 90% | 10.22% | 32.7395 | 4.9037 | 4.9037 | 160.5448 | 72.4005 | 86.46% | 86.46%
8 | 232 | 20 | 5556 | 12 | 21.4 | 603.47 | 125.56 | 729.03 | 125.56 | 62.78 | 232 | 5556 | 720 | 228.8219 | 12.7781 | -13.9492 | 694.284 | 11.3389 | 9.9163 | 54.9909 | 54.9909 | 17.0218 | 162.9782 | 14.7459 | 712.5161 | 712.5161 | 107.1722 | 819.6883 | 0.66774 | 66.77% | 370.663 | 247.5072 | 173.255 | 174.8926 | 174.8926 | 99.06% | 11.35% | 11.35% | 95% | 10.79% | 39.9791 | 4.6738 | 4.6738 | 186.8536 | 88.4103 | 106.8% | 106.8%
8 | 232 | 20 | 5557 | 13 | 22.1 | 638.89 | 135.5 | 774.39 | 135.5 | 67.75 | 232 | 5557 | 780 | 228.8219 | 12.7781 | -13.9492 | 754.284 | 12.3389 | -5.0837 | 55.7319 | 55.7319 | 8.8284 | 188.8284 | 12.0975 | 755.9209 | 755.9209 | 115.6565 | 871.5773 | 0.6776 | 67.76% | 394.1273 | 267.0617 | 186.9432 | 174.0614 | 174.0614 | 107.4% | 11.36% | 11.36% | 95% | 10.79% | 42.5352 | 4.5443 | 4.5443 | 193.2934 | 94.0628 | 111% | 111%
8 | 232 | 20 | 5558 | 14 | 23.2 | 624.86 | 137.78 | 762.64 | 137.78 | 68.89 | 232 | 5558 | 840 | 228.8219 | 12.7781 | -13.9492 | 814.284 | 13.3389 | -20.0837 | 52.0388 | 52.0388 | 32.985 | 212.985 | 22.7274 | 731.0018 | 731.0018 | 117.6026 | 848.6044 | 0.67699 | 67.7% | 383.7389 | 259.7867 | 181.8507 | 278.4421 | 278.4421 | 65.31% | 11.36% | 11.36% | 95% | 10.79% | 41.4151 | 4.3478 | 4.3478 | 180.0647 | 91.5859 | 64.67% | 64.67%
8 | 232 | 20 | 5559 | 15 | 24 | 584.72 | 136.72 | 721.44 | 136.72 | 68.36 | 232 | 5559 | 900 | 228.8219 | 12.7781 | -13.9492 | 874.284 | 14.3389 | -35.0837 | 45.0478 | 45.0478 | 52.5027 | 232.5027 | 36.4356 | 664.7228 | 664.7228 | 116.6978 | 781.4206 | 0.66827 | 66.83% | 353.3584 | 236.1395 | 165.2977 | 270.7615 | 270.7615 | 61.05% | 11.35% | 11.35% | 90% | 10.21% | 36.0889 | 4.2102 | 4.2102 | 151.9416 | 79.8074 | 56.12% | 56.12%
8 | 232 | 20 | 5560 | 16 | 22.8 | 496.81 | 117.56 | 614.37 | 117.56 | 58.78 | 232 | 5560 | 960 | 228.8219 | 12.7781 | -13.9492 | 934.284 | 15.3389 | -50.0837 | 36.1372 | 36.1372 | 67.8466 | 247.8466 | 50.7772 | 532.7123 | 532.7123 | 100.3437 | 633.0561 | 0.63238 | 63.24% | 286.268 | 181.0292 | 126.7204 | 162.2369 | 162.2369 | 78.11% | 11.33% | 11.33% | 90% | 10.19% | 29.1812 | 4.4183 | 4.4183 | 128.9307 | 64.5316 | 79.47% | 79.47%
8 | 232 | 20 | 5561 | 17 | 23.1 | 365.14 | 108.61 | 473.75 | 108.61 | 54.31 | 232 | 5561 | 1020 | 228.8219 | 12.7781 | -13.9492 | 994.284 | 16.3389 | -65.0837 | 26.2661 | 26.2661 | 80.505 | 260.505 | 65.3216 | 344.4995 | 344.4995 | 92.7044 | 437.2039 | 0.55698 | 55.7% | 197.7036 | 110.1167 | 77.0817 | 266.424 | 266.424 | 28.93% | 11.29% | 11.29% | 85% | 9.597% | 18.9729 | 4.3653 | 4.3653 | 82.8225 | 41.9568 | 31.09% | 31.09%
8 | 232 | 20 | 5562 | 18 | 22.2 | 205.61 | 98.28 | 303.89 | 98.28 | 49.14 | 232 | 5562 | 1080 | 228.8219 | 12.7781 | -13.9492 | 1054.284 | 17.3389 | -80.0837 | 16.0326 | 16.0326 | 91.7342 | 271.7342 | 79.9373 | 130.0772 | 130.0772 | 83.8872 | 213.9644 | 0.29014 | 29.01% | 96.7547 | 28.0724 | 19.6507 | 138.2436 | 138.2436 | 14.21% | 11.28% | 11.28% | 80% | 9.025% | 8.732 | 4.5261 | 4.5261 | 39.5218 | 19.31 | 28.59% | 28.59%
8 | 232 | 20 | 5563 | 19 | 21.1 | 79.17 | 60.28 | 139.45 | 60.28 | 30.14 | 232 | 5563 | 1140 | 228.8219 | 12.7781 | -13.9492 | 1114.284 | 18.3389 | -95.0837 | 5.8539 | 5.8539 | 102.4486 | 282.4486 | 94.5605 | 0 | 0 | 51.4522 | 51.4522 | -1.3795 | 0% | 23.2667 | 0 | 0 | 164.3217 | 164.3217 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7303 | 4.7303 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5564 | 20 | 18.2 | 0 | 16.06 | 16.06 | 16.06 | 8.03 | 232 | 5564 | 1200 | 228.8219 | 12.7781 | -13.9492 | 1174.284 | 19.3389 | -110.0837 | -3.9088 | 0 | 108.8424 | 288.8424 | 103.2012 | 0 | 0 | 13.7081 | 13.7081 | -7.8581 | 0% | 6.1988 | 0 | 0 | 142.8351 | 142.8351 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3093 | 5.3093 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5565 | 21 | 16.5 | 0 | 0 | 0 | 0 | 0 | 232 | 5565 | 1260 | 228.8219 | 12.7781 | -13.9492 | 1234.284 | 20.3389 | -125.0837 | -12.8676 | 0 | 108.8424 | 288.8424 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7159 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5566 | 22 | 14.5 | 0 | 0 | 0 | 0 | 0 | 232 | 5566 | 1320 | 228.8219 | 12.7781 | -13.9492 | 1294.284 | 21.3389 | -140.0837 | -20.5528 | 0 | 108.8424 | 288.8424 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7889 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5567 | 23 | 13.5 | 0 | 0 | 0 | 0 | 0 | 232 | 5567 | 1380 | 228.8219 | 12.7781 | -13.9492 | 1354.284 | 22.3389 | -155.0837 | -26.3934 | 0 | 108.8424 | 288.8424 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6017 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
8 | 232 | 20 | 5568 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 232 | 5568 | 1440 | 228.8219 | 12.7781 | -13.9492 | 1414.284 | 23.3389 | -170.0837 | -29.783 | 0 | 108.8424 | 288.8424 | 103.2012 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6526 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5569 | 1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 233 | 5569 | 60 | 229.8082 | 12.4589 | -13.8969 | 34.284 | 0.33978 | 174.9032 | -30.587 | 0 | 108.3625 | 71.6375 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1277 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5570 | 2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 233 | 5570 | 120 | 229.8082 | 12.4589 | -13.8969 | 94.284 | 1.3398 | 159.9032 | -28.0846 | 0 | 108.3625 | 71.6375 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8435 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5571 | 3 | 11.1 | 0 | 0 | 0 | 0 | 0 | 233 | 5571 | 180 | 229.8082 | 12.4589 | -13.8969 | 154.284 | 2.3398 | 144.9032 | -22.9488 | 0 | 108.3625 | 71.6375 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6262 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5572 | 4 | 10.5 | 0 | 0 | 0 | 0 | 0 | 233 | 5572 | 240 | 229.8082 | 12.4589 | -13.8969 | 214.284 | 3.3398 | 129.9032 | -15.7688 | 0 | 108.3625 | 71.6375 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5406 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5573 | 5 | 9.9 | 0 | 0 | 0 | 0 | 0 | 233 | 5573 | 300 | 229.8082 | 12.4589 | -13.8969 | 274.284 | 4.3398 | 114.9032 | -7.1444 | 0 | 108.3625 | 71.6375 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.3185 | 2.3185 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5574 | 6 | 9.9 | 0 | 0 | 0 | 0 | 0 | 233 | 5574 | 360 | 229.8082 | 12.4589 | -13.8969 | 334.284 | 5.3398 | 99.9032 | 2.4188 | 2.4188 | 105.6857 | 74.3143 | 99.2742 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 14.8369 | 14.8369 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5575 | 7 | 10.2 | 10.61 | 19.86 | 30.47 | 19.86 | 9.93 | 233 | 5575 | 420 | 229.8082 | 12.4589 | -13.8969 | 394.284 | 6.3398 | 84.9032 | 12.5104 | 12.5104 | 94.9673 | 85.0327 | 84.6409 | 4.5747 | 4.5747 | 16.9516 | 21.5263 | -5.559 | 0% | 9.7342 | 0 | 0 | 186.9253 | 186.9253 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5576 | 8 | 12.3 | 85.14 | 65.5 | 150.64 | 65.5 | 32.75 | 233 | 5576 | 480 | 229.8082 | 12.4589 | -13.8969 | 454.284 | 7.3398 | 69.9032 | 22.7667 | 22.7667 | 83.9773 | 96.0227 | 69.9983 | 75.2543 | 75.2543 | 55.9077 | 131.162 | -0.20317 | 0% | 59.3115 | 0 | 0 | 164.1186 | 164.1186 | 0% | 11.64% | 11.64% | 80% | 9.308% | 5.5208 | 6.669 | 6 | 33.125 | 12.2088 | 20.18% | 20.18%
8 | 233 | 21 | 5577 | 9 | 16.8 | 226.39 | 102.64 | 329.03 | 102.64 | 51.32 | 233 | 5577 | 540 | 229.8082 | 12.4589 | -13.8969 | 514.284 | 8.3398 | 54.9032 | 32.7985 | 32.7985 | 71.8845 | 108.1155 | 55.4001 | 237.3221 | 237.3221 | 87.6087 | 324.9308 | 0.42894 | 42.89% | 146.9337 | 63.0254 | 44.1178 | 180.2928 | 180.2928 | 24.47% | 11.44% | 11.44% | 85% | 9.72% | 14.2824 | 5.6099 | 5.6099 | 80.1223 | 31.5842 | 44.44% | 44.44%
8 | 233 | 21 | 5578 | 10 | 18.6 | 298.25 | 136.39 | 434.64 | 136.39 | 68.2 | 233 | 5578 | 600 | 229.8082 | 12.4589 | -13.8969 | 574.284 | 9.3398 | 39.9032 | 42.0817 | 42.0817 | 57.5618 | 122.4382 | 40.9399 | 336.1693 | 336.1693 | 116.4161 | 452.5855 | 0.5436 | 54.36% | 204.6591 | 111.2533 | 77.8773 | 183.1829 | 183.1829 | 42.51% | 11.38% | 11.38% | 85% | 9.672% | 19.7945 | 5.2259 | 5.2259 | 103.4449 | 43.7738 | 56.47% | 56.47%
8 | 233 | 21 | 5579 | 11 | 20.6 | 362 | 181.81 | 543.81 | 181.81 | 90.91 | 233 | 5579 | 660 | 229.8082 | 12.4589 | -13.8969 | 634.284 | 10.3398 | 24.9032 | 49.7946 | 49.7946 | 39.5648 | 140.4352 | 26.8835 | 422.7619 | 422.7619 | 155.1845 | 577.9465 | 0.60772 | 60.77% | 261.3474 | 158.8261 | 111.1782 | 180.1547 | 180.1547 | 61.71% | 11.34% | 11.34% | 90% | 10.21% | 26.6841 | 4.8259 | 4.8259 | 128.7759 | 59.0095 | 71.48% | 71.48%
8 | 233 | 21 | 5580 | 12 | 21.9 | 387.5 | 186.33 | 573.83 | 186.33 | 93.17 | 233 | 5580 | 720 | 229.8082 | 12.4589 | -13.8969 | 694.284 | 11.3398 | 9.9032 | 54.6811 | 54.6811 | 16.8867 | 163.1133 | 14.5035 | 459.7743 | 459.7743 | 159.0426 | 618.8169 | 0.62527 | 62.53% | 279.829 | 174.9693 | 122.4785 | 167.7645 | 167.7645 | 73.01% | 11.33% | 11.33% | 90% | 10.2% | 28.5419 | 4.581 | 4.581 | 130.7491 | 63.1178 | 77.94% | 77.94%
8 | 233 | 21 | 5581 | 13 | 22.4 | 470 | 210.33 | 680.33 | 210.33 | 105.17 | 233 | 5581 | 780 | 229.8082 | 12.4589 | -13.8969 | 754.284 | 12.3398 | -5.0968 | 55.4131 | 55.4131 | 8.7901 | 188.7901 | 11.8145 | 558.8026 | 558.8026 | 179.5279 | 738.3305 | 0.65567 | 65.57% | 333.873 | 218.9118 | 153.2383 | 168.7162 | 168.7162 | 90.83% | 11.34% | 11.34% | 90% | 10.21% | 34.0867 | 4.4899 | 4.4899 | 153.0451 | 75.3797 | 90.71% | 90.71%
8 | 233 | 21 | 5582 | 14 | 23.7 | 448.39 | 185.06 | 633.45 | 185.06 | 92.53 | 233 | 5582 | 840 | 229.8082 | 12.4589 | -13.8969 | 814.284 | 13.3398 | -20.0968 | 51.7388 | 51.7388 | 32.807 | 212.807 | 22.594 | 527.2271 | 527.2271 | 157.9586 | 685.1857 | 0.64827 | 64.83% | 309.841 | 200.8599 | 140.6019 | 280.8658 | 280.8658 | 50.06% | 11.33% | 11.33% | 90% | 10.2% | 31.5907 | 4.2613 | 4.2613 | 134.6166 | 69.86 | 47.93% | 47.93%
8 | 233 | 21 | 5583 | 15 | 23.8 | 383.83 | 201.81 | 585.64 | 201.81 | 100.91 | 233 | 5583 | 900 | 229.8082 | 12.4589 | -13.8969 | 874.284 | 14.3398 | -35.0968 | 44.7753 | 44.7753 | 52.2671 | 232.2671 | 36.3681 | 438.8137 | 438.8137 | 172.2556 | 611.0693 | 0.62973 | 62.97% | 276.3255 | 174.0107 | 121.8075 | 292.1848 | 292.1848 | 41.69% | 11.31% | 11.31% | 90% | 10.18% | 28.1334 | 4.2442 | 4.2442 | 119.4033 | 62.2146 | 40.87% | 40.87%
8 | 233 | 21 | 5584 | 16 | 23.8 | 222.56 | 182.56 | 405.12 | 182.56 | 91.28 | 233 | 5584 | 960 | 229.8082 | 12.4589 | -13.8969 | 934.284 | 15.3398 | -50.0968 | 35.8862 | 35.8862 | 67.6023 | 247.6023 | 50.7446 | 240.2539 | 240.2539 | 155.8247 | 396.0786 | 0.53514 | 53.51% | 179.1067 | 95.8468 | 67.0928 | 281.4811 | 281.4811 | 23.84% | 11.27% | 11.27% | 85% | 9.577% | 17.1538 | 4.2442 | 4.2442 | 72.804 | 37.9342 | 25.86% | 25.86%
8 | 233 | 21 | 5585 | 17 | 23.6 | 173.19 | 160.56 | 333.75 | 160.56 | 80.28 | 233 | 5585 | 1020 | 229.8082 | 12.4589 | -13.8969 | 994.284 | 16.3398 | -65.0968 | 26.0268 | 26.0268 | 80.2692 | 260.2692 | 65.3126 | 164.8522 | 164.8522 | 137.0465 | 301.8987 | 0.44984 | 44.98% | 136.5186 | 61.4114 | 42.988 | 278.8158 | 278.8158 | 15.42% | 11.25% | 11.25% | 85% | 9.565% | 13.0585 | 4.2784 | 4.2784 | 55.87 | 28.8777 | 20.04% | 20.04%
8 | 233 | 21 | 5586 | 18 | 23.2 | 80.5 | 113.94 | 194.44 | 113.94 | 56.97 | 233 | 5586 | 1080 | 229.8082 | 12.4589 | -13.8969 | 1054.284 | 17.3398 | -80.0968 | 15.7962 | 15.7962 | 91.5108 | 271.5108 | 79.9477 | 51.6173 | 51.6173 | 97.2539 | 148.8712 | 0.079999 | 8% | 67.3195 | 5.3855 | 3.7698 | 265.2478 | 265.2478 | 1.421% | 11.24% | 11.24% | 80% | 8.99% | 6.052 | 4.3478 | 4.3478 | 26.3128 | 13.3834 | 9.92% | 9.92%
8 | 233 | 21 | 5587 | 19 | 21.7 | 17.5 | 54.67 | 72.17 | 54.67 | 27.34 | 233 | 5587 | 1140 | 229.8082 | 12.4589 | -13.8969 | 1114.284 | 18.3398 | -95.0968 | 5.6127 | 5.6127 | 102.238 | 282.238 | 94.5892 | 0 | 0 | 46.6638 | 46.6638 | -1.5755 | 0% | 21.1014 | 0 | 0 | 159.8366 | 159.8366 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.6179 | 4.6179 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5588 | 20 | 18.4 | 0 | 13.61 | 13.61 | 13.61 | 6.81 | 233 | 5588 | 1200 | 229.8082 | 12.4589 | -13.8969 | 1174.284 | 19.3398 | -110.0968 | -4.161 | 0 | 108.3625 | 288.3625 | 102.8711 | 0 | 0 | 11.6169 | 11.6169 | -9.3792 | 0% | 5.2531 | 0 | 0 | 143.8975 | 143.8975 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5589 | 21 | 15.3 | 0 | 0 | 0 | 0 | 0 | 233 | 5589 | 1260 | 229.8082 | 12.4589 | -13.8969 | 1234.284 | 20.3398 | -125.0968 | -13.1361 | 0 | 108.3625 | 288.3625 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.26 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5590 | 22 | 13.7 | 0 | 0 | 0 | 0 | 0 | 233 | 5590 | 1320 | 229.8082 | 12.4589 | -13.8969 | 1294.284 | 21.3398 | -140.0968 | -20.8406 | 0 | 108.3625 | 288.3625 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3705 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5591 | 23 | 12.5 | 0 | 0 | 0 | 0 | 0 | 233 | 5591 | 1380 | 229.8082 | 12.4589 | -13.8969 | 1354.284 | 22.3398 | -155.0968 | -26.6997 | 0 | 108.3625 | 288.3625 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4579 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
8 | 233 | 21 | 5592 | 24 | 11.6 | 0 | 0 | 0 | 0 | 0 | 233 | 5592 | 1440 | 229.8082 | 12.4589 | -13.8969 | 1414.284 | 23.3398 | -170.0968 | -30.101 | 0 | 108.3625 | 288.3625 | 102.8711 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0882 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5593 | 1 | 10.9 | 0 | 0 | 0 | 0 | 0 | 234 | 5593 | 60 | 230.7945 | 12.1361 | -13.8331 | 34.284 | 0.34085 | 174.8873 | -30.9078 | 0 | 107.8779 | 72.1221 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8545 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5594 | 2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 234 | 5594 | 120 | 230.7945 | 12.1361 | -13.8331 | 94.284 | 1.3408 | 159.8873 | -28.3915 | 0 | 107.8779 | 72.1221 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3914 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5595 | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 234 | 5595 | 180 | 230.7945 | 12.1361 | -13.8331 | 154.284 | 2.3408 | 144.8873 | -23.2338 | 0 | 107.8779 | 72.1221 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6904 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5596 | 4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 234 | 5596 | 240 | 230.7945 | 12.1361 | -13.8331 | 214.284 | 3.3408 | 129.8873 | -16.0306 | 0 | 107.8779 | 72.1221 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5597 | 5 | 9.1 | 0 | 0 | 0 | 0 | 0 | 234 | 5597 | 300 | 230.7945 | 12.1361 | -13.8331 | 274.284 | 4.3408 | 114.8873 | -7.3863 | 0 | 107.8779 | 72.1221 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.6252 | 2.6252 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5598 | 6 | 8.4 | 0 | 0 | 0 | 0 | 0 | 234 | 5598 | 360 | 230.7945 | 12.1361 | -13.8331 | 334.284 | 5.3408 | 99.8873 | 2.1913 | 2.1913 | 105.456 | 74.544 | 99.2806 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 15.4521 | 15.4521 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5599 | 7 | 8.8 | 15.92 | 20.75 | 36.67 | 20.75 | 10.38 | 234 | 5599 | 420 | 230.7945 | 12.1361 | -13.8331 | 394.284 | 6.3408 | 84.8873 | 12.2903 | 12.2903 | 94.7251 | 85.2749 | 84.629 | 7.0007 | 7.0007 | 17.7112 | 24.7119 | -4.8714 | 0% | 11.1747 | 0 | 0 | 191.0868 | 191.0868 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5600 | 8 | 11.9 | 117.42 | 53.89 | 171.31 | 53.89 | 26.95 | 234 | 5600 | 480 | 230.7945 | 12.1361 | -13.8331 | 454.284 | 7.3408 | 69.8873 | 22.5461 | 22.5461 | 83.7214 | 96.2786 | 69.968 | 104.9003 | 104.9003 | 45.998 | 150.8982 | -0.077556 | 0% | 68.2362 | 0 | 0 | 171.7481 | 171.7481 | 0% | 11.64% | 11.64% | 80% | 9.313% | 6.3548 | 6.77 | 6 | 38.1288 | 14.0531 | 22.2% | 22.2%
8 | 234 | 22 | 5601 | 9 | 14.7 | 258 | 76.72 | 334.72 | 76.72 | 38.36 | 234 | 5601 | 540 | 230.7945 | 12.1361 | -13.8331 | 514.284 | 8.3408 | 54.8873 | 32.568 | 32.568 | 71.6153 | 108.3847 | 55.3484 | 272.5151 | 272.5151 | 65.4846 | 337.9997 | 0.42941 | 42.94% | 152.8435 | 65.6327 | 45.9429 | 184.5226 | 184.5226 | 24.9% | 11.49% | 11.49% | 85% | 9.764% | 14.9231 | 6.0865 | 6 | 89.5388 | 33.0012 | 48.52% | 48.52%
8 | 234 | 22 | 5602 | 10 | 19.3 | 395.83 | 97.22 | 493.05 | 97.22 | 48.61 | 234 | 5602 | 600 | 230.7945 | 12.1361 | -13.8331 | 574.284 | 9.3408 | 39.8873 | 41.8304 | 41.8304 | 57.2885 | 122.7115 | 40.8591 | 448.8854 | 448.8854 | 82.9825 | 531.8679 | 0.58533 | 58.53% | 240.5107 | 140.779 | 98.5453 | 194.1263 | 194.1263 | 50.76% | 11.36% | 11.36% | 90% | 10.23% | 24.5948 | 5.0828 | 5.0828 | 125.0095 | 54.3893 | 64.4% | 64.4%
8 | 234 | 22 | 5603 | 11 | 21.2 | 520.89 | 119.11 | 640 | 119.11 | 59.56 | 234 | 5603 | 660 | 230.7945 | 12.1361 | -13.8331 | 634.284 | 10.3408 | 24.8873 | 49.5125 | 49.5125 | 39.3212 | 140.6788 | 26.7524 | 611.5775 | 611.5775 | 101.6667 | 713.2443 | 0.64679 | 64.68% | 322.5291 | 208.61 | 146.027 | 191.5043 | 191.5043 | 76.25% | 11.35% | 11.35% | 90% | 10.21% | 32.9355 | 4.7114 | 4.7114 | 155.1725 | 72.834 | 81.03% | 81.03%
8 | 234 | 22 | 5604 | 12 | 23.2 | 548.28 | 137.92 | 686.2 | 137.92 | 68.96 | 234 | 5604 | 720 | 230.7945 | 12.1361 | -13.8331 | 694.284 | 11.3408 | 9.8873 | 54.3681 | 54.3681 | 16.7476 | 163.2524 | 14.2596 | 653.7922 | 653.7922 | 117.7221 | 771.5143 | 0.6643 | 66.43% | 348.8788 | 231.7591 | 162.2314 | 290.5165 | 290.5165 | 55.84% | 11.35% | 11.35% | 90% | 10.21% | 35.6285 | 4.3478 | 4.3478 | 154.9056 | 78.7893 | 53.32% | 53.32%
8 | 234 | 22 | 5605 | 13 | 24.1 | 618.33 | 139.5 | 757.83 | 139.5 | 69.75 | 234 | 5605 | 780 | 230.7945 | 12.1361 | -13.8331 | 754.284 | 12.3408 | -5.1127 | 55.0905 | 55.0905 | 8.7567 | 188.7567 | 11.5314 | 738.7889 | 738.7889 | 119.0707 | 857.8596 | 0.68062 | 68.06% | 387.9241 | 264.0274 | 184.8192 | 288.4901 | 288.4901 | 64.06% | 11.37% | 11.37% | 95% | 10.8% | 41.8834 | 4.1933 | 4.1933 | 175.6302 | 92.6213 | 60.88% | 60.88%
8 | 234 | 22 | 5606 | 14 | 25.6 | 516.06 | 181.53 | 697.59 | 181.53 | 90.77 | 234 | 5606 | 840 | 230.7945 | 12.1361 | -13.8331 | 814.284 | 13.3408 | -20.1127 | 51.4341 | 51.4341 | 32.6334 | 212.6334 | 22.4651 | 609.9275 | 609.9275 | 154.9455 | 764.8731 | 0.66981 | 66.98% | 345.8756 | 231.6693 | 162.1685 | 324.8625 | 324.8625 | 49.92% | 11.34% | 11.34% | 90% | 10.21% | 35.3037 | 3.9484 | 3.9484 | 139.3947 | 78.0711 | 42.91% | 42.91%
8 | 234 | 22 | 5607 | 15 | 25.5 | 471.17 | 167.64 | 638.81 | 167.64 | 83.82 | 234 | 5607 | 900 | 230.7945 | 12.1361 | -13.8331 | 874.284 | 14.3408 | -35.1127 | 44.4979 | 44.4979 | 52.0343 | 232.0343 | 36.3049 | 541.7531 | 541.7531 | 143.0897 | 684.8428 | 0.65381 | 65.38% | 309.6859 | 202.4766 | 141.7336 | 310.5852 | 310.5852 | 45.63% | 11.32% | 11.32% | 90% | 10.19% | 31.5429 | 3.9643 | 3.9643 | 125.0447 | 69.7543 | 40.26% | 40.26%
8 | 234 | 22 | 5608 | 16 | 25.1 | 387.92 | 149.67 | 537.59 | 149.67 | 74.84 | 234 | 5608 | 960 | 230.7945 | 12.1361 | -13.8331 | 934.284 | 15.3408 | -50.1127 | 35.6301 | 35.6301 | 67.3594 | 247.3594 | 50.7157 | 421.6269 | 421.6269 | 127.7513 | 549.3783 | 0.61523 | 61.52% | 248.4289 | 152.8406 | 106.9885 | 301.8603 | 301.8603 | 35.44% | 11.28% | 11.28% | 90% | 10.15% | 25.2243 | 4.0283 | 4.0283 | 101.6114 | 55.7813 | 33.66% | 33.66%
8 | 234 | 22 | 5609 | 17 | 25.4 | 326.06 | 121.39 | 447.45 | 121.39 | 60.7 | 234 | 5609 | 1020 | 230.7945 | 12.1361 | -13.8331 | 994.284 | 16.3408 | -65.1127 | 25.7826 | 25.7826 | 80.034 | 260.034 | 65.3071 | 313.1639 | 313.1639 | 103.6128 | 416.7767 | 0.5567 | 55.67% | 188.4664 | 104.9199 | 73.4439 | 295.8306 | 295.8306 | 24.83% | 11.24% | 11.24% | 85% | 9.552% | 18.0032 | 3.9802 | 3.9802 | 71.6559 | 39.8124 | 24.22% | 24.22%
8 | 234 | 22 | 5610 | 18 | 24.7 | 191.53 | 104.94 | 296.47 | 104.94 | 52.47 | 234 | 5610 | 1080 | 230.7945 | 12.1361 | -13.8331 | 1054.284 | 17.3408 | -80.1127 | 15.555 | 15.555 | 91.2874 | 271.2874 | 79.9612 | 124.5008 | 124.5008 | 89.5719 | 214.0727 | 0.31556 | 31.56% | 96.8037 | 30.5477 | 21.3834 | 279.6735 | 279.6735 | 7.646% | 11.2% | 11.2% | 80% | 8.96% | 8.674 | 4.0935 | 4.0935 | 35.5069 | 19.1818 | 12.7% | 12.7%
8 | 234 | 22 | 5611 | 19 | 22.9 | 66.11 | 57.5 | 123.61 | 57.5 | 28.75 | 234 | 5611 | 1140 | 230.7945 | 12.1361 | -13.8331 | 1114.284 | 18.3408 | -95.1127 | 5.367 | 5.367 | 102.0272 | 282.0272 | 94.6207 | 0 | 0 | 49.0793 | 49.0793 | -1.4053 | 0% | 22.1937 | 0 | 0 | 167.592 | 167.592 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.4006 | 4.4006 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5612 | 20 | 19.4 | 0 | 16.81 | 16.81 | 16.81 | 8.41 | 234 | 5612 | 1200 | 230.7945 | 12.1361 | -13.8331 | 1174.284 | 19.3408 | -110.1127 | -4.4178 | 0 | 107.8779 | 287.8779 | 102.5373 | 0 | 0 | 14.3482 | 14.3482 | -7.2862 | 0% | 6.4883 | 0 | 0 | 145.9285 | 145.9285 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0626 | 5.0626 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5613 | 21 | 17 | 0 | 0 | 0 | 0 | 0 | 234 | 5613 | 1260 | 230.7945 | 12.1361 | -13.8331 | 1234.284 | 20.3408 | -125.1127 | -13.409 | 0 | 107.8779 | 287.8779 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.7798 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5614 | 22 | 15.5 | 0 | 0 | 0 | 0 | 0 | 234 | 5614 | 1320 | 230.7945 | 12.1361 | -13.8331 | 1294.284 | 21.3408 | -140.1127 | -21.1327 | 0 | 107.8779 | 287.8779 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1478 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5615 | 23 | 14.7 | 0 | 0 | 0 | 0 | 0 | 234 | 5615 | 1380 | 230.7945 | 12.1361 | -13.8331 | 1354.284 | 22.3408 | -155.1127 | -27.0102 | 0 | 107.8779 | 287.8779 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5991 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
8 | 234 | 22 | 5616 | 24 | 14.1 | 0 | 0 | 0 | 0 | 0 | 234 | 5616 | 1440 | 230.7945 | 12.1361 | -13.8331 | 1414.284 | 23.3408 | -170.1127 | -30.4229 | 0 | 107.8779 | 287.8779 | 102.5373 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7456 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5617 | 1 | 13.5 | 0 | 0 | 0 | 0 | 0 | 235 | 5617 | 60 | 231.7808 | 11.8098 | -13.7577 | 34.284 | 0.34211 | 174.8684 | -31.232 | 0 | 107.3889 | 72.6111 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7475 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5618 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 235 | 5618 | 120 | 231.7808 | 11.8098 | -13.7577 | 94.284 | 1.3421 | 159.8684 | -28.7009 | 0 | 107.3889 | 72.6111 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8739 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5619 | 3 | 12.6 | 0 | 0 | 0 | 0 | 0 | 235 | 5619 | 180 | 231.7808 | 11.8098 | -13.7577 | 154.284 | 2.3421 | 144.8684 | -23.5206 | 0 | 107.3889 | 72.6111 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8479 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5620 | 4 | 12.2 | 0 | 0 | 0 | 0 | 0 | 235 | 5620 | 240 | 231.7808 | 11.8098 | -13.7577 | 214.284 | 3.3421 | 129.8684 | -16.2936 | 0 | 107.3889 | 72.6111 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4575 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5621 | 5 | 11.9 | 0 | 0 | 0 | 0 | 0 | 235 | 5621 | 300 | 231.7808 | 11.8098 | -13.7577 | 274.284 | 4.3421 | 114.8684 | -7.629 | 0 | 107.3889 | 72.6111 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.4684 | 1.4684 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5622 | 6 | 11.5 | 0 | 0 | 0 | 0 | 0 | 235 | 5622 | 360 | 231.7808 | 11.8098 | -13.7577 | 334.284 | 5.3421 | 99.8684 | 1.963 | 1.963 | 105.222 | 74.778 | 99.2839 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 11.7705 | 11.7705 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5623 | 7 | 12.4 | 12.83 | 18.94 | 31.77 | 18.94 | 9.47 | 235 | 5623 | 420 | 231.7808 | 11.8098 | -13.7577 | 394.284 | 6.3421 | 84.8684 | 12.0694 | 12.0694 | 94.4786 | 85.5214 | 84.6144 | 5.7591 | 5.7591 | 16.1663 | 21.9254 | -5.2106 | 0% | 9.9146 | 0 | 0 | 181.9136 | 181.9136 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5624 | 8 | 14.7 | 100.06 | 63.47 | 163.53 | 63.47 | 31.74 | 235 | 5624 | 480 | 231.7808 | 11.8098 | -13.7577 | 454.284 | 7.3421 | 69.8684 | 22.3246 | 22.3246 | 83.4615 | 96.5385 | 69.9354 | 90.3734 | 90.3734 | 54.175 | 144.5484 | -0.071907 | 0% | 65.3648 | 0 | 0 | 158.8105 | 158.8105 | 0% | 11.54% | 11.54% | 80% | 9.234% | 6.0361 | 6.0865 | 6 | 36.2165 | 13.3483 | 22.8% | 22.8%
8 | 235 | 23 | 5625 | 9 | 17.9 | 193.11 | 104.67 | 297.78 | 104.67 | 52.34 | 235 | 5625 | 540 | 231.7808 | 11.8098 | -13.7577 | 514.284 | 8.3421 | 54.8684 | 32.3362 | 32.3362 | 71.3423 | 108.6577 | 55.2948 | 205.554 | 205.554 | 89.3414 | 294.8954 | 0.39908 | 39.91% | 133.3517 | 53.218 | 37.2526 | 170.4106 | 170.4106 | 21.86% | 11.41% | 11.41% | 80% | 9.128% | 12.1727 | 5.3726 | 5.3726 | 65.3985 | 26.9189 | 38.38% | 38.38%
8 | 235 | 23 | 5626 | 10 | 21.2 | 294.31 | 145.14 | 439.45 | 145.14 | 72.57 | 235 | 5626 | 600 | 231.7808 | 11.8098 | -13.7577 | 574.284 | 9.3421 | 39.8684 | 41.5774 | 41.5774 | 57.0115 | 122.9885 | 40.7767 | 335.833 | 335.833 | 123.8847 | 459.7178 | 0.5601 | 56.01% | 207.8844 | 116.4357 | 81.505 | 178.2733 | 178.2733 | 45.72% | 11.33% | 11.33% | 85% | 9.63% | 20.0195 | 4.7114 | 4.7114 | 94.3198 | 44.2713 | 52.91% | 52.91%
8 | 235 | 23 | 5627 | 11 | 23.3 | 369.86 | 174.11 | 543.97 | 174.11 | 87.06 | 235 | 5627 | 660 | 231.7808 | 11.8098 | -13.7577 | 634.284 | 10.3421 | 24.8684 | 49.2281 | 49.2281 | 39.0741 | 140.9259 | 26.6206 | 436.6115 | 436.6115 | 148.6122 | 585.2237 | 0.62019 | 62.02% | 264.6382 | 164.1272 | 114.8891 | 273.4235 | 273.4235 | 42.02% | 11.31% | 11.31% | 90% | 10.18% | 26.9447 | 4.3304 | 4.3304 | 116.6801 | 59.5858 | 42.67% | 42.67%
8 | 235 | 23 | 5628 | 12 | 24.7 | 482.72 | 170.06 | 652.78 | 170.06 | 85.03 | 235 | 5628 | 720 | 231.7808 | 11.8098 | -13.7577 | 694.284 | 11.3421 | 9.8684 | 54.0522 | 54.0522 | 16.6046 | 163.3954 | 14.0143 | 578.5319 | 578.5319 | 145.1553 | 723.6872 | 0.65952 | 65.95% | 327.2514 | 215.8277 | 151.0794 | 282.5531 | 282.5531 | 53.47% | 11.33% | 11.33% | 90% | 10.2% | 33.3765 | 4.0935 | 4.0935 | 136.6259 | 73.8092 | 48.35% | 48.35%
8 | 235 | 23 | 5629 | 13 | 26.2 | 448.61 | 160.22 | 608.83 | 160.22 | 80.11 | 235 | 5629 | 780 | 231.7808 | 11.8098 | -13.7577 | 754.284 | 12.3421 | -5.1316 | 54.7641 | 54.7641 | 8.7282 | 188.7282 | 11.2487 | 538.6884 | 538.6884 | 136.7563 | 675.4448 | 0.65392 | 65.39% | 305.4361 | 199.7317 | 139.8122 | 299.803 | 299.803 | 46.63% | 11.31% | 11.31% | 90% | 10.18% | 31.089 | 3.8549 | 3.8549 | 119.8451 | 68.7506 | 39.97% | 39.97%
8 | 235 | 23 | 5630 | 14 | 24.5 | 301.61 | 152.72 | 454.33 | 152.72 | 76.36 | 235 | 5630 | 840 | 231.7808 | 11.8098 | -13.7577 | 814.284 | 13.3421 | -20.1316 | 51.125 | 51.125 | 32.4643 | 212.4643 | 22.341 | 358.3359 | 358.3359 | 130.3547 | 488.6906 | 0.58916 | 58.92% | 220.9859 | 130.1968 | 91.1377 | 265.4052 | 265.4052 | 34.34% | 11.27% | 11.27% | 85% | 9.584% | 21.1786 | 4.1265 | 4.1265 | 87.3931 | 46.8347 | 32.93% | 32.93%
8 | 235 | 23 | 5631 | 15 | 24.8 | 255.69 | 127.08 | 382.77 | 127.08 | 63.54 | 235 | 5631 | 900 | 231.7808 | 11.8098 | -13.7577 | 874.284 | 14.3421 | -35.1316 | 44.2154 | 44.2154 | 51.8043 | 231.8043 | 36.246 | 295.7021 | 295.7021 | 108.4696 | 404.1717 | 0.54582 | 54.58% | 182.7664 | 99.7585 | 69.8309 | 269.173 | 269.173 | 25.94% | 11.25% | 11.25% | 85% | 9.56% | 17.4732 | 4.0771 | 4.0771 | 71.2395 | 38.6403 | 26.47% | 26.47%
8 | 235 | 23 | 5632 | 16 | 26.8 | 195.89 | 138.67 | 334.56 | 138.67 | 69.34 | 235 | 5632 | 960 | 231.7808 | 11.8098 | -13.7577 | 934.284 | 15.3421 | -50.1316 | 35.369 | 35.369 | 67.118 | 247.118 | 50.6908 | 214.3899 | 214.3899 | 118.3622 | 332.7521 | 0.50317 | 50.32% | 150.4705 | 75.7128 | 52.999 | 288.285 | 288.285 | 18.38% | 11.18% | 11.18% | 85% | 9.501% | 14.2957 | 3.7639 | 3.7639 | 53.8073 | 31.6137 | 18.66% | 18.66%
8 | 235 | 23 | 5633 | 17 | 25.4 | 155.42 | 113.47 | 268.89 | 113.47 | 56.74 | 235 | 5633 | 1020 | 231.7808 | 11.8098 | -13.7577 | 994.284 | 16.3421 | -65.1316 | 25.5335 | 25.5335 | 79.7993 | 259.7993 | 65.3051 | 150.6417 | 150.6417 | 96.8527 | 247.4944 | 0.38756 | 38.76% | 111.9169 | 43.3741 | 30.3619 | 265.8982 | 265.8982 | 11.42% | 11.19% | 11.19% | 80% | 8.95% | 10.0169 | 3.9802 | 3.9802 | 39.8692 | 22.1515 | 14.99% | 14.99%
8 | 235 | 23 | 5634 | 18 | 23 | 89.86 | 90.61 | 180.47 | 90.61 | 45.31 | 235 | 5634 | 1080 | 231.7808 | 11.8098 | -13.7577 | 1054.284 | 17.3421 | -80.1316 | 15.309 | 15.309 | 91.0642 | 271.0642 | 79.9779 | 59.2296 | 59.2296 | 77.3405 | 136.5701 | 0.011624 | 1.162% | 61.757 | 0.71788 | 0.50252 | 127.6017 | 127.6017 | 0.3938% | 11.24% | 11.24% | 80% | 8.994% | 5.5544 | 4.3829 | 4.3829 | 24.3446 | 12.2831 | 19.08% | 19.08%
8 | 235 | 23 | 5635 | 19 | 20 | 34.58 | 53.19 | 87.77 | 53.19 | 26.6 | 235 | 5635 | 1140 | 231.7808 | 11.8098 | -13.7577 | 1114.284 | 18.3421 | -95.1316 | 5.1166 | 5.1166 | 101.8163 | 281.8163 | 94.6551 | 0 | 0 | 45.4005 | 45.4005 | -1.7237 | 0% | 20.5301 | 0 | 0 | 156.2543 | 156.2543 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5636 | 20 | 18.3 | 0 | 10.78 | 10.78 | 10.78 | 5.39 | 235 | 5636 | 1200 | 231.7808 | 11.8098 | -13.7577 | 1174.284 | 19.3421 | -110.1316 | -4.679 | 0 | 107.3889 | 287.3889 | 102.1999 | 0 | 0 | 9.2013 | 9.2013 | -12.0766 | 0% | 4.1608 | 0 | 0 | 142.2525 | 142.2525 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5637 | 21 | 16.7 | 0 | 0 | 0 | 0 | 0 | 235 | 5637 | 1260 | 231.7808 | 11.8098 | -13.7577 | 1234.284 | 20.3421 | -125.1316 | -13.6863 | 0 | 107.3889 | 287.3889 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2895 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5638 | 22 | 15.9 | 0 | 0 | 0 | 0 | 0 | 235 | 5638 | 1320 | 231.7808 | 11.8098 | -13.7577 | 1294.284 | 21.3421 | -140.1316 | -21.4292 | 0 | 107.3889 | 287.3889 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9968 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5639 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 235 | 5639 | 1380 | 231.7808 | 11.8098 | -13.7577 | 1354.284 | 22.3421 | -155.1316 | -27.3249 | 0 | 107.3889 | 287.3889 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7328 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
8 | 235 | 23 | 5640 | 24 | 14.3 | 0 | 0 | 0 | 0 | 0 | 235 | 5640 | 1440 | 231.7808 | 11.8098 | -13.7577 | 1414.284 | 23.3421 | -170.1316 | -30.7486 | 0 | 107.3889 | 287.3889 | 102.1999 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1639 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5641 | 1 | 13.8 | 0 | 0 | 0 | 0 | 0 | 236 | 5641 | 60 | 232.7671 | 11.4801 | -13.6708 | 34.284 | 0.34355 | 174.8467 | -31.5593 | 0 | 106.8954 | 73.1046 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4429 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5642 | 2 | 13.5 | 0 | 0 | 0 | 0 | 0 | 236 | 5642 | 120 | 232.7671 | 11.4801 | -13.6708 | 94.284 | 1.3436 | 159.8467 | -29.0127 | 0 | 106.8954 | 73.1046 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3883 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5643 | 3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 236 | 5643 | 180 | 232.7671 | 11.4801 | -13.6708 | 154.284 | 2.3436 | 144.8467 | -23.809 | 0 | 106.8954 | 73.1046 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3337 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5644 | 4 | 12.6 | 0 | 0 | 0 | 0 | 0 | 236 | 5644 | 240 | 232.7671 | 11.4801 | -13.6708 | 214.284 | 3.3436 | 129.8467 | -16.5577 | 0 | 106.8954 | 73.1046 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2481 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5645 | 5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 236 | 5645 | 300 | 232.7671 | 11.4801 | -13.6708 | 274.284 | 4.3436 | 114.8467 | -7.8725 | 0 | 106.8954 | 73.1046 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.7003 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5646 | 6 | 11.9 | 0 | 0 | 0 | 0 | 0 | 236 | 5646 | 360 | 232.7671 | 11.4801 | -13.6708 | 334.284 | 5.3436 | 99.8467 | 1.7341 | 1.7341 | 104.9836 | 75.0164 | 99.2844 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.1325 | 7.1325 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5647 | 7 | 12.2 | 6.61 | 15.33 | 21.94 | 15.33 | 7.67 | 236 | 5647 | 420 | 232.7671 | 11.4801 | -13.6708 | 394.284 | 6.3436 | 84.8467 | 11.8479 | 11.8479 | 94.2281 | 85.7719 | 84.5972 | 3.0313 | 3.0313 | 13.085 | 16.1163 | -7.4071 | 0% | 7.2878 | 0 | 0 | 171.7637 | 171.7637 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5648 | 8 | 14.6 | 43.89 | 51.53 | 95.42 | 51.53 | 25.77 | 236 | 5648 | 480 | 232.7671 | 11.4801 | -13.6708 | 454.284 | 7.3436 | 69.8467 | 22.1021 | 22.1021 | 83.1977 | 96.8023 | 69.9004 | 40.0866 | 40.0866 | 43.9836 | 84.0702 | -0.70472 | 0% | 38.0166 | 0 | 0 | 186.6411 | 186.6411 | 0% | 11.56% | 11.56% | 80% | 9.252% | 3.5172 | 6.1099 | 6 | 21.1031 | 7.7779 | 11.31% | 11.31%
8 | 236 | 24 | 5649 | 9 | 18.3 | 119.44 | 86.25 | 205.69 | 86.25 | 43.13 | 236 | 5649 | 540 | 232.7671 | 11.4801 | -13.6708 | 514.284 | 8.3436 | 54.8467 | 32.1031 | 32.1031 | 71.0655 | 108.9345 | 55.2393 | 128.139 | 128.139 | 73.619 | 201.758 | 0.21657 | 21.66% | 91.235 | 19.7588 | 13.8312 | 156.4551 | 156.4551 | 8.84% | 11.41% | 11.41% | 80% | 9.126% | 8.3264 | 5.2884 | 5.2884 | 44.0331 | 18.4131 | 28.14% | 28.14%
8 | 236 | 24 | 5650 | 10 | 21.5 | 215.89 | 162.72 | 378.61 | 162.72 | 81.36 | 236 | 5650 | 600 | 232.7671 | 11.4801 | -13.6708 | 574.284 | 9.3436 | 39.8467 | 41.3226 | 41.3226 | 56.7309 | 123.2691 | 40.693 | 247.9046 | 247.9046 | 138.8902 | 386.7949 | 0.51581 | 51.58% | 174.9086 | 90.2193 | 63.1535 | 166.9366 | 166.9366 | 37.83% | 11.32% | 11.32% | 85% | 9.62% | 16.8266 | 4.6551 | 4.6551 | 78.3291 | 37.2105 | 46.92% | 46.92%
8 | 236 | 24 | 5651 | 11 | 22.9 | 326.39 | 205.78 | 532.17 | 205.78 | 102.89 | 236 | 5651 | 660 | 232.7671 | 11.4801 | -13.6708 | 634.284 | 10.3436 | 24.8467 | 48.9413 | 48.9413 | 38.8237 | 141.1763 | 26.488 | 387.4191 | 387.4191 | 175.6442 | 563.0633 | 0.61143 | 61.14% | 254.6172 | 155.6798 | 108.9758 | 168.4607 | 168.4607 | 64.69% | 11.31% | 11.31% | 90% | 10.18% | 25.9271 | 4.4006 | 4.4006 | 114.0938 | 57.3355 | 67.73% | 67.73%
8 | 236 | 24 | 5652 | 12 | 24.8 | 363.83 | 252.83 | 616.66 | 252.83 | 126.42 | 236 | 5652 | 720 | 232.7671 | 11.4801 | -13.6708 | 694.284 | 11.3436 | 9.8467 | 53.7334 | 53.7334 | 16.458 | 163.542 | 13.7679 | 438.2838 | 438.2838 | 215.8039 | 654.0877 | 0.64447 | 64.45% | 295.7785 | 190.6201 | 133.4341 | 270.3068 | 270.3068 | 49.36% | 11.31% | 11.31% | 90% | 10.18% | 30.1166 | 4.0771 | 4.0771 | 122.7876 | 66.6001 | 45.43% | 45.43%
8 | 236 | 24 | 5653 | 13 | 26.2 | 385.83 | 243.47 | 629.3 | 243.47 | 121.74 | 236 | 5653 | 780 | 232.7671 | 11.4801 | -13.6708 | 754.284 | 12.3436 | -5.1533 | 54.434 | 54.434 | 8.7044 | 188.7044 | 10.9667 | 465.6532 | 465.6532 | 207.8146 | 673.4678 | 0.65348 | 65.35% | 304.5421 | 199.0129 | 139.309 | 282.4079 | 282.4079 | 49.33% | 11.31% | 11.31% | 90% | 10.18% | 30.9962 | 3.8549 | 3.8549 | 119.4872 | 68.5453 | 42.31% | 42.31%
8 | 236 | 24 | 5654 | 14 | 27.1 | 301.81 | 194.39 | 496.2 | 194.39 | 97.2 | 236 | 5654 | 840 | 232.7671 | 11.4801 | -13.6708 | 814.284 | 13.3436 | -20.1533 | 50.8113 | 50.8113 | 32.2995 | 212.2995 | 22.222 | 360.4751 | 360.4751 | 165.9222 | 526.3974 | 0.61504 | 61.5% | 238.0369 | 146.4022 | 102.4815 | 293.845 | 293.845 | 34.88% | 11.25% | 11.25% | 90% | 10.12% | 24.0909 | 3.7193 | 3.7193 | 89.6015 | 53.2748 | 30.49% | 30.49%
8 | 236 | 24 | 5655 | 15 | 27 | 283.53 | 154.64 | 438.17 | 154.64 | 77.32 | 236 | 5655 | 900 | 232.7671 | 11.4801 | -13.6708 | 874.284 | 14.3436 | -35.1533 | 43.9281 | 43.9281 | 51.5773 | 231.5773 | 36.1916 | 329.8308 | 329.8308 | 131.9935 | 461.8242 | 0.58816 | 58.82% | 208.8369 | 122.8301 | 85.9811 | 288.0076 | 288.0076 | 29.85% | 11.22% | 11.22% | 85% | 9.539% | 19.92 | 3.7341 | 3.7341 | 74.3832 | 44.0513 | 25.83% | 25.83%
8 | 236 | 24 | 5656 | 16 | 27.1 | 212.72 | 174.11 | 386.83 | 174.11 | 87.06 | 236 | 5656 | 960 | 232.7671 | 11.4801 | -13.6708 | 934.284 | 15.3436 | -50.1533 | 35.103 | 35.103 | 66.8781 | 246.8781 | 50.6697 | 234.4498 | 234.4498 | 148.6122 | 383.062 | 0.54433 | 54.43% | 173.2206 | 94.2899 | 66.0029 | 287.0004 | 287.0004 | 23% | 11.19% | 11.19% | 85% | 9.511% | 16.4747 | 3.7193 | 3.7193 | 61.2745 | 36.4323 | 21.35% | 21.35%
8 | 236 | 24 | 5657 | 17 | 26.2 | 114.22 | 140.22 | 254.44 | 140.22 | 70.11 | 236 | 5657 | 1020 | 232.7671 | 11.4801 | -13.6708 | 994.284 | 16.3436 | -65.1533 | 25.2795 | 25.2795 | 79.5653 | 259.5653 | 65.3066 | 111.7399 | 111.7399 | 119.6853 | 231.4251 | 0.36598 | 36.6% | 104.6505 | 38.3 | 26.81 | 266.4518 | 266.4518 | 10.06% | 11.16% | 11.16% | 80% | 8.926% | 9.3416 | 3.8549 | 3.8549 | 36.011 | 20.6581 | 13.52% | 13.52%
8 | 236 | 24 | 5658 | 18 | 26.1 | 68.39 | 104.67 | 173.06 | 104.67 | 52.34 | 236 | 5658 | 1080 | 232.7671 | 11.4801 | -13.6708 | 1054.284 | 17.3436 | -80.1533 | 15.0584 | 15.0584 | 90.8411 | 270.8411 | 79.9978 | 45.7205 | 45.7205 | 89.3414 | 135.062 | 0.051896 | 5.19% | 61.075 | 3.1695 | 2.2187 | 258.3245 | 258.3245 | 0.8589% | 11.13% | 11.13% | 80% | 8.903% | 5.4376 | 3.8703 | 3.8703 | 21.0452 | 12.0247 | 8.147% | 8.147%
8 | 236 | 24 | 5659 | 19 | 23.9 | 13.11 | 53.56 | 66.67 | 53.56 | 26.78 | 236 | 5659 | 1140 | 232.7671 | 11.4801 | -13.6708 | 1114.284 | 18.3436 | -95.1533 | 4.8618 | 4.8618 | 101.6052 | 281.6052 | 94.6924 | 0 | 0 | 45.7163 | 45.7163 | -1.5207 | 0% | 20.6729 | 0 | 0 | 174.5985 | 174.5985 | 0% | 11.19% | 0% | 80% | 0% | 0 | 4.2272 | 4.2272 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5660 | 20 | 20.7 | 0 | 13.47 | 13.47 | 13.47 | 6.74 | 236 | 5660 | 1200 | 232.7671 | 11.4801 | -13.6708 | 1174.284 | 19.3436 | -110.1533 | -4.9446 | 0 | 106.8954 | 286.8954 | 101.859 | 0 | 0 | 11.4974 | 11.4974 | -9.0435 | 0% | 5.1991 | 0 | 0 | 145.0765 | 145.0765 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.8067 | 4.8067 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5661 | 21 | 18.7 | 0 | 0 | 0 | 0 | 0 | 236 | 5661 | 1260 | 232.7671 | 11.4801 | -13.6708 | 1234.284 | 20.3436 | -125.1533 | -13.9679 | 0 | 106.8954 | 286.8954 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.1153 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2053 | 5.2053 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5662 | 22 | 17.4 | 0 | 0 | 0 | 0 | 0 | 236 | 5662 | 1320 | 232.7671 | 11.4801 | -13.6708 | 1294.284 | 21.3436 | -140.1533 | -21.7299 | 0 | 106.8954 | 286.8954 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.4919 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5663 | 23 | 16.4 | 0 | 0 | 0 | 0 | 0 | 236 | 5663 | 1380 | 232.7671 | 11.4801 | -13.6708 | 1354.284 | 22.3436 | -155.1533 | -27.6436 | 0 | 106.8954 | 286.8954 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5041 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
8 | 236 | 24 | 5664 | 24 | 15.8 | 0 | 0 | 0 | 0 | 0 | 236 | 5664 | 1440 | 232.7671 | 11.4801 | -13.6708 | 1414.284 | 23.3436 | -170.1533 | -31.0781 | 0 | 106.8954 | 286.8954 | 101.859 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9067 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5665 | 1 | 15.1 | 0 | 0 | 0 | 0 | 0 | 237 | 5665 | 60 | 233.7534 | 11.1471 | -13.5728 | 34.284 | 0.34519 | 174.8222 | -31.8897 | 0 | 106.3977 | 73.6023 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9098 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5666 | 2 | 14.6 | 0 | 0 | 0 | 0 | 0 | 237 | 5666 | 120 | 233.7534 | 11.1471 | -13.5728 | 94.284 | 1.3452 | 159.8222 | -29.3268 | 0 | 106.3977 | 73.6023 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.902 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5667 | 3 | 14.2 | 0 | 0 | 0 | 0 | 0 | 237 | 5667 | 180 | 233.7534 | 11.1471 | -13.5728 | 154.284 | 2.3452 | 144.8222 | -24.0991 | 0 | 106.3977 | 73.6023 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7419 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5668 | 4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 237 | 5668 | 240 | 233.7534 | 11.1471 | -13.5728 | 214.284 | 3.3452 | 129.8222 | -16.8229 | 0 | 106.3977 | 73.6023 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8087 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5669 | 5 | 12.8 | 0 | 0 | 0 | 0 | 0 | 237 | 5669 | 300 | 233.7534 | 11.1471 | -13.5728 | 274.284 | 4.3452 | 114.8222 | -8.1167 | 0 | 106.3977 | 73.6023 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.9075 | 5.9075 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5670 | 6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 237 | 5670 | 360 | 233.7534 | 11.1471 | -13.5728 | 334.284 | 5.3452 | 99.8222 | 1.5046 | 1.5046 | 104.741 | 75.259 | 99.282 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 19.0738 | 19.0738 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5671 | 7 | 13.2 | 8.11 | 19.44 | 27.55 | 19.44 | 9.72 | 237 | 5671 | 420 | 233.7534 | 11.1471 | -13.5728 | 394.284 | 6.3452 | 84.8222 | 11.6257 | 11.6257 | 93.9735 | 86.0265 | 84.5775 | 3.8031 | 3.8031 | 16.5931 | 20.3962 | -5.5714 | 0% | 9.2232 | 0 | 0 | 192.5836 | 192.5836 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5672 | 8 | 15.3 | 99.78 | 59.78 | 159.56 | 59.78 | 29.89 | 237 | 5672 | 480 | 233.7534 | 11.1471 | -13.5728 | 454.284 | 7.3452 | 69.8222 | 21.8787 | 21.8787 | 82.93 | 97.07 | 69.8632 | 92.1807 | 92.1807 | 51.0254 | 143.2061 | -0.070615 | 0% | 64.7578 | 0 | 0 | 171.4969 | 171.4969 | 0% | 11.52% | 11.52% | 80% | 9.217% | 5.969 | 5.9472 | 5.9472 | 35.4986 | 13.1999 | 20.7% | 20.7%
8 | 237 | 25 | 5673 | 9 | 19.5 | 226.58 | 83.06 | 309.64 | 83.06 | 41.53 | 237 | 5673 | 540 | 233.7534 | 11.1471 | -13.5728 | 514.284 | 8.3452 | 54.8222 | 31.8688 | 31.8688 | 70.7851 | 109.2149 | 55.1819 | 245.0323 | 245.0323 | 70.8961 | 315.9284 | 0.43727 | 43.73% | 142.8628 | 62.47 | 43.729 | 185.7742 | 185.7742 | 23.54% | 11.37% | 11.37% | 85% | 9.661% | 13.8013 | 5.0425 | 5.0425 | 69.5926 | 30.5203 | 37.46% | 37.46%
8 | 237 | 25 | 5674 | 10 | 21.6 | 383.67 | 96.39 | 480.06 | 96.39 | 48.2 | 237 | 5674 | 600 | 233.7534 | 11.1471 | -13.5728 | 574.284 | 9.3452 | 39.8222 | 41.066 | 41.066 | 56.4469 | 123.5531 | 40.6079 | 443.3898 | 443.3898 | 82.274 | 525.6638 | 0.59236 | 59.24% | 237.7052 | 140.8063 | 98.5644 | 192.3173 | 192.3173 | 51.25% | 11.33% | 11.33% | 90% | 10.2% | 24.2342 | 4.6364 | 4.6364 | 112.3605 | 53.5918 | 58.42% | 58.42%
8 | 237 | 25 | 5675 | 11 | 22.8 | 500.69 | 118.67 | 619.36 | 118.67 | 59.34 | 237 | 5675 | 660 | 233.7534 | 11.1471 | -13.5728 | 634.284 | 10.3452 | 24.8222 | 48.6521 | 48.6521 | 38.5701 | 141.4299 | 26.3549 | 597.6312 | 597.6312 | 101.2912 | 698.9223 | 0.64855 | 64.86% | 316.0527 | 204.9761 | 143.4833 | 188.6281 | 188.6281 | 76.07% | 11.34% | 11.34% | 90% | 10.2% | 32.2462 | 4.4183 | 4.4183 | 142.4727 | 71.3096 | 75.53% | 75.53%
8 | 237 | 25 | 5676 | 12 | 24.6 | 584.5 | 123.94 | 708.44 | 123.94 | 61.97 | 237 | 5676 | 720 | 233.7534 | 11.1471 | -13.5728 | 694.284 | 11.3452 | 9.8222 | 53.4116 | 53.4116 | 16.3078 | 163.6922 | 13.5207 | 707.7771 | 707.7771 | 105.7894 | 813.5665 | 0.67522 | 67.52% | 367.8948 | 248.4083 | 173.8858 | 275.6262 | 275.6262 | 63.09% | 11.36% | 11.36% | 95% | 10.79% | 39.6872 | 4.1099 | 4.1099 | 163.1122 | 87.7648 | 59.18% | 59.18%
8 | 237 | 25 | 5677 | 13 | 26.7 | 549.58 | 175.97 | 725.55 | 175.97 | 87.99 | 237 | 5677 | 780 | 233.7534 | 11.1471 | -13.5728 | 754.284 | 12.3452 | -5.1778 | 54.1003 | 54.1003 | 8.6851 | 188.6851 | 10.6859 | 666.6909 | 666.6909 | 150.1998 | 816.8906 | 0.6812 | 68.12% | 369.398 | 251.6351 | 176.1445 | 305.2808 | 305.2808 | 57.7% | 11.36% | 11.36% | 95% | 10.79% | 39.8592 | 3.7789 | 3.7789 | 150.6229 | 88.1451 | 49.34% | 49.34%
8 | 237 | 25 | 5678 | 14 | 27 | 353.25 | 188.14 | 541.39 | 188.14 | 94.07 | 237 | 5678 | 840 | 233.7534 | 11.1471 | -13.5728 | 814.284 | 13.3452 | -20.1778 | 50.4932 | 50.4932 | 32.1391 | 212.1391 | 22.1084 | 424.1813 | 424.1813 | 160.5875 | 584.7688 | 0.63354 | 63.35% | 264.4325 | 167.529 | 117.2703 | 304.4819 | 304.4819 | 38.51% | 11.27% | 11.27% | 90% | 10.14% | 26.8193 | 3.7341 | 3.7341 | 100.1461 | 59.3086 | 32.89% | 32.89%
8 | 237 | 25 | 5679 | 15 | 27.6 | 287.83 | 183.39 | 471.22 | 183.39 | 91.7 | 237 | 5679 | 900 | 233.7534 | 11.1471 | -13.5728 | 874.284 | 14.3452 | -35.1778 | 43.636 | 43.636 | 51.3532 | 231.3532 | 36.1418 | 336.833 | 336.833 | 156.5332 | 493.3662 | 0.60452 | 60.45% | 223.1002 | 134.8684 | 94.4079 | 305.575 | 305.575 | 30.9% | 11.22% | 11.22% | 85% | 9.54% | 21.2843 | 3.6464 | 3.6464 | 77.612 | 47.0684 | 25.4% | 25.4%
8 | 237 | 25 | 5680 | 16 | 27.6 | 312.5 | 148.28 | 460.78 | 148.28 | 74.14 | 237 | 5680 | 960 | 233.7534 | 11.1471 | -13.5728 | 934.284 | 15.3452 | -50.1778 | 34.8321 | 34.8321 | 66.6398 | 246.6398 | 50.6526 | 346.8852 | 346.8852 | 126.5649 | 473.4501 | 0.59613 | 59.61% | 214.0941 | 127.6275 | 89.3393 | 305.0217 | 305.0217 | 29.29% | 11.22% | 11.22% | 85% | 9.533% | 20.41 | 3.6464 | 3.6464 | 74.4237 | 45.1348 | 24.4% | 24.4%
8 | 237 | 25 | 5681 | 17 | 27.3 | 218.56 | 117.22 | 335.78 | 117.22 | 58.61 | 237 | 5681 | 1020 | 233.7534 | 11.1471 | -13.5728 | 994.284 | 16.3452 | -65.1778 | 25.0209 | 25.0209 | 79.332 | 259.332 | 65.3116 | 215.8394 | 215.8394 | 100.0535 | 315.893 | 0.49045 | 49.05% | 142.8468 | 70.0597 | 49.0418 | 276.0109 | 276.0109 | 17.77% | 11.16% | 11.16% | 85% | 9.484% | 13.5476 | 3.69 | 3.69 | 49.9899 | 29.9592 | 18.11% | 18.11%
8 | 237 | 25 | 5682 | 18 | 26.1 | 135.56 | 80.5 | 216.06 | 80.5 | 40.25 | 237 | 5682 | 1080 | 233.7534 | 11.1471 | -13.5728 | 1054.284 | 17.3452 | -80.1778 | 14.8033 | 14.8033 | 90.6182 | 270.6182 | 80.0208 | 91.9421 | 91.9421 | 68.711 | 160.6531 | 0.1717 | 17.17% | 72.6473 | 12.4737 | 8.7316 | 267.4975 | 267.4975 | 3.264% | 11.14% | 0% | 80% | 0% | 0 | 3.8703 | 3.8703 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5683 | 19 | 24.8 | 28.33 | 43.33 | 71.66 | 43.33 | 21.67 | 237 | 5683 | 1140 | 233.7534 | 11.1471 | -13.5728 | 1114.284 | 18.3452 | -95.1778 | 4.6025 | 4.6025 | 101.3941 | 281.3941 | 94.7325 | 0 | 0 | 36.9845 | 36.9845 | -2.0174 | 0% | 16.7244 | 0 | 0 | 265.8293 | 265.8293 | 0% | 11.15% | 0% | 80% | 0% | 0 | 4.0771 | 4.0771 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5684 | 20 | 23 | 0 | 9.22 | 9.22 | 9.22 | 4.61 | 237 | 5684 | 1200 | 233.7534 | 11.1471 | -13.5728 | 1174.284 | 19.3452 | -110.1778 | -5.2145 | 0 | 106.3977 | 286.3977 | 101.5146 | 0 | 0 | 7.8698 | 7.8698 | -12.9467 | 0% | 3.5587 | 0 | 0 | 149.0392 | 149.0392 | 0% | 11.22% | 0% | 80% | 0% | 0 | 4.3829 | 4.3829 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5685 | 21 | 19.5 | 0 | 0 | 0 | 0 | 0 | 237 | 5685 | 1260 | 233.7534 | 11.1471 | -13.5728 | 1234.284 | 20.3452 | -125.1778 | -14.2538 | 0 | 106.3977 | 286.3977 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.6888 | 0 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0425 | 5.0425 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5686 | 22 | 18 | 0 | 0 | 0 | 0 | 0 | 237 | 5686 | 1320 | 233.7534 | 11.1471 | -13.5728 | 1294.284 | 21.3452 | -140.1778 | -22.0348 | 0 | 106.3977 | 286.3977 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7995 | 0 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5687 | 23 | 16.7 | 0 | 0 | 0 | 0 | 0 | 237 | 5687 | 1380 | 233.7534 | 11.1471 | -13.5728 | 1354.284 | 22.3452 | -155.1778 | -27.9664 | 0 | 106.3977 | 286.3977 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.011 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
8 | 237 | 25 | 5688 | 24 | 15.7 | 0 | 0 | 0 | 0 | 0 | 237 | 5688 | 1440 | 233.7534 | 11.1471 | -13.5728 | 1414.284 | 23.3452 | -170.1778 | -31.4114 | 0 | 106.3977 | 286.3977 | 101.5146 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7652 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5689 | 1 | 15.3 | 0 | 0 | 0 | 0 | 0 | 238 | 5689 | 60 | 234.7397 | 10.8107 | -13.4636 | 34.284 | 0.34701 | 174.7949 | -32.2232 | 0 | 105.8957 | 74.1043 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7069 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5690 | 2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 238 | 5690 | 120 | 234.7397 | 10.8107 | -13.4636 | 94.284 | 1.347 | 159.7949 | -29.6433 | 0 | 105.8957 | 74.1043 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1098 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5691 | 3 | 13.6 | 0 | 0 | 0 | 0 | 0 | 238 | 5691 | 180 | 234.7397 | 10.8107 | -13.4636 | 154.284 | 2.347 | 144.7949 | -24.3907 | 0 | 105.8957 | 74.1043 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2746 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5692 | 4 | 13.6 | 0 | 0 | 0 | 0 | 0 | 238 | 5692 | 240 | 234.7397 | 10.8107 | -13.4636 | 214.284 | 3.347 | 129.7949 | -17.0891 | 0 | 105.8957 | 74.1043 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2746 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5693 | 5 | 12.6 | 0 | 0 | 0 | 0 | 0 | 238 | 5693 | 300 | 234.7397 | 10.8107 | -13.4636 | 274.284 | 4.347 | 114.7949 | -8.3616 | 0 | 105.8957 | 74.1043 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.81587 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5694 | 6 | 12.3 | 0 | 0 | 0 | 0 | 0 | 238 | 5694 | 360 | 234.7397 | 10.8107 | -13.4636 | 334.284 | 5.347 | 99.7949 | 1.2746 | 1.2746 | 104.4941 | 75.5059 | 99.2767 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.1186 | 8.1186 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5695 | 7 | 12.8 | 7.92 | 14.11 | 22.03 | 14.11 | 7.06 | 238 | 5695 | 420 | 234.7397 | 10.8107 | -13.4636 | 394.284 | 6.347 | 84.7949 | 11.4028 | 11.4028 | 93.715 | 86.285 | 84.5551 | 3.8012 | 3.8012 | 12.0436 | 15.8448 | -7.4607 | 0% | 7.165 | 0 | 0 | 173.2184 | 173.2184 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5696 | 8 | 16 | 62.92 | 59.94 | 122.86 | 59.94 | 29.97 | 238 | 5696 | 480 | 234.7397 | 10.8107 | -13.4636 | 454.284 | 7.347 | 69.7949 | 21.6545 | 21.6545 | 82.6585 | 97.3415 | 69.8238 | 58.8106 | 58.8106 | 51.162 | 109.9726 | -0.32054 | 0% | 49.7296 | 0 | 0 | 190.7792 | 190.7792 | 0% | 11.5% | 11.5% | 80% | 9.203% | 4.5766 | 5.7878 | 5.7878 | 26.4887 | 10.1208 | 13.88% | 13.88%
8 | 238 | 26 | 5697 | 9 | 17.6 | 138.06 | 78.94 | 217 | 78.94 | 39.47 | 238 | 5697 | 540 | 234.7397 | 10.8107 | -13.4636 | 514.284 | 8.347 | 54.7949 | 31.6332 | 31.6332 | 70.501 | 109.499 | 55.1228 | 150.5217 | 150.5217 | 67.3795 | 217.9012 | 0.25293 | 25.29% | 98.5349 | 24.9226 | 17.4458 | 156.3356 | 156.3356 | 11.16% | 11.43% | 11.43% | 80% | 9.143% | 9.0091 | 5.4364 | 5.4364 | 48.9775 | 19.9229 | 31.33% | 31.33%
8 | 238 | 26 | 5698 | 10 | 20.2 | 206.89 | 113.75 | 320.64 | 113.75 | 56.88 | 238 | 5698 | 600 | 234.7397 | 10.8107 | -13.4636 | 574.284 | 9.347 | 39.7949 | 40.8076 | 40.8076 | 56.1597 | 123.8403 | 40.5217 | 240.6494 | 240.6494 | 97.0917 | 337.7411 | 0.46552 | 46.55% | 152.7265 | 71.0977 | 49.7684 | 162.3504 | 162.3504 | 30.65% | 11.35% | 11.35% | 85% | 9.645% | 14.7303 | 4.9037 | 4.9037 | 72.2329 | 32.5747 | 44.49% | 44.49%
8 | 238 | 26 | 5699 | 11 | 23.1 | 311.33 | 167.44 | 478.77 | 167.44 | 83.72 | 238 | 5699 | 660 | 234.7397 | 10.8107 | -13.4636 | 634.284 | 10.347 | 24.7949 | 48.3607 | 48.3607 | 38.3135 | 141.6865 | 26.2214 | 373.7138 | 373.7138 | 142.919 | 516.6328 | 0.59496 | 59.5% | 233.6213 | 138.9945 | 97.2961 | 168.0461 | 168.0461 | 57.9% | 11.3% | 11.3% | 90% | 10.17% | 23.767 | 4.3653 | 4.3653 | 103.7506 | 52.5587 | 61.74% | 61.74%
8 | 238 | 26 | 5700 | 12 | 23.6 | 367.72 | 155.14 | 522.86 | 155.14 | 77.57 | 238 | 5700 | 720 | 234.7397 | 10.8107 | -13.4636 | 694.284 | 11.347 | 9.7949 | 53.0869 | 53.0869 | 16.1543 | 163.8457 | 13.2729 | 447.625 | 447.625 | 132.4203 | 580.0453 | 0.61967 | 61.97% | 262.2965 | 162.5368 | 113.7758 | 168.0038 | 168.0038 | 67.72% | 11.31% | 11.31% | 90% | 10.18% | 26.6955 | 4.2784 | 4.2784 | 114.2151 | 59.0347 | 67.98% | 67.98%
8 | 238 | 26 | 5701 | 13 | 24.5 | 317.78 | 121.75 | 439.53 | 121.75 | 60.88 | 238 | 5701 | 780 | 234.7397 | 10.8107 | -13.4636 | 754.284 | 12.347 | -5.2051 | 53.763 | 53.763 | 8.6703 | 188.6703 | 10.4067 | 387.5042 | 387.5042 | 103.9201 | 491.4243 | 0.59036 | 59.04% | 222.2221 | 131.1907 | 91.8335 | 178.338 | 178.338 | 51.49% | 11.28% | 11.28% | 85% | 9.584% | 21.2984 | 4.1265 | 4.1265 | 87.8873 | 47.0995 | 49.28% | 49.28%
8 | 238 | 26 | 5702 | 14 | 25.7 | 244.94 | 169.78 | 414.72 | 169.78 | 84.89 | 238 | 5702 | 840 | 234.7397 | 10.8107 | -13.4636 | 814.284 | 13.347 | -20.2051 | 50.1709 | 50.1709 | 31.983 | 211.983 | 22.0002 | 295.7246 | 295.7246 | 144.9163 | 440.6409 | 0.57154 | 57.15% | 199.2578 | 113.8847 | 79.7193 | 249.5126 | 249.5126 | 31.95% | 11.24% | 11.24% | 85% | 9.553% | 19.036 | 3.9327 | 3.9327 | 74.8623 | 42.0964 | 30% | 30%
8 | 238 | 26 | 5703 | 15 | 25.8 | 361.61 | 209.58 | 571.19 | 209.58 | 104.79 | 238 | 5703 | 900 | 234.7397 | 10.8107 | -13.4636 | 874.284 | 14.347 | -35.2051 | 43.3392 | 43.3392 | 51.132 | 231.132 | 36.0966 | 425.7365 | 425.7365 | 178.8877 | 604.6242 | 0.63494 | 63.49% | 273.4111 | 173.5999 | 121.52 | 267.3757 | 267.3757 | 45.45% | 11.29% | 11.29% | 90% | 10.16% | 27.7805 | 3.917 | 3.917 | 108.8157 | 61.4341 | 40.7% | 40.7%
8 | 238 | 26 | 5704 | 16 | 24.8 | 225.97 | 228.06 | 454.03 | 228.06 | 114.03 | 238 | 5704 | 960 | 234.7397 | 10.8107 | -13.4636 | 934.284 | 15.347 | -50.2051 | 34.5565 | 34.5565 | 66.403 | 246.403 | 50.6394 | 252.6539 | 252.6539 | 194.6614 | 447.3153 | 0.57073 | 57.07% | 202.276 | 115.4442 | 80.8109 | 252.3463 | 252.3463 | 32.02% | 11.26% | 11.26% | 85% | 9.57% | 19.3579 | 4.0771 | 4.0771 | 78.9238 | 42.8083 | 31.28% | 31.28%
8 | 238 | 26 | 5705 | 17 | 24.5 | 96.89 | 134.44 | 231.33 | 134.44 | 67.22 | 238 | 5705 | 1020 | 234.7397 | 10.8107 | -13.4636 | 994.284 | 16.347 | -65.2051 | 24.7576 | 24.7576 | 79.0994 | 259.0994 | 65.32 | 96.6055 | 96.6055 | 114.7517 | 211.3572 | 0.30726 | 30.73% | 95.5757 | 29.367 | 20.5569 | 233.8196 | 233.8196 | 8.792% | 11.21% | 11.21% | 80% | 8.965% | 8.5684 | 4.1265 | 4.1265 | 35.3573 | 18.9483 | 15.12% | 15.12%
8 | 238 | 26 | 5706 | 18 | 23.4 | 55.61 | 80.56 | 136.17 | 80.56 | 40.28 | 238 | 5706 | 1080 | 234.7397 | 10.8107 | -13.4636 | 1054.284 | 17.347 | -80.2051 | 14.5436 | 14.5436 | 90.3955 | 270.3955 | 80.0469 | 38.276 | 38.276 | 68.7623 | 107.0383 | -0.19893 | 0% | 48.4027 | 0 | 0 | 173.4347 | 173.4347 | 0% | 11.22% | 0% | 80% | 0% | 0 | 4.313 | 4.313 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5707 | 19 | 22 | 9.44 | 40.97 | 50.41 | 40.97 | 20.49 | 238 | 5707 | 1140 | 234.7397 | 10.8107 | -13.4636 | 1114.284 | 18.347 | -95.2051 | 4.3388 | 4.3388 | 101.1829 | 281.1829 | 94.7753 | 0 | 0 | 34.9701 | 34.9701 | -2.3525 | 0% | 15.8135 | 0 | 0 | 155.819 | 155.819 | 0% | 11.27% | 0% | 80% | 0% | 0 | 4.5626 | 4.5626 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5708 | 20 | 21.6 | 0 | 11.67 | 11.67 | 11.67 | 5.84 | 238 | 5708 | 1200 | 234.7397 | 10.8107 | -13.4636 | 1174.284 | 19.347 | -110.2051 | -5.4887 | 0 | 105.8957 | 285.8957 | 101.1669 | 0 | 0 | 9.961 | 9.961 | -10.3649 | 0% | 4.5043 | 0 | 0 | 146.7883 | 146.7883 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.6364 | 4.6364 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5709 | 21 | 19.3 | 0 | 0 | 0 | 0 | 0 | 238 | 5709 | 1260 | 234.7397 | 10.8107 | -13.4636 | 1234.284 | 20.347 | -125.2051 | -14.5438 | 0 | 105.8957 | 285.8957 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.763 | 0 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0828 | 5.0828 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5710 | 22 | 17.7 | 0 | 0 | 0 | 0 | 0 | 238 | 5710 | 1320 | 234.7397 | 10.8107 | -13.4636 | 1294.284 | 21.347 | -140.2051 | -22.3437 | 0 | 105.8957 | 285.8957 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.584 | 0 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4151 | 5.4151 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5711 | 23 | 17.4 | 0 | 0 | 0 | 0 | 0 | 238 | 5711 | 1380 | 234.7397 | 10.8107 | -13.4636 | 1354.284 | 22.347 | -155.2051 | -28.2931 | 0 | 105.8957 | 285.8957 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5296 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
8 | 238 | 26 | 5712 | 24 | 16.5 | 0 | 0 | 0 | 0 | 0 | 238 | 5712 | 1440 | 234.7397 | 10.8107 | -13.4636 | 1414.284 | 23.347 | -170.2051 | -31.7482 | 0 | 105.8957 | 285.8957 | 101.1669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3897 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5713 | 1 | 16.4 | 0 | 0 | 0 | 0 | 0 | 239 | 5713 | 60 | 235.726 | 10.4711 | -13.3436 | 34.284 | 0.34901 | 174.7649 | -32.5597 | 0 | 105.3896 | 74.6104 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5652 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5714 | 2 | 16.6 | 0 | 0 | 0 | 0 | 0 | 239 | 5714 | 120 | 235.726 | 10.4711 | -13.3436 | 94.284 | 1.349 | 159.7649 | -29.9619 | 0 | 105.3896 | 74.6104 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6574 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5715 | 3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 239 | 5715 | 180 | 235.726 | 10.4711 | -13.3436 | 154.284 | 2.349 | 144.7649 | -24.6838 | 0 | 105.3896 | 74.6104 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.6639 | 0 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5716 | 4 | 15.4 | 0 | 0 | 0 | 0 | 0 | 239 | 5716 | 240 | 235.726 | 10.4711 | -13.3436 | 214.284 | 3.349 | 129.7649 | -17.3562 | 0 | 105.3896 | 74.6104 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8831 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5717 | 5 | 14.9 | 0 | 0 | 0 | 0 | 0 | 239 | 5717 | 300 | 235.726 | 10.4711 | -13.3436 | 274.284 | 4.349 | 114.7649 | -8.6071 | 0 | 105.3896 | 74.6104 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.6608 | 5.6608 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5718 | 6 | 12.4 | 0 | 0 | 0 | 0 | 0 | 239 | 5718 | 360 | 235.726 | 10.4711 | -13.3436 | 334.284 | 5.349 | 99.7649 | 1.0439 | 1.0439 | 104.2431 | 75.7569 | 99.2685 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 13.457 | 13.457 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5719 | 7 | 12.5 | 5.78 | 16.11 | 21.89 | 16.11 | 8.06 | 239 | 5719 | 420 | 235.726 | 10.4711 | -13.3436 | 394.284 | 6.349 | 84.7649 | 11.1793 | 11.1793 | 93.4525 | 86.5475 | 84.5303 | 2.8417 | 2.8417 | 13.7507 | 16.5924 | -7.1299 | 0% | 7.5031 | 0 | 0 | 182.4925 | 182.4925 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5720 | 8 | 15.4 | 49.72 | 72.72 | 122.44 | 72.72 | 36.36 | 239 | 5720 | 480 | 235.726 | 10.4711 | -13.3436 | 454.284 | 7.349 | 69.7649 | 21.4294 | 21.4294 | 82.3833 | 97.6167 | 69.7823 | 47.0302 | 47.0302 | 62.0704 | 109.1006 | -0.34195 | 0% | 49.3353 | 0 | 0 | 201.4479 | 201.4479 | 0% | 11.53% | 11.53% | 80% | 9.221% | 4.5494 | 5.9242 | 5.9242 | 26.9516 | 10.0606 | 13.38% | 13.38%
8 | 239 | 27 | 5721 | 9 | 18.3 | 163.39 | 123.89 | 287.28 | 123.89 | 61.95 | 239 | 5721 | 540 | 235.726 | 10.4711 | -13.3436 | 514.284 | 8.349 | 54.7649 | 31.3963 | 31.3963 | 70.2135 | 109.7865 | 55.0619 | 179.6163 | 179.6163 | 105.7467 | 285.363 | 0.38867 | 38.87% | 129.0411 | 50.155 | 35.1085 | 173.1065 | 173.1065 | 20.28% | 11.4% | 11.4% | 80% | 9.12% | 11.7687 | 5.2884 | 5.2884 | 62.2369 | 26.0254 | 35.95% | 35.95%
8 | 239 | 27 | 5722 | 10 | 20.9 | 300 | 130.83 | 430.83 | 130.83 | 65.42 | 239 | 5722 | 600 | 235.726 | 10.4711 | -13.3436 | 574.284 | 9.349 | 39.7649 | 40.5475 | 40.5475 | 55.8692 | 124.1308 | 40.4344 | 351.2573 | 351.2573 | 111.6704 | 462.9277 | 0.56037 | 56.04% | 209.3359 | 117.306 | 82.1142 | 180.7356 | 180.7356 | 45.43% | 11.34% | 11.34% | 85% | 9.635% | 20.1696 | 4.7684 | 4.7684 | 96.1756 | 44.6032 | 53.21% | 53.21%
8 | 239 | 27 | 5723 | 11 | 22.9 | 494.17 | 123.56 | 617.73 | 123.56 | 61.78 | 239 | 5723 | 660 | 235.726 | 10.4711 | -13.3436 | 634.284 | 10.349 | 24.7649 | 48.0669 | 48.0669 | 38.054 | 141.946 | 26.0878 | 596.5981 | 596.5981 | 105.4651 | 702.0631 | 0.64955 | 64.96% | 317.4729 | 206.2158 | 144.351 | 182.561 | 182.561 | 79.07% | 11.34% | 11.34% | 90% | 10.2% | 32.3909 | 4.4006 | 4.4006 | 142.5381 | 71.6297 | 78.08% | 78.08%
8 | 239 | 27 | 5724 | 12 | 24.2 | 577.36 | 138.75 | 716.11 | 138.75 | 69.38 | 239 | 5724 | 720 | 235.726 | 10.4711 | -13.3436 | 694.284 | 11.349 | 9.7649 | 52.7594 | 52.7594 | 15.9976 | 164.0024 | 13.0249 | 706.5759 | 706.5759 | 118.4305 | 825.0065 | 0.67596 | 67.6% | 373.0679 | 252.1801 | 176.526 | 273.154 | 273.154 | 64.63% | 11.36% | 11.36% | 95% | 10.79% | 40.2536 | 4.1765 | 4.1765 | 168.1192 | 89.0173 | 61.55% | 61.55%
8 | 239 | 27 | 5725 | 13 | 25.5 | 485 | 189.17 | 674.17 | 189.17 | 94.59 | 239 | 5725 | 780 | 235.726 | 10.4711 | -13.3436 | 754.284 | 12.349 | -5.2351 | 53.4222 | 53.4222 | 8.6596 | 188.6596 | 10.1297 | 594.5344 | 594.5344 | 161.4667 | 756.0011 | 0.66795 | 66.79% | 341.8637 | 228.3475 | 159.8433 | 286.7191 | 286.7191 | 55.75% | 11.34% | 11.34% | 90% | 10.2% | 34.8866 | 3.9643 | 3.9643 | 138.3 | 77.1486 | 48.24% | 48.24%
8 | 239 | 27 | 5726 | 14 | 25.5 | 465.97 | 203.47 | 669.44 | 203.47 | 101.74 | 239 | 5726 | 840 | 235.726 | 10.4711 | -13.3436 | 814.284 | 13.349 | -20.2351 | 49.8443 | 49.8443 | 31.831 | 211.831 | 21.8978 | 565.6855 | 565.6855 | 173.6725 | 739.358 | 0.66489 | 66.49% | 334.3377 | 222.2966 | 155.6076 | 278.4812 | 278.4812 | 55.88% | 11.33% | 11.33% | 90% | 10.2% | 34.1034 | 3.9643 | 3.9643 | 135.1953 | 75.4167 | 48.55% | 48.55%
8 | 239 | 27 | 5727 | 15 | 25.3 | 439.17 | 185.61 | 624.78 | 185.61 | 92.81 | 239 | 5727 | 900 | 235.726 | 10.4711 | -13.3436 | 874.284 | 14.349 | -35.2351 | 43.0378 | 43.0378 | 50.9137 | 230.9137 | 36.0561 | 520.2244 | 520.2244 | 158.428 | 678.6525 | 0.65182 | 65.18% | 306.8866 | 200.0335 | 140.0234 | 275.2934 | 275.2934 | 50.86% | 11.32% | 11.32% | 90% | 10.18% | 31.2563 | 3.9962 | 3.9962 | 124.905 | 69.1205 | 45.37% | 45.37%
8 | 239 | 27 | 5728 | 16 | 25.5 | 400.5 | 155.14 | 555.64 | 155.14 | 77.57 | 239 | 5728 | 960 | 235.726 | 10.4711 | -13.3436 | 934.284 | 15.349 | -50.2351 | 34.2762 | 34.2762 | 66.168 | 246.168 | 50.6302 | 451.0907 | 451.0907 | 132.4203 | 583.5109 | 0.62773 | 62.77% | 263.8636 | 165.6355 | 115.9448 | 278.1872 | 278.1872 | 41.68% | 11.29% | 11.29% | 90% | 10.16% | 26.8029 | 3.9643 | 3.9643 | 106.2541 | 59.2722 | 38.2% | 38.2%
8 | 239 | 27 | 5729 | 17 | 25.3 | 298.94 | 126.61 | 425.55 | 126.61 | 63.31 | 239 | 5729 | 1020 | 235.726 | 10.4711 | -13.3436 | 994.284 | 16.349 | -65.2351 | 24.4897 | 24.4897 | 78.8676 | 258.8676 | 65.332 | 300.9818 | 300.9818 | 108.0684 | 409.0502 | 0.55151 | 55.15% | 184.9725 | 102.0145 | 71.4102 | 268.5183 | 268.5183 | 26.59% | 11.24% | 11.24% | 85% | 9.552% | 17.6692 | 3.9962 | 3.9962 | 70.6088 | 39.0738 | 26.3% | 26.3%
8 | 239 | 27 | 5730 | 18 | 24.9 | 177.36 | 94.22 | 271.58 | 94.22 | 47.11 | 239 | 5730 | 1080 | 235.726 | 10.4711 | -13.3436 | 1054.284 | 17.349 | -80.2351 | 14.2795 | 14.2795 | 90.173 | 270.173 | 80.0761 | 123.9246 | 123.9246 | 80.4218 | 204.3464 | 0.29441 | 29.44% | 92.4054 | 27.2048 | 19.0434 | 252.2816 | 252.2816 | 7.548% | 11.19% | 0% | 80% | 0% | 0 | 4.0608 | 4.0608 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5731 | 19 | 23.2 | 53.19 | 49.78 | 102.97 | 49.78 | 24.89 | 239 | 5731 | 1140 | 235.726 | 10.4711 | -13.3436 | 1114.284 | 18.349 | -95.2351 | 4.0709 | 4.0709 | 100.9716 | 280.9716 | 94.8209 | 0 | 0 | 42.4899 | 42.4899 | -1.7327 | 0% | 19.2139 | 0 | 0 | 167.4108 | 167.4108 | 0% | 11.22% | 0% | 80% | 0% | 0 | 4.3478 | 4.3478 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5732 | 20 | 20.2 | 0 | 9.72 | 9.72 | 9.72 | 4.86 | 239 | 5732 | 1200 | 235.726 | 10.4711 | -13.3436 | 1174.284 | 19.349 | -110.2351 | -5.767 | 0 | 105.3896 | 285.3896 | 100.8158 | 0 | 0 | 8.2965 | 8.2965 | -12.9749 | 0% | 3.7517 | 0 | 0 | 144.8174 | 144.8174 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.9037 | 4.9037 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5733 | 21 | 19 | 0 | 0 | 0 | 0 | 0 | 239 | 5733 | 1260 | 235.726 | 10.4711 | -13.3436 | 1234.284 | 20.349 | -125.2351 | -14.8378 | 0 | 105.3896 | 285.3896 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.5264 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5734 | 22 | 16.4 | 0 | 0 | 0 | 0 | 0 | 239 | 5734 | 1320 | 235.726 | 10.4711 | -13.3436 | 1294.284 | 21.349 | -140.2351 | -22.6567 | 0 | 105.3896 | 285.3896 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3742 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5735 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 239 | 5735 | 1380 | 235.726 | 10.4711 | -13.3436 | 1354.284 | 22.349 | -155.2351 | -28.6237 | 0 | 105.3896 | 285.3896 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9048 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
8 | 239 | 27 | 5736 | 24 | 13.9 | 0 | 0 | 0 | 0 | 0 | 239 | 5736 | 1440 | 235.726 | 10.4711 | -13.3436 | 1414.284 | 23.349 | -170.2351 | -32.0886 | 0 | 105.3896 | 285.3896 | 100.8158 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9781 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5737 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 240 | 5737 | 60 | 236.7123 | 10.1284 | -13.2128 | 34.284 | 0.35119 | 174.7322 | -32.8991 | 0 | 104.8795 | 75.1205 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0712 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5738 | 2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 240 | 5738 | 120 | 236.7123 | 10.1284 | -13.2128 | 94.284 | 1.3512 | 159.7322 | -30.2827 | 0 | 104.8795 | 75.1205 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4019 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5739 | 3 | 11.8 | 0 | 0 | 0 | 0 | 0 | 240 | 5739 | 180 | 236.7123 | 10.1284 | -13.2128 | 154.284 | 2.3512 | 144.7322 | -24.9783 | 0 | 104.8795 | 75.1205 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7325 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5740 | 4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 240 | 5740 | 240 | 236.7123 | 10.1284 | -13.2128 | 214.284 | 3.3512 | 129.7322 | -17.6243 | 0 | 104.8795 | 75.1205 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3421 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5741 | 5 | 10.5 | 0 | 0 | 0 | 0 | 0 | 240 | 5741 | 300 | 236.7123 | 10.1284 | -13.2128 | 274.284 | 4.3512 | 114.7322 | -8.8533 | 0 | 104.8795 | 75.1205 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.2229 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5742 | 6 | 10.2 | 0 | 0 | 0 | 0 | 0 | 240 | 5742 | 360 | 236.7123 | 10.1284 | -13.2128 | 334.284 | 5.3512 | 99.7322 | 0.81276 | 0.81276 | 103.9879 | 76.0121 | 99.2576 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.749 | 8.749 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5743 | 7 | 10.4 | 5.56 | 16.72 | 22.28 | 16.72 | 8.36 | 240 | 5743 | 420 | 236.7123 | 10.1284 | -13.2128 | 394.284 | 6.3512 | 84.7322 | 10.9552 | 10.9552 | 93.1863 | 86.8137 | 84.503 | 2.8026 | 2.8026 | 14.2714 | 17.074 | -7.1909 | 0% | 7.7209 | 0 | 0 | 175.132 | 175.132 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5744 | 8 | 12.6 | 63.94 | 63.89 | 127.83 | 63.89 | 31.95 | 240 | 5744 | 480 | 236.7123 | 10.1284 | -13.2128 | 454.284 | 7.3512 | 69.7322 | 21.2034 | 21.2034 | 82.1046 | 97.8954 | 69.7387 | 61.2215 | 61.2215 | 54.5335 | 115.7551 | -0.33126 | 0% | 52.3444 | 0 | 0 | 192.3867 | 192.3867 | 0% | 11.63% | 11.63% | 80% | 9.304% | 4.8703 | 6.5939 | 6 | 29.222 | 10.7703 | 15.19% | 15.19%
8 | 240 | 28 | 5745 | 9 | 16.6 | 149.11 | 120 | 269.11 | 120 | 60 | 240 | 5745 | 540 | 236.7123 | 10.1284 | -13.2128 | 514.284 | 8.3512 | 54.7322 | 31.1582 | 31.1582 | 69.9226 | 110.0774 | 54.9995 | 165.3007 | 165.3007 | 102.4264 | 267.7271 | 0.34712 | 34.71% | 121.0662 | 42.0249 | 29.4174 | 163.8534 | 163.8534 | 17.95% | 11.45% | 11.45% | 80% | 9.161% | 11.0912 | 5.6539 | 5.6539 | 62.7087 | 24.5271 | 38.27% | 38.27%
8 | 240 | 28 | 5746 | 10 | 19.3 | 209.86 | 145.42 | 355.28 | 145.42 | 72.71 | 240 | 5746 | 600 | 236.7123 | 10.1284 | -13.2128 | 574.284 | 9.3512 | 39.7322 | 40.2856 | 40.2856 | 55.5757 | 124.4243 | 40.3461 | 247.3626 | 247.3626 | 124.1237 | 371.4863 | 0.49093 | 49.09% | 167.9861 | 82.4693 | 57.7285 | 168.4363 | 168.4363 | 34.27% | 11.37% | 11.37% | 85% | 9.663% | 16.2329 | 5.0828 | 5.0828 | 82.5077 | 35.8976 | 48.98% | 48.98%
8 | 240 | 28 | 5747 | 11 | 21.3 | 288.67 | 162.22 | 450.89 | 162.22 | 81.11 | 240 | 5747 | 660 | 236.7123 | 10.1284 | -13.2128 | 634.284 | 10.3512 | 24.7322 | 47.7709 | 47.7709 | 37.7919 | 142.2081 | 25.9542 | 350.5321 | 350.5321 | 138.4634 | 488.9956 | 0.57515 | 57.51% | 221.1238 | 127.1789 | 89.0253 | 167.0837 | 167.0837 | 53.28% | 11.33% | 11.33% | 85% | 9.63% | 21.2949 | 4.6926 | 4.6926 | 99.9274 | 47.0917 | 59.81% | 59.81%
8 | 240 | 28 | 5748 | 12 | 23.1 | 245.28 | 206.61 | 451.89 | 206.61 | 103.31 | 240 | 5748 | 720 | 236.7123 | 10.1284 | -13.2128 | 694.284 | 11.3512 | 9.7322 | 52.4291 | 52.4291 | 15.8379 | 164.1621 | 12.777 | 301.8 | 301.8 | 176.3527 | 478.1527 | 0.57813 | 57.81% | 216.2207 | 125.0044 | 87.503 | 260.0787 | 260.0787 | 33.64% | 11.3% | 11.3% | 85% | 9.603% | 20.7627 | 4.3653 | 4.3653 | 90.6358 | 45.9149 | 34.85% | 34.85%
8 | 240 | 28 | 5749 | 13 | 25.3 | 234.94 | 271.44 | 506.38 | 271.44 | 135.72 | 240 | 5749 | 780 | 236.7123 | 10.1284 | -13.2128 | 754.284 | 12.3512 | -5.2678 | 53.078 | 53.078 | 8.6531 | 188.6531 | 9.8555 | 289.5389 | 289.5389 | 231.6885 | 521.2274 | 0.60585 | 60.59% | 235.699 | 142.7986 | 99.959 | 298.8949 | 298.8949 | 33.44% | 11.27% | 11.27% | 90% | 10.14% | 23.9085 | 3.9962 | 3.9962 | 95.5421 | 52.8716 | 31.97% | 31.97%
8 | 240 | 28 | 5750 | 14 | 25.7 | 295 | 217.22 | 512.22 | 217.22 | 108.61 | 240 | 5750 | 840 | 236.7123 | 10.1284 | -13.2128 | 814.284 | 13.3512 | -20.2678 | 49.5136 | 49.5136 | 31.6832 | 211.6832 | 21.8014 | 360.1301 | 360.1301 | 185.4089 | 545.539 | 0.61624 | 61.62% | 246.6927 | 152.0224 | 106.4156 | 296.2313 | 296.2313 | 35.92% | 11.27% | 11.27% | 90% | 10.15% | 25.027 | 3.9327 | 3.9327 | 98.423 | 55.345 | 33.23% | 33.23%
8 | 240 | 28 | 5751 | 15 | 25.6 | 253.83 | 153.83 | 407.66 | 153.83 | 76.92 | 240 | 5751 | 900 | 236.7123 | 10.1284 | -13.2128 | 874.284 | 14.3512 | -35.2678 | 42.7319 | 42.7319 | 50.6983 | 230.6983 | 36.0204 | 302.5484 | 302.5484 | 131.3021 | 433.8505 | 0.56742 | 56.74% | 196.1872 | 111.3198 | 77.9239 | 285.6857 | 285.6857 | 27.28% | 11.24% | 11.24% | 85% | 9.553% | 18.7424 | 3.9484 | 3.9484 | 74.0034 | 41.4472 | 25.9% | 25.9%
8 | 240 | 28 | 5752 | 16 | 25.7 | 188.94 | 170 | 358.94 | 170 | 85 | 240 | 5752 | 960 | 236.7123 | 10.1284 | -13.2128 | 934.284 | 15.3512 | -50.2678 | 33.9912 | 33.9912 | 65.9345 | 245.9345 | 50.6251 | 214.397 | 214.397 | 145.1041 | 359.501 | 0.51908 | 51.91% | 162.5664 | 84.3847 | 59.0693 | 284.4282 | 284.4282 | 20.77% | 11.21% | 11.21% | 85% | 9.532% | 15.4955 | 3.9327 | 3.9327 | 60.9389 | 34.267 | 21.43% | 21.43%
8 | 240 | 28 | 5753 | 17 | 25.3 | 128.56 | 136.81 | 265.37 | 136.81 | 68.41 | 240 | 5753 | 1020 | 236.7123 | 10.1284 | -13.2128 | 994.284 | 16.3512 | -65.2678 | 24.2172 | 24.2172 | 78.6365 | 258.6365 | 65.3474 | 130.7282 | 130.7282 | 116.7746 | 247.5028 | 0.38671 | 38.67% | 111.9208 | 43.2809 | 30.2966 | 270.4896 | 270.4896 | 11.2% | 11.19% | 11.19% | 80% | 8.953% | 10.02 | 3.9962 | 3.9962 | 40.0415 | 22.1583 | 14.8% | 14.8%
8 | 240 | 28 | 5754 | 18 | 24.7 | 59.5 | 93.89 | 153.39 | 93.89 | 46.95 | 240 | 5754 | 1080 | 236.7123 | 10.1284 | -13.2128 | 1054.284 | 17.3512 | -80.2678 | 14.011 | 14.011 | 89.9508 | 269.9508 | 80.1084 | 42.2176 | 42.2176 | 80.1401 | 122.3578 | -0.05055 | 0% | 55.3302 | 0 | 0 | 251.141 | 251.141 | 0% | 11.18% | 0% | 80% | 0% | 0 | 4.0935 | 4.0935 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5755 | 19 | 23 | 9.5 | 48 | 57.5 | 48 | 24 | 240 | 5755 | 1140 | 236.7123 | 10.1284 | -13.2128 | 1114.284 | 18.3512 | -95.2678 | 3.7987 | 3.7987 | 100.7603 | 280.7603 | 94.8691 | 0 | 0 | 40.9706 | 40.9706 | -1.8373 | 0% | 18.5269 | 0 | 0 | 159.2821 | 159.2821 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.3829 | 4.3829 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5756 | 20 | 21 | 0 | 7.28 | 7.28 | 7.28 | 3.64 | 240 | 5756 | 1200 | 236.7123 | 10.1284 | -13.2128 | 1174.284 | 19.3512 | -110.2678 | -6.0494 | 0 | 104.8795 | 284.8795 | 100.4616 | 0 | 0 | 6.2139 | 6.2139 | -17.3108 | 0% | 2.8099 | 0 | 0 | 146.7794 | 146.7794 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7493 | 4.7493 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5757 | 21 | 19 | 0 | 0 | 0 | 0 | 0 | 240 | 5757 | 1260 | 236.7123 | 10.1284 | -13.2128 | 1234.284 | 20.3512 | -125.2678 | -15.1359 | 0 | 104.8795 | 284.8795 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.2039 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5758 | 22 | 16.9 | 0 | 0 | 0 | 0 | 0 | 240 | 5758 | 1320 | 236.7123 | 10.1284 | -13.2128 | 1294.284 | 21.3512 | -140.2678 | -22.9735 | 0 | 104.8795 | 284.8795 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8788 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5759 | 23 | 15.3 | 0 | 0 | 0 | 0 | 0 | 240 | 5759 | 1380 | 236.7123 | 10.1284 | -13.2128 | 1354.284 | 22.3512 | -155.2678 | -28.9581 | 0 | 104.8795 | 284.8795 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7335 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
8 | 240 | 28 | 5760 | 24 | 13.9 | 0 | 0 | 0 | 0 | 0 | 240 | 5760 | 1440 | 236.7123 | 10.1284 | -13.2128 | 1414.284 | 23.3512 | -170.2678 | -32.4325 | 0 | 104.8795 | 284.8795 | 100.4616 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2833 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5761 | 1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 241 | 5761 | 60 | 237.6986 | 9.7826 | -13.0715 | 34.284 | 0.35354 | 174.6969 | -33.2413 | 0 | 104.3655 | 75.6345 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.49 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5762 | 2 | 12.6 | 0 | 0 | 0 | 0 | 0 | 241 | 5762 | 120 | 237.6986 | 9.7826 | -13.0715 | 94.284 | 1.3535 | 159.6969 | -30.6056 | 0 | 104.3655 | 75.6345 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9103 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5763 | 3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 241 | 5763 | 180 | 237.6986 | 9.7826 | -13.0715 | 154.284 | 2.3535 | 144.6969 | -25.2742 | 0 | 104.3655 | 75.6345 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2449 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5764 | 4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 241 | 5764 | 240 | 237.6986 | 9.7826 | -13.0715 | 214.284 | 3.3535 | 129.6969 | -17.8931 | 0 | 104.3655 | 75.6345 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3973 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5765 | 5 | 10.6 | 0 | 0 | 0 | 0 | 0 | 241 | 5765 | 300 | 237.6986 | 9.7826 | -13.0715 | 274.284 | 4.3535 | 114.6969 | -9.1 | 0 | 104.3655 | 75.6345 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.4119 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5766 | 6 | 10.3 | 0 | 0 | 0 | 0 | 0 | 241 | 5766 | 360 | 237.6986 | 9.7826 | -13.0715 | 334.284 | 5.3535 | 99.6969 | 0.5811 | 0.5811 | 103.7288 | 76.2712 | 99.2438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.65859 | 0.65859 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5767 | 7 | 10.4 | 5.28 | 21.33 | 26.61 | 21.33 | 10.67 | 241 | 5767 | 420 | 237.6986 | 9.7826 | -13.0715 | 394.284 | 6.3535 | 84.6969 | 10.7304 | 10.7304 | 92.9163 | 87.0837 | 84.4733 | 2.7312 | 2.7312 | 18.2063 | 20.9374 | -5.7156 | 0% | 9.4679 | 0 | 0 | 161.2795 | 161.2795 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5768 | 8 | 12.5 | 37.36 | 78.67 | 116.03 | 78.67 | 39.34 | 241 | 5768 | 480 | 237.6986 | 9.7826 | -13.0715 | 454.284 | 7.3535 | 69.6969 | 20.9765 | 20.9765 | 81.8224 | 98.1776 | 69.6931 | 36.2187 | 36.2187 | 67.149 | 103.3677 | -0.46953 | 0% | 46.7429 | 0 | 0 | 174.9544 | 174.9544 | 0% | 11.64% | 11.64% | 80% | 9.311% | 4.3525 | 6.6189 | 6 | 26.1147 | 9.6251 | 14.93% | 14.93%
8 | 241 | 29 | 5769 | 9 | 16.6 | 92.5 | 140.33 | 232.83 | 140.33 | 70.17 | 241 | 5769 | 540 | 237.6986 | 9.7826 | -13.0715 | 514.284 | 8.3535 | 54.6969 | 30.9188 | 30.9188 | 69.6285 | 110.3715 | 54.9356 | 103.4228 | 103.4228 | 119.7791 | 223.2019 | 0.25598 | 25.6% | 100.9319 | 25.8369 | 18.0858 | 145.4639 | 145.4639 | 12.43% | 11.46% | 11.46% | 80% | 9.168% | 9.2533 | 5.6539 | 5.6539 | 52.3177 | 20.4629 | 35.97% | 35.97%
8 | 241 | 29 | 5770 | 10 | 19 | 123.75 | 173.83 | 297.58 | 173.83 | 86.92 | 241 | 5770 | 600 | 237.6986 | 9.7826 | -13.0715 | 574.284 | 9.3535 | 39.6969 | 40.022 | 40.022 | 55.2793 | 124.7207 | 40.257 | 146.8557 | 146.8557 | 148.3732 | 295.2289 | 0.40782 | 40.78% | 133.5025 | 54.4443 | 38.111 | 150.1973 | 150.1973 | 25.37% | 11.38% | 11.38% | 80% | 9.104% | 12.1538 | 5.1437 | 5.1437 | 62.5156 | 26.8771 | 41.62% | 41.62%
8 | 241 | 29 | 5771 | 11 | 21.7 | 136.53 | 184.39 | 320.92 | 184.39 | 92.2 | 241 | 5771 | 660 | 237.6986 | 9.7826 | -13.0715 | 634.284 | 10.3535 | 24.6969 | 47.4726 | 47.4726 | 37.5272 | 142.4728 | 25.8207 | 166.7663 | 166.7663 | 157.3867 | 324.153 | 0.46146 | 46.15% | 146.582 | 67.6418 | 47.3493 | 149.7753 | 149.7753 | 31.61% | 11.31% | 11.31% | 85% | 9.611% | 14.0886 | 4.6179 | 4.6179 | 65.0592 | 31.1556 | 43.44% | 43.44%
8 | 241 | 29 | 5772 | 12 | 23 | 150.69 | 160.33 | 311.02 | 160.33 | 80.17 | 241 | 5772 | 720 | 237.6986 | 9.7826 | -13.0715 | 694.284 | 11.3535 | 9.6969 | 52.096 | 52.096 | 15.6754 | 164.3246 | 12.5296 | 186.4303 | 186.4303 | 136.8502 | 323.2805 | 0.46926 | 46.93% | 146.1874 | 68.6 | 48.02 | 143.0595 | 143.0595 | 33.57% | 11.27% | 11.27% | 85% | 9.582% | 14.0082 | 4.3829 | 4.3829 | 61.3964 | 30.9778 | 42.92% | 42.92%
8 | 241 | 29 | 5773 | 13 | 25 | 170.56 | 191.06 | 361.62 | 191.06 | 95.53 | 241 | 5773 | 780 | 237.6986 | 9.7826 | -13.0715 | 754.284 | 12.3535 | -5.3031 | 52.7304 | 52.7304 | 8.6505 | 188.6505 | 9.5846 | 211.3348 | 211.3348 | 163.0799 | 374.4147 | 0.52645 | 52.64% | 169.3103 | 89.1329 | 62.393 | 274.8302 | 274.8302 | 22.7% | 11.23% | 11.23% | 85% | 9.55% | 16.1687 | 4.0445 | 4.0445 | 65.3942 | 35.7556 | 23.79% | 23.79%
8 | 241 | 29 | 5774 | 14 | 23.9 | 141.44 | 178.28 | 319.72 | 178.28 | 89.14 | 241 | 5774 | 840 | 237.6986 | 9.7826 | -13.0715 | 814.284 | 13.3535 | -20.3031 | 49.1789 | 49.1789 | 31.5395 | 211.5395 | 21.7113 | 173.6446 | 173.6446 | 152.1715 | 325.8161 | 0.47782 | 47.78% | 147.334 | 70.3988 | 49.2792 | 263.245 | 263.245 | 18.72% | 11.25% | 11.25% | 85% | 9.563% | 14.0892 | 4.2272 | 4.2272 | 59.5571 | 31.157 | 22.62% | 22.62%
8 | 241 | 29 | 5775 | 15 | 25.1 | 221.61 | 225.56 | 447.17 | 225.56 | 112.78 | 241 | 5775 | 900 | 237.6986 | 9.7826 | -13.0715 | 874.284 | 14.3535 | -35.3031 | 42.4215 | 42.4215 | 50.4858 | 230.4858 | 35.9895 | 265.8102 | 265.8102 | 192.5275 | 458.3377 | 0.57773 | 57.77% | 207.2603 | 119.7411 | 83.8188 | 272.4582 | 272.4582 | 30.76% | 11.26% | 11.26% | 85% | 9.568% | 19.8301 | 4.0283 | 4.0283 | 79.882 | 43.8526 | 29.32% | 29.32%
8 | 241 | 29 | 5776 | 16 | 25.4 | 229.11 | 179.5 | 408.61 | 179.5 | 89.75 | 241 | 5776 | 960 | 237.6986 | 9.7826 | -13.0715 | 934.284 | 15.3535 | -50.3031 | 33.7018 | 33.7018 | 65.7028 | 245.7028 | 50.624 | 261.9513 | 261.9513 | 153.2128 | 415.1641 | 0.55574 | 55.57% | 187.7372 | 104.3336 | 73.0335 | 288.5357 | 288.5357 | 25.31% | 11.24% | 11.24% | 85% | 9.552% | 17.9327 | 3.9802 | 3.9802 | 71.3756 | 39.6567 | 24.74% | 24.74%
8 | 241 | 29 | 5777 | 17 | 25.3 | 177 | 138.19 | 315.19 | 138.19 | 69.1 | 241 | 5777 | 1020 | 237.6986 | 9.7826 | -13.0715 | 994.284 | 16.3535 | -65.3031 | 23.9404 | 23.9404 | 78.4063 | 258.4063 | 65.3663 | 181.811 | 181.811 | 117.9525 | 299.7635 | 0.45946 | 45.95% | 135.5531 | 62.2813 | 43.5969 | 282.0475 | 282.0475 | 15.46% | 11.21% | 11.21% | 80% | 8.965% | 12.1523 | 3.9962 | 3.9962 | 48.5623 | 26.8736 | 17.22% | 17.22%
8 | 241 | 29 | 5778 | 18 | 24.5 | 130.56 | 109.39 | 239.95 | 109.39 | 54.7 | 241 | 5778 | 1080 | 237.6986 | 9.7826 | -13.0715 | 1054.284 | 17.3535 | -80.3031 | 13.7382 | 13.7382 | 89.7289 | 269.7289 | 80.1437 | 94.1068 | 94.1068 | 93.3702 | 187.477 | 0.24399 | 24.4% | 84.7771 | 20.6849 | 14.4794 | 266.6564 | 266.6564 | 5.43% | 11.2% | 0% | 80% | 0% | 0 | 4.1265 | 4.1265 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5779 | 19 | 22.9 | 28.39 | 53.19 | 81.58 | 53.19 | 26.6 | 241 | 5779 | 1140 | 237.6986 | 9.7826 | -13.0715 | 1114.284 | 18.3535 | -95.3031 | 3.5224 | 3.5224 | 100.549 | 280.549 | 94.92 | 0 | 0 | 45.4005 | 45.4005 | -1.5843 | 0% | 20.5301 | 0 | 0 | 160.2015 | 160.2015 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.4006 | 4.4006 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5780 | 20 | 19.9 | 0 | 8.94 | 8.94 | 8.94 | 4.47 | 241 | 5780 | 1200 | 237.6986 | 9.7826 | -13.0715 | 1174.284 | 19.3535 | -110.3031 | -6.3359 | 0 | 104.3655 | 284.3655 | 100.1041 | 0 | 0 | 7.6308 | 7.6308 | -14.2636 | 0% | 3.4506 | 0 | 0 | 145.1095 | 145.1095 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5781 | 21 | 17.3 | 0 | 0 | 0 | 0 | 0 | 241 | 5781 | 1260 | 237.6986 | 9.7826 | -13.0715 | 1234.284 | 20.3535 | -125.3031 | -15.4379 | 0 | 104.3655 | 284.3655 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.7662 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5782 | 22 | 15.6 | 0 | 0 | 0 | 0 | 0 | 241 | 5782 | 1320 | 237.6986 | 9.7826 | -13.0715 | 1294.284 | 21.3535 | -140.3031 | -23.2943 | 0 | 104.3655 | 284.3655 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7053 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5783 | 23 | 14.6 | 0 | 0 | 0 | 0 | 0 | 241 | 5783 | 1380 | 237.6986 | 9.7826 | -13.0715 | 1354.284 | 22.3535 | -155.3031 | -29.2963 | 0 | 104.3655 | 284.3655 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8875 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
8 | 241 | 29 | 5784 | 24 | 13.8 | 0 | 0 | 0 | 0 | 0 | 241 | 5784 | 1440 | 237.6986 | 9.7826 | -13.0715 | 1414.284 | 23.3535 | -170.3031 | -32.7799 | 0 | 104.3655 | 284.3655 | 100.1041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.765 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5785 | 1 | 12.9 | 0 | 0 | 0 | 0 | 0 | 242 | 5785 | 60 | 238.6849 | 9.4337 | -12.9199 | 34.284 | 0.35607 | 174.659 | -33.5863 | 0 | 103.8476 | 76.1524 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.739 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5786 | 2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 242 | 5786 | 120 | 238.6849 | 9.4337 | -12.9199 | 94.284 | 1.3561 | 159.659 | -30.9305 | 0 | 103.8476 | 76.1524 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2693 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5787 | 3 | 11.3 | 0 | 0 | 0 | 0 | 0 | 242 | 5787 | 180 | 238.6849 | 9.4337 | -12.9199 | 154.284 | 2.3561 | 144.659 | -25.5714 | 0 | 103.8476 | 76.1524 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5804 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5788 | 4 | 10.6 | 0 | 0 | 0 | 0 | 0 | 242 | 5788 | 240 | 238.6849 | 9.4337 | -12.9199 | 214.284 | 3.3561 | 129.659 | -18.1628 | 0 | 103.8476 | 76.1524 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6472 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5789 | 5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 242 | 5789 | 300 | 238.6849 | 9.4337 | -12.9199 | 274.284 | 4.3561 | 114.659 | -9.3472 | 0 | 103.8476 | 76.1524 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3931 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5790 | 6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 242 | 5790 | 360 | 238.6849 | 9.4337 | -12.9199 | 334.284 | 5.3561 | 99.659 | 0.34897 | 0.34897 | 103.4657 | 76.5343 | 99.2272 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.0904 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5791 | 7 | 10.1 | 0.56 | 7.17 | 7.73 | 7.17 | 3.59 | 242 | 5791 | 420 | 238.6849 | 9.4337 | -12.9199 | 394.284 | 6.3561 | 84.659 | 10.5051 | 10.5051 | 92.6427 | 87.3573 | 84.4413 | 0.29752 | 0.29752 | 6.12 | 6.4175 | -20.5757 | 0% | 2.902 | 0 | 0 | 152.7488 | 152.7488 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5792 | 8 | 13.1 | 16.67 | 45.42 | 62.09 | 45.42 | 22.71 | 242 | 5792 | 480 | 238.6849 | 9.4337 | -12.9199 | 454.284 | 7.3561 | 69.659 | 20.7488 | 20.7488 | 81.5367 | 98.4633 | 69.6456 | 16.3668 | 16.3668 | 38.7684 | 55.1352 | -1.5586 | 0% | 24.9321 | 0 | 0 | 164.8737 | 164.8737 | 0% | 11.63% | 11.63% | 80% | 9.308% | 2.3206 | 6.4703 | 6 | 13.9237 | 5.1318 | 8.445% | 8.445%
8 | 242 | 30 | 5793 | 9 | 16.6 | 35.83 | 115.06 | 150.89 | 115.06 | 57.53 | 242 | 5793 | 540 | 238.6849 | 9.4337 | -12.9199 | 514.284 | 8.3561 | 54.659 | 30.6781 | 30.6781 | 69.3313 | 110.6687 | 54.8703 | 40.4097 | 40.4097 | 98.2099 | 138.6196 | -0.078403 | 0% | 62.6838 | 0 | 0 | 153.9759 | 153.9759 | 0% | 11.48% | 11.48% | 80% | 9.181% | 5.7547 | 5.6539 | 5.6539 | 32.5368 | 12.726 | 21.13% | 21.13%
8 | 242 | 30 | 5794 | 10 | 20 | 87.36 | 153.47 | 240.83 | 153.47 | 76.74 | 242 | 5794 | 600 | 238.6849 | 9.4337 | -12.9199 | 574.284 | 9.3561 | 39.659 | 39.7566 | 39.7566 | 54.9802 | 125.0198 | 40.1672 | 104.3855 | 104.3855 | 130.9948 | 235.3803 | 0.31646 | 31.65% | 106.439 | 33.6836 | 23.5785 | 141.1088 | 141.1088 | 16.71% | 11.35% | 11.35% | 80% | 9.082% | 9.6664 | 4.943 | 4.943 | 47.7808 | 21.3763 | 33.86% | 33.86%
8 | 242 | 30 | 5795 | 11 | 21.1 | 178.47 | 181.81 | 360.28 | 181.81 | 90.91 | 242 | 5795 | 660 | 238.6849 | 9.4337 | -12.9199 | 634.284 | 10.3561 | 24.659 | 47.172 | 47.172 | 37.2601 | 142.7399 | 25.6877 | 219.2968 | 219.2968 | 155.1845 | 374.4814 | 0.504 | 50.4% | 169.3405 | 85.3475 | 59.7433 | 143.7946 | 143.7946 | 41.55% | 11.33% | 11.33% | 85% | 9.627% | 16.3029 | 4.7303 | 4.7303 | 77.1181 | 36.0525 | 53.63% | 53.63%
8 | 242 | 30 | 5796 | 12 | 22.6 | 191.39 | 195 | 386.39 | 195 | 97.5 | 242 | 5796 | 720 | 238.6849 | 9.4337 | -12.9199 | 694.284 | 11.3561 | 9.659 | 51.7603 | 51.7603 | 15.5102 | 164.4898 | 12.283 | 238.0981 | 238.0981 | 166.4429 | 404.541 | 0.53436 | 53.44% | 182.9334 | 97.7524 | 68.4267 | 140.5786 | 140.5786 | 48.68% | 11.3% | 11.3% | 85% | 9.601% | 17.5637 | 4.4539 | 4.4539 | 78.2276 | 38.8405 | 55.65% | 55.65%
8 | 242 | 30 | 5797 | 13 | 23 | 183.75 | 172.72 | 356.47 | 172.72 | 86.36 | 242 | 5797 | 780 | 238.6849 | 9.4337 | -12.9199 | 754.284 | 12.3561 | -5.341 | 52.3795 | 52.3795 | 8.6516 | 188.6516 | 9.3178 | 228.9256 | 228.9256 | 147.4257 | 376.3514 | 0.51646 | 51.65% | 170.1861 | 87.8949 | 61.5264 | 138.3493 | 138.3493 | 44.47% | 11.28% | 11.28% | 85% | 9.59% | 16.3205 | 4.3829 | 4.3829 | 71.531 | 36.0913 | 51.7% | 51.7%
8 | 242 | 30 | 5798 | 14 | 25.3 | 141.25 | 168.75 | 310 | 168.75 | 84.38 | 242 | 5798 | 840 | 238.6849 | 9.4337 | -12.9199 | 814.284 | 13.3561 | -20.341 | 48.8402 | 48.8402 | 31.3997 | 211.3997 | 21.6275 | 174.4057 | 174.4057 | 144.0371 | 318.4428 | 0.47967 | 47.97% | 143.9998 | 69.0725 | 48.3507 | 285.4044 | 285.4044 | 16.94% | 11.21% | 11.21% | 85% | 9.53% | 13.723 | 3.9962 | 3.9962 | 54.8393 | 30.3472 | 19.21% | 19.21%
8 | 242 | 30 | 5799 | 15 | 24.9 | 123.11 | 198.19 | 321.3 | 198.19 | 99.1 | 242 | 5799 | 900 | 238.6849 | 9.4337 | -12.9199 | 874.284 | 14.3561 | -35.341 | 42.1068 | 42.1068 | 50.2763 | 230.2763 | 35.9636 | 148.6083 | 148.6083 | 169.1657 | 317.7741 | 0.4763 | 47.63% | 143.6974 | 68.4436 | 47.9105 | 287.7871 | 287.7871 | 16.65% | 11.22% | 11.22% | 85% | 9.539% | 13.7069 | 4.0608 | 4.0608 | 55.6604 | 30.3116 | 19.34% | 19.34%
8 | 242 | 30 | 5800 | 16 | 25.8 | 69.58 | 164.11 | 233.69 | 164.11 | 82.06 | 242 | 5800 | 960 | 238.6849 | 9.4337 | -12.9199 | 934.284 | 15.3561 | -50.341 | 33.408 | 33.408 | 65.4728 | 245.4728 | 50.6269 | 80.1663 | 80.1663 | 140.0766 | 220.243 | 0.33989 | 33.99% | 99.5939 | 33.8509 | 23.6956 | 287.1934 | 287.1934 | 8.251% | 11.17% | 11.17% | 80% | 8.934% | 8.8974 | 3.917 | 3.917 | 34.8508 | 19.6757 | 12.13% | 12.13%
8 | 242 | 30 | 5801 | 17 | 25.3 | 43.67 | 133.75 | 177.42 | 133.75 | 66.88 | 242 | 5801 | 1020 | 238.6849 | 9.4337 | -12.9199 | 994.284 | 16.3561 | -65.341 | 23.6593 | 23.6593 | 78.1769 | 258.1769 | 65.3886 | 45.3203 | 45.3203 | 114.1628 | 159.483 | 0.15641 | 15.64% | 72.1182 | 11.2797 | 7.8958 | 283.0131 | 283.0131 | 2.79% | 11.17% | 11.17% | 80% | 8.932% | 6.4418 | 3.9962 | 3.9962 | 25.7423 | 14.2454 | 9.096% | 9.096%
8 | 242 | 30 | 5802 | 18 | 24.4 | 54.44 | 110.42 | 164.86 | 110.42 | 55.21 | 242 | 5802 | 1080 | 238.6849 | 9.4337 | -12.9199 | 1054.284 | 17.3561 | -80.341 | 13.4613 | 13.4613 | 89.5072 | 269.5072 | 80.1819 | 39.878 | 39.878 | 94.2494 | 134.1274 | 0.01965 | 1.965% | 60.6524 | 1.1918 | 0.83427 | 275.5215 | 275.5215 | 0.3028% | 11.19% | 0% | 80% | 0% | 0 | 4.1431 | 4.1431 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5803 | 19 | 22.6 | 18.47 | 57 | 75.47 | 57 | 28.5 | 242 | 5803 | 1140 | 238.6849 | 9.4337 | -12.9199 | 1114.284 | 18.3561 | -95.341 | 3.2421 | 3.2421 | 100.3376 | 280.3376 | 94.9735 | 0 | 0 | 48.6525 | 48.6525 | -1.438 | 0% | 22.0007 | 0 | 0 | 156.4485 | 156.4485 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4539 | 4.4539 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5804 | 20 | 18.7 | 0 | 6.94 | 6.94 | 6.94 | 3.47 | 242 | 5804 | 1200 | 238.6849 | 9.4337 | -12.9199 | 1174.284 | 19.3561 | -110.341 | -6.6262 | 0 | 103.8476 | 283.8476 | 99.7436 | 0 | 0 | 5.9237 | 5.9237 | -19.0537 | 0% | 2.6787 | 0 | 0 | 142.4503 | 142.4503 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2053 | 5.2053 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5805 | 21 | 15.5 | 0 | 0 | 0 | 0 | 0 | 242 | 5805 | 1260 | 238.6849 | 9.4337 | -12.9199 | 1234.284 | 20.3561 | -125.341 | -15.7438 | 0 | 103.8476 | 283.8476 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.754 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5806 | 22 | 13.8 | 0 | 0 | 0 | 0 | 0 | 242 | 5806 | 1320 | 238.6849 | 9.4337 | -12.9199 | 1294.284 | 21.3561 | -140.341 | -23.6188 | 0 | 103.8476 | 283.8476 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2627 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5807 | 23 | 13 | 0 | 0 | 0 | 0 | 0 | 242 | 5807 | 1380 | 238.6849 | 9.4337 | -12.9199 | 1354.284 | 22.3561 | -155.341 | -29.638 | 0 | 103.8476 | 283.8476 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1835 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
8 | 242 | 30 | 5808 | 24 | 12.2 | 0 | 0 | 0 | 0 | 0 | 242 | 5808 | 1440 | 238.6849 | 9.4337 | -12.9199 | 1414.284 | 23.3561 | -170.341 | -33.1306 | 0 | 103.8476 | 283.8476 | 99.7436 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1042 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5809 | 1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 243 | 5809 | 60 | 239.6712 | 9.0819 | -12.7582 | 34.284 | 0.35876 | 174.6186 | -33.934 | 0 | 103.326 | 76.674 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8004 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5810 | 2 | 10.8 | 0 | 0 | 0 | 0 | 0 | 243 | 5810 | 120 | 239.6712 | 9.0819 | -12.7582 | 94.284 | 1.3588 | 159.6186 | -31.2573 | 0 | 103.326 | 76.674 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.594 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5811 | 3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 243 | 5811 | 180 | 239.6712 | 9.0819 | -12.7582 | 154.284 | 2.3588 | 144.6186 | -25.8698 | 0 | 103.326 | 76.674 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0828 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5812 | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 243 | 5812 | 240 | 239.6712 | 9.0819 | -12.7582 | 214.284 | 3.3588 | 129.6186 | -18.4332 | 0 | 103.326 | 76.674 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9972 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5813 | 5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 243 | 5813 | 300 | 239.6712 | 9.0819 | -12.7582 | 274.284 | 4.3588 | 114.6186 | -9.595 | 0 | 103.326 | 76.674 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.9984 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5814 | 6 | 8.6 | 0 | 0 | 0 | 0 | 0 | 243 | 5814 | 360 | 239.6712 | 9.0819 | -12.7582 | 334.284 | 5.3588 | 99.6186 | 0.11639 | 0.11639 | 103.1987 | 76.8013 | 99.2079 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.0372 | 7.0372 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5815 | 7 | 9 | 6.72 | 13.56 | 20.28 | 13.56 | 6.78 | 243 | 5815 | 420 | 239.6712 | 9.0819 | -12.7582 | 394.284 | 6.3588 | 84.6186 | 10.2792 | 10.2792 | 92.3655 | 87.6345 | 84.4069 | 3.6703 | 3.6703 | 11.5742 | 15.2445 | -8.3652 | 0% | 6.8936 | 0 | 0 | 174.9989 | 174.9989 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5816 | 8 | 11.4 | 68.83 | 62 | 130.83 | 62 | 31 | 243 | 5816 | 480 | 239.6712 | 9.0819 | -12.7582 | 454.284 | 7.3588 | 69.6186 | 20.5202 | 20.5202 | 81.2478 | 98.7522 | 69.5962 | 68.4564 | 68.4564 | 52.9203 | 121.3767 | -0.3015 | 0% | 54.8865 | 0 | 0 | 193.1321 | 193.1321 | 0% | 11.67% | 11.67% | 80% | 9.338% | 5.1255 | 6.8978 | 6 | 30.7531 | 11.3346 | 15.92% | 15.92%
8 | 243 | 31 | 5817 | 9 | 16.3 | 163.75 | 78.19 | 241.94 | 78.19 | 39.1 | 243 | 5817 | 540 | 239.6712 | 9.0819 | -12.7582 | 514.284 | 8.3588 | 54.6186 | 30.4362 | 30.4362 | 69.031 | 110.969 | 54.8036 | 186.3132 | 186.3132 | 66.7393 | 253.0525 | 0.31796 | 31.8% | 114.4303 | 36.3846 | 25.4692 | 164.7302 | 164.7302 | 15.46% | 11.46% | 11.46% | 80% | 9.171% | 10.494 | 5.7206 | 5.7206 | 60.0315 | 23.2065 | 36.44% | 36.44%
8 | 243 | 31 | 5818 | 10 | 19.1 | 302.5 | 77.72 | 380.22 | 77.72 | 38.86 | 243 | 5818 | 600 | 239.6712 | 9.0819 | -12.7582 | 574.284 | 9.3588 | 39.6186 | 39.4895 | 39.4895 | 54.6785 | 125.3215 | 40.0769 | 363.9784 | 363.9784 | 66.3382 | 430.3166 | 0.5327 | 53.27% | 194.5891 | 103.6581 | 72.5607 | 172.4261 | 172.4261 | 42.08% | 11.37% | 11.37% | 85% | 9.665% | 18.8066 | 5.1233 | 5.1233 | 96.3519 | 41.589 | 55.88% | 55.88%
8 | 243 | 31 | 5819 | 11 | 21.8 | 419.94 | 74.31 | 494.25 | 74.31 | 37.16 | 243 | 5819 | 660 | 239.6712 | 9.0819 | -12.7582 | 634.284 | 10.3588 | 24.6186 | 46.8693 | 46.8693 | 36.9909 | 143.0091 | 25.5552 | 519.1278 | 519.1278 | 63.4276 | 582.5553 | 0.61377 | 61.38% | 263.4315 | 161.6873 | 113.1811 | 172.5861 | 172.5861 | 65.58% | 11.33% | 11.33% | 90% | 10.2% | 26.8632 | 4.5994 | 4.5994 | 123.5542 | 59.4056 | 71.59% | 71.59%
8 | 243 | 31 | 5820 | 12 | 21.8 | 492.56 | 89.94 | 582.5 | 89.94 | 44.97 | 243 | 5820 | 720 | 239.6712 | 9.0819 | -12.7582 | 694.284 | 11.3588 | 9.6186 | 51.4219 | 51.4219 | 15.3426 | 164.6574 | 12.0377 | 616.2119 | 616.2119 | 76.7686 | 692.9805 | 0.64409 | 64.41% | 313.3658 | 201.8345 | 141.2841 | 163.274 | 163.274 | 86.53% | 11.34% | 11.34% | 90% | 10.21% | 31.9861 | 4.5994 | 4.5994 | 147.1161 | 70.7344 | 90.1% | 90.1%
8 | 243 | 31 | 5821 | 13 | 23.4 | 529.94 | 114.22 | 644.16 | 114.22 | 57.11 | 243 | 5821 | 780 | 239.6712 | 9.0819 | -12.7582 | 754.284 | 12.3588 | -5.3814 | 52.0255 | 52.0255 | 8.6565 | 188.6565 | 9.0558 | 663.8904 | 663.8904 | 97.4929 | 761.3833 | 0.663 | 66.3% | 344.2975 | 228.2708 | 159.7896 | 302.2387 | 302.2387 | 52.87% | 11.34% | 11.34% | 90% | 10.21% | 35.1538 | 4.313 | 4.313 | 151.6177 | 77.7395 | 50.16% | 50.16%
8 | 243 | 31 | 5822 | 14 | 24.8 | 521.89 | 108.47 | 630.36 | 108.47 | 54.24 | 243 | 5822 | 840 | 239.6712 | 9.0819 | -12.7582 | 814.284 | 13.3588 | -20.3814 | 48.4977 | 48.4977 | 31.2639 | 211.2639 | 21.5503 | 648.1354 | 648.1354 | 92.5849 | 740.7204 | 0.66313 | 66.31% | 334.9538 | 222.1171 | 155.482 | 312.3112 | 312.3112 | 49.78% | 11.34% | 11.34% | 90% | 10.2% | 34.1744 | 4.0771 | 4.0771 | 139.3317 | 75.5736 | 44.61% | 44.61%
8 | 243 | 31 | 5823 | 15 | 25 | 479.17 | 113.47 | 592.64 | 113.47 | 56.74 | 243 | 5823 | 900 | 239.6712 | 9.0819 | -12.7582 | 874.284 | 14.3588 | -35.3814 | 41.7878 | 41.7878 | 50.0696 | 230.0696 | 35.9427 | 582.1629 | 582.1629 | 96.8527 | 679.0156 | 0.65095 | 65.1% | 307.0509 | 199.8763 | 139.9134 | 304.0317 | 304.0317 | 46.02% | 11.32% | 11.32% | 90% | 10.19% | 31.2788 | 4.0445 | 4.0445 | 126.5072 | 69.1703 | 41.61% | 41.61%
8 | 243 | 31 | 5824 | 16 | 23.1 | 381.17 | 104.03 | 485.2 | 104.03 | 52.02 | 243 | 5824 | 960 | 239.6712 | 9.0819 | -12.7582 | 934.284 | 15.3588 | -50.3814 | 33.1098 | 33.1098 | 65.2445 | 245.2445 | 50.6339 | 442.5966 | 442.5966 | 88.7952 | 531.3918 | 0.60076 | 60.08% | 240.2954 | 144.3604 | 101.0523 | 278.9823 | 278.9823 | 36.22% | 11.31% | 11.31% | 90% | 10.18% | 24.4515 | 4.3653 | 4.3653 | 106.7383 | 54.0722 | 38.26% | 38.26%
8 | 243 | 31 | 5825 | 17 | 22.85 | 227.36 | 114.86 | 342.22 | 114.86 | 57.43 | 243 | 5825 | 1020 | 239.6712 | 9.0819 | -12.7582 | 994.284 | 16.3588 | -65.3814 | 23.3739 | 23.3739 | 77.9484 | 257.9484 | 65.4144 | 238.434 | 238.434 | 98.0391 | 336.4731 | 0.48142 | 48.14% | 152.1531 | 73.2498 | 51.2748 | 142.5539 | 142.5539 | 35.97% | 11.28% | 11.28% | 85% | 9.587% | 14.5876 | 4.4094 | 4.4094 | 64.3227 | 32.2592 | 45.12% | 45.12%
8 | 243 | 31 | 5826 | 18 | 22.13 | 88.11 | 97.56 | 185.67 | 97.56 | 48.78 | 243 | 5826 | 1080 | 239.6712 | 9.0819 | -12.7582 | 1054.284 | 17.3588 | -80.3814 | 13.1803 | 13.1803 | 89.2859 | 269.2859 | 80.2231 | 65.6188 | 65.6188 | 83.2727 | 148.8915 | 0.064537 | 6.454% | 67.3287 | 4.3452 | 3.0416 | 128.9028 | 128.9028 | 2.36% | 11.28% | 0% | 80% | 0% | 0 | 4.5388 | 4.5388 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5827 | 19 | 20.75 | 20.69 | 50 | 70.69 | 50 | 25 | 243 | 5827 | 1140 | 239.6712 | 9.0819 | -12.7582 | 1114.284 | 18.3588 | -95.3814 | 2.9579 | 2.9579 | 100.1262 | 280.1262 | 95.0295 | 0 | 0 | 42.6777 | 42.6777 | -1.8463 | 0% | 19.2988 | 0 | 0 | 157.9065 | 157.9065 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.7971 | 4.7971 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5828 | 20 | 18.81 | 0 | 6.53 | 6.53 | 6.53 | 3.27 | 243 | 5828 | 1200 | 239.6712 | 9.0819 | -12.7582 | 1174.284 | 19.3588 | -110.3814 | -6.9204 | 0 | 103.326 | 283.326 | 99.38 | 0 | 0 | 5.5737 | 5.5737 | -20.2567 | 0% | 2.5204 | 0 | 0 | 143.9439 | 143.9439 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1826 | 5.1826 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5829 | 21 | 16.96 | 0 | 0 | 0 | 0 | 0 | 243 | 5829 | 1260 | 239.6712 | 9.0819 | -12.7582 | 1234.284 | 20.3588 | -125.3814 | -16.0533 | 0 | 103.326 | 283.326 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9171 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.5748 | 5.5748 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5830 | 22 | 15.47 | 0 | 0 | 0 | 0 | 0 | 243 | 5830 | 1320 | 239.6712 | 9.0819 | -12.7582 | 1294.284 | 21.3588 | -140.3814 | -23.9469 | 0 | 103.326 | 283.326 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7889 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9081 | 5.9081 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5831 | 23 | 14.21 | 0 | 0 | 0 | 0 | 0 | 243 | 5831 | 1380 | 239.6712 | 9.0819 | -12.7582 | 1354.284 | 22.3588 | -155.3814 | -29.9834 | 0 | 103.326 | 283.326 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1312 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2021 | 6 | 0 | 0 | 0% | 0%
8 | 243 | 31 | 5832 | 24 | 12.98 | 0 | 0 | 0 | 0 | 0 | 243 | 5832 | 1440 | 239.6712 | 9.0819 | -12.7582 | 1414.284 | 23.3588 | -170.3814 | -33.4845 | 0 | 103.326 | 283.326 | 99.38 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4277 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4998 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5833 | 1 | 11.93 | 0 | 0 | 0 | 0 | 0 | 244 | 5833 | 60 | 240.6575 | 8.7272 | -12.5867 | 34.284 | 0.36162 | 174.5757 | -34.2843 | 0 | 102.8007 | 77.1993 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4476 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7623 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5834 | 2 | 11.19 | 0 | 0 | 0 | 0 | 0 | 244 | 5834 | 120 | 240.6575 | 8.7272 | -12.5867 | 94.284 | 1.3616 | 159.5757 | -31.586 | 0 | 102.8007 | 77.1993 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0509 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.952 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5835 | 3 | 10.57 | 0 | 0 | 0 | 0 | 0 | 244 | 5835 | 180 | 240.6575 | 8.7272 | -12.5867 | 154.284 | 2.3616 | 144.5757 | -26.1693 | 0 | 102.8007 | 77.1993 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4714 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1138 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5836 | 4 | 10.12 | 0 | 0 | 0 | 0 | 0 | 244 | 5836 | 240 | 240.6575 | 8.7272 | -12.5867 | 214.284 | 3.3616 | 129.5757 | -18.7042 | 0 | 102.8007 | 77.1993 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1572 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.233 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5837 | 5 | 9.77 | 0 | 0 | 0 | 0 | 0 | 244 | 5837 | 300 | 240.6575 | 8.7272 | -12.5867 | 274.284 | 4.3616 | 114.5757 | -9.8431 | 0 | 102.8007 | 77.1993 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.8595 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3266 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5838 | 6 | 9.68 | 0 | 0 | 0 | 0 | 0 | 244 | 5838 | 360 | 240.6575 | 8.7272 | -12.5867 | 334.284 | 5.3616 | 99.5757 | -0.11661 | 0 | 102.8007 | 77.1993 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.0005 | 6.0005 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3509 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5839 | 7 | 10.28 | 5.33 | 11.44 | 16.77 | 11.44 | 5.72 | 244 | 5839 | 420 | 240.6575 | 8.7272 | -12.5867 | 394.284 | 6.3616 | 84.5757 | 10.0527 | 10.0527 | 92.0849 | 87.9151 | 84.3703 | 2.9954 | 2.9954 | 9.7647 | 12.7601 | -9.9157 | 0% | 5.7701 | 0 | 0 | 171.9845 | 171.9845 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1905 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5840 | 8 | 11.7 | 40.83 | 49.94 | 90.77 | 49.94 | 24.97 | 244 | 5840 | 480 | 240.6575 | 8.7272 | -12.5867 | 454.284 | 7.3616 | 69.5757 | 20.2907 | 20.2907 | 80.9557 | 99.0443 | 69.545 | 41.1464 | 41.1464 | 42.6265 | 83.7729 | -0.78944 | 0% | 37.8821 | 0 | 0 | 186.1843 | 186.1843 | 0% | 11.68% | 11.68% | 80% | 9.343% | 3.5394 | 6.8209 | 6 | 21.2363 | 7.827 | 11.41% | 11.41%
9 | 244 | 1 | 5841 | 9 | 15.7 | 143.89 | 107.28 | 251.17 | 107.28 | 53.64 | 244 | 5841 | 540 | 240.6575 | 8.7272 | -12.5867 | 514.284 | 8.3616 | 54.5757 | 30.1931 | 30.1931 | 68.7279 | 111.2721 | 54.7358 | 165.1861 | 165.1861 | 91.5692 | 256.7553 | 0.3197 | 31.97% | 116.1048 | 37.1191 | 25.9834 | 159.2703 | 159.2703 | 16.31% | 11.48% | 11.48% | 80% | 9.184% | 10.6635 | 5.8557 | 5.8557 | 62.442 | 23.5814 | 39.21% | 39.21%
9 | 244 | 1 | 5842 | 10 | 19.7 | 203.56 | 162.83 | 366.39 | 162.83 | 81.42 | 244 | 5842 | 600 | 240.6575 | 8.7272 | -12.5867 | 574.284 | 9.3616 | 39.5757 | 39.2207 | 39.2207 | 54.3743 | 125.6257 | 39.9861 | 246.6639 | 246.6639 | 138.9841 | 385.648 | 0.50472 | 50.47% | 174.39 | 88.0174 | 61.6122 | 168.3393 | 168.3393 | 36.6% | 11.36% | 11.36% | 85% | 9.655% | 16.8374 | 5.0025 | 5.0025 | 84.2286 | 37.2344 | 50.04% | 50.04%
9 | 244 | 1 | 5843 | 11 | 22.3 | 304.11 | 188.94 | 493.05 | 188.94 | 94.47 | 244 | 5843 | 660 | 240.6575 | 8.7272 | -12.5867 | 634.284 | 10.3616 | 24.5757 | 46.5643 | 46.5643 | 36.7196 | 143.2804 | 25.4236 | 378.2426 | 378.2426 | 161.2704 | 539.513 | 0.60061 | 60.06% | 243.9678 | 146.5299 | 102.5709 | 170.273 | 170.273 | 60.24% | 11.32% | 11.32% | 90% | 10.19% | 24.8533 | 4.508 | 4.508 | 112.0378 | 54.961 | 65.8% | 65.8%
9 | 244 | 1 | 5844 | 12 | 23.7 | 495.89 | 165.97 | 661.86 | 165.97 | 82.99 | 244 | 5844 | 720 | 240.6575 | 8.7272 | -12.5867 | 694.284 | 11.3616 | 9.5757 | 51.0809 | 51.0809 | 15.1727 | 164.8273 | 11.7941 | 623.9076 | 623.9076 | 141.6643 | 765.5719 | 0.66462 | 66.46% | 346.1916 | 230.0858 | 161.0601 | 298.6505 | 298.6505 | 53.93% | 11.34% | 11.34% | 90% | 10.21% | 35.3479 | 4.2613 | 4.2613 | 150.627 | 78.1687 | 50.44% | 50.44%
9 | 244 | 1 | 5845 | 13 | 24.8 | 469.94 | 189.44 | 659.38 | 189.44 | 94.72 | 244 | 5845 | 780 | 240.6575 | 8.7272 | -12.5867 | 754.284 | 12.3616 | -5.4243 | 51.6683 | 51.6683 | 8.6647 | 188.6647 | 8.7995 | 592.0305 | 592.0305 | 161.6972 | 753.7277 | 0.66556 | 66.56% | 340.8357 | 226.8461 | 158.7923 | 305.804 | 305.804 | 51.93% | 11.34% | 11.34% | 90% | 10.21% | 34.785 | 4.0771 | 4.0771 | 141.8213 | 76.924 | 46.38% | 46.38%
9 | 244 | 1 | 5846 | 14 | 26.2 | 439.67 | 215.22 | 654.89 | 215.22 | 107.61 | 244 | 5846 | 840 | 240.6575 | 8.7272 | -12.5867 | 814.284 | 13.3616 | -20.4243 | 48.1514 | 48.1514 | 31.1318 | 211.1318 | 21.48 | 549.2374 | 549.2374 | 183.7018 | 732.9392 | 0.6657 | 66.57% | 331.4351 | 220.6348 | 154.4444 | 322.2072 | 322.2072 | 47.93% | 11.33% | 11.33% | 90% | 10.2% | 33.7938 | 3.8549 | 3.8549 | 130.2719 | 74.7321 | 40.43% | 40.43%
9 | 244 | 1 | 5847 | 15 | 26.2 | 390.69 | 192.08 | 582.77 | 192.08 | 96.04 | 244 | 5847 | 900 | 240.6575 | 8.7272 | -12.5867 | 874.284 | 14.3616 | -35.4243 | 41.4647 | 41.4647 | 49.8658 | 229.8658 | 35.9268 | 477.7825 | 477.7825 | 163.9505 | 641.7331 | 0.64604 | 64.6% | 290.1917 | 187.4751 | 131.2326 | 337.928 | 337.928 | 38.83% | 11.3% | 11.3% | 90% | 10.17% | 29.5074 | 3.8549 | 3.8549 | 113.7479 | 65.2529 | 33.66% | 33.66%
9 | 244 | 1 | 5848 | 16 | 26.3 | 301.94 | 184.03 | 485.97 | 184.03 | 92.02 | 244 | 5848 | 960 | 240.6575 | 8.7272 | -12.5867 | 934.284 | 15.3616 | -50.4243 | 32.8074 | 32.8074 | 65.0179 | 245.0179 | 50.6449 | 353.3811 | 353.3811 | 157.0794 | 510.4606 | 0.60583 | 60.58% | 230.8303 | 139.8443 | 97.891 | 319.8584 | 319.8584 | 30.6% | 11.25% | 11.25% | 90% | 10.13% | 23.375 | 3.8396 | 3.8396 | 89.7498 | 51.6918 | 28.06% | 28.06%
9 | 244 | 1 | 5849 | 17 | 26.9 | 176.94 | 130.78 | 307.72 | 130.78 | 65.39 | 244 | 5849 | 1020 | 240.6575 | 8.7272 | -12.5867 | 994.284 | 16.3616 | -65.4243 | 23.0843 | 23.0843 | 77.7208 | 257.7208 | 65.4436 | 187.5469 | 187.5469 | 111.6277 | 299.1746 | 0.47012 | 47.01% | 135.2868 | 63.6005 | 44.5203 | 315.0867 | 315.0867 | 14.13% | 11.16% | 11.16% | 80% | 8.93% | 12.0805 | 3.749 | 3.749 | 45.2892 | 26.7149 | 14.37% | 14.37%
9 | 244 | 1 | 5850 | 18 | 24.7 | 85.69 | 83.33 | 169.02 | 83.33 | 41.67 | 244 | 5850 | 1080 | 240.6575 | 8.7272 | -12.5867 | 1054.284 | 17.3616 | -80.4243 | 12.8952 | 12.8952 | 89.0649 | 269.0649 | 80.2673 | 64.911 | 64.911 | 71.1266 | 136.0376 | 0.035383 | 3.538% | 61.5162 | 2.1766 | 1.5236 | 272.4468 | 272.4468 | 0.5592% | 11.18% | 0% | 80% | 0% | 0 | 4.0935 | 4.0935 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5851 | 19 | 23 | 14.44 | 52.64 | 67.08 | 52.64 | 26.32 | 244 | 5851 | 1140 | 240.6575 | 8.7272 | -12.5867 | 1114.284 | 18.3616 | -95.4243 | 2.6697 | 2.6697 | 99.9148 | 279.9148 | 95.0879 | 0 | 0 | 44.9311 | 44.9311 | -1.6045 | 0% | 20.3178 | 0 | 0 | 159.9116 | 159.9116 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.3829 | 4.3829 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5852 | 20 | 19.7 | 0 | 6.53 | 6.53 | 6.53 | 3.27 | 244 | 5852 | 1200 | 240.6575 | 8.7272 | -12.5867 | 1174.284 | 19.3616 | -110.4243 | -7.2183 | 0 | 102.8007 | 282.8007 | 99.0135 | 0 | 0 | 5.5737 | 5.5737 | -19.9037 | 0% | 2.5204 | 0 | 0 | 144.405 | 144.405 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5853 | 21 | 17 | 0 | 0 | 0 | 0 | 0 | 244 | 5853 | 1260 | 240.6575 | 8.7272 | -12.5867 | 1234.284 | 20.3616 | -125.4243 | -16.3666 | 0 | 102.8007 | 282.8007 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.723 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5661 | 5.5661 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5854 | 22 | 15.9 | 0 | 0 | 0 | 0 | 0 | 244 | 5854 | 1320 | 240.6575 | 8.7272 | -12.5867 | 1294.284 | 21.3616 | -140.4243 | -24.2787 | 0 | 102.8007 | 282.8007 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9707 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5855 | 23 | 14.8 | 0 | 0 | 0 | 0 | 0 | 244 | 5855 | 1380 | 240.6575 | 8.7272 | -12.5867 | 1354.284 | 22.3616 | -155.4243 | -30.3322 | 0 | 102.8007 | 282.8007 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1226 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
9 | 244 | 1 | 5856 | 24 | 13.5 | 0 | 0 | 0 | 0 | 0 | 244 | 5856 | 1440 | 240.6575 | 8.7272 | -12.5867 | 1414.284 | 23.3616 | -170.4243 | -33.8417 | 0 | 102.8007 | 282.8007 | 99.0135 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5794 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5857 | 1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 245 | 5857 | 60 | 241.6438 | 8.3697 | -12.4055 | 34.284 | 0.36464 | 174.5304 | -34.6372 | 0 | 102.2719 | 77.7281 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8821 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5858 | 2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 245 | 5858 | 120 | 241.6438 | 8.3697 | -12.4055 | 94.284 | 1.3646 | 159.5304 | -31.9164 | 0 | 102.2719 | 77.7281 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8273 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5859 | 3 | 11.2 | 0 | 0 | 0 | 0 | 0 | 245 | 5859 | 180 | 241.6438 | 8.3697 | -12.4055 | 154.284 | 2.3646 | 144.5304 | -26.4699 | 0 | 102.2719 | 77.7281 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.163 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5860 | 4 | 11 | 0 | 0 | 0 | 0 | 0 | 245 | 5860 | 240 | 241.6438 | 8.3697 | -12.4055 | 214.284 | 3.3646 | 129.5304 | -18.9759 | 0 | 102.2719 | 77.7281 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4678 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5861 | 5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 245 | 5861 | 300 | 241.6438 | 8.3697 | -12.4055 | 274.284 | 4.3646 | 114.5304 | -10.0917 | 0 | 102.2719 | 77.7281 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.6965 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5862 | 6 | 10.2 | 0 | 0 | 0 | 0 | 0 | 245 | 5862 | 360 | 241.6438 | 8.3697 | -12.4055 | 334.284 | 5.3646 | 99.5304 | -0.35 | 0 | 102.2719 | 77.7281 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.4839 | 5.4839 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5863 | 7 | 10.3 | 4.11 | 11.44 | 15.55 | 11.44 | 5.72 | 245 | 5863 | 420 | 241.6438 | 8.3697 | -12.4055 | 394.284 | 6.3646 | 84.5304 | 9.8257 | 9.8257 | 91.8009 | 88.1991 | 84.3314 | 0 | 0 | 9.7647 | 9.7647 | -13.1993 | 0% | 4.4156 | 0 | 0 | 169.1168 | 169.1168 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5864 | 8 | 12.8 | 47.72 | 56.33 | 104.05 | 56.33 | 28.17 | 245 | 5864 | 480 | 241.6438 | 8.3697 | -12.4055 | 454.284 | 7.3646 | 69.5304 | 20.0605 | 20.0605 | 80.6605 | 99.3395 | 69.4921 | 48.739 | 48.739 | 48.0807 | 96.8196 | -0.54854 | 0% | 43.7818 | 0 | 0 | 185.2994 | 185.2994 | 0% | 11.63% | 11.63% | 80% | 9.304% | 4.0736 | 6.5443 | 6 | 24.4417 | 9.0085 | 13.19% | 13.19%
9 | 245 | 2 | 5865 | 9 | 15.6 | 116.72 | 93.67 | 210.39 | 93.67 | 46.84 | 245 | 5865 | 540 | 241.6438 | 8.3697 | -12.4055 | 514.284 | 8.3646 | 54.5304 | 29.9487 | 29.9487 | 68.4221 | 111.5779 | 54.6668 | 135.2155 | 135.2155 | 79.9523 | 215.1678 | 0.22505 | 22.5% | 97.2989 | 21.897 | 15.3279 | 153.5409 | 153.5409 | 9.983% | 11.49% | 11.49% | 80% | 9.195% | 8.9465 | 5.8784 | 5.8784 | 52.5912 | 19.7843 | 34.25% | 34.25%
9 | 245 | 2 | 5866 | 10 | 19.2 | 185.89 | 106.06 | 291.95 | 106.06 | 53.03 | 245 | 5866 | 600 | 241.6438 | 8.3697 | -12.4055 | 574.284 | 9.3646 | 39.5304 | 38.9501 | 38.9501 | 54.0678 | 125.9322 | 39.895 | 226.8675 | 226.8675 | 90.5279 | 317.3954 | 0.43688 | 43.69% | 143.5262 | 62.7036 | 43.8925 | 160.572 | 160.572 | 27.34% | 11.37% | 11.37% | 85% | 9.667% | 13.875 | 5.103 | 5.103 | 70.8043 | 30.6834 | 44.1% | 44.1%
9 | 245 | 2 | 5867 | 11 | 23.3 | 337.22 | 141.33 | 478.55 | 141.33 | 70.67 | 245 | 5867 | 660 | 241.6438 | 8.3697 | -12.4055 | 634.284 | 10.3646 | 24.5304 | 46.2572 | 46.2572 | 36.4464 | 143.5536 | 25.293 | 422.0252 | 422.0252 | 120.6327 | 542.6579 | 0.60578 | 60.58% | 245.3899 | 148.6516 | 104.0561 | 277.4531 | 277.4531 | 37.5% | 11.31% | 11.31% | 90% | 10.17% | 24.9678 | 4.3304 | 4.3304 | 108.1196 | 55.2142 | 38.97% | 38.97%
9 | 245 | 2 | 5868 | 12 | 25.1 | 312.92 | 131.81 | 444.73 | 131.81 | 65.91 | 245 | 5868 | 720 | 241.6438 | 8.3697 | -12.4055 | 694.284 | 11.3646 | 9.5304 | 50.7373 | 50.7373 | 15.0006 | 164.9994 | 11.5527 | 395.9696 | 395.9696 | 112.5069 | 508.4765 | 0.60004 | 60% | 229.9331 | 137.97 | 96.579 | 286.414 | 286.414 | 33.72% | 11.27% | 11.27% | 90% | 10.14% | 23.3226 | 4.0283 | 4.0283 | 93.9507 | 51.5758 | 32.8% | 32.8%
9 | 245 | 2 | 5869 | 13 | 25.4 | 343.06 | 178.47 | 521.53 | 178.47 | 89.24 | 245 | 5869 | 780 | 241.6438 | 8.3697 | -12.4055 | 754.284 | 12.3646 | -5.4696 | 51.3081 | 51.3081 | 8.6763 | 188.6763 | 8.5499 | 434.6435 | 434.6435 | 152.3337 | 586.9772 | 0.62841 | 62.84% | 265.4311 | 166.7995 | 116.7596 | 297.1457 | 297.1457 | 39.29% | 11.29% | 11.29% | 90% | 10.16% | 26.9674 | 3.9802 | 3.9802 | 107.3352 | 59.6361 | 36.12% | 36.12%
9 | 245 | 2 | 5870 | 14 | 25.9 | 322.36 | 197.78 | 520.14 | 197.78 | 98.89 | 245 | 5870 | 840 | 241.6438 | 8.3697 | -12.4055 | 814.284 | 13.3646 | -20.4696 | 47.8016 | 47.8016 | 31.0035 | 211.0035 | 21.4167 | 405.0913 | 405.0913 | 168.8158 | 573.9071 | 0.62626 | 62.63% | 259.5208 | 162.5281 | 113.7697 | 304.4492 | 304.4492 | 37.37% | 11.28% | 11.28% | 90% | 10.15% | 26.3434 | 3.9014 | 3.9014 | 102.7748 | 58.256 | 33.76% | 33.76%
9 | 245 | 2 | 5871 | 15 | 25.3 | 289.03 | 220.42 | 509.45 | 220.42 | 110.21 | 245 | 5871 | 900 | 241.6438 | 8.3697 | -12.4055 | 874.284 | 14.3646 | -35.4696 | 41.1376 | 41.1376 | 49.6649 | 229.6649 | 35.916 | 355.8135 | 355.8135 | 188.1402 | 543.9538 | 0.61413 | 61.41% | 245.9759 | 151.0612 | 105.7429 | 310.3524 | 310.3524 | 34.07% | 11.28% | 11.28% | 90% | 10.15% | 24.9656 | 3.9962 | 3.9962 | 99.7665 | 55.2093 | 32.15% | 32.15%
9 | 245 | 2 | 5872 | 16 | 27.2 | 308.75 | 173.11 | 481.86 | 173.11 | 86.56 | 245 | 5872 | 960 | 241.6438 | 8.3697 | -12.4055 | 934.284 | 15.3646 | -50.4696 | 32.5008 | 32.5008 | 64.793 | 244.793 | 50.66 | 364.2636 | 364.2636 | 147.7586 | 512.0223 | 0.61015 | 61.01% | 231.5365 | 141.271 | 98.8897 | 327.0078 | 327.0078 | 30.24% | 11.24% | 11.24% | 90% | 10.11% | 23.418 | 3.7046 | 3.7046 | 86.7542 | 51.7868 | 26.53% | 26.53%
9 | 245 | 2 | 5873 | 17 | 21.8 | 226.39 | 139.03 | 365.42 | 139.03 | 69.52 | 245 | 5873 | 1020 | 241.6438 | 8.3697 | -12.4055 | 994.284 | 16.3646 | -65.4696 | 22.7907 | 22.7907 | 77.4941 | 257.4941 | 65.4761 | 242.5825 | 242.5825 | 118.6695 | 361.252 | 0.49724 | 49.72% | 163.3582 | 81.2283 | 56.8598 | 143.4222 | 143.4222 | 39.65% | 11.31% | 11.31% | 85% | 9.612% | 15.7024 | 4.5994 | 4.5994 | 72.2215 | 34.7246 | 50.36% | 50.36%
9 | 245 | 2 | 5874 | 18 | 19.5 | 174.17 | 95 | 269.17 | 95 | 47.5 | 245 | 5874 | 1080 | 241.6438 | 8.3697 | -12.4055 | 1054.284 | 17.3646 | -80.4696 | 12.6063 | 12.6063 | 88.8443 | 268.8443 | 80.3142 | 134.2639 | 134.2639 | 81.0876 | 215.3515 | 0.266 | 26.6% | 97.3819 | 25.9033 | 18.1323 | 131.5873 | 131.5873 | 13.78% | 11.37% | 0% | 80% | 0% | 0 | 5.0425 | 5.0425 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5875 | 19 | 18.2 | 19.78 | 49.03 | 68.81 | 49.03 | 24.52 | 245 | 5875 | 1140 | 241.6438 | 8.3697 | -12.4055 | 1114.284 | 18.3646 | -95.4696 | 2.3779 | 2.3779 | 99.7034 | 279.7034 | 95.1487 | 0 | 0 | 41.8497 | 41.8497 | -2.0333 | 0% | 18.9244 | 0 | 0 | 154.6635 | 154.6635 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.3093 | 5.3093 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5876 | 20 | 18.3 | 0 | 5.56 | 5.56 | 5.56 | 2.78 | 245 | 5876 | 1200 | 241.6438 | 8.3697 | -12.4055 | 1174.284 | 19.3646 | -110.4696 | -7.5199 | 0 | 102.2719 | 282.2719 | 98.6441 | 0 | 0 | 4.7458 | 4.7458 | -24.1696 | 0% | 2.146 | 0 | 0 | 143.3709 | 143.3709 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5877 | 21 | 16.9 | 0 | 0 | 0 | 0 | 0 | 245 | 5877 | 1260 | 241.6438 | 8.3697 | -12.4055 | 1234.284 | 20.3646 | -125.4696 | -16.6834 | 0 | 102.2719 | 282.2719 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9065 | 0 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5878 | 22 | 16.5 | 0 | 0 | 0 | 0 | 0 | 245 | 5878 | 1320 | 241.6438 | 8.3697 | -12.4055 | 1294.284 | 21.3646 | -140.4696 | -24.6139 | 0 | 102.2719 | 282.2719 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2176 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5879 | 23 | 15.6 | 0 | 0 | 0 | 0 | 0 | 245 | 5879 | 1380 | 241.6438 | 8.3697 | -12.4055 | 1354.284 | 22.3646 | -155.4696 | -30.6844 | 0 | 102.2719 | 282.2719 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1628 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
9 | 245 | 2 | 5880 | 24 | 14.1 | 0 | 0 | 0 | 0 | 0 | 245 | 5880 | 1440 | 241.6438 | 8.3697 | -12.4055 | 1414.284 | 23.3646 | -170.4696 | -34.2019 | 0 | 102.2719 | 282.2719 | 98.6441 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0225 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5881 | 1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 246 | 5881 | 60 | 242.6301 | 8.0095 | -12.215 | 34.284 | 0.36782 | 174.4827 | -34.9924 | 0 | 101.7396 | 78.2604 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.624 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5882 | 2 | 12.6 | 0 | 0 | 0 | 0 | 0 | 246 | 5882 | 120 | 242.6301 | 8.0095 | -12.215 | 94.284 | 1.3678 | 159.4827 | -32.2485 | 0 | 101.7396 | 78.2604 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.928 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5883 | 3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 246 | 5883 | 180 | 242.6301 | 8.0095 | -12.215 | 154.284 | 2.3678 | 144.4827 | -26.7716 | 0 | 101.7396 | 78.2604 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2319 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5884 | 4 | 11.5 | 0 | 0 | 0 | 0 | 0 | 246 | 5884 | 240 | 242.6301 | 8.0095 | -12.215 | 214.284 | 3.3678 | 129.4827 | -19.2481 | 0 | 101.7396 | 78.2604 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1463 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5885 | 5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 246 | 5885 | 300 | 242.6301 | 8.0095 | -12.215 | 274.284 | 4.3678 | 114.4827 | -10.3407 | 0 | 101.7396 | 78.2604 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.6026 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5886 | 6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 246 | 5886 | 360 | 242.6301 | 8.0095 | -12.215 | 334.284 | 5.3678 | 99.4827 | -0.58377 | 0 | 101.7396 | 78.2604 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.5097 | 5.5097 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5887 | 7 | 10.6 | 3.56 | 9.44 | 13 | 9.44 | 4.72 | 246 | 5887 | 420 | 242.6301 | 8.0095 | -12.215 | 394.284 | 6.3678 | 84.4827 | 9.5982 | 9.5982 | 91.5136 | 88.4864 | 84.2905 | 0 | 0 | 8.0575 | 8.0575 | -16.0794 | 0% | 3.6436 | 0 | 0 | 168.3965 | 168.3965 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5888 | 8 | 11.7 | 41.61 | 41.67 | 83.28 | 41.67 | 20.84 | 246 | 5888 | 480 | 242.6301 | 8.0095 | -12.215 | 454.284 | 7.3678 | 69.4827 | 19.8293 | 19.8293 | 80.3624 | 99.6376 | 69.4376 | 43.0828 | 43.0828 | 35.5676 | 78.6504 | -0.89322 | 0% | 35.5657 | 0 | 0 | 181.4848 | 181.4848 | 0% | 11.68% | 11.68% | 80% | 9.345% | 3.3236 | 6.8209 | 6 | 19.9418 | 7.3499 | 10.99% | 10.99%
9 | 246 | 3 | 5889 | 9 | 14.1 | 116.61 | 82.44 | 199.05 | 82.44 | 41.22 | 246 | 5889 | 540 | 242.6301 | 8.0095 | -12.215 | 514.284 | 8.3678 | 54.4827 | 29.703 | 29.703 | 68.1136 | 111.8864 | 54.5968 | 136.3366 | 136.3366 | 70.3669 | 206.7035 | 0.18487 | 18.49% | 93.4713 | 17.2799 | 12.0959 | 170.7345 | 170.7345 | 7.085% | 11.54% | 11.54% | 80% | 9.236% | 8.6327 | 6.2283 | 6 | 51.7959 | 19.0903 | 30.34% | 30.34%
9 | 246 | 3 | 5890 | 10 | 16.2 | 213.56 | 131.89 | 345.45 | 131.89 | 65.95 | 246 | 5890 | 600 | 242.6301 | 8.0095 | -12.215 | 574.284 | 9.3678 | 39.4827 | 38.6778 | 38.6778 | 53.7592 | 126.2408 | 39.8037 | 262.5302 | 262.5302 | 112.5752 | 375.1054 | 0.47551 | 47.55% | 169.6227 | 80.6574 | 56.4602 | 157.8718 | 157.8718 | 35.76% | 11.44% | 11.44% | 85% | 9.725% | 16.4953 | 5.7429 | 5.7429 | 94.7307 | 36.4778 | 60% | 60%
9 | 246 | 3 | 5891 | 11 | 20 | 253.11 | 151.11 | 404.22 | 151.11 | 75.56 | 246 | 5891 | 660 | 242.6301 | 8.0095 | -12.215 | 634.284 | 10.3678 | 24.4827 | 45.9479 | 45.9479 | 36.1715 | 143.8285 | 25.1636 | 318.7515 | 318.7515 | 128.9805 | 447.7319 | 0.54769 | 54.77% | 202.4644 | 110.888 | 77.6216 | 159.2462 | 159.2462 | 48.74% | 11.35% | 11.35% | 85% | 9.649% | 19.5362 | 4.943 | 4.943 | 96.5674 | 43.2025 | 60.64% | 60.64%
9 | 246 | 3 | 5892 | 12 | 21.1 | 354.39 | 186.33 | 540.72 | 186.33 | 93.17 | 246 | 5892 | 720 | 242.6301 | 8.0095 | -12.215 | 694.284 | 11.3678 | 9.4827 | 50.3913 | 50.3913 | 14.8266 | 165.1734 | 11.3141 | 451.0588 | 451.0588 | 159.0426 | 610.1014 | 0.61986 | 61.99% | 275.8879 | 171.0117 | 119.7082 | 156.4492 | 156.4492 | 76.52% | 11.34% | 11.34% | 90% | 10.21% | 28.1584 | 4.7303 | 4.7303 | 133.198 | 62.2698 | 85.14% | 85.14%
9 | 246 | 3 | 5893 | 13 | 22.6 | 446.44 | 149.22 | 595.66 | 149.22 | 74.61 | 246 | 5893 | 780 | 242.6301 | 8.0095 | -12.215 | 754.284 | 12.3678 | -5.5173 | 50.945 | 50.945 | 8.6911 | 188.6911 | 8.3078 | 568.8754 | 568.8754 | 127.3672 | 696.2426 | 0.64733 | 64.73% | 314.8409 | 203.806 | 142.6642 | 158.4085 | 158.4085 | 90.06% | 11.34% | 11.34% | 90% | 10.2% | 32.1246 | 4.4539 | 4.4539 | 143.0811 | 71.0407 | 90.32% | 90.32%
9 | 246 | 3 | 5894 | 14 | 25.6 | 369.22 | 190.14 | 559.36 | 190.14 | 95.07 | 246 | 5894 | 840 | 242.6301 | 8.0095 | -12.215 | 814.284 | 13.3678 | -20.5173 | 47.4481 | 47.4481 | 30.8787 | 210.8787 | 21.3605 | 466.7751 | 466.7751 | 162.2946 | 629.0698 | 0.64084 | 64.08% | 284.4653 | 182.2954 | 127.6068 | 290.0088 | 290.0088 | 44% | 11.3% | 11.3% | 90% | 10.17% | 28.9285 | 3.9484 | 3.9484 | 114.2223 | 63.9727 | 39.39% | 39.39%
9 | 246 | 3 | 5895 | 15 | 26.3 | 317.78 | 179.72 | 497.5 | 179.72 | 89.86 | 246 | 5895 | 900 | 242.6301 | 8.0095 | -12.215 | 874.284 | 14.3678 | -35.5173 | 40.8066 | 40.8066 | 49.4667 | 229.4667 | 35.9104 | 393.8462 | 393.8462 | 153.4006 | 547.2469 | 0.61915 | 61.92% | 247.465 | 153.2186 | 107.253 | 295.7847 | 295.7847 | 36.26% | 11.26% | 11.26% | 90% | 10.14% | 25.088 | 3.8396 | 3.8396 | 96.3266 | 55.4798 | 32.57% | 32.57%
9 | 246 | 3 | 5896 | 16 | 26.8 | 319.03 | 173.89 | 492.92 | 173.89 | 86.95 | 246 | 5896 | 960 | 242.6301 | 8.0095 | -12.215 | 934.284 | 15.3678 | -50.5173 | 32.1903 | 32.1903 | 64.5699 | 244.5699 | 50.6791 | 379.4726 | 379.4726 | 148.4244 | 527.897 | 0.61438 | 61.44% | 238.715 | 146.6614 | 102.663 | 313.3642 | 313.3642 | 32.76% | 11.25% | 11.25% | 90% | 10.13% | 24.1704 | 3.7639 | 3.7639 | 90.9745 | 53.4507 | 29.03% | 29.03%
9 | 246 | 3 | 5897 | 17 | 26.1 | 208.94 | 132.83 | 341.77 | 132.83 | 66.42 | 246 | 5897 | 1020 | 242.6301 | 8.0095 | -12.215 | 994.284 | 16.3678 | -65.5173 | 22.4932 | 22.4932 | 77.2682 | 257.2682 | 65.512 | 226.3778 | 226.3778 | 113.3775 | 339.7553 | 0.50502 | 50.5% | 153.6373 | 77.5896 | 54.3127 | 294.6648 | 294.6648 | 18.43% | 11.2% | 11.2% | 85% | 9.518% | 14.6231 | 3.8703 | 3.8703 | 56.5961 | 32.3377 | 19.21% | 19.21%
9 | 246 | 3 | 5898 | 18 | 25.9 | 103.67 | 88.94 | 192.61 | 88.94 | 44.47 | 246 | 5898 | 1080 | 242.6301 | 8.0095 | -12.215 | 1054.284 | 17.3678 | -80.5173 | 12.3135 | 12.3135 | 88.624 | 268.624 | 80.364 | 81.3702 | 81.3702 | 75.915 | 157.2852 | 0.15547 | 15.55% | 71.1244 | 11.0574 | 7.7402 | 282.3089 | 282.3089 | 2.742% | 11.14% | 0% | 80% | 0% | 0 | 3.9014 | 3.9014 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5899 | 19 | 24.4 | 21.33 | 47.17 | 68.5 | 47.17 | 23.59 | 246 | 5899 | 1140 | 242.6301 | 8.0095 | -12.215 | 1114.284 | 18.3678 | -95.5173 | 2.0823 | 2.0823 | 99.492 | 279.492 | 95.2119 | 0 | 0 | 40.2621 | 40.2621 | -1.8089 | 0% | 18.2065 | 0 | 0 | 290.4476 | 290.4476 | 0% | 11.17% | 0% | 80% | 0% | 0 | 4.1431 | 4.1431 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5900 | 20 | 22.1 | 0 | 3.75 | 3.75 | 3.75 | 1.88 | 246 | 5900 | 1200 | 242.6301 | 8.0095 | -12.215 | 1174.284 | 19.3678 | -110.5173 | -7.8249 | 0 | 101.7396 | 281.7396 | 98.2719 | 0 | 0 | 3.2008 | 3.2008 | -33.6137 | 0% | 1.4474 | 0 | 0 | 148.0666 | 148.0666 | 0% | 11.26% | 0% | 80% | 0% | 0 | 4.5443 | 4.5443 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5901 | 21 | 18.3 | 0 | 0 | 0 | 0 | 0 | 246 | 5901 | 1260 | 242.6301 | 8.0095 | -12.215 | 1234.284 | 20.3678 | -125.5173 | -17.0036 | 0 | 101.7396 | 281.7396 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.5568 | 0 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5902 | 22 | 16.3 | 0 | 0 | 0 | 0 | 0 | 246 | 5902 | 1320 | 242.6301 | 8.0095 | -12.215 | 1294.284 | 21.3678 | -140.5173 | -24.9526 | 0 | 101.7396 | 281.7396 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1214 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5903 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 246 | 5903 | 1380 | 242.6301 | 8.0095 | -12.215 | 1354.284 | 22.3678 | -155.5173 | -31.0399 | 0 | 101.7396 | 281.7396 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6445 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
9 | 246 | 3 | 5904 | 24 | 14.1 | 0 | 0 | 0 | 0 | 0 | 246 | 5904 | 1440 | 242.6301 | 8.0095 | -12.215 | 1414.284 | 23.3678 | -170.5173 | -34.5652 | 0 | 101.7396 | 281.7396 | 98.2719 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5581 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5905 | 1 | 14.2 | 0 | 0 | 0 | 0 | 0 | 247 | 5905 | 60 | 243.6164 | 7.6467 | -12.0153 | 34.284 | 0.37114 | 174.4328 | -35.3501 | 0 | 101.204 | 78.796 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4139 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5906 | 2 | 14.5 | 0 | 0 | 0 | 0 | 0 | 247 | 5906 | 120 | 243.6164 | 7.6467 | -12.0153 | 94.284 | 1.3711 | 159.4328 | -32.5823 | 0 | 101.204 | 78.796 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5387 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5907 | 3 | 14.5 | 0 | 0 | 0 | 0 | 0 | 247 | 5907 | 180 | 243.6164 | 7.6467 | -12.0153 | 154.284 | 2.3711 | 144.4328 | -27.0742 | 0 | 101.204 | 78.796 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1207 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5908 | 4 | 13.6 | 0 | 0 | 0 | 0 | 0 | 247 | 5908 | 240 | 243.6164 | 7.6467 | -12.0153 | 214.284 | 3.3711 | 129.4328 | -19.5209 | 0 | 101.204 | 78.796 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4923 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5909 | 5 | 13.2 | 0 | 0 | 0 | 0 | 0 | 247 | 5909 | 300 | 243.6164 | 7.6467 | -12.0153 | 274.284 | 4.3711 | 114.4328 | -10.5899 | 0 | 101.204 | 78.796 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.0053 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5910 | 6 | 13.1 | 0 | 0 | 0 | 0 | 0 | 247 | 5910 | 360 | 243.6164 | 7.6467 | -12.0153 | 334.284 | 5.3711 | 99.4328 | -0.8179 | 0 | 101.204 | 78.796 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.7932 | 7.7932 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5911 | 7 | 13.2 | 4.72 | 13.39 | 18.11 | 13.39 | 6.7 | 247 | 5911 | 420 | 243.6164 | 7.6467 | -12.0153 | 394.284 | 6.3711 | 84.4328 | 9.3701 | 9.3701 | 91.2231 | 88.7769 | 84.2475 | 0 | 0 | 11.4291 | 11.4291 | -10.5735 | 0% | 5.1682 | 0 | 0 | 170.3619 | 170.3619 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5912 | 8 | 14 | 30.22 | 44.22 | 74.44 | 44.22 | 22.11 | 247 | 5912 | 480 | 243.6164 | 7.6467 | -12.0153 | 454.284 | 7.3711 | 69.4328 | 19.5974 | 19.5974 | 80.0613 | 99.9387 | 69.3816 | 31.7277 | 31.7277 | 37.7441 | 69.4718 | -1.0414 | 0% | 31.4152 | 0 | 0 | 181.8015 | 181.8015 | 0% | 11.59% | 11.59% | 80% | 9.274% | 2.9136 | 6.2522 | 6 | 17.4815 | 6.4431 | 9.616% | 9.616%
9 | 247 | 4 | 5913 | 9 | 17.3 | 59.44 | 96.53 | 155.97 | 96.53 | 48.27 | 247 | 5913 | 540 | 243.6164 | 7.6467 | -12.0153 | 514.284 | 8.3711 | 54.4328 | 29.4561 | 29.4561 | 67.8026 | 112.1974 | 54.5258 | 70.1468 | 70.1468 | 82.3935 | 152.5403 | 0.012412 | 1.241% | 68.9787 | 0.85617 | 0.59932 | 170.6132 | 170.6132 | 0.3513% | 11.45% | 11.45% | 80% | 9.159% | 6.3174 | 5.501 | 5.501 | 34.7519 | 13.9704 | 20.37% | 20.37%
9 | 247 | 4 | 5914 | 10 | 21.7 | 175.56 | 181.17 | 356.73 | 181.17 | 90.59 | 247 | 5914 | 600 | 243.6164 | 7.6467 | -12.0153 | 574.284 | 9.3711 | 39.4328 | 38.4039 | 38.4039 | 53.4485 | 126.5515 | 39.7124 | 217.4041 | 217.4041 | 154.6383 | 372.0424 | 0.50555 | 50.56% | 168.2376 | 85.0529 | 59.537 | 164.3314 | 164.3314 | 36.23% | 11.31% | 11.31% | 85% | 9.615% | 16.1764 | 4.6179 | 4.6179 | 74.7004 | 35.7726 | 45.46% | 45.46%
9 | 247 | 4 | 5915 | 11 | 22.9 | 290.33 | 202.56 | 492.89 | 202.56 | 101.28 | 247 | 5915 | 660 | 243.6164 | 7.6467 | -12.0153 | 634.284 | 10.3711 | 24.4328 | 45.6365 | 45.6365 | 35.8951 | 144.1049 | 25.0356 | 367.9468 | 367.9468 | 172.8958 | 540.8426 | 0.60351 | 60.35% | 244.569 | 147.601 | 103.3207 | 165.7789 | 165.7789 | 62.32% | 11.31% | 11.31% | 90% | 10.18% | 24.8961 | 4.4006 | 4.4006 | 109.5568 | 55.0556 | 66.09% | 66.09%
9 | 247 | 4 | 5916 | 12 | 24.1 | 368.89 | 228.28 | 597.17 | 228.28 | 114.14 | 247 | 5916 | 720 | 243.6164 | 7.6467 | -12.0153 | 694.284 | 11.3711 | 9.4328 | 50.0428 | 50.0428 | 14.6508 | 165.3492 | 11.0788 | 472.2818 | 472.2818 | 194.8492 | 667.131 | 0.64534 | 64.53% | 301.6766 | 194.6844 | 136.2791 | 269.1109 | 269.1109 | 50.64% | 11.32% | 11.32% | 90% | 10.19% | 30.7403 | 4.1933 | 4.1933 | 128.904 | 67.9795 | 47.9% | 47.9%
9 | 247 | 4 | 5917 | 13 | 25.3 | 321.53 | 220.14 | 541.67 | 220.14 | 110.07 | 247 | 5917 | 780 | 243.6164 | 7.6467 | -12.0153 | 754.284 | 12.3711 | -5.5672 | 50.5789 | 50.5789 | 8.7089 | 188.7089 | 8.0745 | 412.0937 | 412.0937 | 187.9012 | 599.9949 | 0.63186 | 63.19% | 271.3177 | 171.436 | 120.0052 | 288.1962 | 288.1962 | 41.64% | 11.29% | 11.29% | 90% | 10.16% | 27.5776 | 3.9962 | 3.9962 | 110.2045 | 60.9855 | 38.24% | 38.24%
9 | 247 | 4 | 5918 | 14 | 26.5 | 258.33 | 245.61 | 503.94 | 245.61 | 122.81 | 247 | 5918 | 840 | 243.6164 | 7.6467 | -12.0153 | 814.284 | 13.3711 | -20.5672 | 47.0913 | 47.0913 | 30.7575 | 210.7575 | 21.3117 | 328.5795 | 328.5795 | 209.6412 | 538.2208 | 0.61684 | 61.68% | 243.3834 | 150.1283 | 105.0898 | 301.7794 | 301.7794 | 34.82% | 11.26% | 11.26% | 90% | 10.13% | 24.661 | 3.8091 | 3.8091 | 93.9356 | 54.5356 | 31.13% | 31.13%
9 | 247 | 4 | 5919 | 15 | 25.2 | 126.94 | 228.94 | 355.88 | 228.94 | 114.47 | 247 | 5919 | 900 | 243.6164 | 7.6467 | -12.0153 | 874.284 | 14.3711 | -35.5672 | 40.4717 | 40.4717 | 49.2713 | 229.2713 | 35.9098 | 158.4013 | 158.4013 | 195.4125 | 353.8138 | 0.51149 | 51.15% | 159.9946 | 81.8359 | 57.2851 | 286.9089 | 286.9089 | 19.97% | 11.22% | 11.22% | 85% | 9.541% | 15.2647 | 4.0122 | 4.0122 | 61.2449 | 33.7564 | 21.35% | 21.35%
9 | 247 | 4 | 5920 | 16 | 25.9 | 158.94 | 138.75 | 297.69 | 138.75 | 69.38 | 247 | 5920 | 960 | 243.6164 | 7.6467 | -12.0153 | 934.284 | 15.3711 | -50.5672 | 31.8758 | 31.8758 | 64.3485 | 244.3485 | 50.7023 | 190.6239 | 190.6239 | 118.4305 | 309.0545 | 0.47395 | 47.39% | 139.7544 | 66.236 | 46.3652 | 293.7824 | 293.7824 | 15.78% | 11.19% | 11.19% | 85% | 9.514% | 13.2959 | 3.9014 | 3.9014 | 51.8722 | 29.4028 | 17.66% | 17.66%
9 | 247 | 4 | 5921 | 17 | 25 | 210.42 | 123.19 | 333.61 | 123.19 | 61.6 | 247 | 5921 | 1020 | 243.6164 | 7.6467 | -12.0153 | 994.284 | 16.3711 | -65.5672 | 22.1918 | 22.1918 | 77.0433 | 257.0433 | 65.5513 | 230.5709 | 230.5709 | 105.1492 | 335.7201 | 0.49446 | 49.45% | 151.8126 | 75.0647 | 52.5453 | 278.6233 | 278.6233 | 18.86% | 11.22% | 11.22% | 85% | 9.541% | 14.484 | 4.0445 | 4.0445 | 58.5803 | 32.03 | 21.02% | 21.02%
9 | 247 | 4 | 5922 | 18 | 25 | 104.44 | 85.33 | 189.77 | 85.33 | 42.67 | 247 | 5922 | 1080 | 243.6164 | 7.6467 | -12.0153 | 1054.284 | 17.3711 | -80.5672 | 12.0171 | 12.0171 | 88.4041 | 268.4041 | 80.4165 | 83.5125 | 83.5125 | 72.8337 | 156.3462 | 0.13932 | 13.93% | 70.6998 | 9.85 | 6.895 | 267.6576 | 267.6576 | 2.576% | 11.17% | 0% | 80% | 0% | 0 | 4.0445 | 4.0445 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5923 | 19 | 22.8 | 20.22 | 38.47 | 58.69 | 38.47 | 19.24 | 247 | 5923 | 1140 | 243.6164 | 7.6467 | -12.0153 | 1114.284 | 18.3711 | -95.5672 | 1.7832 | 1.7832 | 99.2806 | 279.2806 | 95.2772 | 0 | 0 | 32.8362 | 32.8362 | -2.5048 | 0% | 14.8485 | 0 | 0 | 159.3958 | 159.3958 | 0% | 11.23% | 0% | 80% | 0% | 0 | 4.4183 | 4.4183 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5924 | 20 | 20.1 | 0 | 3.14 | 3.14 | 3.14 | 1.57 | 247 | 5924 | 1200 | 243.6164 | 7.6467 | -12.0153 | 1174.284 | 19.3711 | -110.5672 | -8.1335 | 0 | 101.204 | 281.204 | 97.897 | 0 | 0 | 2.6802 | 2.6802 | -41.9313 | 0% | 1.212 | 0 | 0 | 144.7535 | 144.7535 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5925 | 21 | 19 | 0 | 0 | 0 | 0 | 0 | 247 | 5925 | 1260 | 243.6164 | 7.6467 | -12.0153 | 1234.284 | 20.3711 | -125.5672 | -17.3272 | 0 | 101.204 | 281.204 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7894 | 0 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5926 | 22 | 16.4 | 0 | 0 | 0 | 0 | 0 | 247 | 5926 | 1320 | 243.6164 | 7.6467 | -12.0153 | 1294.284 | 21.3711 | -140.5672 | -25.2945 | 0 | 101.204 | 281.204 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3151 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5927 | 23 | 14.8 | 0 | 0 | 0 | 0 | 0 | 247 | 5927 | 1380 | 243.6164 | 7.6467 | -12.0153 | 1354.284 | 22.3711 | -155.5672 | -31.3987 | 0 | 101.204 | 281.204 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3354 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
9 | 247 | 4 | 5928 | 24 | 13.8 | 0 | 0 | 0 | 0 | 0 | 247 | 5928 | 1440 | 243.6164 | 7.6467 | -12.0153 | 1414.284 | 23.3711 | -170.5672 | -34.9314 | 0 | 101.204 | 281.204 | 97.897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4414 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5929 | 1 | 12.9 | 0 | 0 | 0 | 0 | 0 | 248 | 5929 | 60 | 244.6027 | 7.2813 | -11.8068 | 34.284 | 0.37462 | 174.3807 | -35.7101 | 0 | 100.6652 | 79.3348 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4594 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5930 | 2 | 12.2 | 0 | 0 | 0 | 0 | 0 | 248 | 5930 | 120 | 244.6027 | 7.2813 | -11.8068 | 94.284 | 1.3746 | 159.3807 | -32.9176 | 0 | 100.6652 | 79.3348 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.063 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5931 | 3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 248 | 5931 | 180 | 244.6027 | 7.2813 | -11.8068 | 154.284 | 2.3746 | 144.3807 | -27.3776 | 0 | 100.6652 | 79.3348 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5143 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5932 | 4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 248 | 5932 | 240 | 244.6027 | 7.2813 | -11.8068 | 214.284 | 3.3746 | 129.3807 | -19.7942 | 0 | 100.6652 | 79.3348 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9715 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5933 | 5 | 10.7 | 0 | 0 | 0 | 0 | 0 | 248 | 5933 | 300 | 244.6027 | 7.2813 | -11.8068 | 274.284 | 4.3746 | 114.3807 | -10.8395 | 0 | 100.6652 | 79.3348 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.7598 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5934 | 6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 248 | 5934 | 360 | 244.6027 | 7.2813 | -11.8068 | 334.284 | 5.3746 | 99.3807 | -1.0524 | 0 | 100.6652 | 79.3348 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.5235 | 4.5235 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5935 | 7 | 10.5 | 3.28 | 10.69 | 13.97 | 10.69 | 5.35 | 248 | 5935 | 420 | 244.6027 | 7.2813 | -11.8068 | 394.284 | 6.3746 | 84.3807 | 9.1415 | 9.1415 | 90.9296 | 89.0704 | 84.2024 | 0 | 0 | 9.1245 | 9.1245 | -14.1307 | 0% | 4.1261 | 0 | 0 | 167.177 | 167.177 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5936 | 8 | 12.4 | 48 | 43.33 | 91.33 | 43.33 | 21.67 | 248 | 5936 | 480 | 244.6027 | 7.2813 | -11.8068 | 454.284 | 7.3746 | 69.3807 | 19.3646 | 19.3646 | 79.7576 | 100.2424 | 69.3241 | 51.1128 | 51.1128 | 36.9845 | 88.0973 | -0.69289 | 0% | 39.8376 | 0 | 0 | 181.4877 | 181.4877 | 0% | 11.65% | 11.65% | 80% | 9.32% | 3.7127 | 6.6439 | 6 | 22.2764 | 8.2104 | 12.27% | 12.27%
9 | 248 | 5 | 5937 | 9 | 15 | 117.5 | 73.56 | 191.06 | 73.56 | 36.78 | 248 | 5937 | 540 | 244.6027 | 7.2813 | -11.8068 | 514.284 | 8.3746 | 54.3807 | 29.208 | 29.208 | 67.4892 | 112.5108 | 54.4541 | 139.9832 | 139.9832 | 62.7874 | 202.7706 | 0.18295 | 18.3% | 91.6929 | 16.7755 | 11.7429 | 169.8481 | 169.8481 | 6.914% | 11.52% | 11.52% | 80% | 9.213% | 8.4477 | 6.0165 | 6 | 50.6859 | 18.6812 | 29.84% | 29.84%
9 | 248 | 5 | 5938 | 10 | 20.2 | 201.44 | 111.94 | 313.38 | 111.94 | 55.97 | 248 | 5938 | 600 | 244.6027 | 7.2813 | -11.8068 | 574.284 | 9.3746 | 39.3807 | 38.1282 | 38.1282 | 53.136 | 126.864 | 39.6212 | 251.3102 | 251.3102 | 95.5468 | 346.857 | 0.47442 | 47.44% | 156.8487 | 74.412 | 52.0884 | 159.8342 | 159.8342 | 32.59% | 11.35% | 11.35% | 85% | 9.645% | 15.128 | 4.9037 | 4.9037 | 74.1832 | 33.4542 | 46.41% | 46.41%
9 | 248 | 5 | 5939 | 11 | 21.5 | 247.08 | 194.72 | 441.8 | 194.72 | 97.36 | 248 | 5939 | 660 | 244.6027 | 7.2813 | -11.8068 | 634.284 | 10.3746 | 24.3807 | 45.323 | 45.323 | 35.6174 | 144.3826 | 24.9094 | 315.147 | 315.147 | 166.2039 | 481.3509 | 0.57242 | 57.24% | 217.6669 | 124.5969 | 87.2179 | 160.5111 | 160.5111 | 54.34% | 11.33% | 11.33% | 85% | 9.627% | 20.9545 | 4.6551 | 4.6551 | 97.5446 | 46.3389 | 60.77% | 60.77%
9 | 248 | 5 | 5940 | 12 | 24.7 | 224.17 | 192.78 | 416.95 | 192.78 | 96.39 | 248 | 5940 | 720 | 244.6027 | 7.2813 | -11.8068 | 694.284 | 11.3746 | 9.3807 | 49.6919 | 49.6919 | 14.4734 | 165.5266 | 10.8473 | 288.7114 | 288.7114 | 164.548 | 453.2594 | 0.57331 | 57.33% | 204.9639 | 117.5086 | 82.256 | 273.5184 | 273.5184 | 30.07% | 11.26% | 11.26% | 85% | 9.573% | 19.6212 | 4.0935 | 4.0935 | 80.319 | 43.3906 | 29.37% | 29.37%
9 | 248 | 5 | 5941 | 13 | 26.1 | 273 | 170.14 | 443.14 | 170.14 | 85.07 | 248 | 5941 | 780 | 244.6027 | 7.2813 | -11.8068 | 754.284 | 12.3746 | -5.6193 | 50.2101 | 50.2101 | 8.7295 | 188.7295 | 7.8512 | 351.955 | 351.955 | 145.2236 | 497.1786 | 0.59969 | 59.97% | 224.8242 | 134.8238 | 94.3767 | 303.7712 | 303.7712 | 31.07% | 11.25% | 11.25% | 85% | 9.563% | 21.4996 | 3.8703 | 3.8703 | 83.2102 | 47.5444 | 27.39% | 27.39%
9 | 248 | 5 | 5942 | 14 | 26.3 | 178.39 | 158.28 | 336.67 | 158.28 | 79.14 | 248 | 5942 | 840 | 244.6027 | 7.2813 | -11.8068 | 814.284 | 13.3746 | -20.6193 | 46.7311 | 46.7311 | 30.6397 | 210.6397 | 21.2704 | 228.3032 | 228.3032 | 135.1004 | 363.4036 | 0.52564 | 52.56% | 164.3311 | 86.379 | 60.4653 | 293.7792 | 293.7792 | 20.58% | 11.2% | 11.2% | 85% | 9.521% | 15.6453 | 3.8396 | 3.8396 | 60.0711 | 34.5982 | 20.45% | 20.45%
9 | 248 | 5 | 5943 | 15 | 27 | 236.44 | 172.17 | 408.61 | 172.17 | 86.09 | 248 | 5943 | 900 | 244.6027 | 7.2813 | -11.8068 | 874.284 | 14.3746 | -35.6193 | 40.1332 | 40.1332 | 49.0787 | 229.0787 | 35.9145 | 297.0855 | 297.0855 | 146.9563 | 444.0417 | 0.57952 | 57.95% | 200.7957 | 116.365 | 81.4555 | 309.3849 | 309.3849 | 26.33% | 11.21% | 11.21% | 85% | 9.533% | 19.1413 | 3.7341 | 3.7341 | 71.4754 | 42.3292 | 23.1% | 23.1%
9 | 248 | 5 | 5944 | 16 | 26.3 | 152.17 | 144.03 | 296.2 | 144.03 | 72.02 | 248 | 5944 | 960 | 244.6027 | 7.2813 | -11.8068 | 934.284 | 15.3746 | -50.6193 | 31.5576 | 31.5576 | 64.1289 | 244.1289 | 50.7294 | 184.0454 | 184.0454 | 122.9373 | 306.9827 | 0.47448 | 47.45% | 138.8176 | 65.8661 | 46.1063 | 299.0482 | 299.0482 | 15.42% | 11.18% | 11.18% | 85% | 9.504% | 13.1932 | 3.8396 | 3.8396 | 50.6561 | 29.1756 | 16.94% | 16.94%
9 | 248 | 5 | 5945 | 17 | 26 | 144.78 | 122.22 | 267 | 122.22 | 61.11 | 248 | 5945 | 1020 | 244.6027 | 7.2813 | -11.8068 | 994.284 | 16.3746 | -65.6193 | 21.8867 | 21.8867 | 76.8193 | 256.8193 | 65.5937 | 160.4835 | 160.4835 | 104.3213 | 264.8048 | 0.41959 | 41.96% | 119.7447 | 50.2441 | 35.1709 | 291.2016 | 291.2016 | 12.08% | 11.18% | 11.18% | 80% | 8.94% | 10.7055 | 3.8858 | 3.8858 | 41.5996 | 23.6744 | 14.29% | 14.29%
9 | 248 | 5 | 5946 | 18 | 25.2 | 92.17 | 79.67 | 171.84 | 79.67 | 39.84 | 248 | 5946 | 1080 | 244.6027 | 7.2813 | -11.8068 | 1054.284 | 17.3746 | -80.6193 | 11.7171 | 11.7171 | 88.1845 | 268.1845 | 80.4718 | 75.1298 | 75.1298 | 68.0026 | 143.1324 | 0.080939 | 8.094% | 64.7245 | 5.2387 | 3.6671 | 276.4991 | 276.4991 | 1.326% | 11.16% | 0% | 80% | 0% | 0 | 4.0122 | 4.0122 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5947 | 19 | 23 | 10.83 | 34.78 | 45.61 | 34.78 | 17.39 | 248 | 5947 | 1140 | 244.6027 | 7.2813 | -11.8068 | 1114.284 | 18.3746 | -95.6193 | 1.4807 | 1.4807 | 99.0691 | 279.0691 | 95.3448 | 0 | 0 | 29.6866 | 29.6866 | -2.8412 | 0% | 13.4243 | 0 | 0 | 158.1117 | 158.1117 | 0% | 11.22% | 0% | 80% | 0% | 0 | 4.3829 | 4.3829 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5948 | 20 | 20.7 | 0 | 2.5 | 2.5 | 2.5 | 1.25 | 248 | 5948 | 1200 | 244.6027 | 7.2813 | -11.8068 | 1174.284 | 19.3746 | -110.6193 | -8.4453 | 0 | 100.6652 | 280.6652 | 97.5195 | 0 | 0 | 2.1339 | 2.1339 | -52.2542 | 0% | 0.96494 | 0 | 0 | 145.939 | 145.939 | 0% | 11.32% | 0% | 80% | 0% | 0 | 4.8067 | 4.8067 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5949 | 21 | 17.5 | 0 | 0 | 0 | 0 | 0 | 248 | 5949 | 1260 | 244.6027 | 7.2813 | -11.8068 | 1234.284 | 20.3746 | -125.6193 | -17.654 | 0 | 100.6652 | 280.6652 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.4944 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4579 | 5.4579 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5950 | 22 | 15.5 | 0 | 0 | 0 | 0 | 0 | 248 | 5950 | 1320 | 244.6027 | 7.2813 | -11.8068 | 1294.284 | 21.3746 | -140.6193 | -25.6397 | 0 | 100.6652 | 280.6652 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8863 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9013 | 5.9013 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5951 | 23 | 14.6 | 0 | 0 | 0 | 0 | 0 | 248 | 5951 | 1380 | 244.6027 | 7.2813 | -11.8068 | 1354.284 | 22.3746 | -155.6193 | -31.7605 | 0 | 100.6652 | 280.6652 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7948 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
9 | 248 | 5 | 5952 | 24 | 13.1 | 0 | 0 | 0 | 0 | 0 | 248 | 5952 | 1440 | 244.6027 | 7.2813 | -11.8068 | 1414.284 | 23.3746 | -170.6193 | -35.3004 | 0 | 100.6652 | 280.6652 | 97.5195 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6177 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5953 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 249 | 5953 | 60 | 245.589 | 6.9134 | -11.5898 | 34.284 | 0.37824 | 174.3264 | -36.0722 | 0 | 100.1232 | 79.8768 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2894 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5954 | 2 | 13.2 | 0 | 0 | 0 | 0 | 0 | 249 | 5954 | 120 | 245.589 | 6.9134 | -11.5898 | 94.284 | 1.3782 | 159.3264 | -33.2544 | 0 | 100.1232 | 79.8768 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3528 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5955 | 3 | 12.4 | 0 | 0 | 0 | 0 | 0 | 249 | 5955 | 180 | 245.589 | 6.9134 | -11.5898 | 154.284 | 2.3782 | 144.3264 | -27.682 | 0 | 100.1232 | 79.8768 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9402 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5956 | 4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 249 | 5956 | 240 | 245.589 | 6.9134 | -11.5898 | 214.284 | 3.3782 | 129.3264 | -20.0678 | 0 | 100.1232 | 79.8768 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8545 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5957 | 5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 249 | 5957 | 300 | 245.589 | 6.9134 | -11.5898 | 274.284 | 4.3782 | 114.3264 | -11.0894 | 0 | 100.1232 | 79.8768 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.3724 | 2.3724 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5958 | 6 | 11.5 | 0 | 0 | 0 | 0 | 0 | 249 | 5958 | 360 | 245.589 | 6.9134 | -11.5898 | 334.284 | 5.3782 | 99.3264 | -1.2871 | 0 | 100.1232 | 79.8768 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 14.1661 | 14.1661 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5959 | 7 | 10.7 | 1.67 | 7 | 8.67 | 7 | 3.5 | 249 | 5959 | 420 | 245.589 | 6.9134 | -11.5898 | 394.284 | 6.3782 | 84.3264 | 8.9123 | 8.9123 | 90.633 | 89.367 | 84.1555 | 0 | 0 | 5.9749 | 5.9749 | -21.9256 | 0% | 2.7018 | 0 | 0 | 181.4184 | 181.4184 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5960 | 8 | 12.1 | 53.47 | 34.94 | 88.41 | 34.94 | 17.47 | 249 | 5960 | 480 | 245.589 | 6.9134 | -11.5898 | 454.284 | 7.3782 | 69.3264 | 19.131 | 19.131 | 79.4512 | 100.5488 | 69.2652 | 57.7631 | 57.7631 | 29.8232 | 87.5863 | -0.70952 | 0% | 39.6065 | 0 | 0 | 197.8879 | 197.8879 | 0% | 11.66% | 11.66% | 80% | 9.329% | 3.695 | 6.7193 | 6 | 22.1699 | 8.1711 | 11.2% | 11.2%
9 | 249 | 6 | 5961 | 9 | 15.4 | 180.22 | 64.31 | 244.53 | 64.31 | 32.16 | 249 | 5961 | 540 | 245.589 | 6.9134 | -11.5898 | 514.284 | 8.3782 | 54.3264 | 28.9586 | 28.9586 | 67.1736 | 112.8264 | 54.3817 | 216.7737 | 216.7737 | 54.892 | 271.6657 | 0.34379 | 34.38% | 122.8472 | 42.2334 | 29.5634 | 169.6997 | 169.6997 | 17.42% | 11.49% | 11.49% | 80% | 9.189% | 11.2879 | 5.9242 | 5.9242 | 66.8713 | 24.9621 | 39.41% | 39.41%
9 | 249 | 6 | 5962 | 10 | 18.7 | 279.39 | 94.67 | 374.06 | 94.67 | 47.34 | 249 | 5962 | 600 | 245.589 | 6.9134 | -11.5898 | 574.284 | 9.3782 | 39.3264 | 37.8508 | 37.8508 | 52.8218 | 127.1782 | 39.5303 | 351.1857 | 351.1857 | 80.8059 | 431.9916 | 0.5317 | 53.17% | 195.3466 | 103.8663 | 72.7064 | 177.0124 | 177.0124 | 41.07% | 11.38% | 11.38% | 85% | 9.672% | 18.8931 | 5.2053 | 5.2053 | 98.3437 | 41.7804 | 55.56% | 55.56%
9 | 249 | 6 | 5963 | 11 | 22.5 | 271.06 | 201.44 | 472.5 | 201.44 | 100.72 | 249 | 5963 | 660 | 245.589 | 6.9134 | -11.5898 | 634.284 | 10.3782 | 24.3264 | 45.0075 | 45.0075 | 35.3384 | 144.6616 | 24.785 | 347.981 | 347.981 | 171.9398 | 519.9208 | 0.59378 | 59.38% | 235.1082 | 139.6029 | 97.722 | 177.394 | 177.394 | 55.09% | 11.31% | 11.31% | 90% | 10.18% | 23.939 | 4.4719 | 4.4719 | 107.0524 | 52.9391 | 60.35% | 60.35%
9 | 249 | 6 | 5964 | 12 | 25.2 | 337.78 | 150.61 | 488.39 | 150.61 | 75.31 | 249 | 5964 | 720 | 245.589 | 6.9134 | -11.5898 | 694.284 | 11.3782 | 9.3264 | 49.3386 | 49.3386 | 14.2945 | 165.7055 | 10.6205 | 437.655 | 437.655 | 128.5537 | 566.2086 | 0.62122 | 62.12% | 256.0395 | 159.056 | 111.3392 | 308.3699 | 308.3699 | 36.11% | 11.29% | 11.29% | 90% | 10.16% | 26.005 | 4.0122 | 4.0122 | 104.3371 | 57.5077 | 33.84% | 33.84%
9 | 249 | 6 | 5965 | 13 | 25.5 | 379.5 | 145.61 | 525.11 | 145.61 | 72.81 | 249 | 5965 | 780 | 245.589 | 6.9134 | -11.5898 | 754.284 | 12.3782 | -5.6736 | 49.8386 | 49.8386 | 8.7528 | 188.7528 | 7.639 | 492.171 | 492.171 | 124.2859 | 616.4569 | 0.63715 | 63.72% | 278.7618 | 177.6136 | 124.3295 | 303.0968 | 303.0968 | 41.02% | 11.3% | 11.3% | 90% | 10.17% | 28.3412 | 3.9643 | 3.9643 | 112.3525 | 62.6741 | 37.07% | 37.07%
9 | 249 | 6 | 5966 | 14 | 26.8 | 392.72 | 198.75 | 591.47 | 198.75 | 99.38 | 249 | 5966 | 840 | 245.589 | 6.9134 | -11.5898 | 814.284 | 13.3782 | -20.6736 | 46.3677 | 46.3677 | 30.5252 | 210.5252 | 21.2367 | 505.7468 | 505.7468 | 169.6437 | 675.3906 | 0.65579 | 65.58% | 305.4116 | 200.2855 | 140.1998 | 313.4575 | 313.4575 | 44.73% | 11.31% | 11.31% | 90% | 10.17% | 31.0752 | 3.7639 | 3.7639 | 116.9633 | 68.72 | 37.31% | 37.31%
9 | 249 | 6 | 5967 | 15 | 26.7 | 444.11 | 178.06 | 622.17 | 178.06 | 89.03 | 249 | 5967 | 900 | 245.589 | 6.9134 | -11.5898 | 874.284 | 14.3782 | -35.6736 | 39.791 | 39.791 | 48.8887 | 228.8887 | 35.9243 | 561.9423 | 561.9423 | 151.9837 | 713.9261 | 0.66349 | 66.35% | 322.8374 | 214.2004 | 149.9402 | 322.6839 | 322.6839 | 46.47% | 11.32% | 11.32% | 90% | 10.19% | 32.8915 | 3.7789 | 3.7789 | 124.2928 | 72.7366 | 38.52% | 38.52%
9 | 249 | 6 | 5968 | 16 | 27 | 331.17 | 160 | 491.17 | 160 | 80 | 249 | 5968 | 960 | 245.589 | 6.9134 | -11.5898 | 934.284 | 15.3782 | -50.6736 | 31.2356 | 31.2356 | 63.911 | 243.911 | 50.7606 | 403.9768 | 403.9768 | 136.5685 | 540.5453 | 0.6196 | 61.96% | 244.4346 | 151.4507 | 106.0155 | 319.5229 | 319.5229 | 33.18% | 11.25% | 11.25% | 90% | 10.13% | 24.7536 | 3.7341 | 3.7341 | 92.4326 | 54.7405 | 28.93% | 28.93%
9 | 249 | 6 | 5969 | 17 | 26 | 253.83 | 132.56 | 386.39 | 132.56 | 66.28 | 249 | 5969 | 1020 | 245.589 | 6.9134 | -11.5898 | 994.284 | 16.3782 | -65.6736 | 21.5779 | 21.5779 | 76.5963 | 256.5963 | 65.6394 | 284.6897 | 284.6897 | 113.147 | 397.8367 | 0.54813 | 54.81% | 179.9018 | 98.6103 | 69.0272 | 309.5707 | 309.5707 | 22.3% | 11.22% | 11.22% | 85% | 9.536% | 17.1561 | 3.8858 | 3.8858 | 66.6653 | 37.9393 | 21.53% | 21.53%
9 | 249 | 6 | 5970 | 18 | 25.7 | 148.47 | 68.47 | 216.94 | 68.47 | 34.24 | 249 | 5970 | 1080 | 245.589 | 6.9134 | -11.5898 | 1054.284 | 17.3782 | -80.6736 | 11.4135 | 11.4135 | 87.9653 | 267.9653 | 80.5296 | 123.4481 | 123.4481 | 58.4428 | 181.8909 | 0.24086 | 24.09% | 82.2511 | 19.8112 | 13.8679 | 300.8159 | 300.8159 | 4.61% | 11.16% | 0% | 80% | 0% | 0 | 3.9327 | 3.9327 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5971 | 19 | 22.6 | 23.33 | 38.11 | 61.44 | 38.11 | 19.06 | 249 | 5971 | 1140 | 245.589 | 6.9134 | -11.5898 | 1114.284 | 18.3782 | -95.6736 | 1.1748 | 1.1748 | 98.8577 | 278.8577 | 95.4145 | 0 | 0 | 32.5289 | 32.5289 | -2.5493 | 0% | 14.7096 | 0 | 0 | 161.6677 | 161.6677 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4539 | 4.4539 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5972 | 20 | 19.9 | 0 | 3 | 3 | 3 | 1.5 | 249 | 5972 | 1200 | 245.589 | 6.9134 | -11.5898 | 1174.284 | 19.3782 | -110.6736 | -8.7604 | 0 | 100.1232 | 280.1232 | 97.1394 | 0 | 0 | 2.5607 | 2.5607 | -44.0976 | 0% | 1.1579 | 0 | 0 | 145.3048 | 145.3048 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9628 | 4.9628 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5973 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 249 | 5973 | 1260 | 245.589 | 6.9134 | -11.5898 | 1234.284 | 20.3782 | -125.6736 | -17.984 | 0 | 100.1232 | 280.1232 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.6683 | 0 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5974 | 22 | 18.6 | 0 | 0 | 0 | 0 | 0 | 249 | 5974 | 1320 | 245.589 | 6.9134 | -11.5898 | 1294.284 | 21.3782 | -140.6736 | -25.9879 | 0 | 100.1232 | 280.1232 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.6506 | 0 | 0% | 11.41% | 0% | 80% | 0% | 0 | 5.2259 | 5.2259 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5975 | 23 | 17.2 | 0 | 0 | 0 | 0 | 0 | 249 | 5975 | 1380 | 245.589 | 6.9134 | -11.5898 | 1354.284 | 22.3782 | -155.6736 | -32.1253 | 0 | 100.1232 | 280.1232 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1524 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5226 | 5.5226 | 0 | 0 | 0% | 0%
9 | 249 | 6 | 5976 | 24 | 15.2 | 0 | 0 | 0 | 0 | 0 | 249 | 5976 | 1440 | 245.589 | 6.9134 | -11.5898 | 1414.284 | 23.3782 | -170.6736 | -35.6723 | 0 | 100.1232 | 280.1232 | 97.1394 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5685 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5977 | 1 | 14.2 | 0 | 0 | 0 | 0 | 0 | 250 | 5977 | 60 | 246.5753 | 6.543 | -11.3645 | 34.284 | 0.38199 | 174.2701 | -36.4365 | 0 | 99.5781 | 80.4219 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4864 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5978 | 2 | 13.9 | 0 | 0 | 0 | 0 | 0 | 250 | 5978 | 120 | 246.5753 | 6.543 | -11.3645 | 94.284 | 1.382 | 159.2701 | -33.5926 | 0 | 99.5781 | 80.4219 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3831 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5979 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 250 | 5979 | 180 | 246.5753 | 6.543 | -11.3645 | 154.284 | 2.382 | 144.2701 | -27.987 | 0 | 99.5781 | 80.4219 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1943 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5980 | 4 | 11.6 | 0 | 0 | 0 | 0 | 0 | 250 | 5980 | 240 | 246.5753 | 6.543 | -11.3645 | 214.284 | 3.382 | 129.2701 | -20.3419 | 0 | 99.5781 | 80.4219 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3278 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5981 | 5 | 10.9 | 0 | 0 | 0 | 0 | 0 | 250 | 5981 | 300 | 246.5753 | 6.543 | -11.3645 | 274.284 | 4.382 | 114.2701 | -11.3395 | 0 | 99.5781 | 80.4219 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.50546 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5982 | 6 | 11 | 0 | 0 | 0 | 0 | 0 | 250 | 5982 | 360 | 246.5753 | 6.543 | -11.3645 | 334.284 | 5.382 | 99.2701 | -1.5222 | 0 | 99.5781 | 80.4219 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.2944 | 10.2944 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5983 | 7 | 10.8 | 2.22 | 8.75 | 10.97 | 8.75 | 4.38 | 250 | 5983 | 420 | 246.5753 | 6.543 | -11.3645 | 394.284 | 6.382 | 84.2701 | 8.6827 | 8.6827 | 90.3337 | 89.6663 | 84.1067 | 0 | 0 | 7.4686 | 7.4686 | -17.3485 | 0% | 3.3773 | 0 | 0 | 176.0968 | 176.0968 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5984 | 8 | 12.2 | 34.58 | 50.61 | 85.19 | 50.61 | 25.31 | 250 | 5984 | 480 | 246.5753 | 6.543 | -11.3645 | 454.284 | 7.382 | 69.2701 | 18.8965 | 18.8965 | 79.1423 | 100.8577 | 69.2051 | 37.9075 | 37.9075 | 43.1983 | 81.1058 | -0.82761 | 0% | 36.676 | 0 | 0 | 191.0289 | 191.0289 | 0% | 11.66% | 11.66% | 80% | 9.328% | 3.4213 | 6.6941 | 6 | 20.5276 | 7.5658 | 10.75% | 10.75%
9 | 250 | 7 | 5985 | 9 | 16.7 | 112.17 | 111.11 | 223.28 | 111.11 | 55.56 | 250 | 5985 | 540 | 246.5753 | 6.543 | -11.3645 | 514.284 | 8.382 | 54.2701 | 28.708 | 28.708 | 66.8559 | 113.1441 | 54.3087 | 136.2392 | 136.2392 | 94.8383 | 231.0775 | 0.27563 | 27.56% | 104.4933 | 28.8018 | 20.1612 | 163.7478 | 163.7478 | 12.31% | 11.46% | 11.46% | 80% | 9.164% | 9.576 | 5.6319 | 5.6319 | 53.9307 | 21.1764 | 32.94% | 32.94%
9 | 250 | 7 | 5986 | 10 | 17.9 | 261.94 | 161.81 | 423.75 | 161.81 | 80.91 | 250 | 5986 | 600 | 246.5753 | 6.543 | -11.3645 | 574.284 | 9.382 | 39.2701 | 37.5718 | 37.5718 | 52.506 | 127.494 | 39.4397 | 331.7634 | 331.7634 | 138.1135 | 469.8769 | 0.54987 | 54.99% | 212.4783 | 116.8357 | 81.785 | 172.5597 | 172.5597 | 47.4% | 11.39% | 11.39% | 85% | 9.682% | 20.5713 | 5.3726 | 5.3726 | 110.5206 | 45.4916 | 64.05% | 64.05%
9 | 250 | 7 | 5987 | 11 | 20.3 | 353.56 | 156.06 | 509.62 | 156.06 | 78.03 | 250 | 5987 | 660 | 246.5753 | 6.543 | -11.3645 | 634.284 | 10.382 | 24.2701 | 44.6899 | 44.6899 | 35.0584 | 144.9416 | 24.6628 | 456.8774 | 456.8774 | 133.2055 | 590.0829 | 0.61064 | 61.06% | 266.8355 | 162.9407 | 114.0585 | 171.3515 | 171.3515 | 66.56% | 11.35% | 11.35% | 90% | 10.21% | 27.2537 | 4.8842 | 4.8842 | 133.1114 | 60.2692 | 77.68% | 77.68%
9 | 250 | 7 | 5988 | 12 | 23.1 | 442.44 | 165.5 | 607.94 | 165.5 | 82.75 | 250 | 5988 | 720 | 246.5753 | 6.543 | -11.3645 | 694.284 | 11.382 | 9.2701 | 48.9831 | 48.9831 | 14.1144 | 165.8856 | 10.3989 | 576.7573 | 576.7573 | 141.2631 | 718.0204 | 0.65359 | 65.36% | 324.6888 | 212.2128 | 148.5489 | 168.8168 | 168.8168 | 87.99% | 11.34% | 11.34% | 90% | 10.2% | 33.132 | 4.3653 | 4.3653 | 144.6315 | 73.2684 | 85.67% | 85.67%
9 | 250 | 7 | 5989 | 13 | 24.5 | 472.56 | 184.58 | 657.14 | 184.58 | 92.29 | 250 | 5989 | 780 | 246.5753 | 6.543 | -11.3645 | 754.284 | 12.382 | -5.7299 | 49.4644 | 49.4644 | 8.7786 | 188.7786 | 7.4394 | 616.5532 | 616.5532 | 157.5489 | 774.1021 | 0.66837 | 66.84% | 350.049 | 233.9635 | 163.7744 | 282.8028 | 282.8028 | 57.91% | 11.35% | 11.35% | 90% | 10.21% | 35.7436 | 4.1265 | 4.1265 | 147.4951 | 79.0438 | 52.15% | 52.15%
9 | 250 | 7 | 5990 | 14 | 25.8 | 449.5 | 170.42 | 619.92 | 170.42 | 85.21 | 250 | 5990 | 840 | 246.5753 | 6.543 | -11.3645 | 814.284 | 13.382 | -20.7299 | 46.0012 | 46.0012 | 30.4138 | 210.4138 | 21.2108 | 582.5345 | 582.5345 | 145.4626 | 727.9971 | 0.66359 | 66.36% | 329.2003 | 218.4545 | 152.9181 | 302.2276 | 302.2276 | 50.6% | 11.33% | 11.33% | 90% | 10.2% | 33.5657 | 3.917 | 3.917 | 131.4761 | 74.2275 | 43.5% | 43.5%
9 | 250 | 7 | 5991 | 15 | 26.5 | 347.17 | 166.61 | 513.78 | 166.61 | 83.31 | 250 | 5991 | 900 | 246.5753 | 6.543 | -11.3645 | 874.284 | 14.382 | -35.7299 | 39.4454 | 39.4454 | 48.7014 | 228.7014 | 35.9393 | 442.4104 | 442.4104 | 142.2105 | 584.6209 | 0.63169 | 63.17% | 264.3656 | 166.998 | 116.8986 | 306.1746 | 306.1746 | 38.18% | 11.28% | 11.28% | 90% | 10.15% | 26.8265 | 3.8091 | 3.8091 | 102.1842 | 59.3244 | 33.37% | 33.37%
9 | 250 | 7 | 5992 | 16 | 26.6 | 262.44 | 149.39 | 411.83 | 149.39 | 74.7 | 250 | 5992 | 960 | 246.5753 | 6.543 | -11.3645 | 934.284 | 15.382 | -50.7299 | 30.9101 | 30.9101 | 63.6948 | 243.6948 | 50.7957 | 322.9268 | 322.9268 | 127.5123 | 450.4391 | 0.58083 | 58.08% | 203.6886 | 118.3092 | 82.8164 | 305.7761 | 305.7761 | 27.08% | 11.23% | 11.23% | 85% | 9.541% | 19.4346 | 3.7939 | 3.7939 | 73.7338 | 42.9779 | 24.11% | 24.11%
9 | 250 | 7 | 5993 | 17 | 25.1 | 217.56 | 116.39 | 333.95 | 116.39 | 58.2 | 250 | 5993 | 1020 | 246.5753 | 6.543 | -11.3645 | 994.284 | 16.382 | -65.7299 | 21.2657 | 21.2657 | 76.3741 | 256.3741 | 65.6883 | 246.9571 | 246.9571 | 99.3451 | 346.3022 | 0.50453 | 50.45% | 156.5979 | 79.0085 | 55.306 | 294.6655 | 294.6655 | 18.77% | 11.22% | 11.22% | 85% | 9.541% | 14.941 | 4.0283 | 4.0283 | 60.1872 | 33.0408 | 20.43% | 20.43%
9 | 250 | 7 | 5994 | 18 | 25.1 | 83.28 | 79.72 | 163 | 79.72 | 39.86 | 250 | 5994 | 1080 | 246.5753 | 6.543 | -11.3645 | 1054.284 | 17.382 | -80.7299 | 11.1066 | 11.1066 | 87.7464 | 267.7464 | 80.59 | 70.6835 | 70.6835 | 68.0453 | 138.7288 | 0.05645 | 5.645% | 62.7331 | 3.5413 | 2.4789 | 275.9264 | 275.9264 | 0.8984% | 11.17% | 0% | 80% | 0% | 0 | 4.0283 | 4.0283 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5995 | 19 | 20.9 | 19.03 | 37.28 | 56.31 | 37.28 | 18.64 | 250 | 5995 | 1140 | 246.5753 | 6.543 | -11.3645 | 1114.284 | 18.382 | -95.7299 | 0.8657 | 0.8657 | 98.6462 | 278.6462 | 95.4862 | 0 | 0 | 31.8205 | 31.8205 | -2.7403 | 0% | 14.3892 | 0 | 0 | 157.7648 | 157.7648 | 0% | 11.31% | 0% | 80% | 0% | 0 | 4.7684 | 4.7684 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5996 | 20 | 18.5 | 0 | 4.72 | 4.72 | 4.72 | 2.36 | 250 | 5996 | 1200 | 246.5753 | 6.543 | -11.3645 | 1174.284 | 19.382 | -110.7299 | -9.0786 | 0 | 99.5781 | 279.5781 | 96.7569 | 0 | 0 | 4.0288 | 4.0288 | -28.5037 | 0% | 1.8218 | 0 | 0 | 143.0903 | 143.0903 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5997 | 21 | 16.5 | 0 | 0 | 0 | 0 | 0 | 250 | 5997 | 1260 | 246.5753 | 6.543 | -11.3645 | 1234.284 | 20.382 | -125.7299 | -18.317 | 0 | 99.5781 | 279.5781 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9723 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6761 | 5.6761 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5998 | 22 | 15.2 | 0 | 0 | 0 | 0 | 0 | 250 | 5998 | 1320 | 246.5753 | 6.543 | -11.3645 | 1294.284 | 21.382 | -140.7299 | -26.3392 | 0 | 99.5781 | 279.5781 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6438 | 0 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 5999 | 23 | 14.1 | 0 | 0 | 0 | 0 | 0 | 250 | 5999 | 1380 | 246.5753 | 6.543 | -11.3645 | 1354.284 | 22.382 | -155.7299 | -32.4931 | 0 | 99.5781 | 279.5781 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7597 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
9 | 250 | 7 | 6000 | 24 | 13.2 | 0 | 0 | 0 | 0 | 0 | 250 | 6000 | 1440 | 246.5753 | 6.543 | -11.3645 | 1414.284 | 23.382 | -170.7299 | -36.0467 | 0 | 99.5781 | 279.5781 | 96.7569 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5708 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6001 | 1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 251 | 6001 | 60 | 247.5616 | 6.1704 | -11.1312 | 34.284 | 0.38588 | 174.2118 | -36.8028 | 0 | 99.0301 | 80.9699 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0183 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6002 | 2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 251 | 6002 | 120 | 247.5616 | 6.1704 | -11.1312 | 94.284 | 1.3859 | 159.2118 | -33.932 | 0 | 99.0301 | 80.9699 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6277 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6003 | 3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 251 | 6003 | 180 | 247.5616 | 6.1704 | -11.1312 | 154.284 | 2.3859 | 144.2118 | -28.2928 | 0 | 99.0301 | 80.9699 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0846 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6004 | 4 | 11.1 | 0 | 0 | 0 | 0 | 0 | 251 | 6004 | 240 | 247.5616 | 6.1704 | -11.1312 | 214.284 | 3.3859 | 129.2118 | -20.6162 | 0 | 99.0301 | 80.9699 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6942 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6005 | 5 | 10.5 | 0 | 0 | 0 | 0 | 0 | 251 | 6005 | 300 | 247.5616 | 6.1704 | -11.1312 | 274.284 | 4.3859 | 114.2118 | -11.5897 | 0 | 99.0301 | 80.9699 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.6353 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6006 | 6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 251 | 6006 | 360 | 247.5616 | 6.1704 | -11.1312 | 334.284 | 5.3859 | 99.2118 | -1.7575 | 0 | 99.0301 | 80.9699 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.0809 | 3.0809 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6007 | 7 | 10.2 | 1.39 | 7.92 | 9.31 | 7.92 | 3.96 | 251 | 6007 | 420 | 247.5616 | 6.1704 | -11.1312 | 394.284 | 6.3859 | 84.2118 | 8.4526 | 8.4526 | 90.0315 | 89.9685 | 84.0561 | 0 | 0 | 6.7601 | 6.7601 | -19.4575 | 0% | 3.0569 | 0 | 0 | 163.4037 | 163.4037 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6008 | 8 | 11.6 | 28.33 | 52.78 | 81.11 | 52.78 | 26.39 | 251 | 6008 | 480 | 247.5616 | 6.1704 | -11.1312 | 454.284 | 7.3859 | 69.2118 | 18.6613 | 18.6613 | 78.831 | 101.169 | 69.1438 | 31.5219 | 31.5219 | 45.0505 | 76.5725 | -0.9423 | 0% | 34.6261 | 0 | 0 | 175.6618 | 175.6618 | 0% | 11.69% | 11.69% | 80% | 9.349% | 3.2372 | 6.8464 | 6 | 19.4231 | 7.1587 | 11.06% | 11.06%
9 | 251 | 8 | 6009 | 9 | 14.2 | 104.03 | 93.33 | 197.36 | 93.33 | 46.67 | 251 | 6009 | 540 | 247.5616 | 6.1704 | -11.1312 | 514.284 | 8.3859 | 54.2118 | 28.4561 | 28.4561 | 66.5363 | 113.4637 | 54.2353 | 127.6033 | 127.6033 | 79.6621 | 207.2654 | 0.18765 | 18.76% | 93.7254 | 17.5873 | 12.3111 | 164.9621 | 164.9621 | 7.463% | 11.54% | 11.54% | 80% | 9.233% | 8.6535 | 6.2045 | 6 | 51.9212 | 19.1365 | 31.47% | 31.47%
9 | 251 | 8 | 6010 | 10 | 18.2 | 141.06 | 124.67 | 265.73 | 124.67 | 62.34 | 251 | 6010 | 600 | 247.5616 | 6.1704 | -11.1312 | 574.284 | 9.3859 | 39.2118 | 37.2911 | 37.2911 | 52.1888 | 127.8112 | 39.3498 | 180.0404 | 180.0404 | 106.4125 | 286.4529 | 0.38948 | 38.95% | 129.534 | 50.4507 | 35.3155 | 150.363 | 150.363 | 23.49% | 11.4% | 11.4% | 80% | 9.122% | 11.8164 | 5.3093 | 5.3093 | 62.7371 | 26.131 | 41.72% | 41.72%
9 | 251 | 8 | 6011 | 11 | 21.7 | 145.14 | 147.83 | 292.97 | 147.83 | 73.92 | 251 | 6011 | 660 | 247.5616 | 6.1704 | -11.1312 | 634.284 | 10.3859 | 24.2118 | 44.3704 | 44.3704 | 34.7775 | 145.2225 | 24.5429 | 188.8 | 188.8 | 126.1808 | 314.9808 | 0.45149 | 45.15% | 142.4343 | 64.3071 | 45.015 | 150.2557 | 150.2557 | 29.96% | 11.31% | 11.31% | 85% | 9.611% | 13.6889 | 4.6179 | 4.6179 | 63.2135 | 30.2717 | 42.07% | 42.07%
9 | 251 | 8 | 6012 | 12 | 22.8 | 183.89 | 197.22 | 381.11 | 197.22 | 98.61 | 251 | 6012 | 720 | 247.5616 | 6.1704 | -11.1312 | 694.284 | 11.3859 | 9.2118 | 48.6254 | 48.6254 | 13.9332 | 166.0668 | 10.1833 | 241.1943 | 241.1943 | 168.3378 | 409.5321 | 0.5387 | 53.87% | 185.1904 | 99.7628 | 69.834 | 146.4642 | 146.4642 | 47.68% | 11.29% | 11.29% | 85% | 9.598% | 17.7747 | 4.4183 | 4.4183 | 78.5338 | 39.3072 | 53.62% | 53.62%
9 | 251 | 8 | 6013 | 13 | 24.5 | 158.47 | 166.25 | 324.72 | 166.25 | 83.13 | 251 | 6013 | 780 | 247.5616 | 6.1704 | -11.1312 | 754.284 | 12.3859 | -5.7882 | 49.0878 | 49.0878 | 8.8068 | 188.8068 | 7.2539 | 208.0175 | 208.0175 | 141.9033 | 349.9207 | 0.50396 | 50.4% | 158.2342 | 79.7444 | 55.8211 | 267.701 | 267.701 | 20.85% | 11.24% | 11.24% | 85% | 9.555% | 15.1185 | 4.1265 | 4.1265 | 62.3861 | 33.4332 | 23.3% | 23.3%
9 | 251 | 8 | 6014 | 14 | 26.3 | 155.14 | 138.28 | 293.42 | 138.28 | 69.14 | 251 | 6014 | 840 | 247.5616 | 6.1704 | -11.1312 | 814.284 | 13.3859 | -20.7882 | 45.6317 | 45.6317 | 30.3056 | 210.3056 | 21.1927 | 202.3443 | 202.3443 | 118.0294 | 320.3736 | 0.48825 | 48.83% | 144.873 | 70.7346 | 49.5142 | 287.9897 | 287.9897 | 17.19% | 11.19% | 11.19% | 85% | 9.508% | 13.7744 | 3.8396 | 3.8396 | 52.8877 | 30.4609 | 18.36% | 18.36%
9 | 251 | 8 | 6015 | 15 | 26.8 | 133.11 | 158.47 | 291.58 | 158.47 | 79.24 | 251 | 6015 | 900 | 247.5616 | 6.1704 | -11.1312 | 874.284 | 14.3859 | -35.7882 | 39.0965 | 39.0965 | 48.5166 | 228.5166 | 35.9596 | 170.851 | 170.851 | 135.2626 | 306.1136 | 0.477 | 47.7% | 138.4246 | 66.0279 | 46.2195 | 302.2948 | 302.2948 | 15.29% | 11.17% | 11.17% | 85% | 9.492% | 13.1395 | 3.7639 | 3.7639 | 49.4556 | 29.0569 | 16.36% | 16.36%
9 | 251 | 8 | 6016 | 16 | 26.4 | 99.78 | 138.61 | 238.39 | 138.61 | 69.31 | 251 | 6016 | 960 | 247.5616 | 6.1704 | -11.1312 | 934.284 | 15.3859 | -50.7882 | 30.5811 | 30.5811 | 63.4803 | 243.4803 | 50.8348 | 123.8644 | 123.8644 | 118.311 | 242.1754 | 0.38717 | 38.72% | 109.5117 | 42.3999 | 29.6799 | 290.1517 | 290.1517 | 10.23% | 11.16% | 11.16% | 80% | 8.925% | 9.7734 | 3.8243 | 3.8243 | 37.3762 | 21.613 | 12.88% | 12.88%
9 | 251 | 8 | 6017 | 17 | 26.3 | 43.47 | 122.36 | 165.83 | 122.36 | 61.18 | 251 | 6017 | 1020 | 247.5616 | 6.1704 | -11.1312 | 994.284 | 16.3859 | -65.7882 | 20.95 | 20.95 | 76.1529 | 256.1529 | 65.7403 | 49.9525 | 49.9525 | 104.4408 | 154.3933 | 0.14881 | 14.88% | 69.8166 | 10.3893 | 7.2725 | 283.9761 | 283.9761 | 2.561% | 11.13% | 11.13% | 80% | 8.903% | 6.2155 | 3.8396 | 3.8396 | 23.8648 | 13.7451 | 8.404% | 8.404%
9 | 251 | 8 | 6018 | 18 | 25.4 | 7.22 | 55.22 | 62.44 | 55.22 | 27.61 | 251 | 6018 | 1080 | 247.5616 | 6.1704 | -11.1312 | 1054.284 | 17.3859 | -80.7882 | 10.7965 | 10.7965 | 87.5279 | 267.5279 | 80.6529 | 6.2601 | 6.2601 | 47.1332 | 53.3933 | -1.1263 | 0% | 24.1444 | 0 | 0 | 307.828 | 307.828 | 0% | 11.13% | 0% | 80% | 0% | 0 | 3.9802 | 3.9802 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6019 | 19 | 22.7 | 1.53 | 20.42 | 21.95 | 20.42 | 10.21 | 251 | 6019 | 1140 | 247.5616 | 6.1704 | -11.1312 | 1114.284 | 18.3859 | -95.7882 | 0.55348 | 0.55348 | 98.4347 | 278.4347 | 95.5598 | 0 | 0 | 17.4296 | 17.4296 | -5.4419 | 0% | 7.8816 | 0 | 0 | 154.817 | 154.817 | 0% | 11.24% | 0% | 80% | 0% | 0 | 4.4361 | 4.4361 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6020 | 20 | 19 | 0 | 0 | 0 | 0 | 0 | 251 | 6020 | 1200 | 247.5616 | 6.1704 | -11.1312 | 1174.284 | 19.3859 | -110.7882 | -9.3997 | 0 | 99.0301 | 279.0301 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.2298 | 143.2298 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6021 | 21 | 16.7 | 0 | 0 | 0 | 0 | 0 | 251 | 6021 | 1260 | 247.5616 | 6.1704 | -11.1312 | 1234.284 | 20.3859 | -125.7882 | -18.6529 | 0 | 99.0301 | 279.0301 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.3993 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6022 | 22 | 15.4 | 0 | 0 | 0 | 0 | 0 | 251 | 6022 | 1320 | 247.5616 | 6.1704 | -11.1312 | 1294.284 | 21.3859 | -140.7882 | -26.6933 | 0 | 99.0301 | 279.0301 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4282 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6023 | 23 | 14.5 | 0 | 0 | 0 | 0 | 0 | 251 | 6023 | 1380 | 247.5616 | 6.1704 | -11.1312 | 1354.284 | 22.3859 | -155.7882 | -32.8637 | 0 | 99.0301 | 279.0301 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3423 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
9 | 251 | 8 | 6024 | 24 | 13.7 | 0 | 0 | 0 | 0 | 0 | 251 | 6024 | 1440 | 247.5616 | 6.1704 | -11.1312 | 1414.284 | 23.3859 | -170.7882 | -36.4238 | 0 | 99.0301 | 279.0301 | 96.372 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1041 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6025 | 1 | 13.3 | 0 | 0 | 0 | 0 | 0 | 252 | 6025 | 60 | 248.5479 | 5.7955 | -10.8902 | 34.284 | 0.3899 | 174.1516 | -37.171 | 0 | 98.4793 | 81.5207 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6026 | 2 | 12.3 | 0 | 0 | 0 | 0 | 0 | 252 | 6026 | 120 | 248.5479 | 5.7955 | -10.8902 | 94.284 | 1.3899 | 159.1516 | -34.2727 | 0 | 98.4793 | 81.5207 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7571 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6027 | 3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 252 | 6027 | 180 | 248.5479 | 5.7955 | -10.8902 | 154.284 | 2.3899 | 144.1516 | -28.5991 | 0 | 98.4793 | 81.5207 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5093 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6028 | 4 | 11 | 0 | 0 | 0 | 0 | 0 | 252 | 6028 | 240 | 248.5479 | 5.7955 | -10.8902 | 214.284 | 3.3899 | 129.1516 | -20.8908 | 0 | 98.4793 | 81.5207 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2713 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6029 | 5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 252 | 6029 | 300 | 248.5479 | 5.7955 | -10.8902 | 274.284 | 4.3899 | 114.1516 | -11.8402 | 0 | 98.4793 | 81.5207 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.6492 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6030 | 6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 252 | 6030 | 360 | 248.5479 | 5.7955 | -10.8902 | 334.284 | 5.3899 | 99.1516 | -1.9931 | 0 | 98.4793 | 81.5207 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.4565 | 6.4565 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6031 | 7 | 9.7 | 2.28 | 6.53 | 8.81 | 6.53 | 3.27 | 252 | 6031 | 420 | 248.5479 | 5.7955 | -10.8902 | 394.284 | 6.3899 | 84.1516 | 8.222 | 8.222 | 89.7267 | 90.2733 | 84.0039 | 0 | 0 | 5.5737 | 5.5737 | -23.98 | 0% | 2.5204 | 0 | 0 | 170.6439 | 170.6439 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6032 | 8 | 11.8 | 49.5 | 44.17 | 93.67 | 44.17 | 22.09 | 252 | 6032 | 480 | 248.5479 | 5.7955 | -10.8902 | 454.284 | 7.3899 | 69.1516 | 18.4252 | 18.4252 | 78.5174 | 101.4826 | 69.0814 | 55.9172 | 55.9172 | 37.7015 | 93.6186 | -0.61939 | 0% | 42.3343 | 0 | 0 | 187.0387 | 187.0387 | 0% | 11.67% | 11.67% | 80% | 9.336% | 3.9525 | 6.7954 | 6 | 23.7152 | 8.7407 | 12.68% | 12.68%
9 | 252 | 9 | 6033 | 9 | 15.1 | 137.83 | 97 | 234.83 | 97 | 48.5 | 252 | 6033 | 540 | 248.5479 | 5.7955 | -10.8902 | 514.284 | 8.3899 | 54.1516 | 28.2031 | 28.2031 | 66.2148 | 113.7852 | 54.1615 | 170.7577 | 170.7577 | 82.7947 | 253.5524 | 0.30823 | 30.82% | 114.6564 | 35.3407 | 24.7385 | 157.8934 | 157.8934 | 15.67% | 11.5% | 11.5% | 80% | 9.199% | 10.5477 | 5.9933 | 5.9933 | 63.2158 | 23.3253 | 40.04% | 40.04%
9 | 252 | 9 | 6034 | 10 | 17.7 | 209.31 | 142.5 | 351.81 | 142.5 | 71.25 | 252 | 6034 | 600 | 248.5479 | 5.7955 | -10.8902 | 574.284 | 9.3899 | 39.1516 | 37.0088 | 37.0088 | 51.8704 | 128.1296 | 39.2605 | 269.2367 | 269.2367 | 121.6314 | 390.8681 | 0.49736 | 49.74% | 176.7505 | 87.9089 | 61.5362 | 165.0336 | 165.0336 | 37.29% | 11.4% | 11.4% | 85% | 9.693% | 17.1328 | 5.4151 | 5.4151 | 92.7752 | 37.8876 | 56.22% | 56.22%
9 | 252 | 9 | 6035 | 11 | 19.8 | 318.94 | 144.94 | 463.88 | 144.94 | 72.47 | 252 | 6035 | 660 | 248.5479 | 5.7955 | -10.8902 | 634.284 | 10.3899 | 24.1516 | 44.0488 | 44.0488 | 34.4959 | 145.5041 | 24.4257 | 417.6705 | 417.6705 | 123.714 | 541.3846 | 0.59122 | 59.12% | 244.8141 | 144.738 | 101.3166 | 165.6634 | 165.6634 | 61.16% | 11.35% | 11.35% | 90% | 10.22% | 25.0184 | 4.9826 | 4.9826 | 124.6564 | 55.326 | 75.25% | 75.25%
9 | 252 | 9 | 6036 | 12 | 22.1 | 423.94 | 131.89 | 555.83 | 131.89 | 65.95 | 252 | 6036 | 720 | 248.5479 | 5.7955 | -10.8902 | 694.284 | 11.3899 | 9.1516 | 48.2655 | 48.2655 | 13.751 | 166.249 | 9.9745 | 559.5162 | 559.5162 | 112.5752 | 672.0913 | 0.64009 | 64.01% | 303.9197 | 194.5348 | 136.1744 | 161.6067 | 161.6067 | 84.26% | 11.34% | 11.34% | 90% | 10.2% | 31.0105 | 4.5443 | 4.5443 | 140.9213 | 68.5769 | 87.2% | 87.2%
9 | 252 | 9 | 6037 | 13 | 23.3 | 429.58 | 164.86 | 594.44 | 164.86 | 82.43 | 252 | 6037 | 780 | 248.5479 | 5.7955 | -10.8902 | 754.284 | 12.3899 | -5.8484 | 48.7087 | 48.7087 | 8.8372 | 188.8372 | 7.0839 | 567.3693 | 567.3693 | 140.7168 | 708.0861 | 0.65209 | 65.21% | 320.1966 | 208.7962 | 146.1573 | 268.2253 | 268.2253 | 54.49% | 11.34% | 11.34% | 90% | 10.2% | 32.6658 | 4.3304 | 4.3304 | 141.4544 | 72.2374 | 52.74% | 52.74%
9 | 252 | 9 | 6038 | 14 | 25.1 | 436.94 | 174.94 | 611.88 | 174.94 | 87.47 | 252 | 6038 | 840 | 248.5479 | 5.7955 | -10.8902 | 814.284 | 13.3899 | -20.8484 | 45.2594 | 45.2594 | 30.2003 | 210.2003 | 21.1826 | 573.5848 | 573.5848 | 149.3206 | 722.9055 | 0.66054 | 66.05% | 326.8979 | 215.9297 | 151.1508 | 286.8267 | 286.8267 | 52.7% | 11.33% | 11.33% | 90% | 10.2% | 33.3349 | 4.0283 | 4.0283 | 134.2834 | 73.7171 | 46.82% | 46.82%
9 | 252 | 9 | 6039 | 15 | 25.7 | 359.86 | 166.81 | 526.67 | 166.81 | 83.41 | 252 | 6039 | 900 | 248.5479 | 5.7955 | -10.8902 | 874.284 | 14.3899 | -35.8484 | 38.7443 | 38.7443 | 48.3344 | 228.3344 | 35.985 | 465.2713 | 465.2713 | 142.3812 | 607.6525 | 0.63543 | 63.54% | 274.7805 | 174.6049 | 122.2234 | 293.5347 | 293.5347 | 41.64% | 11.29% | 11.29% | 90% | 10.16% | 27.9246 | 3.9327 | 3.9327 | 109.8186 | 61.7529 | 37.41% | 37.41%
9 | 252 | 9 | 6040 | 16 | 25.8 | 301.44 | 118.94 | 420.38 | 118.94 | 59.47 | 252 | 6040 | 960 | 248.5479 | 5.7955 | -10.8902 | 934.284 | 15.3899 | -50.8484 | 30.2488 | 30.2488 | 63.2674 | 243.2674 | 50.8777 | 377.5676 | 377.5676 | 101.5216 | 479.0893 | 0.59064 | 59.06% | 216.6442 | 127.9593 | 89.5715 | 290.5036 | 290.5036 | 30.83% | 11.25% | 11.25% | 85% | 9.562% | 20.7159 | 3.917 | 3.917 | 81.1438 | 45.8114 | 27.93% | 27.93%
9 | 252 | 9 | 6041 | 17 | 25.2 | 279.17 | 89.94 | 369.11 | 89.94 | 44.97 | 252 | 6041 | 1020 | 248.5479 | 5.7955 | -10.8902 | 994.284 | 16.3899 | -65.8484 | 20.6311 | 20.6311 | 75.9327 | 255.9327 | 65.7953 | 324.8448 | 324.8448 | 76.7686 | 401.6134 | 0.54631 | 54.63% | 181.6096 | 99.2144 | 69.4501 | 278.3826 | 278.3826 | 24.95% | 11.24% | 11.24% | 85% | 9.552% | 17.348 | 4.0122 | 4.0122 | 69.6036 | 38.3635 | 25% | 25%
9 | 252 | 9 | 6042 | 18 | 24.6 | 142.92 | 75.28 | 218.2 | 75.28 | 37.64 | 252 | 6042 | 1080 | 248.5479 | 5.7955 | -10.8902 | 1054.284 | 17.3899 | -80.8484 | 10.4832 | 10.4832 | 87.3098 | 267.3098 | 80.7182 | 126.6946 | 126.6946 | 64.2555 | 190.9501 | 0.2553 | 25.53% | 86.3476 | 22.0444 | 15.4311 | 261.4297 | 261.4297 | 5.903% | 11.2% | 0% | 80% | 0% | 0 | 4.1099 | 4.1099 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6043 | 19 | 21.8 | 15.69 | 29.22 | 44.91 | 29.22 | 14.61 | 252 | 6043 | 1140 | 248.5479 | 5.7955 | -10.8902 | 1114.284 | 18.3899 | -95.8484 | 0.23826 | 0.23826 | 98.2231 | 278.2231 | 95.6352 | 0 | 0 | 24.9408 | 24.9408 | -3.6392 | 0% | 11.2782 | 0 | 0 | 159.4303 | 159.4303 | 0% | 11.28% | 0% | 80% | 0% | 0 | 4.5994 | 4.5994 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6044 | 20 | 18.4 | 0 | 1.19 | 1.19 | 1.19 | 0.6 | 252 | 6044 | 1200 | 248.5479 | 5.7955 | -10.8902 | 1174.284 | 19.3899 | -110.8484 | -9.7238 | 0 | 98.4793 | 278.4793 | 95.9848 | 0 | 0 | 1.0157 | 1.0157 | -115.6604 | 0% | 0.45931 | 0 | 0 | 143.4216 | 143.4216 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6045 | 21 | 17.1 | 0 | 0 | 0 | 0 | 0 | 252 | 6045 | 1260 | 248.5479 | 5.7955 | -10.8902 | 1234.284 | 20.3899 | -125.8484 | -18.9917 | 0 | 98.4793 | 278.4793 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.5457 | 0 | 0% | 11.48% | 0% | 80% | 0% | 0 | 5.5443 | 5.5443 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6046 | 22 | 15.7 | 0 | 0 | 0 | 0 | 0 | 252 | 6046 | 1320 | 248.5479 | 5.7955 | -10.8902 | 1294.284 | 21.3899 | -140.8484 | -27.0502 | 0 | 98.4793 | 278.4793 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4433 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6047 | 23 | 14.6 | 0 | 0 | 0 | 0 | 0 | 252 | 6047 | 1380 | 248.5479 | 5.7955 | -10.8902 | 1354.284 | 22.3899 | -155.8484 | -33.237 | 0 | 98.4793 | 278.4793 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6527 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
9 | 252 | 9 | 6048 | 24 | 13.9 | 0 | 0 | 0 | 0 | 0 | 252 | 6048 | 1440 | 248.5479 | 5.7955 | -10.8902 | 1414.284 | 23.3899 | -170.8484 | -36.8033 | 0 | 98.4793 | 278.4793 | 95.9848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2526 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6049 | 1 | 13.5 | 0 | 0 | 0 | 0 | 0 | 253 | 6049 | 60 | 249.5342 | 5.4185 | -10.6419 | 34.284 | 0.39403 | 174.0895 | -37.5411 | 0 | 97.9257 | 82.0743 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8475 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6050 | 2 | 13.2 | 0 | 0 | 0 | 0 | 0 | 253 | 6050 | 120 | 249.5342 | 5.4185 | -10.6419 | 94.284 | 1.394 | 159.0895 | -34.6146 | 0 | 97.9257 | 82.0743 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5266 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6051 | 3 | 12.6 | 0 | 0 | 0 | 0 | 0 | 253 | 6051 | 180 | 249.5342 | 5.4185 | -10.6419 | 154.284 | 2.394 | 144.0895 | -28.906 | 0 | 97.9257 | 82.0743 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6629 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6052 | 4 | 11.7 | 0 | 0 | 0 | 0 | 0 | 253 | 6052 | 240 | 249.5342 | 5.4185 | -10.6419 | 214.284 | 3.394 | 129.0895 | -21.1656 | 0 | 97.9257 | 82.0743 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0344 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6053 | 5 | 11.1 | 0 | 0 | 0 | 0 | 0 | 253 | 6053 | 300 | 249.5342 | 5.4185 | -10.6419 | 274.284 | 4.394 | 114.0895 | -12.0907 | 0 | 97.9257 | 82.0743 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.442 | 6.442 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6054 | 6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 253 | 6054 | 360 | 249.5342 | 5.4185 | -10.6419 | 334.284 | 5.394 | 99.0895 | -2.2289 | 0 | 97.9257 | 82.0743 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 19.4132 | 19.4132 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6055 | 7 | 10.8 | 2.78 | 6.47 | 9.25 | 6.47 | 3.24 | 253 | 6055 | 420 | 249.5342 | 5.4185 | -10.6419 | 394.284 | 6.394 | 84.0895 | 7.9909 | 7.9909 | 89.4194 | 90.5806 | 83.9501 | 0 | 0 | 5.5225 | 5.5225 | -23.7454 | 0% | 2.4973 | 0 | 0 | 191.7705 | 191.7705 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6056 | 8 | 12.3 | 68.56 | 39.86 | 108.42 | 39.86 | 19.93 | 253 | 6056 | 480 | 249.5342 | 5.4185 | -10.6419 | 454.284 | 7.394 | 69.0895 | 18.1883 | 18.1883 | 78.2017 | 101.7983 | 69.0181 | 78.6489 | 78.6489 | 34.0226 | 112.6715 | -0.36846 | 0% | 50.9501 | 0 | 0 | 211.2549 | 211.2549 | 0% | 11.64% | 11.64% | 80% | 9.314% | 4.7457 | 6.669 | 6 | 28.4744 | 10.4948 | 13.48% | 13.48%
9 | 253 | 10 | 6057 | 9 | 15.8 | 214.22 | 61.33 | 275.55 | 61.33 | 30.67 | 253 | 6057 | 540 | 249.5342 | 5.4185 | -10.6419 | 514.284 | 8.394 | 54.0895 | 27.9488 | 27.9488 | 65.8916 | 114.1084 | 54.0875 | 268.0932 | 268.0932 | 52.3484 | 320.4416 | 0.41666 | 41.67% | 144.9037 | 60.3756 | 42.2629 | 183.7291 | 183.7291 | 23% | 11.46% | 11.46% | 85% | 9.743% | 14.1185 | 5.833 | 5.833 | 82.3529 | 31.2218 | 44.82% | 44.82%
9 | 253 | 10 | 6058 | 10 | 18.9 | 324.31 | 96.81 | 421.12 | 96.81 | 48.41 | 253 | 6058 | 600 | 249.5342 | 5.4185 | -10.6419 | 574.284 | 9.394 | 39.0895 | 36.7249 | 36.7249 | 51.5509 | 128.4491 | 39.1721 | 420.4567 | 420.4567 | 82.6325 | 503.0892 | 0.57107 | 57.11% | 227.497 | 129.9157 | 90.941 | 190.0944 | 190.0944 | 47.84% | 11.37% | 11.37% | 90% | 10.23% | 23.2797 | 5.1642 | 5.1642 | 120.2199 | 51.481 | 63.24% | 63.24%
9 | 253 | 10 | 6059 | 11 | 21.3 | 402.72 | 128.47 | 531.19 | 128.47 | 64.24 | 253 | 6059 | 660 | 249.5342 | 5.4185 | -10.6419 | 634.284 | 10.394 | 24.0895 | 43.7254 | 43.7254 | 34.2138 | 145.7862 | 24.3113 | 530.9695 | 530.9695 | 109.656 | 640.6255 | 0.62932 | 62.93% | 289.6909 | 182.3069 | 127.6148 | 186.5071 | 186.5071 | 68.42% | 11.34% | 11.34% | 90% | 10.21% | 29.5674 | 4.6926 | 4.6926 | 138.7468 | 65.3857 | 74.39% | 74.39%
9 | 253 | 10 | 6060 | 12 | 23.5 | 433 | 166.94 | 599.94 | 166.94 | 83.47 | 253 | 6060 | 720 | 249.5342 | 5.4185 | -10.6419 | 694.284 | 11.394 | 9.0895 | 47.9036 | 47.9036 | 13.568 | 166.432 | 9.7733 | 575.0753 | 575.0753 | 142.4922 | 717.5675 | 0.6547 | 65.47% | 324.484 | 212.4382 | 148.7068 | 276.9694 | 276.9694 | 53.69% | 11.34% | 11.34% | 90% | 10.2% | 33.1055 | 4.2957 | 4.2957 | 142.2107 | 73.21 | 51.35% | 51.35%
9 | 253 | 10 | 6061 | 13 | 23.8 | 368.56 | 186.81 | 555.37 | 186.81 | 93.41 | 253 | 6061 | 780 | 249.5342 | 5.4185 | -10.6419 | 754.284 | 12.394 | -5.9105 | 48.3272 | 48.3272 | 8.8696 | 188.8696 | 6.9309 | 489.8114 | 489.8114 | 159.4523 | 649.2637 | 0.63998 | 64% | 293.5971 | 187.8971 | 131.5279 | 280.8502 | 280.8502 | 46.83% | 11.32% | 11.32% | 90% | 10.19% | 29.913 | 4.2442 | 4.2442 | 126.9561 | 66.1499 | 45.2% | 45.2%
9 | 253 | 10 | 6062 | 14 | 24.7 | 341.94 | 167.08 | 509.02 | 167.08 | 83.54 | 253 | 6062 | 840 | 249.5342 | 5.4185 | -10.6419 | 814.284 | 13.394 | -20.9105 | 44.8842 | 44.8842 | 30.0979 | 210.0979 | 21.1805 | 451.823 | 451.823 | 142.6117 | 594.4347 | 0.6281 | 62.81% | 268.8034 | 168.8355 | 118.1849 | 289.556 | 289.556 | 40.82% | 11.3% | 11.3% | 90% | 10.17% | 27.3345 | 4.0935 | 4.0935 | 111.8933 | 60.4479 | 38.64% | 38.64%
9 | 253 | 10 | 6063 | 15 | 24.8 | 304.67 | 157.78 | 462.45 | 157.78 | 78.89 | 253 | 6063 | 900 | 249.5342 | 5.4185 | -10.6419 | 874.284 | 14.394 | -35.9105 | 38.389 | 38.389 | 48.1547 | 228.1547 | 36.0156 | 396.836 | 396.836 | 134.6737 | 531.5097 | 0.60768 | 60.77% | 240.3487 | 146.0546 | 102.2382 | 289.1737 | 289.1737 | 35.36% | 11.28% | 11.28% | 90% | 10.15% | 24.4026 | 4.0771 | 4.0771 | 99.4914 | 53.9642 | 34.41% | 34.41%
9 | 253 | 10 | 6064 | 16 | 24.6 | 253.11 | 130.14 | 383.25 | 130.14 | 65.07 | 253 | 6064 | 960 | 249.5342 | 5.4185 | -10.6419 | 934.284 | 15.394 | -50.9105 | 29.9133 | 29.9133 | 63.0563 | 243.0563 | 50.9245 | 319.9317 | 319.9317 | 111.0814 | 431.0132 | 0.56091 | 56.09% | 194.9042 | 109.3238 | 76.5267 | 289.3761 | 289.3761 | 26.45% | 11.26% | 11.26% | 85% | 9.57% | 18.652 | 4.1099 | 4.1099 | 76.6587 | 41.2473 | 26.49% | 26.49%
9 | 253 | 10 | 6065 | 17 | 24 | 231.17 | 101.25 | 332.42 | 101.25 | 50.63 | 253 | 6065 | 1020 | 249.5342 | 5.4185 | -10.6419 | 994.284 | 16.394 | -65.9105 | 20.309 | 20.309 | 75.7133 | 255.7133 | 65.8534 | 272.4573 | 272.4573 | 86.4223 | 358.8796 | 0.50847 | 50.85% | 162.2854 | 82.5168 | 57.7617 | 273.8898 | 273.8898 | 21.09% | 11.25% | 11.25% | 85% | 9.567% | 15.5254 | 4.2102 | 4.2102 | 65.3649 | 34.333 | 23.87% | 23.87%
9 | 253 | 10 | 6066 | 18 | 22.1 | 121.61 | 65.83 | 187.44 | 65.83 | 32.92 | 253 | 6066 | 1080 | 249.5342 | 5.4185 | -10.6419 | 1054.284 | 17.394 | -80.9105 | 10.1668 | 10.1668 | 87.092 | 267.092 | 80.7858 | 110.3182 | 110.3182 | 56.1894 | 166.5076 | 0.14238 | 14.24% | 75.2947 | 10.7204 | 7.5043 | 133.7267 | 133.7267 | 5.612% | 11.28% | 0% | 80% | 0% | 0 | 4.5443 | 4.5443 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6067 | 19 | 20.4 | 15.69 | 30.5 | 46.19 | 30.5 | 15.25 | 253 | 6067 | 1140 | 249.5342 | 5.4185 | -10.6419 | 1114.284 | 18.394 | -95.9105 | -0.079831 | 0 | 97.9257 | 277.9257 | 95.5953 | 0 | 0 | 26.0334 | 26.0334 | -3.5703 | 0% | 11.7723 | 0 | 0 | 159.1809 | 159.1809 | 0% | 11.33% | 0% | 80% | 0% | 0 | 4.8647 | 4.8647 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6068 | 20 | 19.6 | 0 | 0 | 0 | 0 | 0 | 253 | 6068 | 1200 | 249.5342 | 5.4185 | -10.6419 | 1174.284 | 19.394 | -110.9105 | -10.0506 | 0 | 97.9257 | 277.9257 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.1198 | 146.1198 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0224 | 5.0224 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6069 | 21 | 17.4 | 0 | 0 | 0 | 0 | 0 | 253 | 6069 | 1260 | 249.5342 | 5.4185 | -10.6419 | 1234.284 | 20.394 | -125.9105 | -19.3331 | 0 | 97.9257 | 277.9257 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.3122 | 0 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.4794 | 5.4794 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6070 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 253 | 6070 | 1320 | 249.5342 | 5.4185 | -10.6419 | 1294.284 | 21.394 | -140.9105 | -27.4097 | 0 | 97.9257 | 277.9257 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8959 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6071 | 23 | 14.5 | 0 | 0 | 0 | 0 | 0 | 253 | 6071 | 1380 | 249.5342 | 5.4185 | -10.6419 | 1354.284 | 22.394 | -155.9105 | -33.6129 | 0 | 97.9257 | 277.9257 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8798 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
9 | 253 | 10 | 6072 | 24 | 13.6 | 0 | 0 | 0 | 0 | 0 | 253 | 6072 | 1440 | 249.5342 | 5.4185 | -10.6419 | 1414.284 | 23.394 | -170.9105 | -37.1853 | 0 | 97.9257 | 277.9257 | 95.5953 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4733 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6073 | 1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 254 | 6073 | 60 | 250.5205 | 5.0394 | -10.3866 | 34.284 | 0.39829 | 174.0257 | -37.913 | 0 | 97.3695 | 82.6305 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2751 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6074 | 2 | 11.6 | 0 | 0 | 0 | 0 | 0 | 254 | 6074 | 120 | 250.5205 | 5.0394 | -10.3866 | 94.284 | 1.3983 | 159.0257 | -34.9575 | 0 | 97.3695 | 82.6305 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.51 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6075 | 3 | 11.4 | 0 | 0 | 0 | 0 | 0 | 254 | 6075 | 180 | 250.5205 | 5.0394 | -10.3866 | 154.284 | 2.3983 | 144.0257 | -29.2134 | 0 | 97.3695 | 82.6305 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2877 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6076 | 4 | 11 | 0 | 0 | 0 | 0 | 0 | 254 | 6076 | 240 | 250.5205 | 5.0394 | -10.3866 | 214.284 | 3.3983 | 129.0257 | -21.4406 | 0 | 97.3695 | 82.6305 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8973 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6077 | 5 | 10.6 | 0 | 0 | 0 | 0 | 0 | 254 | 6077 | 300 | 250.5205 | 5.0394 | -10.3866 | 274.284 | 4.3983 | 114.0257 | -12.3414 | 0 | 97.3695 | 82.6305 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.49394 | 0.49394 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6078 | 6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 254 | 6078 | 360 | 250.5205 | 5.0394 | -10.3866 | 334.284 | 5.3983 | 99.0257 | -2.4649 | 0 | 97.3695 | 82.6305 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.0489 | 10.0489 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6079 | 7 | 10.1 | 2 | 7.36 | 9.36 | 7.36 | 3.68 | 254 | 6079 | 420 | 250.5205 | 5.0394 | -10.3866 | 394.284 | 6.3983 | 84.0257 | 7.7594 | 7.7594 | 89.1096 | 90.8904 | 83.8947 | 0 | 0 | 6.2822 | 6.2822 | -21.0363 | 0% | 2.8408 | 0 | 0 | 174.4578 | 174.4578 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6080 | 8 | 11.7 | 50.97 | 52.56 | 103.53 | 52.56 | 26.28 | 254 | 6080 | 480 | 250.5205 | 5.0394 | -10.3866 | 454.284 | 7.3983 | 69.0257 | 17.9506 | 17.9506 | 77.8839 | 102.1161 | 68.9538 | 59.3918 | 59.3918 | 44.8628 | 104.2546 | -0.4764 | 0% | 47.1439 | 0 | 0 | 190.7287 | 190.7287 | 0% | 11.67% | 11.67% | 80% | 9.336% | 4.4012 | 6.8209 | 6 | 26.4072 | 9.7329 | 13.85% | 13.85%
9 | 254 | 11 | 6081 | 9 | 13.6 | 141.11 | 98.56 | 239.67 | 98.56 | 49.28 | 254 | 6081 | 540 | 250.5205 | 5.0394 | -10.3866 | 514.284 | 8.3983 | 54.0257 | 27.6933 | 27.6933 | 65.5669 | 114.4331 | 54.0134 | 178.4136 | 178.4136 | 84.1262 | 262.5398 | 0.3122 | 31.22% | 118.7205 | 37.064 | 25.9448 | 158.9392 | 158.9392 | 16.32% | 11.54% | 11.54% | 80% | 9.233% | 10.9614 | 6.3484 | 6 | 65.7684 | 24.2402 | 41.38% | 41.38%
9 | 254 | 11 | 6082 | 10 | 17.4 | 221.94 | 135.5 | 357.44 | 135.5 | 67.75 | 254 | 6082 | 600 | 250.5205 | 5.0394 | -10.3866 | 574.284 | 9.3983 | 39.0257 | 36.4393 | 36.4393 | 51.2304 | 128.7696 | 39.0848 | 290.0357 | 290.0357 | 115.6565 | 405.6922 | 0.50691 | 50.69% | 183.454 | 92.9955 | 65.0968 | 167.0912 | 167.0912 | 38.96% | 11.41% | 11.41% | 85% | 9.697% | 17.7898 | 5.4794 | 5.4794 | 97.4769 | 39.3405 | 58.34% | 58.34%
9 | 254 | 11 | 6083 | 11 | 19.2 | 236.94 | 183.75 | 420.69 | 183.75 | 91.88 | 254 | 6083 | 660 | 250.5205 | 5.0394 | -10.3866 | 634.284 | 10.3983 | 24.0257 | 43.4001 | 43.4001 | 33.9312 | 146.0688 | 24.2 | 314.5414 | 314.5414 | 156.8404 | 471.3818 | 0.55681 | 55.68% | 213.1589 | 118.6882 | 83.0817 | 164.3292 | 164.3292 | 50.56% | 11.37% | 11.37% | 85% | 9.661% | 20.5943 | 5.103 | 5.103 | 105.0928 | 45.5425 | 63.95% | 63.95%
9 | 254 | 11 | 6084 | 12 | 20.7 | 241.94 | 156.11 | 398.05 | 156.11 | 78.06 | 254 | 6084 | 720 | 250.5205 | 5.0394 | -10.3866 | 694.284 | 11.3983 | 9.0257 | 47.5396 | 47.5396 | 13.3844 | 166.6156 | 9.5806 | 323.3718 | 323.3718 | 133.2482 | 456.6201 | 0.55605 | 55.6% | 206.4836 | 114.8147 | 80.3703 | 153.565 | 153.565 | 52.34% | 11.34% | 11.34% | 85% | 9.638% | 19.9008 | 4.8067 | 4.8067 | 95.6567 | 44.0089 | 62.29% | 62.29%
9 | 254 | 11 | 6085 | 13 | 20.9 | 282.44 | 156.89 | 439.33 | 156.89 | 78.45 | 254 | 6085 | 780 | 250.5205 | 5.0394 | -10.3866 | 754.284 | 12.3983 | -5.9743 | 47.9435 | 47.9435 | 8.904 | 188.904 | 6.7966 | 377.725 | 377.725 | 133.914 | 511.639 | 0.58357 | 58.36% | 231.3632 | 135.016 | 94.5112 | 153.1822 | 153.1822 | 61.7% | 11.34% | 11.34% | 90% | 10.2% | 23.6082 | 4.7684 | 4.7684 | 112.5722 | 52.2074 | 73.49% | 73.49%
9 | 254 | 11 | 6086 | 14 | 21.7 | 333.67 | 170.61 | 504.28 | 170.61 | 85.31 | 254 | 6086 | 840 | 250.5205 | 5.0394 | -10.3866 | 814.284 | 13.3983 | -20.9743 | 44.5064 | 44.5064 | 29.9982 | 209.9982 | 21.1865 | 443.8254 | 443.8254 | 145.6247 | 589.4501 | 0.61563 | 61.56% | 266.5493 | 164.0956 | 114.8669 | 156.0822 | 156.0822 | 73.59% | 11.33% | 11.33% | 90% | 10.2% | 27.1856 | 4.6179 | 4.6179 | 125.5396 | 60.1185 | 80.43% | 80.43%
9 | 254 | 11 | 6087 | 15 | 22.2 | 314.03 | 167.83 | 481.86 | 167.83 | 83.92 | 254 | 6087 | 900 | 250.5205 | 5.0394 | -10.3866 | 874.284 | 14.3983 | -35.9743 | 38.0308 | 38.0308 | 47.9774 | 227.9774 | 36.0514 | 412.102 | 412.102 | 143.2519 | 555.3539 | 0.60602 | 60.6% | 251.131 | 152.191 | 106.5337 | 153.6949 | 153.6949 | 69.32% | 11.32% | 11.32% | 90% | 10.19% | 25.5906 | 4.5261 | 4.5261 | 115.8258 | 56.5914 | 75.36% | 75.36%
9 | 254 | 11 | 6088 | 16 | 22.2 | 284.17 | 111.17 | 395.34 | 111.17 | 55.59 | 254 | 6088 | 960 | 250.5205 | 5.0394 | -10.3866 | 934.284 | 15.3983 | -50.9743 | 29.5747 | 29.5747 | 62.8467 | 242.8467 | 50.9751 | 362.531 | 362.531 | 94.8895 | 457.4205 | 0.56364 | 56.36% | 206.8456 | 116.5855 | 81.6098 | 148.3295 | 148.3295 | 55.02% | 11.31% | 11.31% | 85% | 9.614% | 19.8861 | 4.5261 | 4.5261 | 90.0063 | 43.9763 | 60.68% | 60.68%
9 | 254 | 11 | 6089 | 17 | 14.2 | 203.06 | 91.44 | 294.5 | 91.44 | 45.72 | 254 | 6089 | 1020 | 250.5205 | 5.0394 | -10.3866 | 994.284 | 16.3983 | -65.9743 | 19.984 | 19.984 | 75.4948 | 255.4948 | 65.9143 | 242.4799 | 242.4799 | 78.0489 | 320.5288 | 0.40544 | 40.54% | 144.9431 | 58.7663 | 41.1364 | 129.0629 | 129.0629 | 31.87% | 11.5% | 11.5% | 85% | 9.779% | 14.1743 | 6.2045 | 6 | 85.0458 | 31.3452 | 65.89% | 65.89%
9 | 254 | 11 | 6090 | 18 | 13.7 | 79.44 | 64.94 | 144.38 | 64.94 | 32.47 | 254 | 6090 | 1080 | 250.5205 | 5.0394 | -10.3866 | 1054.284 | 17.3983 | -80.9743 | 9.8476 | 9.8476 | 86.8745 | 266.8745 | 80.8558 | 0 | 0 | 55.4298 | 55.4298 | -1.5213 | 0% | 25.0653 | 0 | 0 | 158.2244 | 158.2244 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6091 | 19 | 13.4 | 8.56 | 22.83 | 31.39 | 22.83 | 11.42 | 254 | 6091 | 1140 | 250.5205 | 5.0394 | -10.3866 | 1114.284 | 18.3983 | -95.9743 | -0.40067 | 0 | 97.3695 | 277.3695 | 95.2038 | 0 | 0 | 19.4866 | 19.4866 | -5.8455 | 0% | 8.8119 | 0 | 0 | 146.4379 | 146.4379 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6092 | 20 | 13.2 | 0 | 0 | 0 | 0 | 0 | 254 | 6092 | 1200 | 250.5205 | 5.0394 | -10.3866 | 1174.284 | 19.3983 | -110.9743 | -10.38 | 0 | 97.3695 | 277.3695 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.0802 | 137.0802 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6093 | 21 | 13.2 | 0 | 0 | 0 | 0 | 0 | 254 | 6093 | 1260 | 250.5205 | 5.0394 | -10.3866 | 1234.284 | 20.3983 | -125.9743 | -19.677 | 0 | 97.3695 | 277.3695 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.62 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6094 | 22 | 13.2 | 0 | 0 | 0 | 0 | 0 | 254 | 6094 | 1320 | 250.5205 | 5.0394 | -10.3866 | 1294.284 | 21.3983 | -140.9743 | -27.7718 | 0 | 97.3695 | 277.3695 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1801 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6095 | 23 | 13.3 | 0 | 0 | 0 | 0 | 0 | 254 | 6095 | 1380 | 250.5205 | 5.0394 | -10.3866 | 1354.284 | 22.3983 | -155.9743 | -33.9913 | 0 | 97.3695 | 277.3695 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5006 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
9 | 254 | 11 | 6096 | 24 | 12 | 0 | 0 | 0 | 0 | 0 | 254 | 6096 | 1440 | 250.5205 | 5.0394 | -10.3866 | 1414.284 | 23.3983 | -170.9743 | -37.5695 | 0 | 97.3695 | 277.3695 | 95.2038 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9546 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6097 | 1 | 12.2 | 0 | 0 | 0 | 0 | 0 | 255 | 6097 | 60 | 251.5068 | 4.6584 | -10.1246 | 34.284 | 0.40266 | 173.9602 | -38.2865 | 0 | 96.8108 | 83.1892 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1382 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6098 | 2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 255 | 6098 | 120 | 251.5068 | 4.6584 | -10.1246 | 94.284 | 1.4027 | 158.9602 | -35.3014 | 0 | 96.8108 | 83.1892 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2776 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6099 | 3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 255 | 6099 | 180 | 251.5068 | 4.6584 | -10.1246 | 154.284 | 2.4027 | 143.9602 | -29.5212 | 0 | 96.8108 | 83.1892 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3314 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6100 | 4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 255 | 6100 | 240 | 251.5068 | 4.6584 | -10.1246 | 214.284 | 3.4027 | 128.9602 | -21.7157 | 0 | 96.8108 | 83.1892 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5506 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6101 | 5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 255 | 6101 | 300 | 251.5068 | 4.6584 | -10.1246 | 274.284 | 4.4027 | 113.9602 | -12.5921 | 0 | 96.8108 | 83.1892 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.63594 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6102 | 6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 255 | 6102 | 360 | 251.5068 | 4.6584 | -10.1246 | 334.284 | 5.4027 | 98.9602 | -2.7011 | 0 | 96.8108 | 83.1892 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.1092 | 6.1092 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6103 | 7 | 9.8 | 0.97 | 4.5 | 5.47 | 4.5 | 2.25 | 255 | 6103 | 420 | 251.5068 | 4.6584 | -10.1246 | 394.284 | 6.4027 | 83.9602 | 7.5274 | 7.5274 | 88.7976 | 91.2024 | 83.8379 | 0 | 0 | 3.841 | 3.841 | -35.0994 | 0% | 1.7369 | 0 | 0 | 165.5983 | 165.5983 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6104 | 8 | 10.5 | 28.61 | 40.97 | 69.58 | 40.97 | 20.49 | 255 | 6104 | 480 | 251.5068 | 4.6584 | -10.1246 | 454.284 | 7.4027 | 68.9602 | 17.7121 | 17.7121 | 77.5643 | 102.4357 | 68.8888 | 33.871 | 33.871 | 34.9701 | 68.8411 | -1.1755 | 0% | 31.1299 | 0 | 0 | 177.1504 | 177.1504 | 0% | 11.73% | 11.73% | 80% | 9.387% | 2.9222 | 7.1323 | 6 | 17.5334 | 6.4623 | 9.897% | 9.897%
9 | 255 | 12 | 6105 | 9 | 10.5 | 90.97 | 84.5 | 175.47 | 84.5 | 42.25 | 255 | 6105 | 540 | 251.5068 | 4.6584 | -10.1246 | 514.284 | 8.4027 | 53.9602 | 27.4366 | 27.4366 | 65.2408 | 114.7592 | 53.9393 | 116.2166 | 116.2166 | 72.1253 | 188.3418 | 0.080466 | 8.047% | 85.1682 | 6.8532 | 4.7972 | 162.2189 | 162.2189 | 2.957% | 11.67% | 11.67% | 80% | 9.337% | 7.9524 | 7.1323 | 6 | 47.7143 | 17.586 | 29.41% | 29.41%
9 | 255 | 12 | 6106 | 10 | 12.1 | 168.33 | 120 | 288.33 | 120 | 60 | 255 | 6106 | 600 | 251.5068 | 4.6584 | -10.1246 | 574.284 | 9.4027 | 38.9602 | 36.1522 | 36.1522 | 50.9092 | 129.0908 | 38.9986 | 221.7535 | 221.7535 | 102.4264 | 324.1799 | 0.39508 | 39.51% | 146.5942 | 57.9165 | 40.5415 | 147.3347 | 147.3347 | 27.52% | 11.56% | 11.56% | 85% | 9.825% | 14.4028 | 6.7193 | 6 | 86.4167 | 31.8505 | 58.65% | 58.65%
9 | 255 | 12 | 6107 | 11 | 13.7 | 259.67 | 154.78 | 414.45 | 154.78 | 77.39 | 255 | 6107 | 660 | 251.5068 | 4.6584 | -10.1246 | 634.284 | 10.4027 | 23.9602 | 43.0729 | 43.0729 | 33.6485 | 146.3515 | 24.0921 | 347.1087 | 347.1087 | 132.113 | 479.2217 | 0.53504 | 53.5% | 216.704 | 115.9461 | 81.1623 | 149.3445 | 149.3445 | 54.35% | 11.46% | 11.46% | 85% | 9.744% | 21.1149 | 6.3243 | 6 | 126.6897 | 46.6938 | 84.83% | 84.83%
9 | 255 | 12 | 6108 | 12 | 14 | 253.39 | 193.83 | 447.22 | 193.83 | 96.92 | 255 | 6108 | 720 | 251.5068 | 4.6584 | -10.1246 | 694.284 | 11.4027 | 8.9602 | 47.1736 | 47.1736 | 13.2004 | 166.7996 | 9.3974 | 340.8559 | 340.8559 | 165.4443 | 506.3002 | 0.55078 | 55.08% | 228.9489 | 126.1008 | 88.2705 | 142.0756 | 142.0756 | 62.13% | 11.45% | 11.45% | 90% | 10.3% | 23.591 | 6.2522 | 6 | 141.5458 | 52.1693 | 99.63% | 99.63%
9 | 255 | 12 | 6109 | 13 | 14.2 | 345.83 | 175.28 | 521.11 | 175.28 | 87.64 | 255 | 6109 | 780 | 251.5068 | 4.6584 | -10.1246 | 754.284 | 12.4027 | -6.0398 | 47.5577 | 47.5577 | 8.9401 | 188.9401 | 6.6823 | 465.4479 | 465.4479 | 149.6108 | 615.0587 | 0.5963 | 59.63% | 278.1296 | 165.8482 | 116.0937 | 143.3057 | 143.3057 | 81.01% | 11.41% | 11.41% | 90% | 10.27% | 28.5636 | 6.2045 | 6 | 171.3817 | 63.1659 | 119.6% | 119.6%
9 | 255 | 12 | 6110 | 14 | 15.5 | 241.11 | 165.22 | 406.33 | 165.22 | 82.61 | 255 | 6110 | 840 | 251.5068 | 4.6584 | -10.1246 | 814.284 | 13.4027 | -21.0398 | 44.1261 | 44.1261 | 29.9011 | 209.9011 | 21.2006 | 322.865 | 322.865 | 141.0241 | 463.8891 | 0.53498 | 53.5% | 209.7707 | 112.2221 | 78.5555 | 139.7265 | 139.7265 | 56.22% | 11.44% | 11.44% | 85% | 9.72% | 20.3895 | 5.9013 | 5.9013 | 120.3242 | 45.0896 | 86.11% | 86.11%
9 | 255 | 12 | 6111 | 15 | 15 | 271.67 | 148.56 | 420.23 | 148.56 | 74.28 | 255 | 6111 | 900 | 251.5068 | 4.6584 | -10.1246 | 874.284 | 14.4027 | -36.0398 | 37.6697 | 37.6697 | 47.8025 | 227.8025 | 36.0923 | 359.2291 | 359.2291 | 126.8039 | 486.033 | 0.5449 | 54.49% | 219.7841 | 119.7609 | 83.8326 | 137.2947 | 137.2947 | 61.06% | 11.44% | 11.44% | 85% | 9.723% | 21.3687 | 6.0165 | 6 | 128.2122 | 47.255 | 93.38% | 93.38%
9 | 255 | 12 | 6112 | 16 | 15.1 | 224.58 | 115.33 | 339.91 | 115.33 | 57.67 | 255 | 6112 | 960 | 251.5068 | 4.6584 | -10.1246 | 934.284 | 15.4027 | -51.0398 | 29.2331 | 29.2331 | 62.6388 | 242.6388 | 51.0295 | 289.2165 | 289.2165 | 98.4403 | 387.6568 | 0.47974 | 47.97% | 175.2984 | 84.0969 | 58.8678 | 132.5691 | 132.5691 | 44.41% | 11.46% | 11.46% | 85% | 9.744% | 17.0805 | 5.9933 | 5.9933 | 102.3687 | 37.772 | 77.22% | 77.22%
9 | 255 | 12 | 6113 | 17 | 14.7 | 154.31 | 98.06 | 252.37 | 98.06 | 49.03 | 255 | 6113 | 1020 | 251.5068 | 4.6584 | -10.1246 | 994.284 | 16.4027 | -66.0398 | 19.656 | 19.656 | 75.2773 | 255.2773 | 65.9782 | 186.7494 | 186.7494 | 83.6994 | 270.4489 | 0.33585 | 33.58% | 122.297 | 41.0733 | 28.7513 | 125.6523 | 125.6523 | 22.88% | 11.51% | 11.51% | 80% | 9.205% | 11.2575 | 6.0865 | 6 | 67.5453 | 24.8951 | 53.76% | 53.76%
9 | 255 | 12 | 6114 | 18 | 14.4 | 64.11 | 62.83 | 126.94 | 62.83 | 31.42 | 255 | 6114 | 1080 | 251.5068 | 4.6584 | -10.1246 | 1054.284 | 17.4027 | -81.0398 | 9.5257 | 9.5257 | 86.6575 | 266.6575 | 80.9278 | 0 | 0 | 53.6288 | 53.6288 | -1.5696 | 0% | 24.2509 | 0 | 0 | 157.2014 | 157.2014 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6115 | 19 | 13.4 | 7 | 24.67 | 31.67 | 24.67 | 12.34 | 255 | 6115 | 1140 | 251.5068 | 4.6584 | -10.1246 | 1114.284 | 18.4027 | -96.0398 | -0.72413 | 0 | 96.8108 | 276.8108 | 94.8103 | 0 | 0 | 21.0572 | 21.0572 | -5.3495 | 0% | 9.522 | 0 | 0 | 146.1054 | 146.1054 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6116 | 20 | 12.5 | 0 | 0 | 0 | 0 | 0 | 255 | 6116 | 1200 | 251.5068 | 4.6584 | -10.1246 | 1174.284 | 19.4027 | -111.0398 | -10.7119 | 0 | 96.8108 | 276.8108 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.8749 | 136.8749 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6117 | 21 | 10.7 | 0 | 0 | 0 | 0 | 0 | 255 | 6117 | 1260 | 251.5068 | 4.6584 | -10.1246 | 1234.284 | 20.4027 | -126.0398 | -20.0234 | 0 | 96.8108 | 276.8108 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3112 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6118 | 22 | 10.2 | 0 | 0 | 0 | 0 | 0 | 255 | 6118 | 1320 | 251.5068 | 4.6584 | -10.1246 | 1294.284 | 21.4027 | -141.0398 | -28.1362 | 0 | 96.8108 | 276.8108 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3965 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6119 | 23 | 9 | 0 | 0 | 0 | 0 | 0 | 255 | 6119 | 1380 | 251.5068 | 4.6584 | -10.1246 | 1354.284 | 22.4027 | -156.0398 | -34.3721 | 0 | 96.8108 | 276.8108 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8219 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
9 | 255 | 12 | 6120 | 24 | 7.8 | 0 | 0 | 0 | 0 | 0 | 255 | 6120 | 1440 | 251.5068 | 4.6584 | -10.1246 | 1414.284 | 23.4027 | -171.0398 | -37.9558 | 0 | 96.8108 | 276.8108 | 94.8103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2472 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6121 | 1 | 6.6 | 0 | 0 | 0 | 0 | 0 | 256 | 6121 | 60 | 252.4932 | 4.2754 | -9.8563 | 34.284 | 0.40713 | 173.8931 | -38.6616 | 0 | 96.2497 | 83.7503 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3262 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6122 | 2 | 5.7 | 0 | 0 | 0 | 0 | 0 | 256 | 6122 | 120 | 252.4932 | 4.2754 | -9.8563 | 94.284 | 1.4071 | 158.8931 | -35.6462 | 0 | 96.2497 | 83.7503 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.1295 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6123 | 3 | 4.9 | 0 | 0 | 0 | 0 | 0 | 256 | 6123 | 180 | 252.4932 | 4.2754 | -9.8563 | 154.284 | 2.4071 | 143.8931 | -29.8294 | 0 | 96.2497 | 83.7503 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7803 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6124 | 4 | 4.4 | 0 | 0 | 0 | 0 | 0 | 256 | 6124 | 240 | 252.4932 | 4.2754 | -9.8563 | 214.284 | 3.4071 | 128.8931 | -21.9909 | 0 | 96.2497 | 83.7503 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5423 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6125 | 5 | 4.1 | 0 | 0 | 0 | 0 | 0 | 256 | 6125 | 300 | 252.4932 | 4.2754 | -9.8563 | 274.284 | 4.4071 | 113.8931 | -12.8429 | 0 | 96.2497 | 83.7503 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.5251 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6126 | 6 | 4.2 | 0 | 0 | 0 | 0 | 0 | 256 | 6126 | 360 | 252.4932 | 4.2754 | -9.8563 | 334.284 | 5.4071 | 98.8931 | -2.9375 | 0 | 96.2497 | 83.7503 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.9047 | 4.9047 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6127 | 7 | 3.6 | 0.69 | 4.31 | 5 | 4.31 | 2.16 | 256 | 6127 | 420 | 252.4932 | 4.2754 | -9.8563 | 394.284 | 6.4071 | 83.8931 | 7.295 | 7.295 | 88.4834 | 91.5166 | 83.7798 | 0 | 0 | 3.6788 | 3.6788 | -40.692 | 0% | 1.6636 | 0 | 0 | 169.1366 | 169.1366 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6128 | 8 | 4.7 | 28.28 | 43.47 | 71.75 | 43.47 | 21.74 | 256 | 6128 | 480 | 252.4932 | 4.2754 | -9.8563 | 454.284 | 7.4071 | 68.8931 | 17.4728 | 17.4728 | 77.2429 | 102.7571 | 68.8232 | 34.025 | 34.025 | 37.104 | 71.129 | -1.3049 | 0% | 32.1645 | 0 | 0 | 183.2973 | 183.2973 | 0% | 11.97% | 11.97% | 80% | 9.572% | 3.0789 | 8.7795 | 6 | 18.4733 | 6.8087 | 10.08% | 10.08%
9 | 256 | 13 | 6129 | 9 | 8.6 | 75.14 | 88.89 | 164.03 | 88.89 | 44.45 | 256 | 6129 | 540 | 252.4932 | 4.2754 | -9.8563 | 514.284 | 8.4071 | 53.8931 | 27.1787 | 27.1787 | 64.9135 | 115.0865 | 53.8654 | 97.0054 | 97.0054 | 75.8724 | 172.8777 | -0.0099836 | 0% | 78.1753 | 0 | 0 | 173.6994 | 173.6994 | 0% | 11.75% | 11.75% | 80% | 9.396% | 7.3455 | 7.6459 | 6 | 44.0729 | 16.2439 | 25.37% | 25.37%
9 | 256 | 13 | 6130 | 10 | 9.8 | 163.47 | 142.83 | 306.3 | 142.83 | 71.42 | 256 | 6130 | 600 | 252.4932 | 4.2754 | -9.8563 | 574.284 | 9.4071 | 38.8931 | 35.8635 | 35.8635 | 50.5874 | 129.4126 | 38.9137 | 217.1091 | 217.1091 | 121.913 | 339.0221 | 0.39723 | 39.72% | 153.3058 | 60.8973 | 42.6281 | 158.9769 | 158.9769 | 26.81% | 11.61% | 11.61% | 85% | 9.869% | 15.1298 | 7.3186 | 6 | 90.7787 | 33.4582 | 57.1% | 57.1%
9 | 256 | 13 | 6131 | 11 | 11.1 | 390.83 | 154.78 | 545.61 | 154.78 | 77.39 | 256 | 6131 | 660 | 252.4932 | 4.2754 | -9.8563 | 634.284 | 10.4071 | 23.8931 | 42.7439 | 42.7439 | 33.3658 | 146.6342 | 23.9877 | 526.0985 | 526.0985 | 132.113 | 658.2115 | 0.59909 | 59.91% | 297.6433 | 178.3137 | 124.8196 | 163.6299 | 163.6299 | 76.28% | 11.42% | 11.42% | 90% | 10.28% | 30.5955 | 6.9753 | 6 | 183.5732 | 67.6593 | 112.2% | 112.2%
9 | 256 | 13 | 6132 | 12 | 12.4 | 429.78 | 178.33 | 608.11 | 178.33 | 89.17 | 256 | 6132 | 720 | 252.4932 | 4.2754 | -9.8563 | 694.284 | 11.4071 | 8.8931 | 46.8058 | 46.8058 | 13.0161 | 166.9839 | 9.2244 | 581.8934 | 581.8934 | 152.2142 | 734.1075 | 0.62436 | 62.44% | 331.9634 | 207.266 | 145.0862 | 155.7121 | 155.7121 | 93.18% | 11.38% | 11.38% | 90% | 10.24% | 33.9983 | 6.6439 | 6 | 203.99 | 75.1843 | 131% | 131%
9 | 256 | 13 | 6133 | 13 | 12.7 | 433.89 | 214.22 | 648.11 | 214.22 | 107.11 | 256 | 6133 | 780 | 252.4932 | 4.2754 | -9.8563 | 754.284 | 12.4071 | -6.1069 | 47.1698 | 47.1698 | 8.9778 | 188.9778 | 6.5895 | 587.7288 | 587.7288 | 182.8482 | 770.577 | 0.63376 | 63.38% | 348.4549 | 220.8373 | 154.5861 | 154.6696 | 154.6696 | 99.95% | 11.36% | 11.36% | 90% | 10.23% | 35.638 | 6.5691 | 6 | 213.8279 | 78.8102 | 138.2% | 138.2%
9 | 256 | 13 | 6134 | 14 | 11.5 | 434.03 | 198.06 | 632.09 | 198.06 | 99.03 | 256 | 6134 | 840 | 252.4932 | 4.2754 | -9.8563 | 814.284 | 13.4071 | -21.1069 | 43.7434 | 43.7434 | 29.8066 | 209.8066 | 21.2229 | 585.155 | 585.155 | 169.0548 | 754.2097 | 0.6264 | 62.64% | 341.0536 | 213.6349 | 149.5444 | 150.5702 | 150.5702 | 99.32% | 11.37% | 11.37% | 90% | 10.24% | 34.9105 | 6.8721 | 6 | 209.4629 | 77.2014 | 139.1% | 139.1%
9 | 256 | 13 | 6135 | 15 | 10.7 | 430.5 | 165.28 | 595.78 | 165.28 | 82.64 | 256 | 6135 | 900 | 252.4932 | 4.2754 | -9.8563 | 874.284 | 14.4071 | -36.1069 | 37.3059 | 37.3059 | 47.6298 | 227.6298 | 36.1383 | 573.6457 | 573.6457 | 141.0753 | 714.721 | 0.61399 | 61.4% | 323.1968 | 198.4387 | 138.9071 | 144.8985 | 144.8985 | 95.87% | 11.4% | 11.4% | 90% | 10.26% | 33.1473 | 7.0797 | 6 | 198.8835 | 73.3022 | 137.3% | 137.3%
9 | 256 | 13 | 6136 | 16 | 10.6 | 226.39 | 185.83 | 412.22 | 185.83 | 92.92 | 256 | 6136 | 960 | 252.4932 | 4.2754 | -9.8563 | 934.284 | 15.4071 | -51.1069 | 28.8888 | 28.8888 | 62.4324 | 242.4324 | 51.0875 | 294.3487 | 294.3487 | 158.6158 | 452.9646 | 0.50367 | 50.37% | 204.8306 | 103.167 | 72.2169 | 134.5769 | 134.5769 | 53.66% | 11.53% | 11.53% | 85% | 9.802% | 20.0769 | 7.1059 | 6 | 120.4613 | 44.3982 | 89.51% | 89.51%
9 | 256 | 13 | 6137 | 17 | 11.8 | 130.36 | 119.25 | 249.61 | 119.25 | 59.63 | 256 | 6137 | 1020 | 252.4932 | 4.2754 | -9.8563 | 994.284 | 16.4071 | -66.1069 | 19.3252 | 19.3252 | 75.0606 | 255.0606 | 66.0448 | 159.9403 | 159.9403 | 101.7862 | 261.7266 | 0.29486 | 29.49% | 118.3528 | 34.8972 | 24.428 | 125.5748 | 125.5748 | 19.45% | 11.59% | 11.59% | 80% | 9.276% | 10.9782 | 6.7954 | 6 | 65.8691 | 24.2773 | 52.45% | 52.45%
9 | 256 | 13 | 6138 | 18 | 12.3 | 66.86 | 64.72 | 131.58 | 64.72 | 32.36 | 256 | 6138 | 1080 | 252.4932 | 4.2754 | -9.8563 | 1054.284 | 17.4071 | -81.1069 | 9.2011 | 9.2011 | 86.4407 | 266.4407 | 81.002 | 0 | 0 | 55.242 | 55.242 | -1.5873 | 0% | 24.9804 | 0 | 0 | 158.104 | 158.104 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6139 | 19 | 10.8 | 7.22 | 26.03 | 33.25 | 26.03 | 13.02 | 256 | 6139 | 1140 | 252.4932 | 4.2754 | -9.8563 | 1114.284 | 18.4071 | -96.1069 | -1.0501 | 0 | 96.2497 | 276.2497 | 94.4148 | 0 | 0 | 22.218 | 22.218 | -5.298 | 0% | 10.047 | 0 | 0 | 145.5582 | 145.5582 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6140 | 20 | 10.3 | 0 | 0 | 0 | 0 | 0 | 256 | 6140 | 1200 | 252.4932 | 4.2754 | -9.8563 | 1174.284 | 19.4071 | -111.1069 | -11.0462 | 0 | 96.2497 | 276.2497 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.8136 | 135.8136 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6141 | 21 | 9.7 | 0 | 0 | 0 | 0 | 0 | 256 | 6141 | 1260 | 252.4932 | 4.2754 | -9.8563 | 1234.284 | 20.4071 | -126.1069 | -20.3721 | 0 | 96.2497 | 276.2497 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7644 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6142 | 22 | 9.7 | 0 | 0 | 0 | 0 | 0 | 256 | 6142 | 1320 | 252.4932 | 4.2754 | -9.8563 | 1294.284 | 21.4071 | -141.1069 | -28.503 | 0 | 96.2497 | 276.2497 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.307 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6143 | 23 | 10.1 | 0 | 0 | 0 | 0 | 0 | 256 | 6143 | 1380 | 252.4932 | 4.2754 | -9.8563 | 1354.284 | 22.4071 | -156.1069 | -34.7552 | 0 | 96.2497 | 276.2497 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.129 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
9 | 256 | 13 | 6144 | 24 | 9.5 | 0 | 0 | 0 | 0 | 0 | 256 | 6144 | 1440 | 252.4932 | 4.2754 | -9.8563 | 1414.284 | 23.4071 | -171.1069 | -38.3443 | 0 | 96.2497 | 276.2497 | 94.4148 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.475 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6145 | 1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 257 | 6145 | 60 | 253.4795 | 3.8907 | -9.5819 | 34.284 | 0.4117 | 173.8245 | -39.0382 | 0 | 95.6863 | 84.3137 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6331 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6146 | 2 | 8.2 | 0 | 0 | 0 | 0 | 0 | 257 | 6146 | 120 | 253.4795 | 3.8907 | -9.5819 | 94.284 | 1.4117 | 158.8245 | -35.9918 | 0 | 95.6863 | 84.3137 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5706 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6147 | 3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 257 | 6147 | 180 | 253.4795 | 3.8907 | -9.5819 | 154.284 | 2.4117 | 143.8245 | -30.1378 | 0 | 95.6863 | 84.3137 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8985 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6148 | 4 | 8.3 | 0 | 0 | 0 | 0 | 0 | 257 | 6148 | 240 | 253.4795 | 3.8907 | -9.5819 | 214.284 | 3.4117 | 128.8245 | -22.2661 | 0 | 95.6863 | 84.3137 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8985 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6149 | 5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 257 | 6149 | 300 | 253.4795 | 3.8907 | -9.5819 | 274.284 | 4.4117 | 113.8245 | -13.0936 | 0 | 95.6863 | 84.3137 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.93817 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6150 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 257 | 6150 | 360 | 253.4795 | 3.8907 | -9.5819 | 334.284 | 5.4117 | 98.8245 | -3.1741 | 0 | 95.6863 | 84.3137 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 9.0433 | 9.0433 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6151 | 7 | 7.9 | 0.42 | 5.61 | 6.03 | 5.61 | 2.81 | 257 | 6151 | 420 | 253.4795 | 3.8907 | -9.5819 | 394.284 | 6.4117 | 83.8245 | 7.0621 | 7.0621 | 88.1671 | 91.8329 | 83.7204 | 0 | 0 | 4.7884 | 4.7884 | -28.9282 | 0% | 2.1653 | 0 | 0 | 173.914 | 173.914 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6152 | 8 | 8.5 | 21.44 | 54.72 | 76.16 | 54.72 | 27.36 | 257 | 6152 | 480 | 253.4795 | 3.8907 | -9.5819 | 454.284 | 7.4117 | 68.8245 | 17.2327 | 17.2327 | 76.9199 | 103.0801 | 68.7569 | 26.2217 | 26.2217 | 46.7064 | 72.9282 | -1.1288 | 0% | 32.9781 | 0 | 0 | 187.3495 | 187.3495 | 0% | 11.81% | 11.81% | 80% | 9.449% | 3.1163 | 7.6737 | 6 | 18.6976 | 6.8913 | 9.98% | 9.98%
9 | 257 | 14 | 6153 | 9 | 9.7 | 101.39 | 103.67 | 205.06 | 103.67 | 51.84 | 257 | 6153 | 540 | 253.4795 | 3.8907 | -9.5819 | 514.284 | 8.4117 | 53.8245 | 26.9196 | 26.9196 | 64.585 | 115.415 | 53.7917 | 132.2907 | 132.2907 | 88.4879 | 220.7786 | 0.17831 | 17.83% | 99.8361 | 17.8019 | 12.4613 | 155.0128 | 155.0128 | 8.039% | 11.68% | 11.68% | 80% | 9.344% | 9.3288 | 7.3455 | 6 | 55.9727 | 20.6298 | 36.11% | 36.11%
9 | 257 | 14 | 6154 | 10 | 11.4 | 230.22 | 133.28 | 363.5 | 133.28 | 66.64 | 257 | 6154 | 600 | 253.4795 | 3.8907 | -9.5819 | 574.284 | 9.4117 | 38.8245 | 35.5733 | 35.5733 | 50.2651 | 129.7349 | 38.8304 | 308.2845 | 308.2845 | 113.7616 | 422.0461 | 0.48607 | 48.61% | 190.8493 | 92.7659 | 64.9361 | 163.3354 | 163.3354 | 39.76% | 11.53% | 11.53% | 85% | 9.801% | 18.7054 | 6.8978 | 6 | 112.2326 | 41.3654 | 68.71% | 68.71%
9 | 257 | 14 | 6155 | 11 | 12 | 395.33 | 142 | 537.33 | 142 | 71 | 257 | 6155 | 660 | 253.4795 | 3.8907 | -9.5819 | 634.284 | 10.4117 | 23.8245 | 42.4132 | 42.4132 | 33.0831 | 146.9169 | 23.8872 | 535.9268 | 535.9268 | 121.2046 | 657.1314 | 0.60192 | 60.19% | 297.1548 | 178.8629 | 125.204 | 164.1345 | 164.1345 | 76.28% | 11.41% | 11.41% | 90% | 10.27% | 30.5278 | 6.7446 | 6 | 183.167 | 67.5096 | 111.6% | 111.6%
9 | 257 | 14 | 6156 | 12 | 14.2 | 520.28 | 127.92 | 648.2 | 127.92 | 63.96 | 257 | 6156 | 720 | 253.4795 | 3.8907 | -9.5819 | 694.284 | 11.4117 | 8.8245 | 46.4361 | 46.4361 | 12.8317 | 167.1683 | 9.0629 | 709.0538 | 709.0538 | 109.1865 | 818.2403 | 0.64787 | 64.79% | 370.0083 | 239.7187 | 167.8031 | 159.9348 | 159.9348 | 104.9% | 11.35% | 11.35% | 95% | 10.78% | 39.8827 | 6.2045 | 6 | 239.2963 | 88.1971 | 149.6% | 149.6%
9 | 257 | 14 | 6157 | 13 | 13.4 | 471.53 | 179.67 | 651.2 | 179.67 | 89.84 | 257 | 6157 | 780 | 253.4795 | 3.8907 | -9.5819 | 754.284 | 12.4117 | -6.1755 | 46.78 | 46.78 | 9.017 | 189.017 | 6.5194 | 642.8737 | 642.8737 | 153.3579 | 796.2316 | 0.64126 | 64.13% | 360.0559 | 230.8907 | 161.6235 | 156.2767 | 156.2767 | 103.4% | 11.35% | 11.35% | 90% | 10.22% | 36.7906 | 6.397 | 6 | 220.7438 | 81.3592 | 141.3% | 141.3%
9 | 257 | 14 | 6158 | 14 | 13.3 | 428 | 168.47 | 596.47 | 168.47 | 84.24 | 257 | 6158 | 840 | 253.4795 | 3.8907 | -9.5819 | 814.284 | 13.4117 | -21.1755 | 43.3584 | 43.3584 | 29.7144 | 209.7144 | 21.2534 | 580.9984 | 580.9984 | 143.7981 | 724.7966 | 0.62491 | 62.49% | 327.753 | 204.8156 | 143.3709 | 152.8251 | 152.8251 | 93.81% | 11.38% | 11.38% | 90% | 10.24% | 33.5676 | 6.4214 | 6 | 201.4057 | 74.2318 | 131.8% | 131.8%
9 | 257 | 14 | 6159 | 15 | 13.7 | 405.5 | 177.92 | 583.42 | 177.92 | 88.96 | 257 | 6159 | 900 | 253.4795 | 3.8907 | -9.5819 | 874.284 | 14.4117 | -36.1755 | 36.9396 | 36.9396 | 47.4594 | 227.4594 | 36.1894 | 544.5622 | 544.5622 | 151.8642 | 696.4264 | 0.61893 | 61.89% | 314.924 | 194.915 | 136.4405 | 150.2483 | 150.2483 | 90.81% | 11.39% | 11.39% | 90% | 10.25% | 32.2769 | 6.3243 | 6 | 193.6612 | 71.3774 | 128.9% | 128.9%
9 | 257 | 14 | 6160 | 16 | 13 | 293.94 | 147.83 | 441.77 | 147.83 | 73.92 | 257 | 6160 | 960 | 253.4795 | 3.8907 | -9.5819 | 934.284 | 15.4117 | -51.1755 | 28.5418 | 28.5418 | 62.2276 | 242.2276 | 51.1491 | 385.9099 | 385.9099 | 126.1808 | 512.0907 | 0.54918 | 54.92% | 231.5674 | 127.1713 | 89.0199 | 141.2331 | 141.2331 | 63.03% | 11.46% | 11.46% | 90% | 10.32% | 23.8898 | 6.4949 | 6 | 143.3387 | 52.8301 | 101.5% | 101.5%
9 | 257 | 14 | 6161 | 17 | 12.3 | 217.44 | 113.19 | 330.63 | 113.19 | 56.6 | 257 | 6161 | 1020 | 253.4795 | 3.8907 | -9.5819 | 994.284 | 16.4117 | -66.1755 | 18.9919 | 18.9919 | 74.8448 | 254.8448 | 66.1141 | 270.5463 | 270.5463 | 96.6137 | 367.16 | 0.4442 | 44.42% | 166.0298 | 73.7512 | 51.6258 | 132.1281 | 132.1281 | 39.07% | 11.54% | 11.54% | 85% | 9.805% | 16.2792 | 6.669 | 6 | 97.6754 | 36.0001 | 73.92% | 73.92%
9 | 257 | 14 | 6162 | 18 | 12.4 | 81.81 | 70.5 | 152.31 | 70.5 | 35.25 | 257 | 6162 | 1080 | 253.4795 | 3.8907 | -9.5819 | 1054.284 | 17.4117 | -81.1755 | 8.8739 | 8.8739 | 86.2242 | 266.2242 | 81.0782 | 0 | 0 | 60.1755 | 60.1755 | -1.3875 | 0% | 27.2114 | 0 | 0 | 118.2544 | 118.2544 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6163 | 19 | 11.8 | 9.5 | 20.83 | 30.33 | 20.83 | 10.42 | 257 | 6163 | 1140 | 253.4795 | 3.8907 | -9.5819 | 1114.284 | 18.4117 | -96.1755 | -1.3784 | 0 | 95.6863 | 275.6863 | 94.0175 | 0 | 0 | 17.7795 | 17.7795 | -6.6909 | 0% | 8.0399 | 0 | 0 | 147.0469 | 147.0469 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6164 | 20 | 11.1 | 0 | 0 | 0 | 0 | 0 | 257 | 6164 | 1200 | 253.4795 | 3.8907 | -9.5819 | 1174.284 | 19.4117 | -111.1755 | -11.3827 | 0 | 95.6863 | 275.6863 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.3195 | 136.3195 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6165 | 21 | 9.9 | 0 | 0 | 0 | 0 | 0 | 257 | 6165 | 1260 | 253.4795 | 3.8907 | -9.5819 | 1234.284 | 20.4117 | -126.1755 | -20.723 | 0 | 95.6863 | 275.6863 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3593 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6166 | 22 | 9.4 | 0 | 0 | 0 | 0 | 0 | 257 | 6166 | 1320 | 253.4795 | 3.8907 | -9.5819 | 1294.284 | 21.4117 | -141.1755 | -28.8719 | 0 | 95.6863 | 275.6863 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8205 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6167 | 23 | 8.3 | 0 | 0 | 0 | 0 | 0 | 257 | 6167 | 1380 | 253.4795 | 3.8907 | -9.5819 | 1354.284 | 22.4117 | -156.1755 | -35.1404 | 0 | 95.6863 | 275.6863 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9772 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
9 | 257 | 14 | 6168 | 24 | 7.3 | 0 | 0 | 0 | 0 | 0 | 257 | 6168 | 1440 | 253.4795 | 3.8907 | -9.5819 | 1414.284 | 23.4117 | -171.1755 | -38.7347 | 0 | 95.6863 | 275.6863 | 94.0175 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9815 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6169 | 1 | 6.7 | 0 | 0 | 0 | 0 | 0 | 258 | 6169 | 60 | 254.4658 | 3.5043 | -9.3019 | 34.284 | 0.41637 | 173.7545 | -39.4161 | 0 | 95.1207 | 84.8793 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5173 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6170 | 2 | 7.3 | 0 | 0 | 0 | 0 | 0 | 258 | 6170 | 120 | 254.4658 | 3.5043 | -9.3019 | 94.284 | 1.4164 | 158.7545 | -36.3381 | 0 | 95.1207 | 84.8793 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0196 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6171 | 3 | 7.2 | 0 | 0 | 0 | 0 | 0 | 258 | 6171 | 180 | 254.4658 | 3.5043 | -9.3019 | 154.284 | 2.4164 | 143.7545 | -30.4464 | 0 | 95.1207 | 84.8793 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5888 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6172 | 4 | 8.3 | 0 | 0 | 0 | 0 | 0 | 258 | 6172 | 240 | 254.4658 | 3.5043 | -9.3019 | 214.284 | 3.4164 | 128.7545 | -22.5412 | 0 | 95.1207 | 84.8793 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9124 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6173 | 5 | 8.4 | 0 | 0 | 0 | 0 | 0 | 258 | 6173 | 300 | 254.4658 | 3.5043 | -9.3019 | 274.284 | 4.4164 | 113.7545 | -13.3444 | 0 | 95.1207 | 84.8793 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.66166 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6174 | 6 | 7.3 | 0 | 0 | 0 | 0 | 0 | 258 | 6174 | 360 | 254.4658 | 3.5043 | -9.3019 | 334.284 | 5.4164 | 98.7545 | -3.4108 | 0 | 95.1207 | 84.8793 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.4831 | 7.4831 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6175 | 7 | 6.4 | 0.47 | 5 | 5.47 | 5 | 2.5 | 258 | 6175 | 420 | 254.4658 | 3.5043 | -9.3019 | 394.284 | 6.4164 | 83.7545 | 6.8288 | 6.8288 | 87.8489 | 92.1511 | 83.6599 | 0 | 0 | 4.2678 | 4.2678 | -33.3896 | 0% | 1.9299 | 0 | 0 | 171.0773 | 171.0773 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6176 | 8 | 8.3 | 31.94 | 37.5 | 69.44 | 37.5 | 18.75 | 258 | 6176 | 480 | 254.4658 | 3.5043 | -9.3019 | 454.284 | 7.4164 | 68.7545 | 16.9918 | 16.9918 | 76.5955 | 103.4045 | 68.6902 | 39.7192 | 39.7192 | 32.0083 | 71.7274 | -1.1677 | 0% | 32.4351 | 0 | 0 | 185.8995 | 185.8995 | 0% | 11.82% | 11.82% | 80% | 9.457% | 3.0672 | 7.7294 | 6 | 18.4034 | 6.7829 | 9.9% | 9.9%
9 | 258 | 15 | 6177 | 9 | 10.7 | 139.58 | 60.06 | 199.64 | 60.06 | 30.03 | 258 | 6177 | 540 | 254.4658 | 3.5043 | -9.3019 | 514.284 | 8.4164 | 53.7545 | 26.6594 | 26.6594 | 64.2556 | 115.7444 | 53.7184 | 184.0864 | 184.0864 | 51.2644 | 235.3508 | 0.22696 | 22.7% | 106.4256 | 24.1546 | 16.9082 | 176.0477 | 176.0477 | 9.604% | 11.64% | 11.64% | 80% | 9.313% | 9.9111 | 7.0797 | 6 | 59.4663 | 21.9174 | 33.78% | 33.78%
9 | 258 | 15 | 6178 | 10 | 13.4 | 246.67 | 76.06 | 322.73 | 76.06 | 38.03 | 258 | 6178 | 600 | 254.4658 | 3.5043 | -9.3019 | 574.284 | 9.4164 | 38.7545 | 35.2816 | 35.2816 | 49.9426 | 130.0574 | 38.7486 | 333.0668 | 333.0668 | 64.9213 | 397.9881 | 0.47842 | 47.84% | 179.9702 | 86.1018 | 60.2713 | 161.5134 | 161.5134 | 37.32% | 11.5% | 11.5% | 85% | 9.773% | 17.5889 | 6.397 | 6 | 105.5335 | 38.8963 | 65.34% | 65.34%
9 | 258 | 15 | 6179 | 11 | 17 | 315.97 | 105.61 | 421.58 | 105.61 | 52.81 | 258 | 6179 | 660 | 254.4658 | 3.5043 | -9.3019 | 634.284 | 10.4164 | 23.7545 | 42.0808 | 42.0808 | 32.8008 | 147.1992 | 23.7907 | 431.4088 | 431.4088 | 90.1438 | 521.5526 | 0.57119 | 57.12% | 235.8461 | 134.7138 | 94.2996 | 162.6084 | 162.6084 | 57.99% | 11.4% | 11.4% | 90% | 10.26% | 24.1934 | 5.5661 | 5.5661 | 134.6631 | 53.5016 | 82.81% | 82.81%
9 | 258 | 15 | 6180 | 12 | 17.3 | 317 | 142.5 | 459.5 | 142.5 | 71.25 | 258 | 6180 | 720 | 254.4658 | 3.5043 | -9.3019 | 694.284 | 11.4164 | 8.7545 | 46.0647 | 46.0647 | 12.6472 | 167.3528 | 8.9136 | 434.8856 | 434.8856 | 121.6314 | 556.517 | 0.58703 | 58.7% | 251.657 | 147.7295 | 103.4107 | 152.2272 | 152.2272 | 67.93% | 11.39% | 11.39% | 90% | 10.25% | 25.7932 | 5.501 | 5.501 | 141.8871 | 57.0393 | 93.21% | 93.21%
9 | 258 | 15 | 6181 | 13 | 18.5 | 326.61 | 159.03 | 485.64 | 159.03 | 79.52 | 258 | 6181 | 780 | 254.4658 | 3.5043 | -9.3019 | 754.284 | 12.4164 | -6.2455 | 46.3883 | 46.3883 | 9.0574 | 189.0574 | 6.4731 | 448.2238 | 448.2238 | 135.7406 | 583.9644 | 0.60181 | 60.18% | 264.0687 | 158.9182 | 111.2427 | 151.8109 | 151.8109 | 73.28% | 11.37% | 11.37% | 90% | 10.23% | 27.0217 | 5.2467 | 5.2467 | 141.7742 | 59.7562 | 93.39% | 93.39%
9 | 258 | 15 | 6182 | 14 | 18.4 | 276.61 | 136.44 | 413.05 | 136.44 | 68.22 | 258 | 6182 | 840 | 254.4658 | 3.5043 | -9.3019 | 814.284 | 13.4164 | -21.2455 | 42.9712 | 42.9712 | 29.6246 | 209.6246 | 21.292 | 378.1064 | 378.1064 | 116.4588 | 494.5653 | 0.56481 | 56.48% | 223.6424 | 126.3149 | 88.4205 | 146.8329 | 146.8329 | 60.22% | 11.38% | 11.38% | 85% | 9.672% | 21.6308 | 5.2675 | 5.2675 | 113.9398 | 47.8346 | 77.6% | 77.6%
9 | 258 | 15 | 6183 | 15 | 18 | 176.39 | 133.39 | 309.78 | 133.39 | 66.7 | 258 | 6183 | 900 | 254.4658 | 3.5043 | -9.3019 | 874.284 | 14.4164 | -36.2455 | 36.5708 | 36.5708 | 47.2911 | 227.2911 | 36.2454 | 238.7604 | 238.7604 | 113.8555 | 352.6159 | 0.46599 | 46.6% | 159.4529 | 74.3041 | 52.0129 | 138.7451 | 138.7451 | 37.49% | 11.4% | 11.4% | 85% | 9.691% | 15.4526 | 5.3514 | 5.3514 | 82.6932 | 34.1721 | 59.6% | 59.6%
9 | 258 | 15 | 6184 | 16 | 17.4 | 176.39 | 124.5 | 300.89 | 124.5 | 62.25 | 258 | 6184 | 960 | 254.4658 | 3.5043 | -9.3019 | 934.284 | 15.4164 | -51.2455 | 28.1922 | 28.1922 | 62.0244 | 242.0244 | 51.2143 | 233.8807 | 233.8807 | 106.2674 | 340.1481 | 0.44967 | 44.97% | 153.8149 | 69.1656 | 48.4159 | 135.2954 | 135.2954 | 35.79% | 11.42% | 11.42% | 85% | 9.705% | 14.9279 | 5.4794 | 5.4794 | 81.7956 | 33.0117 | 60.46% | 60.46%
9 | 258 | 15 | 6185 | 17 | 15.4 | 96.33 | 95.61 | 191.94 | 95.61 | 47.81 | 258 | 6185 | 1020 | 254.4658 | 3.5043 | -9.3019 | 994.284 | 16.4164 | -66.2455 | 18.656 | 18.656 | 74.6298 | 254.6298 | 66.1861 | 121.59 | 121.59 | 81.6082 | 203.1982 | 0.18872 | 18.87% | 91.8862 | 17.3407 | 12.1385 | 124.1964 | 124.1964 | 9.774% | 11.5% | 11.5% | 80% | 9.202% | 8.4557 | 5.9242 | 5.9242 | 50.0933 | 18.6991 | 40.33% | 40.33%
9 | 258 | 15 | 6186 | 18 | 14.1 | 64.03 | 63.11 | 127.14 | 63.11 | 31.56 | 258 | 6186 | 1080 | 254.4658 | 3.5043 | -9.3019 | 1054.284 | 17.4164 | -81.2455 | 8.5445 | 8.5445 | 86.0081 | 266.0081 | 81.1563 | 0 | 0 | 53.8678 | 53.8678 | -1.5718 | 0% | 24.359 | 0 | 0 | 157.2637 | 157.2637 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6187 | 19 | 12.7 | 11.33 | 23.39 | 34.72 | 23.39 | 11.7 | 258 | 6187 | 1140 | 254.4658 | 3.5043 | -9.3019 | 1114.284 | 18.4164 | -96.2455 | -1.7089 | 0 | 95.1207 | 275.1207 | 93.6185 | 0 | 0 | 19.9646 | 19.9646 | -5.7667 | 0% | 9.028 | 0 | 0 | 146.2494 | 146.2494 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6188 | 20 | 12.1 | 0 | 0 | 0 | 0 | 0 | 258 | 6188 | 1200 | 254.4658 | 3.5043 | -9.3019 | 1174.284 | 19.4164 | -111.2455 | -11.7214 | 0 | 95.1207 | 275.1207 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.7415 | 136.7415 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6189 | 21 | 12.5 | 0 | 0 | 0 | 0 | 0 | 258 | 6189 | 1260 | 254.4658 | 3.5043 | -9.3019 | 1234.284 | 20.4164 | -126.2455 | -21.0758 | 0 | 95.1207 | 275.1207 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0859 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6190 | 22 | 11.9 | 0 | 0 | 0 | 0 | 0 | 258 | 6190 | 1320 | 254.4658 | 3.5043 | -9.3019 | 1294.284 | 21.4164 | -141.2455 | -29.2429 | 0 | 95.1207 | 275.1207 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3424 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6191 | 23 | 10.9 | 0 | 0 | 0 | 0 | 0 | 258 | 6191 | 1380 | 254.4658 | 3.5043 | -9.3019 | 1354.284 | 22.4164 | -156.2455 | -35.5276 | 0 | 95.1207 | 275.1207 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2831 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
9 | 258 | 15 | 6192 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 258 | 6192 | 1440 | 254.4658 | 3.5043 | -9.3019 | 1414.284 | 23.4164 | -171.2455 | -39.127 | 0 | 95.1207 | 275.1207 | 93.6185 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5474 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6193 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 259 | 6193 | 60 | 255.4521 | 3.1163 | -9.0165 | 34.284 | 0.42112 | 173.6831 | -39.7954 | 0 | 94.5531 | 85.4469 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.984 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6194 | 2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 259 | 6194 | 120 | 255.4521 | 3.1163 | -9.0165 | 94.284 | 1.4211 | 158.6831 | -36.685 | 0 | 94.5531 | 85.4469 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1979 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6195 | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 259 | 6195 | 180 | 255.4521 | 3.1163 | -9.0165 | 154.284 | 2.4211 | 143.6831 | -30.7552 | 0 | 94.5531 | 85.4469 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4118 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6196 | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 259 | 6196 | 240 | 255.4521 | 3.1163 | -9.0165 | 214.284 | 3.4211 | 128.6831 | -22.8163 | 0 | 94.5531 | 85.4469 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1738 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6197 | 5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 259 | 6197 | 300 | 255.4521 | 3.1163 | -9.0165 | 274.284 | 4.4211 | 113.6831 | -13.5951 | 0 | 94.5531 | 85.4469 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.2039 | 2.2039 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6198 | 6 | 8.6 | 0 | 0 | 0 | 0 | 0 | 259 | 6198 | 360 | 255.4521 | 3.1163 | -9.0165 | 334.284 | 5.4211 | 98.6831 | -3.6476 | 0 | 94.5531 | 85.4469 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 11.4717 | 11.4717 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6199 | 7 | 8.2 | 0.22 | 3.56 | 3.78 | 3.56 | 1.78 | 259 | 6199 | 420 | 255.4521 | 3.1163 | -9.0165 | 394.284 | 6.4211 | 83.6831 | 6.5951 | 6.5951 | 87.5289 | 92.4711 | 83.5983 | 0 | 0 | 3.0387 | 3.0387 | -45.8161 | 0% | 1.3741 | 0 | 0 | 176.3866 | 176.3866 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6200 | 8 | 9.7 | 42.92 | 31.39 | 74.31 | 31.39 | 15.7 | 259 | 6200 | 480 | 255.4521 | 3.1163 | -9.0165 | 454.284 | 7.4211 | 68.6831 | 16.7501 | 16.7501 | 76.2696 | 103.7304 | 68.6232 | 54.2832 | 54.2832 | 26.793 | 81.0762 | -0.89981 | 0% | 36.6627 | 0 | 0 | 191.8174 | 191.8174 | 0% | 11.76% | 11.76% | 80% | 9.407% | 3.449 | 7.3455 | 6 | 20.6941 | 7.6272 | 10.79% | 10.79%
9 | 259 | 16 | 6201 | 9 | 11.3 | 141.53 | 59.78 | 201.31 | 59.78 | 29.89 | 259 | 6201 | 540 | 255.4521 | 3.1163 | -9.0165 | 514.284 | 8.4211 | 53.6831 | 26.398 | 26.398 | 63.9254 | 116.0746 | 53.6457 | 188.6975 | 188.6975 | 51.0254 | 239.7229 | 0.2433 | 24.33% | 108.4027 | 26.3741 | 18.4619 | 159.4311 | 159.4311 | 11.58% | 11.62% | 11.62% | 80% | 9.296% | 10.0772 | 6.9236 | 6 | 60.4632 | 22.2848 | 37.92% | 37.92%
9 | 259 | 16 | 6202 | 10 | 12.2 | 234.17 | 87.17 | 321.34 | 87.17 | 43.59 | 259 | 6202 | 600 | 255.4521 | 3.1163 | -9.0165 | 574.284 | 9.4211 | 38.6831 | 34.9884 | 34.9884 | 49.6199 | 130.3801 | 38.6687 | 318.8526 | 318.8526 | 74.4042 | 393.2568 | 0.46749 | 46.75% | 177.8307 | 83.135 | 58.1945 | 163.2723 | 163.2723 | 35.64% | 11.53% | 11.53% | 85% | 9.798% | 17.423 | 6.6941 | 6 | 104.538 | 38.5294 | 64.03% | 64.03%
9 | 259 | 16 | 6203 | 11 | 11.6 | 313.33 | 114.94 | 428.27 | 114.94 | 57.47 | 259 | 6203 | 660 | 255.4521 | 3.1163 | -9.0165 | 634.284 | 10.4211 | 23.6831 | 41.7467 | 41.7467 | 32.5189 | 147.4811 | 23.6985 | 430.8969 | 430.8969 | 98.1074 | 529.0043 | 0.55123 | 55.12% | 239.2158 | 131.8619 | 92.3033 | 158.4222 | 158.4222 | 58.26% | 11.48% | 11.48% | 90% | 10.33% | 24.7097 | 6.8464 | 6 | 148.2585 | 54.6434 | 93.58% | 93.58%
9 | 259 | 16 | 6204 | 12 | 12.4 | 356.25 | 140.06 | 496.31 | 140.06 | 70.03 | 259 | 6204 | 720 | 255.4521 | 3.1163 | -9.0165 | 694.284 | 11.4211 | 8.6831 | 45.6917 | 45.6917 | 12.463 | 167.537 | 8.7776 | 492.0093 | 492.0093 | 119.5487 | 611.558 | 0.58837 | 58.84% | 276.5465 | 162.7108 | 113.8976 | 149.9377 | 149.9377 | 75.96% | 11.43% | 11.43% | 90% | 10.29% | 28.4503 | 6.6439 | 6 | 170.7015 | 62.9152 | 113.8% | 113.8%
9 | 259 | 16 | 6205 | 13 | 12.4 | 345.89 | 162 | 507.89 | 162 | 81 | 259 | 6205 | 780 | 255.4521 | 3.1163 | -9.0165 | 754.284 | 12.4211 | -6.3169 | 45.9948 | 45.9948 | 9.099 | 189.099 | 6.4513 | 477.8404 | 477.8404 | 138.2756 | 616.116 | 0.58996 | 59% | 278.6077 | 164.368 | 115.0576 | 147.8806 | 147.8806 | 77.8% | 11.43% | 11.43% | 90% | 10.29% | 28.6575 | 6.6439 | 6 | 171.9451 | 63.3736 | 116.3% | 116.3%
9 | 259 | 16 | 6206 | 14 | 11.8 | 296.67 | 183.39 | 480.06 | 183.39 | 91.7 | 259 | 6206 | 840 | 255.4521 | 3.1163 | -9.0165 | 814.284 | 13.4211 | -21.3169 | 42.582 | 42.582 | 29.5368 | 209.5368 | 21.3387 | 408.3852 | 408.3852 | 156.5332 | 564.9184 | 0.56811 | 56.81% | 255.4561 | 145.1282 | 101.5898 | 144.9749 | 144.9749 | 70.07% | 11.46% | 11.46% | 90% | 10.31% | 26.3432 | 6.7954 | 6 | 158.0592 | 58.2556 | 109% | 109%
9 | 259 | 16 | 6207 | 15 | 12.5 | 220.69 | 171.39 | 392.08 | 171.39 | 85.7 | 259 | 6207 | 900 | 255.4521 | 3.1163 | -9.0165 | 874.284 | 14.4211 | -36.3169 | 36.1997 | 36.1997 | 47.1249 | 227.1249 | 36.3064 | 301.1266 | 301.1266 | 146.2905 | 447.4172 | 0.50977 | 50.98% | 202.322 | 103.1385 | 72.1969 | 139.6244 | 139.6244 | 51.71% | 11.5% | 11.5% | 85% | 9.773% | 19.7726 | 6.6189 | 6 | 118.6355 | 43.7253 | 84.97% | 84.97%
9 | 259 | 16 | 6208 | 16 | 12.2 | 229.11 | 147.17 | 376.28 | 147.17 | 73.59 | 259 | 6208 | 960 | 255.4521 | 3.1163 | -9.0165 | 934.284 | 15.4211 | -51.3169 | 27.8402 | 27.8402 | 61.8226 | 241.8226 | 51.283 | 306.8528 | 306.8528 | 125.6175 | 432.4703 | 0.49801 | 49.8% | 195.563 | 97.3917 | 68.1742 | 136.7381 | 136.7381 | 49.86% | 11.51% | 11.51% | 85% | 9.783% | 19.1324 | 6.6941 | 6 | 114.7942 | 42.3095 | 83.95% | 83.95%
9 | 259 | 16 | 6209 | 17 | 12.4 | 208.11 | 111.39 | 319.5 | 111.39 | 55.7 | 259 | 6209 | 1020 | 255.4521 | 3.1163 | -9.0165 | 994.284 | 16.4211 | -66.3169 | 18.3178 | 18.3178 | 74.4157 | 254.4157 | 66.2606 | 266.5723 | 266.5723 | 95.0773 | 361.6496 | 0.43936 | 43.94% | 163.5379 | 71.8519 | 50.2964 | 132.0286 | 132.0286 | 38.1% | 11.54% | 11.54% | 85% | 9.805% | 16.0348 | 6.6439 | 6 | 96.2088 | 35.4595 | 72.87% | 72.87%
9 | 259 | 16 | 6210 | 18 | 12.6 | 76.67 | 69.67 | 146.34 | 69.67 | 34.84 | 259 | 6210 | 1080 | 255.4521 | 3.1163 | -9.0165 | 1054.284 | 17.4211 | -81.3169 | 8.2128 | 8.2128 | 85.7923 | 265.7923 | 81.2362 | 0 | 0 | 59.4671 | 59.4671 | -1.4058 | 0% | 26.891 | 0 | 0 | 160.7151 | 160.7151 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6211 | 19 | 11.6 | 6.81 | 23 | 29.81 | 23 | 11.5 | 259 | 6211 | 1140 | 255.4521 | 3.1163 | -9.0165 | 1114.284 | 18.4211 | -96.3169 | -2.0415 | 0 | 94.5531 | 274.5531 | 93.2178 | 0 | 0 | 19.6317 | 19.6317 | -6.0074 | 0% | 8.8775 | 0 | 0 | 147.1926 | 147.1926 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6212 | 20 | 9.6 | 0 | 0 | 0 | 0 | 0 | 259 | 6212 | 1200 | 255.4521 | 3.1163 | -9.0165 | 1174.284 | 19.4211 | -111.3169 | -12.062 | 0 | 94.5531 | 274.5531 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.7042 | 134.7042 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6213 | 21 | 8.8 | 0 | 0 | 0 | 0 | 0 | 259 | 6213 | 1260 | 255.4521 | 3.1163 | -9.0165 | 1234.284 | 20.4211 | -126.3169 | -21.4306 | 0 | 94.5531 | 274.5531 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.323 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6214 | 22 | 8.3 | 0 | 0 | 0 | 0 | 0 | 259 | 6214 | 1320 | 255.4521 | 3.1163 | -9.0165 | 1294.284 | 21.4211 | -141.3169 | -29.6157 | 0 | 94.5531 | 274.5531 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7431 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6215 | 23 | 8.1 | 0 | 0 | 0 | 0 | 0 | 259 | 6215 | 1380 | 255.4521 | 3.1163 | -9.0165 | 1354.284 | 22.4211 | -156.3169 | -35.9168 | 0 | 94.5531 | 274.5531 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4998 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
9 | 259 | 16 | 6216 | 24 | 7.1 | 0 | 0 | 0 | 0 | 0 | 259 | 6216 | 1440 | 255.4521 | 3.1163 | -9.0165 | 1414.284 | 23.4211 | -171.3169 | -39.5211 | 0 | 94.5531 | 274.5531 | 93.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4757 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6217 | 1 | 7.1 | 0 | 0 | 0 | 0 | 0 | 260 | 6217 | 60 | 256.4384 | 2.7268 | -8.7262 | 34.284 | 0.42596 | 173.6106 | -40.1758 | 0 | 93.9835 | 86.0165 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9818 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6218 | 2 | 7.4 | 0 | 0 | 0 | 0 | 0 | 260 | 6218 | 120 | 256.4384 | 2.7268 | -8.7262 | 94.284 | 1.426 | 158.6106 | -37.0325 | 0 | 93.9835 | 86.0165 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1139 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6219 | 3 | 6.8 | 0 | 0 | 0 | 0 | 0 | 260 | 6219 | 180 | 256.4384 | 2.7268 | -8.7262 | 154.284 | 2.426 | 143.6106 | -31.0641 | 0 | 93.9835 | 86.0165 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6176 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6220 | 4 | 6.8 | 0 | 0 | 0 | 0 | 0 | 260 | 6220 | 240 | 256.4384 | 2.7268 | -8.7262 | 214.284 | 3.426 | 128.6106 | -23.0913 | 0 | 93.9835 | 86.0165 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6176 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6221 | 5 | 6.9 | 0 | 0 | 0 | 0 | 0 | 260 | 6221 | 300 | 256.4384 | 2.7268 | -8.7262 | 274.284 | 4.426 | 113.6106 | -13.8457 | 0 | 93.9835 | 86.0165 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.7327 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6222 | 6 | 7.7 | 0 | 0 | 0 | 0 | 0 | 260 | 6222 | 360 | 256.4384 | 2.7268 | -8.7262 | 334.284 | 5.426 | 98.6106 | -3.8846 | 0 | 93.9835 | 86.0165 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.1778 | 3.1778 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6223 | 7 | 7.6 | 0.06 | 2.17 | 2.23 | 2.17 | 1.09 | 260 | 6223 | 420 | 256.4384 | 2.7268 | -8.7262 | 394.284 | 6.426 | 83.6106 | 6.361 | 6.361 | 87.2073 | 92.7927 | 83.5358 | 0 | 0 | 1.8522 | 1.8522 | -76.4443 | 0% | 0.83757 | 0 | 0 | 162.982 | 162.982 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6224 | 8 | 8.1 | 17.36 | 34.58 | 51.94 | 34.58 | 17.29 | 260 | 6224 | 480 | 256.4384 | 2.7268 | -8.7262 | 454.284 | 7.426 | 68.6106 | 16.5077 | 16.5077 | 75.9426 | 104.0574 | 68.5559 | 22.3361 | 22.3361 | 29.5159 | 51.852 | -1.9326 | 0% | 23.4475 | 0 | 0 | 172.9676 | 172.9676 | 0% | 11.84% | 11.84% | 80% | 9.473% | 2.2213 | 7.7853 | 6 | 13.3275 | 4.9121 | 7.705% | 7.705%
9 | 260 | 17 | 6225 | 9 | 9.1 | 79.11 | 85.22 | 164.33 | 85.22 | 42.61 | 260 | 6225 | 540 | 256.4384 | 2.7268 | -8.7262 | 514.284 | 8.426 | 53.6106 | 26.1355 | 26.1355 | 63.5945 | 116.4055 | 53.5736 | 106.6407 | 106.6407 | 72.7398 | 179.3805 | 0.026076 | 2.608% | 81.1159 | 2.1152 | 1.4806 | 159.9486 | 159.9486 | 0.9257% | 11.72% | 11.72% | 80% | 9.379% | 7.6081 | 7.5083 | 6 | 45.6483 | 16.8245 | 28.54% | 28.54%
9 | 260 | 17 | 6226 | 10 | 8.9 | 157.78 | 126.53 | 284.31 | 126.53 | 63.27 | 260 | 6226 | 600 | 256.4384 | 2.7268 | -8.7262 | 574.284 | 9.426 | 38.6106 | 34.6937 | 34.6937 | 49.2972 | 130.7028 | 38.5908 | 216.6664 | 216.6664 | 108.0001 | 324.6665 | 0.37274 | 37.27% | 146.8142 | 54.7242 | 38.307 | 142.3853 | 142.3853 | 26.9% | 11.64% | 11.64% | 85% | 9.896% | 14.5285 | 7.5632 | 6 | 87.1712 | 32.1286 | 61.22% | 61.22%
9 | 260 | 17 | 6227 | 11 | 9.9 | 209.31 | 160.28 | 369.59 | 160.28 | 80.14 | 260 | 6227 | 660 | 256.4384 | 2.7268 | -8.7262 | 634.284 | 10.426 | 23.6106 | 41.411 | 41.411 | 32.2376 | 147.7624 | 23.6109 | 289.9481 | 289.9481 | 136.8075 | 426.7556 | 0.4814 | 48.14% | 192.9789 | 92.9002 | 65.0301 | 141.5657 | 141.5657 | 45.94% | 11.56% | 11.56% | 85% | 9.825% | 18.961 | 7.2918 | 6 | 113.7661 | 41.9306 | 80.36% | 80.36%
9 | 260 | 17 | 6228 | 12 | 10.5 | 230.83 | 193.19 | 424.02 | 193.19 | 96.6 | 260 | 6228 | 720 | 256.4384 | 2.7268 | -8.7262 | 694.284 | 11.426 | 8.6106 | 45.3171 | 45.3171 | 12.279 | 167.721 | 8.656 | 320.9535 | 320.9535 | 164.898 | 485.8515 | 0.52352 | 52.35% | 219.702 | 115.0184 | 80.5129 | 135.823 | 135.823 | 59.28% | 11.52% | 11.52% | 85% | 9.789% | 21.506 | 7.1323 | 6 | 129.0361 | 47.5586 | 95% | 95%
9 | 260 | 17 | 6229 | 13 | 11.9 | 258.75 | 180.89 | 439.64 | 180.89 | 90.45 | 260 | 6229 | 780 | 256.4384 | 2.7268 | -8.7262 | 754.284 | 12.426 | -6.3894 | 45.5998 | 45.5998 | 9.1416 | 189.1416 | 6.4545 | 359.861 | 359.861 | 154.3993 | 514.2602 | 0.54533 | 54.53% | 232.5485 | 126.815 | 88.7705 | 136.3875 | 136.3875 | 65.09% | 11.48% | 11.48% | 90% | 10.33% | 24.0254 | 6.77 | 6 | 144.1526 | 53.1301 | 105.7% | 105.7%
9 | 260 | 17 | 6230 | 14 | 11.7 | 257.72 | 142.17 | 399.89 | 142.17 | 71.09 | 260 | 6230 | 840 | 256.4384 | 2.7268 | -8.7262 | 814.284 | 13.426 | -21.3894 | 42.191 | 42.191 | 29.4512 | 209.4512 | 21.3935 | 357.2975 | 357.2975 | 121.3497 | 478.6472 | 0.52512 | 52.51% | 216.4443 | 113.6582 | 79.5607 | 133.2544 | 133.2544 | 59.71% | 11.5% | 11.5% | 85% | 9.774% | 21.155 | 6.8209 | 6 | 126.9302 | 46.7825 | 95.25% | 95.25%
9 | 260 | 17 | 6231 | 15 | 11.2 | 196.39 | 128.06 | 324.45 | 128.06 | 64.03 | 260 | 6231 | 900 | 256.4384 | 2.7268 | -8.7262 | 874.284 | 14.426 | -36.3894 | 35.8264 | 35.8264 | 46.9608 | 226.9608 | 36.3723 | 270.1538 | 270.1538 | 109.306 | 379.4598 | 0.44917 | 44.92% | 171.5917 | 77.0732 | 53.9512 | 127.0857 | 127.0857 | 42.45% | 11.56% | 11.56% | 85% | 9.822% | 16.8541 | 6.9494 | 6 | 101.1246 | 37.2713 | 79.57% | 79.57%
9 | 260 | 17 | 6232 | 16 | 12.3 | 170.33 | 118.61 | 288.94 | 118.61 | 59.31 | 260 | 6232 | 960 | 256.4384 | 2.7268 | -8.7262 | 934.284 | 15.426 | -51.3894 | 27.486 | 27.486 | 61.6222 | 241.6222 | 51.355 | 230.4714 | 230.4714 | 101.24 | 331.7114 | 0.40575 | 40.58% | 149.9999 | 60.8632 | 42.6042 | 125.7807 | 125.7807 | 33.87% | 11.55% | 11.55% | 85% | 9.818% | 14.7266 | 6.669 | 6 | 88.3599 | 32.5667 | 70.25% | 70.25%
9 | 260 | 17 | 6233 | 17 | 13.2 | 109.44 | 95.42 | 204.86 | 95.42 | 47.71 | 260 | 6233 | 1020 | 256.4384 | 2.7268 | -8.7262 | 994.284 | 16.426 | -66.3894 | 17.9774 | 17.9774 | 74.2024 | 254.2024 | 66.3375 | 142.312 | 142.312 | 81.4461 | 223.758 | 0.22286 | 22.29% | 101.1834 | 22.55 | 15.785 | 121.0432 | 121.0432 | 13.04% | 11.57% | 11.57% | 80% | 9.254% | 9.3635 | 6.4458 | 6 | 56.1811 | 20.7066 | 46.41% | 46.41%
9 | 260 | 17 | 6234 | 18 | 12.8 | 56.67 | 51.89 | 108.56 | 51.89 | 25.95 | 260 | 6234 | 1080 | 256.4384 | 2.7268 | -8.7262 | 1054.284 | 17.426 | -81.3894 | 7.879 | 7.879 | 85.5767 | 265.5767 | 81.3179 | 0 | 0 | 44.2909 | 44.2909 | -2.1526 | 0% | 20.0283 | 0 | 0 | 154.4907 | 154.4907 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6235 | 19 | 12 | 5.06 | 15.56 | 20.62 | 15.56 | 7.78 | 260 | 6235 | 1140 | 256.4384 | 2.7268 | -8.7262 | 1114.284 | 18.426 | -96.3894 | -2.376 | 0 | 93.9835 | 273.9835 | 92.8156 | 0 | 0 | 13.2813 | 13.2813 | -9.1946 | 0% | 6.0058 | 0 | 0 | 144.5247 | 144.5247 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6236 | 20 | 9.6 | 0 | 0 | 0 | 0 | 0 | 260 | 6236 | 1200 | 256.4384 | 2.7268 | -8.7262 | 1174.284 | 19.426 | -111.3894 | -12.4044 | 0 | 93.9835 | 273.9835 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.0799 | 134.0799 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6237 | 21 | 9.4 | 0 | 0 | 0 | 0 | 0 | 260 | 6237 | 1260 | 256.4384 | 2.7268 | -8.7262 | 1234.284 | 20.426 | -126.3894 | -21.7872 | 0 | 93.9835 | 273.9835 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5174 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6238 | 22 | 9.2 | 0 | 0 | 0 | 0 | 0 | 260 | 6238 | 1320 | 256.4384 | 2.7268 | -8.7262 | 1294.284 | 21.426 | -141.3894 | -29.9903 | 0 | 93.9835 | 273.9835 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0135 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6239 | 23 | 9.3 | 0 | 0 | 0 | 0 | 0 | 260 | 6239 | 1380 | 256.4384 | 2.7268 | -8.7262 | 1354.284 | 22.426 | -156.3894 | -36.3077 | 0 | 93.9835 | 273.9835 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4504 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
9 | 260 | 17 | 6240 | 24 | 9.3 | 0 | 0 | 0 | 0 | 0 | 260 | 6240 | 1440 | 256.4384 | 2.7268 | -8.7262 | 1414.284 | 23.426 | -171.3894 | -39.9168 | 0 | 93.9835 | 273.9835 | 92.8156 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0397 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6241 | 1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 261 | 6241 | 60 | 257.4247 | 2.3359 | -8.4314 | 34.284 | 0.43088 | 173.5368 | -40.5573 | 0 | 93.4121 | 86.5879 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5148 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6242 | 2 | 7.9 | 0 | 0 | 0 | 0 | 0 | 261 | 6242 | 120 | 257.4247 | 2.3359 | -8.4314 | 94.284 | 1.4309 | 158.5368 | -37.3805 | 0 | 93.4121 | 86.5879 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1397 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8416 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6243 | 3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 261 | 6243 | 180 | 257.4247 | 2.3359 | -8.4314 | 154.284 | 2.4309 | 143.5368 | -31.3729 | 0 | 93.4121 | 86.5879 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4597 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6244 | 4 | 7.1 | 0 | 0 | 0 | 0 | 0 | 261 | 6244 | 240 | 257.4247 | 2.3359 | -8.4314 | 214.284 | 3.4309 | 128.5368 | -23.366 | 0 | 93.4121 | 86.5879 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.0693 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6245 | 5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 261 | 6245 | 300 | 257.4247 | 2.3359 | -8.4314 | 274.284 | 4.4309 | 113.5368 | -14.0961 | 0 | 93.4121 | 86.5879 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2828 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6246 | 6 | 5.9 | 0 | 0 | 0 | 0 | 0 | 261 | 6246 | 360 | 257.4247 | 2.3359 | -8.4314 | 334.284 | 5.4309 | 98.5368 | -4.1216 | 0 | 93.4121 | 86.5879 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.8116 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6247 | 7 | 5 | 0.22 | 2.64 | 2.86 | 2.64 | 1.32 | 261 | 6247 | 420 | 257.4247 | 2.3359 | -8.4314 | 394.284 | 6.4309 | 83.5368 | 6.1265 | 6.1265 | 86.8841 | 93.1159 | 83.4724 | 0 | 0 | 2.2534 | 2.2534 | -65.4431 | 0% | 1.019 | 0 | 0 | 151.0109 | 151.0109 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6248 | 8 | 6.4 | 2.78 | 32.83 | 35.61 | 32.83 | 16.42 | 261 | 6248 | 480 | 257.4247 | 2.3359 | -8.4314 | 454.284 | 7.4309 | 68.5368 | 16.2646 | 16.2646 | 75.6145 | 104.3855 | 68.4885 | 3.6397 | 3.6397 | 28.0222 | 31.6619 | -3.805 | 0% | 14.3175 | 0 | 0 | 160.2995 | 160.2995 | 0% | 11.93% | 11.93% | 80% | 9.541% | 1.3661 | 8.2723 | 6 | 8.1965 | 3.021 | 5.113% | 5.113%
9 | 261 | 18 | 6249 | 9 | 9.8 | 34.03 | 83.83 | 117.86 | 83.83 | 41.92 | 261 | 6249 | 540 | 257.4247 | 2.3359 | -8.4314 | 514.284 | 8.4309 | 53.5368 | 25.8718 | 25.8718 | 63.2632 | 116.7368 | 53.5023 | 46.3854 | 46.3854 | 71.5534 | 117.9388 | -0.36529 | 0% | 53.3319 | 0 | 0 | 149.6912 | 149.6912 | 0% | 11.73% | 11.73% | 80% | 9.388% | 5.0066 | 7.3186 | 6 | 30.0399 | 11.0718 | 20.07% | 20.07%
9 | 261 | 18 | 6250 | 10 | 13.1 | 88.61 | 143.39 | 232 | 143.39 | 71.7 | 261 | 6250 | 600 | 257.4247 | 2.3359 | -8.4314 | 574.284 | 9.4309 | 38.5368 | 34.3976 | 34.3976 | 48.9747 | 131.0253 | 38.5149 | 122.7271 | 122.7271 | 122.391 | 245.1181 | 0.27257 | 27.26% | 110.8424 | 30.2122 | 21.1485 | 138.7492 | 138.7492 | 15.24% | 11.56% | 11.56% | 80% | 9.25% | 10.253 | 6.4703 | 6 | 61.5179 | 22.6736 | 44.34% | 44.34%
9 | 261 | 18 | 6251 | 11 | 15.4 | 193.94 | 164.94 | 358.88 | 164.94 | 82.47 | 261 | 6251 | 660 | 257.4247 | 2.3359 | -8.4314 | 634.284 | 10.4309 | 23.5368 | 41.0738 | 41.0738 | 31.957 | 148.043 | 23.528 | 270.6369 | 270.6369 | 140.7851 | 411.422 | 0.50012 | 50.01% | 186.045 | 93.0444 | 65.1311 | 143.7981 | 143.7981 | 45.29% | 11.45% | 11.45% | 85% | 9.733% | 18.1073 | 5.9242 | 5.9242 | 107.271 | 40.0427 | 74.6% | 74.6%
9 | 261 | 18 | 6252 | 12 | 15.4 | 204.86 | 164.5 | 369.36 | 164.5 | 82.25 | 261 | 6252 | 720 | 257.4247 | 2.3359 | -8.4314 | 694.284 | 11.4309 | 8.5368 | 44.941 | 44.941 | 12.0956 | 167.9044 | 8.5495 | 286.7921 | 286.7921 | 140.4095 | 427.2016 | 0.51134 | 51.13% | 193.1806 | 98.7814 | 69.147 | 137.3093 | 137.3093 | 50.36% | 11.45% | 11.45% | 85% | 9.729% | 18.7953 | 5.9242 | 5.9242 | 111.3465 | 41.564 | 81.09% | 81.09%
9 | 261 | 18 | 6253 | 13 | 15.2 | 329.22 | 155.06 | 484.28 | 155.06 | 77.53 | 261 | 6253 | 780 | 257.4247 | 2.3359 | -8.4314 | 754.284 | 12.4309 | -6.4632 | 45.2032 | 45.2032 | 9.1851 | 189.1851 | 6.483 | 460.9782 | 460.9782 | 132.352 | 593.3302 | 0.59252 | 59.25% | 268.3039 | 158.9758 | 111.2831 | 140.3901 | 140.3901 | 79.27% | 11.41% | 11.41% | 90% | 10.27% | 27.5438 | 5.9702 | 5.9702 | 164.4421 | 60.9107 | 117.1% | 117.1%
9 | 261 | 18 | 6254 | 14 | 14 | 318.89 | 176.72 | 495.61 | 176.72 | 88.36 | 261 | 6254 | 840 | 257.4247 | 2.3359 | -8.4314 | 814.284 | 13.4309 | -21.4632 | 41.7981 | 41.7981 | 29.3675 | 209.3675 | 21.4563 | 445.291 | 445.291 | 150.84 | 596.1309 | 0.58894 | 58.89% | 269.5704 | 158.7604 | 111.1323 | 138.8553 | 138.8553 | 80.03% | 11.42% | 11.42% | 90% | 10.28% | 27.7047 | 6.2522 | 6 | 166.2281 | 61.2665 | 119.7% | 119.7%
9 | 261 | 18 | 6255 | 15 | 15.1 | 248.89 | 148.39 | 397.28 | 148.39 | 74.2 | 261 | 6255 | 900 | 257.4247 | 2.3359 | -8.4314 | 874.284 | 14.4309 | -36.4632 | 35.4511 | 35.4511 | 46.7986 | 226.7986 | 36.443 | 345.2008 | 345.2008 | 126.6588 | 471.8596 | 0.5376 | 53.76% | 213.3749 | 114.7104 | 80.2973 | 134.5619 | 134.5619 | 59.67% | 11.44% | 11.44% | 85% | 9.724% | 20.7494 | 5.9933 | 5.9933 | 124.3575 | 45.8854 | 92.42% | 92.42%
9 | 261 | 18 | 6256 | 16 | 15.4 | 235.22 | 139.86 | 375.08 | 139.86 | 69.93 | 261 | 6256 | 960 | 257.4247 | 2.3359 | -8.4314 | 934.284 | 15.4309 | -51.4632 | 27.1297 | 27.1297 | 61.4233 | 241.4233 | 51.4304 | 321.5999 | 321.5999 | 119.378 | 440.9779 | 0.52048 | 52.05% | 199.4102 | 103.79 | 72.653 | 133.362 | 133.362 | 54.48% | 11.44% | 11.44% | 85% | 9.726% | 19.3954 | 5.9242 | 5.9242 | 114.9021 | 42.8913 | 86.16% | 86.16%
9 | 261 | 18 | 6257 | 17 | 14.9 | 98.19 | 83.89 | 182.08 | 83.89 | 41.95 | 261 | 6257 | 1020 | 257.4247 | 2.3359 | -8.4314 | 994.284 | 16.4309 | -66.4632 | 17.635 | 17.635 | 73.9899 | 253.9899 | 66.4169 | 129.6702 | 129.6702 | 71.6046 | 201.2748 | 0.17721 | 17.72% | 91.0164 | 16.1291 | 11.2904 | 121.1767 | 121.1767 | 9.317% | 11.52% | 11.52% | 80% | 9.216% | 8.388 | 6.0398 | 6 | 50.3282 | 18.5494 | 41.53% | 41.53%
9 | 261 | 18 | 6258 | 18 | 14.6 | 31.53 | 52.78 | 84.31 | 52.78 | 26.39 | 261 | 6258 | 1080 | 257.4247 | 2.3359 | -8.4314 | 1054.284 | 17.4309 | -81.4632 | 7.5433 | 7.5433 | 85.3614 | 265.3614 | 81.4012 | 0 | 0 | 45.0505 | 45.0505 | -2.0115 | 0% | 20.3719 | 0 | 0 | 154.2851 | 154.2851 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6259 | 19 | 13.6 | 1.61 | 13.28 | 14.89 | 13.28 | 6.64 | 261 | 6259 | 1140 | 257.4247 | 2.3359 | -8.4314 | 1114.284 | 18.4309 | -96.4632 | -2.7124 | 0 | 93.4121 | 273.4121 | 92.412 | 0 | 0 | 11.3352 | 11.3352 | -10.5869 | 0% | 5.1258 | 0 | 0 | 144.9519 | 144.9519 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6260 | 20 | 12.9 | 0 | 0 | 0 | 0 | 0 | 261 | 6260 | 1200 | 257.4247 | 2.3359 | -8.4314 | 1174.284 | 19.4309 | -111.4632 | -12.7484 | 0 | 93.4121 | 273.4121 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.8025 | 137.8025 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6261 | 21 | 12 | 0 | 0 | 0 | 0 | 0 | 261 | 6261 | 1260 | 257.4247 | 2.3359 | -8.4314 | 1234.284 | 20.4309 | -126.4632 | -22.1453 | 0 | 93.4121 | 273.4121 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8669 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6262 | 22 | 11.5 | 0 | 0 | 0 | 0 | 0 | 261 | 6262 | 1320 | 257.4247 | 2.3359 | -8.4314 | 1294.284 | 21.4309 | -141.4632 | -30.3666 | 0 | 93.4121 | 273.4121 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8114 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6263 | 23 | 11.3 | 0 | 0 | 0 | 0 | 0 | 261 | 6263 | 1380 | 257.4247 | 2.3359 | -8.4314 | 1354.284 | 22.4309 | -156.4632 | -36.7003 | 0 | 93.4121 | 273.4121 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8267 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
9 | 261 | 18 | 6264 | 24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 261 | 6264 | 1440 | 257.4247 | 2.3359 | -8.4314 | 1414.284 | 23.4309 | -171.4632 | -40.314 | 0 | 93.4121 | 273.4121 | 92.412 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2324 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6265 | 1 | 11.6 | 0 | 0 | 0 | 0 | 0 | 262 | 6265 | 60 | 258.411 | 1.9438 | -8.1323 | 34.284 | 0.43586 | 173.4621 | -40.9398 | 0 | 92.839 | 87.161 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8065 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6266 | 2 | 11.6 | 0 | 0 | 0 | 0 | 0 | 262 | 6266 | 120 | 258.411 | 1.9438 | -8.1323 | 94.284 | 1.4359 | 158.4621 | -37.7289 | 0 | 92.839 | 87.161 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5832 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6267 | 3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 262 | 6267 | 180 | 258.411 | 1.9438 | -8.1323 | 154.284 | 2.4359 | 143.4621 | -31.6817 | 0 | 92.839 | 87.161 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9027 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6268 | 4 | 11.5 | 0 | 0 | 0 | 0 | 0 | 262 | 6268 | 240 | 258.411 | 1.9438 | -8.1323 | 214.284 | 3.4359 | 128.4621 | -23.6406 | 0 | 92.839 | 87.161 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5123 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6269 | 5 | 11.7 | 0 | 0 | 0 | 0 | 0 | 262 | 6269 | 300 | 258.411 | 1.9438 | -8.1323 | 274.284 | 4.4359 | 113.4621 | -14.3465 | 0 | 92.839 | 87.161 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.5276 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6270 | 6 | 11.3 | 0 | 0 | 0 | 0 | 0 | 262 | 6270 | 360 | 258.411 | 1.9438 | -8.1323 | 334.284 | 5.4359 | 98.4621 | -4.3587 | 0 | 92.839 | 87.161 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.1446 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6271 | 7 | 11.2 | 0.22 | 2.83 | 3.05 | 2.83 | 1.42 | 262 | 6271 | 420 | 258.411 | 1.9438 | -8.1323 | 394.284 | 6.4359 | 83.4621 | 5.8916 | 5.8916 | 86.5595 | 93.4405 | 83.4083 | 0 | 0 | 2.4156 | 2.4156 | -54.9368 | 0% | 1.0923 | 0 | 0 | 152.0356 | 152.0356 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6272 | 8 | 11.7 | 3.28 | 34.03 | 37.31 | 34.03 | 17.02 | 262 | 6272 | 480 | 258.411 | 1.9438 | -8.1323 | 454.284 | 7.4359 | 68.4621 | 16.0206 | 16.0206 | 75.2855 | 104.7145 | 68.4211 | 4.371 | 4.371 | 29.0464 | 33.4174 | -3.1905 | 0% | 15.1114 | 0 | 0 | 158.6969 | 158.6969 | 0% | 11.7% | 11.7% | 80% | 9.362% | 1.4147 | 6.8209 | 6 | 8.4879 | 3.1284 | 5.349% | 5.349%
9 | 262 | 19 | 6273 | 9 | 13 | 19.5 | 76.11 | 95.61 | 76.11 | 38.06 | 262 | 6273 | 540 | 258.411 | 1.9438 | -8.1323 | 514.284 | 8.4359 | 53.4621 | 25.6071 | 25.6071 | 62.9314 | 117.0686 | 53.4319 | 26.8805 | 26.8805 | 64.9639 | 91.8444 | -0.6168 | 0% | 41.5321 | 0 | 0 | 143.2257 | 143.2257 | 0% | 11.62% | 11.62% | 80% | 9.3% | 3.8624 | 6.4949 | 6 | 23.1742 | 8.5413 | 16.18% | 16.18%
9 | 262 | 19 | 6274 | 10 | 14.7 | 69.67 | 128.11 | 197.78 | 128.11 | 64.06 | 262 | 6274 | 600 | 258.411 | 1.9438 | -8.1323 | 574.284 | 9.4359 | 38.4621 | 34.1002 | 34.1002 | 48.6526 | 131.3474 | 38.4413 | 97.3326 | 97.3326 | 109.3487 | 206.6813 | 0.19141 | 19.14% | 93.4613 | 17.8894 | 12.5226 | 150.055 | 150.055 | 8.345% | 11.52% | 11.52% | 80% | 9.22% | 8.6171 | 6.0865 | 6 | 51.7026 | 19.0559 | 34.46% | 34.46%
9 | 262 | 19 | 6275 | 11 | 16.3 | 92.17 | 147.56 | 239.73 | 147.56 | 73.78 | 262 | 6275 | 660 | 258.411 | 1.9438 | -8.1323 | 634.284 | 10.4359 | 23.4621 | 40.7351 | 40.7351 | 31.6773 | 148.3227 | 23.4501 | 129.5773 | 129.5773 | 125.9503 | 255.5277 | 0.32267 | 32.27% | 115.5496 | 37.2845 | 26.0991 | 129.9683 | 129.9683 | 20.08% | 11.46% | 11.46% | 80% | 9.17% | 10.5962 | 5.7206 | 5.7206 | 60.616 | 23.4325 | 46.64% | 46.64%
9 | 262 | 19 | 6276 | 12 | 17.5 | 97.36 | 148.06 | 245.42 | 148.06 | 74.03 | 262 | 6276 | 720 | 258.411 | 1.9438 | -8.1323 | 694.284 | 11.4359 | 8.4621 | 44.5634 | 44.5634 | 11.9127 | 168.0873 | 8.4592 | 137.2396 | 137.2396 | 126.3771 | 263.6167 | 0.34765 | 34.76% | 119.2075 | 41.4423 | 29.0096 | 126.8149 | 126.8149 | 22.88% | 11.43% | 11.43% | 80% | 9.141% | 10.8963 | 5.4579 | 5.4579 | 59.4705 | 24.0962 | 46.9% | 46.9%
9 | 262 | 19 | 6277 | 13 | 18 | 123.33 | 171.06 | 294.39 | 171.06 | 85.53 | 262 | 6277 | 780 | 258.411 | 1.9438 | -8.1323 | 754.284 | 12.4359 | -6.5379 | 44.8052 | 44.8052 | 9.2293 | 189.2293 | 6.5366 | 173.8733 | 173.8733 | 146.0088 | 319.8822 | 0.43141 | 43.14% | 144.6507 | 62.4031 | 43.6822 | 128.9771 | 128.9771 | 33.87% | 11.4% | 11.4% | 85% | 9.694% | 14.0226 | 5.3514 | 5.3514 | 75.0404 | 31.0097 | 58.18% | 58.18%
9 | 262 | 19 | 6278 | 14 | 20 | 119.31 | 194.44 | 313.75 | 194.44 | 97.22 | 262 | 6278 | 840 | 258.411 | 1.9438 | -8.1323 | 814.284 | 13.4359 | -21.5379 | 41.4036 | 41.4036 | 29.2855 | 209.2855 | 21.5271 | 167.8173 | 167.8173 | 165.9649 | 333.7822 | 0.46019 | 46.02% | 150.9363 | 69.4595 | 48.6216 | 132.6652 | 132.6652 | 36.65% | 11.35% | 11.35% | 85% | 9.649% | 14.5641 | 4.943 | 4.943 | 71.9906 | 32.2073 | 54.26% | 54.26%
9 | 262 | 19 | 6279 | 15 | 18.8 | 117.08 | 155.56 | 272.64 | 155.56 | 77.78 | 262 | 6279 | 900 | 258.411 | 1.9438 | -8.1323 | 874.284 | 14.4359 | -36.5379 | 35.0739 | 35.0739 | 46.6383 | 226.6383 | 36.5183 | 163.7449 | 163.7449 | 132.7788 | 296.5237 | 0.40805 | 40.81% | 134.088 | 54.7147 | 38.3003 | 127.6566 | 127.6566 | 30% | 11.39% | 11.39% | 80% | 9.108% | 12.213 | 5.1847 | 5.1847 | 63.3204 | 27.0079 | 49.6% | 49.6%
9 | 262 | 19 | 6280 | 16 | 19.9 | 149.67 | 120.56 | 270.23 | 120.56 | 60.28 | 262 | 6280 | 960 | 258.411 | 1.9438 | -8.1323 | 934.284 | 15.4359 | -51.5379 | 26.7714 | 26.7714 | 61.2258 | 241.2258 | 51.509 | 206.8091 | 206.8091 | 102.9044 | 309.7135 | 0.43276 | 43.28% | 140.0525 | 60.6093 | 42.4265 | 128.6257 | 128.6257 | 32.98% | 11.35% | 11.35% | 85% | 9.651% | 13.5172 | 4.9628 | 4.9628 | 67.0823 | 29.892 | 52.15% | 52.15%
9 | 262 | 19 | 6281 | 17 | 19.3 | 77.08 | 96.17 | 173.25 | 96.17 | 48.09 | 262 | 6281 | 1020 | 258.411 | 1.9438 | -8.1323 | 994.284 | 16.4359 | -66.5379 | 17.2906 | 17.2906 | 73.7782 | 253.7782 | 66.4985 | 103.4172 | 103.4172 | 82.0862 | 185.5034 | 0.17705 | 17.7% | 83.8847 | 14.8517 | 10.3962 | 121.691 | 121.691 | 8.543% | 11.38% | 11.38% | 80% | 9.101% | 7.6339 | 5.0828 | 5.0828 | 38.8015 | 16.8818 | 31.89% | 31.89%
9 | 262 | 19 | 6282 | 18 | 18.4 | 26.89 | 53.28 | 80.17 | 53.28 | 26.64 | 262 | 6282 | 1080 | 258.411 | 1.9438 | -8.1323 | 1054.284 | 17.4359 | -81.5379 | 7.2058 | 7.2058 | 85.1464 | 265.1464 | 81.486 | 0 | 0 | 45.4773 | 45.4773 | -1.7972 | 0% | 20.5648 | 0 | 0 | 155.2638 | 155.2638 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6283 | 19 | 16.8 | 1.53 | 15.61 | 17.14 | 15.61 | 7.81 | 262 | 6283 | 1140 | 258.411 | 1.9438 | -8.1323 | 1114.284 | 18.4359 | -96.5379 | -3.0503 | 0 | 92.839 | 272.839 | 92.007 | 0 | 0 | 13.324 | 13.324 | -8.3426 | 0% | 6.0251 | 0 | 0 | 146.3611 | 146.3611 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6284 | 20 | 14.9 | 0 | 0 | 0 | 0 | 0 | 262 | 6284 | 1200 | 258.411 | 1.9438 | -8.1323 | 1174.284 | 19.4359 | -111.5379 | -13.0941 | 0 | 92.839 | 272.839 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.4481 | 138.4481 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6285 | 21 | 13.6 | 0 | 0 | 0 | 0 | 0 | 262 | 6285 | 1260 | 258.411 | 1.9438 | -8.1323 | 1234.284 | 20.4359 | -126.5379 | -22.505 | 0 | 92.839 | 272.839 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5269 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6286 | 22 | 13.1 | 0 | 0 | 0 | 0 | 0 | 262 | 6286 | 1320 | 258.411 | 1.9438 | -8.1323 | 1294.284 | 21.4359 | -141.5379 | -30.7443 | 0 | 92.839 | 272.839 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1906 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6287 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 262 | 6287 | 1380 | 258.411 | 1.9438 | -8.1323 | 1354.284 | 22.4359 | -156.5379 | -37.0944 | 0 | 92.839 | 272.839 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5956 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
9 | 262 | 19 | 6288 | 24 | 12.5 | 0 | 0 | 0 | 0 | 0 | 262 | 6288 | 1440 | 258.411 | 1.9438 | -8.1323 | 1414.284 | 23.4359 | -171.5379 | -40.7126 | 0 | 92.839 | 272.839 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6583 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6289 | 1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 263 | 6289 | 60 | 259.3973 | 1.5504 | -7.8294 | 34.284 | 0.44091 | 173.3864 | -41.3231 | 0 | 92.2643 | 87.7357 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1862 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6290 | 2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 263 | 6290 | 120 | 259.3973 | 1.5504 | -7.8294 | 94.284 | 1.4409 | 158.3864 | -38.0775 | 0 | 92.2643 | 87.7357 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8581 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6291 | 3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 263 | 6291 | 180 | 259.3973 | 1.5504 | -7.8294 | 154.284 | 2.4409 | 143.3864 | -31.9903 | 0 | 92.2643 | 87.7357 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5968 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6292 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 263 | 6292 | 240 | 259.3973 | 1.5504 | -7.8294 | 214.284 | 3.4409 | 128.3864 | -23.9149 | 0 | 92.2643 | 87.7357 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2064 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6293 | 5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 263 | 6293 | 300 | 259.3973 | 1.5504 | -7.8294 | 274.284 | 4.4409 | 113.3864 | -14.5966 | 0 | 92.2643 | 87.7357 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.5809 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6294 | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 263 | 6294 | 360 | 259.3973 | 1.5504 | -7.8294 | 334.284 | 5.4409 | 98.3864 | -4.5959 | 0 | 92.2643 | 87.7357 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.2267 | 4.2267 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6295 | 7 | 9.4 | 0.19 | 3.06 | 3.25 | 3.06 | 1.53 | 263 | 6295 | 420 | 259.3973 | 1.5504 | -7.8294 | 394.284 | 6.4409 | 83.3864 | 5.6563 | 5.6563 | 86.2336 | 93.7664 | 83.3436 | 0 | 0 | 2.6119 | 2.6119 | -52.3536 | 0% | 1.1811 | 0 | 0 | 166.3207 | 166.3207 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6296 | 8 | 9.8 | 28.75 | 30.06 | 58.81 | 30.06 | 15.03 | 263 | 6296 | 480 | 259.3973 | 1.5504 | -7.8294 | 454.284 | 7.4409 | 68.3864 | 15.776 | 15.776 | 74.9557 | 105.0443 | 68.3538 | 39.007 | 39.007 | 25.6578 | 64.6648 | -1.3286 | 0% | 29.2414 | 0 | 0 | 177.4381 | 177.4381 | 0% | 11.76% | 11.76% | 80% | 9.412% | 2.7521 | 7.3186 | 6 | 16.5125 | 6.086 | 9.306% | 9.306%
9 | 263 | 20 | 6297 | 9 | 13.1 | 95 | 62.78 | 157.78 | 62.78 | 31.39 | 263 | 6297 | 540 | 259.3973 | 1.5504 | -7.8294 | 514.284 | 8.4409 | 53.3864 | 25.3412 | 25.3412 | 62.5995 | 117.4005 | 53.3625 | 132.4536 | 132.4536 | 53.5861 | 186.0397 | 0.10381 | 10.38% | 84.1271 | 8.7331 | 6.1132 | 167.0568 | 167.0568 | 3.659% | 11.58% | 11.58% | 80% | 9.268% | 7.7969 | 6.4703 | 6 | 46.7814 | 17.2422 | 28% | 28%
9 | 263 | 20 | 6298 | 10 | 15.2 | 171.89 | 82.83 | 254.72 | 82.83 | 41.42 | 263 | 6298 | 600 | 259.3973 | 1.5504 | -7.8294 | 574.284 | 9.4409 | 38.3864 | 33.8014 | 33.8014 | 48.331 | 131.669 | 38.3702 | 242.245 | 242.245 | 70.6998 | 312.9448 | 0.40305 | 40.3% | 141.5137 | 57.0364 | 39.9255 | 151.534 | 151.534 | 26.35% | 11.48% | 11.48% | 85% | 9.758% | 13.8096 | 5.9702 | 5.9702 | 82.4461 | 30.5387 | 54.41% | 54.41%
9 | 263 | 20 | 6299 | 11 | 17.4 | 310 | 98.25 | 408.25 | 98.25 | 49.13 | 263 | 6299 | 660 | 259.3973 | 1.5504 | -7.8294 | 634.284 | 10.4409 | 23.3864 | 40.395 | 40.395 | 31.3988 | 148.6012 | 23.3774 | 439.0875 | 439.0875 | 83.8616 | 522.9491 | 0.57353 | 57.35% | 236.4776 | 135.6264 | 94.9385 | 154.9227 | 154.9227 | 61.28% | 11.39% | 11.39% | 90% | 10.25% | 24.2448 | 5.4794 | 5.4794 | 132.8463 | 53.6151 | 85.75% | 85.75%
9 | 263 | 20 | 6300 | 12 | 17.9 | 275.56 | 137.56 | 413.12 | 137.56 | 68.78 | 263 | 6300 | 720 | 259.3973 | 1.5504 | -7.8294 | 694.284 | 11.4409 | 8.3864 | 44.1846 | 44.1846 | 11.7307 | 168.2693 | 8.3859 | 391.14 | 391.14 | 117.4148 | 508.5548 | 0.5692 | 56.92% | 229.9685 | 130.8979 | 91.6285 | 145.6445 | 145.6445 | 62.91% | 11.39% | 11.39% | 90% | 10.25% | 23.5651 | 5.3726 | 5.3726 | 126.6048 | 52.1121 | 86.93% | 86.93%
9 | 263 | 20 | 6301 | 13 | 19.3 | 255.78 | 163.06 | 418.84 | 163.06 | 81.53 | 263 | 6301 | 780 | 259.3973 | 1.5504 | -7.8294 | 754.284 | 12.4409 | -6.6136 | 44.4059 | 44.4059 | 9.2741 | 189.2741 | 6.6148 | 363.1041 | 363.1041 | 139.1804 | 502.2845 | 0.57245 | 57.25% | 227.133 | 130.0234 | 91.0164 | 145.2843 | 145.2843 | 62.65% | 11.36% | 11.36% | 90% | 10.23% | 23.2292 | 5.0828 | 5.0828 | 118.0681 | 51.3692 | 81.27% | 81.27%
9 | 263 | 20 | 6302 | 14 | 19.1 | 262 | 168.33 | 430.33 | 168.33 | 84.17 | 263 | 6302 | 840 | 259.3973 | 1.5504 | -7.8294 | 814.284 | 13.4409 | -21.6136 | 41.0076 | 41.0076 | 29.2053 | 209.2053 | 21.6056 | 371.2393 | 371.2393 | 143.6786 | 514.9179 | 0.57728 | 57.73% | 232.8459 | 134.4165 | 94.0916 | 143.9642 | 143.9642 | 65.36% | 11.37% | 11.37% | 90% | 10.23% | 23.819 | 5.1233 | 5.1233 | 122.0321 | 52.6735 | 84.77% | 84.77%
9 | 263 | 20 | 6303 | 15 | 17.7 | 179.39 | 152.56 | 331.95 | 152.56 | 76.28 | 263 | 6303 | 900 | 259.3973 | 1.5504 | -7.8294 | 874.284 | 14.4409 | -36.6136 | 34.6951 | 34.6951 | 46.4798 | 226.4798 | 36.5983 | 253.0188 | 253.0188 | 130.2181 | 383.2369 | 0.49126 | 49.13% | 173.2997 | 85.1344 | 59.5941 | 134.7408 | 134.7408 | 44.23% | 11.4% | 11.4% | 85% | 9.694% | 16.7997 | 5.4151 | 5.4151 | 90.9716 | 37.151 | 67.52% | 67.52%
9 | 263 | 20 | 6304 | 16 | 17.9 | 111.44 | 146.81 | 258.25 | 146.81 | 73.41 | 263 | 6304 | 960 | 259.3973 | 1.5504 | -7.8294 | 934.284 | 15.4409 | -51.6136 | 26.4113 | 26.4113 | 61.0295 | 241.0295 | 51.5907 | 155.6498 | 155.6498 | 125.3102 | 280.96 | 0.379 | 37.9% | 127.0501 | 48.1515 | 33.706 | 129.6847 | 129.6847 | 25.99% | 11.41% | 11.41% | 80% | 9.13% | 11.5991 | 5.3726 | 5.3726 | 62.3169 | 25.6504 | 48.05% | 48.05%
9 | 263 | 20 | 6305 | 17 | 17.3 | 75.89 | 104.86 | 180.75 | 104.86 | 52.43 | 263 | 6305 | 1020 | 259.3973 | 1.5504 | -7.8294 | 994.284 | 16.4409 | -66.6136 | 16.9445 | 16.9445 | 73.5672 | 253.5672 | 66.5822 | 103.4884 | 103.4884 | 89.5036 | 192.9921 | 0.17833 | 17.83% | 87.271 | 15.5632 | 10.8942 | 122.5506 | 122.5506 | 8.89% | 11.44% | 11.44% | 80% | 9.154% | 7.9885 | 5.501 | 5.501 | 43.9446 | 17.6659 | 35.86% | 35.86%
9 | 263 | 20 | 6306 | 18 | 16.2 | 31.89 | 62.17 | 94.06 | 62.17 | 31.09 | 263 | 6306 | 1080 | 259.3973 | 1.5504 | -7.8294 | 1054.284 | 17.4409 | -81.6136 | 6.8667 | 6.8667 | 84.9316 | 264.9316 | 81.5722 | 0 | 0 | 53.0654 | 53.0654 | -1.518 | 0% | 23.9962 | 0 | 0 | 155.0783 | 155.0783 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7429 | 5.7429 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6307 | 19 | 15.8 | 0 | 13.94 | 13.94 | 13.94 | 6.97 | 263 | 6307 | 1140 | 259.3973 | 1.5504 | -7.8294 | 1114.284 | 18.4409 | -96.6136 | -3.3898 | 0 | 92.2643 | 272.2643 | 91.6009 | 0 | 0 | 11.8985 | 11.8985 | -9.6275 | 0% | 5.3805 | 0 | 0 | 146.4697 | 146.4697 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6308 | 20 | 15.1 | 0 | 0 | 0 | 0 | 0 | 263 | 6308 | 1200 | 259.3973 | 1.5504 | -7.8294 | 1174.284 | 19.4409 | -111.6136 | -13.441 | 0 | 92.2643 | 272.2643 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.5468 | 139.5468 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6309 | 21 | 14.6 | 0 | 0 | 0 | 0 | 0 | 263 | 6309 | 1260 | 259.3973 | 1.5504 | -7.8294 | 1234.284 | 20.4409 | -126.6136 | -22.8659 | 0 | 92.2643 | 272.2643 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4466 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6310 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 263 | 6310 | 1320 | 259.3973 | 1.5504 | -7.8294 | 1294.284 | 21.4409 | -141.6136 | -31.1234 | 0 | 92.2643 | 272.2643 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5128 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6311 | 23 | 13.8 | 0 | 0 | 0 | 0 | 0 | 263 | 6311 | 1380 | 259.3973 | 1.5504 | -7.8294 | 1354.284 | 22.4409 | -156.6136 | -37.4899 | 0 | 92.2643 | 272.2643 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3371 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 263 | 20 | 6312 | 24 | 13.8 | 0 | 0 | 0 | 0 | 0 | 263 | 6312 | 1440 | 259.3973 | 1.5504 | -7.8294 | 1414.284 | 23.4409 | -171.6136 | -41.1125 | 0 | 92.2643 | 272.2643 | 91.6009 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8566 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6313 | 1 | 13.8 | 0 | 0 | 0 | 0 | 0 | 264 | 6313 | 60 | 260.3836 | 1.156 | -7.5231 | 34.284 | 0.44602 | 173.3098 | -41.7072 | 0 | 91.6881 | 88.3119 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7554 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6314 | 2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 264 | 6314 | 120 | 260.3836 | 1.156 | -7.5231 | 94.284 | 1.446 | 158.3098 | -38.4263 | 0 | 91.6881 | 88.3119 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2949 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6315 | 3 | 13.7 | 0 | 0 | 0 | 0 | 0 | 264 | 6315 | 180 | 260.3836 | 1.156 | -7.5231 | 154.284 | 2.446 | 143.3098 | -32.2988 | 0 | 91.6881 | 88.3119 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9869 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6316 | 4 | 13.6 | 0 | 0 | 0 | 0 | 0 | 264 | 6316 | 240 | 260.3836 | 1.156 | -7.5231 | 214.284 | 3.446 | 128.3098 | -24.1889 | 0 | 91.6881 | 88.3119 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1393 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6317 | 5 | 13.8 | 0 | 0 | 0 | 0 | 0 | 264 | 6317 | 300 | 260.3836 | 1.156 | -7.5231 | 274.284 | 4.446 | 113.3098 | -14.8466 | 0 | 91.6881 | 88.3119 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.5451 | 2.5451 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6318 | 6 | 13.7 | 0 | 0 | 0 | 0 | 0 | 264 | 6318 | 360 | 260.3836 | 1.156 | -7.5231 | 334.284 | 5.446 | 98.3098 | -4.8331 | 0 | 91.6881 | 88.3119 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 11.2097 | 11.2097 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6319 | 7 | 13.5 | 0 | 1.89 | 1.89 | 1.89 | 0.95 | 264 | 6319 | 420 | 260.3836 | 1.156 | -7.5231 | 394.284 | 6.446 | 83.3098 | 5.4207 | 5.4207 | 85.9067 | 94.0933 | 83.2783 | 0 | 0 | 1.6132 | 1.6132 | -79.3756 | 0% | 0.7295 | 0 | 0 | 173.1503 | 173.1503 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6320 | 8 | 13.8 | 24.94 | 26.89 | 51.83 | 26.89 | 13.45 | 264 | 6320 | 480 | 260.3836 | 1.156 | -7.5231 | 454.284 | 7.446 | 68.3098 | 15.5306 | 15.5306 | 74.6253 | 105.3747 | 68.2868 | 34.4602 | 34.4602 | 22.9521 | 57.4122 | -1.437 | 0% | 25.9618 | 0 | 0 | 184.2266 | 184.2266 | 0% | 11.61% | 11.61% | 80% | 9.284% | 2.4103 | 6.3002 | 6 | 14.462 | 5.3303 | 7.85% | 7.85%
9 | 264 | 21 | 6321 | 9 | 14.6 | 95.97 | 78.83 | 174.8 | 78.83 | 39.42 | 264 | 6321 | 540 | 260.3836 | 1.156 | -7.5231 | 514.284 | 8.446 | 53.3098 | 25.0744 | 25.0744 | 62.2676 | 117.7324 | 53.2943 | 135.3529 | 135.3529 | 67.2856 | 202.6386 | 0.17807 | 17.81% | 91.6332 | 16.3168 | 11.4218 | 171.4838 | 171.4838 | 6.661% | 11.53% | 11.53% | 80% | 9.224% | 8.4518 | 6.1099 | 6 | 50.7109 | 18.6904 | 29.57% | 29.57%
9 | 264 | 21 | 6322 | 10 | 17.3 | 187.5 | 134.31 | 321.81 | 134.31 | 67.16 | 264 | 6322 | 600 | 260.3836 | 1.156 | -7.5231 | 574.284 | 9.446 | 38.3098 | 33.5013 | 33.5013 | 48.01 | 131.99 | 38.3016 | 266.5838 | 266.5838 | 114.6408 | 381.2246 | 0.48726 | 48.73% | 172.3897 | 83.9986 | 58.799 | 159.4573 | 159.4573 | 36.87% | 11.41% | 11.41% | 85% | 9.702% | 16.7254 | 5.501 | 5.501 | 92.0054 | 36.9866 | 57.7% | 57.7%
9 | 264 | 21 | 6323 | 11 | 20 | 288.11 | 157.17 | 445.28 | 157.17 | 78.59 | 264 | 6323 | 660 | 260.3836 | 1.156 | -7.5231 | 634.284 | 10.446 | 23.3098 | 40.0536 | 40.0536 | 31.1214 | 148.8786 | 23.3102 | 411.176 | 411.176 | 134.153 | 545.329 | 0.59356 | 59.36% | 246.5978 | 146.3713 | 102.4599 | 162.0515 | 162.0515 | 63.23% | 11.35% | 11.35% | 90% | 10.22% | 25.1944 | 4.943 | 4.943 | 124.5359 | 55.7152 | 76.85% | 76.85%
9 | 264 | 21 | 6324 | 12 | 21.4 | 327.78 | 174.11 | 501.89 | 174.11 | 87.06 | 264 | 6324 | 720 | 260.3836 | 1.156 | -7.5231 | 694.284 | 11.446 | 8.3098 | 43.8045 | 43.8045 | 11.5495 | 168.4505 | 8.3303 | 468.5375 | 468.5375 | 148.6122 | 617.1496 | 0.62302 | 62.3% | 279.0751 | 173.8705 | 121.7093 | 156.0468 | 156.0468 | 78% | 11.34% | 11.34% | 90% | 10.2% | 28.4772 | 4.6738 | 4.6738 | 133.0961 | 62.9747 | 85.29% | 85.29%
9 | 264 | 21 | 6325 | 13 | 21 | 290.69 | 164.72 | 455.41 | 164.72 | 82.36 | 264 | 6325 | 780 | 260.3836 | 1.156 | -7.5231 | 754.284 | 12.446 | -6.6902 | 44.0054 | 44.0054 | 9.3194 | 189.3194 | 6.7169 | 415.5518 | 415.5518 | 140.5973 | 556.1491 | 0.6016 | 60.16% | 251.4906 | 151.2974 | 105.9082 | 151.1121 | 151.1121 | 70.09% | 11.34% | 11.34% | 90% | 10.2% | 25.6639 | 4.7493 | 4.7493 | 121.8857 | 56.7535 | 80.66% | 80.66%
9 | 264 | 21 | 6326 | 14 | 19.9 | 292.28 | 185.97 | 478.25 | 185.97 | 92.99 | 264 | 6326 | 840 | 260.3836 | 1.156 | -7.5231 | 814.284 | 13.446 | -21.6902 | 40.6102 | 40.6102 | 29.1267 | 209.1267 | 21.6918 | 417.2349 | 417.2349 | 158.7353 | 575.9702 | 0.60438 | 60.44% | 260.4537 | 157.4119 | 110.1883 | 149.5996 | 149.5996 | 73.66% | 11.35% | 11.35% | 90% | 10.22% | 26.6129 | 4.9628 | 4.9628 | 132.0734 | 58.8521 | 88.28% | 88.28%
9 | 264 | 21 | 6327 | 15 | 19.7 | 321.06 | 124.44 | 445.5 | 124.44 | 62.22 | 264 | 6327 | 900 | 260.3836 | 1.156 | -7.5231 | 874.284 | 14.446 | -36.6902 | 34.3146 | 34.3146 | 46.323 | 226.323 | 36.6829 | 456.73 | 456.73 | 106.2162 | 562.9462 | 0.59897 | 59.9% | 254.5643 | 152.4775 | 106.7342 | 145.4562 | 145.4562 | 73.38% | 11.36% | 11.36% | 90% | 10.22% | 26.0173 | 5.0025 | 5.0025 | 130.1508 | 57.5349 | 89.48% | 89.48%
9 | 264 | 21 | 6328 | 16 | 17.8 | 210.61 | 122.72 | 333.33 | 122.72 | 61.36 | 264 | 6328 | 960 | 260.3836 | 1.156 | -7.5231 | 934.284 | 15.446 | -51.6902 | 26.0495 | 26.0495 | 60.8346 | 240.8346 | 51.6755 | 297.3994 | 297.3994 | 104.7481 | 402.1475 | 0.50652 | 50.65% | 181.8511 | 92.1106 | 64.4774 | 136.0789 | 136.0789 | 47.38% | 11.4% | 11.4% | 85% | 9.69% | 17.6216 | 5.3938 | 5.3938 | 95.047 | 38.9686 | 69.85% | 69.85%
9 | 264 | 21 | 6329 | 17 | 17.2 | 150.06 | 121.61 | 271.67 | 121.61 | 60.81 | 264 | 6329 | 1020 | 260.3836 | 1.156 | -7.5231 | 994.284 | 16.446 | -66.6902 | 16.5967 | 16.5967 | 73.357 | 253.357 | 66.6681 | 208.072 | 208.072 | 103.8006 | 311.8727 | 0.41611 | 41.61% | 141.0288 | 58.6833 | 41.0783 | 129.9027 | 129.9027 | 31.62% | 11.43% | 11.43% | 85% | 9.713% | 13.6983 | 5.5226 | 5.5226 | 75.65 | 30.2925 | 58.24% | 58.24%
9 | 264 | 21 | 6330 | 18 | 17.6 | 76.94 | 72.28 | 149.22 | 72.28 | 36.14 | 264 | 6330 | 1080 | 260.3836 | 1.156 | -7.5231 | 1054.284 | 17.446 | -81.6902 | 6.5261 | 6.5261 | 84.717 | 264.717 | 81.6597 | 0 | 0 | 61.6948 | 61.6948 | -1.1423 | 0% | 27.8984 | 0 | 0 | 162.6783 | 162.6783 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6331 | 19 | 15.9 | 0 | 19.5 | 19.5 | 19.5 | 9.75 | 264 | 6331 | 1140 | 260.3836 | 1.156 | -7.5231 | 1114.284 | 18.446 | -96.6902 | -3.7306 | 0 | 91.6881 | 271.6881 | 91.1936 | 0 | 0 | 16.6443 | 16.6443 | -6.6396 | 0% | 7.5265 | 0 | 0 | 147.3736 | 147.3736 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6332 | 20 | 14.8 | 0 | 0 | 0 | 0 | 0 | 264 | 6332 | 1200 | 260.3836 | 1.156 | -7.5231 | 1174.284 | 19.446 | -111.6902 | -13.7893 | 0 | 91.6881 | 271.6881 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.3679 | 138.3679 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6333 | 21 | 14.5 | 0 | 0 | 0 | 0 | 0 | 264 | 6333 | 1260 | 260.3836 | 1.156 | -7.5231 | 1234.284 | 20.446 | -126.6902 | -23.2281 | 0 | 91.6881 | 271.6881 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6427 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6334 | 22 | 13.8 | 0 | 0 | 0 | 0 | 0 | 264 | 6334 | 1320 | 260.3836 | 1.156 | -7.5231 | 1294.284 | 21.446 | -141.6902 | -31.5037 | 0 | 91.6881 | 271.6881 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1367 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6335 | 23 | 12.6 | 0 | 0 | 0 | 0 | 0 | 264 | 6335 | 1380 | 260.3836 | 1.156 | -7.5231 | 1354.284 | 22.446 | -156.6902 | -37.8867 | 0 | 91.6881 | 271.6881 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.505 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
9 | 264 | 21 | 6336 | 24 | 12.6 | 0 | 0 | 0 | 0 | 0 | 264 | 6336 | 1440 | 260.3836 | 1.156 | -7.5231 | 1414.284 | 23.446 | -171.6902 | -41.5136 | 0 | 91.6881 | 271.6881 | 91.1936 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0446 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6337 | 1 | 12.2 | 0 | 0 | 0 | 0 | 0 | 265 | 6337 | 60 | 261.3699 | 0.76057 | -7.2137 | 34.284 | 0.45117 | 173.2324 | -42.092 | 0 | 91.1106 | 88.8894 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1487 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6338 | 2 | 11.8 | 0 | 0 | 0 | 0 | 0 | 265 | 6338 | 120 | 261.3699 | 0.76057 | -7.2137 | 94.284 | 1.4512 | 158.2324 | -38.7752 | 0 | 91.1106 | 88.8894 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.319 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6339 | 3 | 11.1 | 0 | 0 | 0 | 0 | 0 | 265 | 6339 | 180 | 261.3699 | 0.76057 | -7.2137 | 154.284 | 2.4512 | 143.2324 | -32.607 | 0 | 91.1106 | 88.8894 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9466 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6340 | 4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 265 | 6340 | 240 | 261.3699 | 0.76057 | -7.2137 | 214.284 | 3.4512 | 128.2324 | -24.4625 | 0 | 91.1106 | 88.8894 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6418 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6341 | 5 | 11 | 0 | 0 | 0 | 0 | 0 | 265 | 6341 | 300 | 261.3699 | 0.76057 | -7.2137 | 274.284 | 4.4512 | 113.2324 | -15.0963 | 0 | 91.1106 | 88.8894 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.73362 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6342 | 6 | 10.7 | 0 | 0 | 0 | 0 | 0 | 265 | 6342 | 360 | 261.3699 | 0.76057 | -7.2137 | 334.284 | 5.4512 | 98.2324 | -5.0703 | 0 | 91.1106 | 88.8894 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.5679 | 7.5679 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6343 | 7 | 10.6 | 0 | 2.14 | 2.14 | 2.14 | 1.07 | 265 | 6343 | 420 | 261.3699 | 0.76057 | -7.2137 | 394.284 | 6.4512 | 83.2324 | 5.1847 | 5.1847 | 85.5787 | 94.4213 | 83.2125 | 0 | 0 | 1.8266 | 1.8266 | -73.6724 | 0% | 0.82599 | 0 | 0 | 169.844 | 169.844 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6344 | 8 | 11.8 | 27.08 | 28.28 | 55.36 | 28.28 | 14.14 | 265 | 6344 | 480 | 261.3699 | 0.76057 | -7.2137 | 454.284 | 7.4512 | 68.2324 | 15.2846 | 15.2846 | 74.2943 | 105.7057 | 68.22 | 38.1158 | 38.1158 | 24.1385 | 62.2543 | -1.3365 | 0% | 28.1514 | 0 | 0 | 182.6546 | 182.6546 | 0% | 11.68% | 11.68% | 80% | 9.348% | 2.6315 | 6.7954 | 6 | 15.7892 | 5.8194 | 8.644% | 8.644%
9 | 265 | 22 | 6345 | 9 | 12.3 | 96.89 | 61.25 | 158.14 | 61.25 | 30.63 | 265 | 6345 | 540 | 261.3699 | 0.76057 | -7.2137 | 514.284 | 8.4512 | 53.2324 | 24.8064 | 24.8064 | 61.9357 | 118.0643 | 53.2273 | 138.2477 | 138.2477 | 52.2801 | 190.5278 | 0.11065 | 11.07% | 86.1567 | 9.5333 | 6.6733 | 168.5199 | 168.5199 | 3.96% | 11.61% | 11.61% | 80% | 9.288% | 8.0023 | 6.669 | 6 | 48.0139 | 17.6964 | 28.49% | 28.49%
9 | 265 | 22 | 6346 | 10 | 14.2 | 197.72 | 100.89 | 298.61 | 100.89 | 50.45 | 265 | 6346 | 600 | 261.3699 | 0.76057 | -7.2137 | 574.284 | 9.4512 | 38.2324 | 33.1999 | 33.1999 | 47.6899 | 132.3101 | 38.2357 | 283.6272 | 283.6272 | 86.115 | 369.7422 | 0.45849 | 45.85% | 167.1974 | 76.6588 | 53.6611 | 155.3512 | 155.3512 | 34.54% | 11.49% | 11.49% | 85% | 9.766% | 16.3283 | 6.2045 | 6 | 97.9696 | 36.1085 | 63.06% | 63.06%
9 | 265 | 22 | 6347 | 11 | 15.1 | 317.36 | 111.67 | 429.03 | 111.67 | 55.84 | 265 | 6347 | 660 | 261.3699 | 0.76057 | -7.2137 | 634.284 | 10.4512 | 23.2324 | 39.7108 | 39.7108 | 30.8454 | 149.1546 | 23.2486 | 456.3852 | 456.3852 | 95.3163 | 551.7015 | 0.57615 | 57.62% | 249.4794 | 143.7384 | 100.6169 | 155.6657 | 155.6657 | 64.64% | 11.42% | 11.42% | 90% | 10.28% | 25.6391 | 5.9933 | 5.9933 | 153.663 | 56.6985 | 98.71% | 98.71%
9 | 265 | 22 | 6348 | 12 | 14.8 | 335.78 | 143.11 | 478.89 | 143.11 | 71.56 | 265 | 6348 | 720 | 261.3699 | 0.76057 | -7.2137 | 694.284 | 11.4512 | 8.2324 | 43.4233 | 43.4233 | 11.3693 | 168.6307 | 8.2929 | 483.3824 | 483.3824 | 122.152 | 605.5344 | 0.59529 | 59.53% | 273.8226 | 163.0026 | 114.1018 | 146.9081 | 146.9081 | 77.67% | 11.41% | 11.41% | 90% | 10.27% | 28.113 | 6.0631 | 6 | 168.6779 | 62.1693 | 114.8% | 114.8%
9 | 265 | 22 | 6349 | 13 | 15.7 | 392.08 | 141.17 | 533.25 | 141.17 | 70.59 | 265 | 6349 | 780 | 261.3699 | 0.76057 | -7.2137 | 754.284 | 12.4512 | -6.7676 | 43.6039 | 43.6039 | 9.365 | 189.365 | 6.8419 | 564.4566 | 564.4566 | 120.4961 | 684.9528 | 0.62246 | 62.25% | 309.7356 | 192.7983 | 134.9588 | 148.3509 | 148.3509 | 90.97% | 11.38% | 11.38% | 90% | 10.24% | 31.7209 | 5.8557 | 5.8557 | 185.7474 | 70.148 | 125.2% | 125.2%
9 | 265 | 22 | 6350 | 14 | 16.9 | 386.39 | 142.56 | 528.95 | 142.56 | 71.28 | 265 | 6350 | 840 | 261.3699 | 0.76057 | -7.2137 | 814.284 | 13.4512 | -21.7676 | 40.2116 | 40.2116 | 29.0496 | 209.0496 | 21.7857 | 555.7411 | 555.7411 | 121.6826 | 677.4236 | 0.62443 | 62.44% | 306.331 | 191.2822 | 133.8976 | 149.4912 | 149.4912 | 89.57% | 11.37% | 11.37% | 90% | 10.24% | 31.3548 | 5.588 | 5.588 | 175.2094 | 69.3384 | 117.2% | 117.2%
9 | 265 | 22 | 6351 | 15 | 17.4 | 358.39 | 134.03 | 492.42 | 134.03 | 67.02 | 265 | 6351 | 900 | 261.3699 | 0.76057 | -7.2137 | 874.284 | 14.4512 | -36.7676 | 33.9327 | 33.9327 | 46.1679 | 226.1679 | 36.7718 | 514.2778 | 514.2778 | 114.4018 | 628.6795 | 0.61229 | 61.23% | 284.2889 | 174.0667 | 121.8467 | 146.6865 | 146.6865 | 83.07% | 11.38% | 11.38% | 90% | 10.24% | 29.1079 | 5.4794 | 5.4794 | 159.4933 | 64.3695 | 108.7% | 108.7%
9 | 265 | 22 | 6352 | 16 | 17.7 | 269.44 | 94.5 | 363.94 | 94.5 | 47.25 | 265 | 6352 | 960 | 261.3699 | 0.76057 | -7.2137 | 934.284 | 15.4512 | -51.7676 | 25.6862 | 25.6862 | 60.641 | 240.641 | 51.7632 | 384.733 | 384.733 | 80.6608 | 465.3938 | 0.54646 | 54.65% | 210.4511 | 115.0041 | 80.5029 | 140.209 | 140.209 | 57.42% | 11.39% | 11.39% | 85% | 9.685% | 20.3826 | 5.4151 | 5.4151 | 110.3731 | 45.0742 | 78.72% | 78.72%
9 | 265 | 22 | 6353 | 17 | 18.1 | 189.78 | 77.92 | 267.7 | 77.92 | 38.96 | 265 | 6353 | 1020 | 261.3699 | 0.76057 | -7.2137 | 994.284 | 16.4512 | -66.7676 | 16.2475 | 16.2475 | 73.1475 | 253.1475 | 66.7559 | 267.6909 | 267.6909 | 66.5089 | 334.1998 | 0.44803 | 44.8% | 151.1252 | 67.7093 | 47.3965 | 133.9861 | 133.9861 | 35.37% | 11.4% | 11.4% | 85% | 9.691% | 14.6449 | 5.3303 | 5.3303 | 78.0619 | 32.3859 | 58.26% | 58.26%
9 | 265 | 22 | 6354 | 18 | 18.4 | 68.83 | 41.72 | 110.55 | 41.72 | 20.86 | 265 | 6354 | 1080 | 261.3699 | 0.76057 | -7.2137 | 1054.284 | 17.4512 | -81.7676 | 6.1841 | 6.1841 | 84.5026 | 264.5026 | 81.7485 | 0 | 0 | 35.6102 | 35.6102 | -2.518 | 0% | 16.103 | 0 | 0 | 163.9674 | 163.9674 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2675 | 5.2675 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6355 | 19 | 18 | 0 | 10.5 | 10.5 | 10.5 | 5.25 | 265 | 6355 | 1140 | 261.3699 | 0.76057 | -7.2137 | 1114.284 | 18.4512 | -96.7676 | -4.0727 | 0 | 91.1106 | 271.1106 | 90.7853 | 0 | 0 | 8.9623 | 8.9623 | -12.4946 | 0% | 4.0528 | 0 | 0 | 151.7776 | 151.7776 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3514 | 5.3514 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6356 | 20 | 14.9 | 0 | 0 | 0 | 0 | 0 | 265 | 6356 | 1200 | 261.3699 | 0.76057 | -7.2137 | 1174.284 | 19.4512 | -111.7676 | -14.1386 | 0 | 91.1106 | 271.1106 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.8167 | 139.8167 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6357 | 21 | 14.5 | 0 | 0 | 0 | 0 | 0 | 265 | 6357 | 1260 | 261.3699 | 0.76057 | -7.2137 | 1234.284 | 20.4512 | -126.7676 | -23.5912 | 0 | 91.1106 | 271.1106 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4474 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6358 | 22 | 14.2 | 0 | 0 | 0 | 0 | 0 | 265 | 6358 | 1320 | 261.3699 | 0.76057 | -7.2137 | 1294.284 | 21.4512 | -141.7676 | -31.885 | 0 | 91.1106 | 271.1106 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4183 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6359 | 23 | 13.9 | 0 | 0 | 0 | 0 | 0 | 265 | 6359 | 1380 | 261.3699 | 0.76057 | -7.2137 | 1354.284 | 22.4512 | -156.7676 | -38.2846 | 0 | 91.1106 | 271.1106 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4363 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
9 | 265 | 22 | 6360 | 24 | 13.8 | 0 | 0 | 0 | 0 | 0 | 265 | 6360 | 1440 | 261.3699 | 0.76057 | -7.2137 | 1414.284 | 23.4512 | -171.7676 | -41.9158 | 0 | 91.1106 | 271.1106 | 90.7853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1495 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6361 | 1 | 13.7 | 0 | 0 | 0 | 0 | 0 | 266 | 6361 | 60 | 262.3562 | 0.36431 | -6.9016 | 34.284 | 0.45637 | 173.1544 | -42.4773 | 0 | 90.532 | 89.468 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4098 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6362 | 2 | 13.9 | 0 | 0 | 0 | 0 | 0 | 266 | 6362 | 120 | 262.3562 | 0.36431 | -6.9016 | 94.284 | 1.4564 | 158.1544 | -39.1242 | 0 | 90.532 | 89.468 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.671 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6363 | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 266 | 6363 | 180 | 262.3562 | 0.36431 | -6.9016 | 154.284 | 2.4564 | 143.1544 | -32.9148 | 0 | 90.532 | 89.468 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0847 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6364 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 266 | 6364 | 240 | 262.3562 | 0.36431 | -6.9016 | 214.284 | 3.4564 | 128.1544 | -24.7357 | 0 | 90.532 | 89.468 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0847 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6365 | 5 | 14.3 | 0 | 0 | 0 | 0 | 0 | 266 | 6365 | 300 | 262.3562 | 0.36431 | -6.9016 | 274.284 | 4.4564 | 113.1544 | -15.3457 | 0 | 90.532 | 89.468 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.8119 | 2.8119 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6366 | 6 | 14.4 | 0 | 0 | 0 | 0 | 0 | 266 | 6366 | 360 | 262.3562 | 0.36431 | -6.9016 | 334.284 | 5.4564 | 98.1544 | -5.3075 | 0 | 90.532 | 89.468 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 11.0421 | 11.0421 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6367 | 7 | 14.5 | 0 | 1.39 | 1.39 | 1.39 | 0.7 | 266 | 6367 | 420 | 262.3562 | 0.36431 | -6.9016 | 394.284 | 6.4564 | 83.1544 | 4.9484 | 4.9484 | 85.2499 | 94.7501 | 83.1465 | 0 | 0 | 1.1864 | 1.1864 | -106.2943 | 0% | 0.53651 | 0 | 0 | 172.3369 | 172.3369 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6368 | 8 | 14.7 | 29.44 | 22.28 | 51.72 | 22.28 | 11.14 | 266 | 6368 | 480 | 262.3562 | 0.36431 | -6.9016 | 454.284 | 7.4564 | 68.1544 | 15.0378 | 15.0378 | 73.9631 | 106.0369 | 68.1537 | 42.2233 | 42.2233 | 19.0172 | 61.2405 | -1.2634 | 0% | 27.693 | 0 | 0 | 182.9287 | 182.9287 | 0% | 11.57% | 11.57% | 80% | 9.254% | 2.5627 | 6.0865 | 6 | 15.376 | 5.6671 | 8.405% | 8.405%
9 | 266 | 23 | 6369 | 9 | 15.5 | 100.61 | 67.17 | 167.78 | 67.17 | 33.59 | 266 | 6369 | 540 | 262.3562 | 0.36431 | -6.9016 | 514.284 | 8.4564 | 53.1544 | 24.5375 | 24.5375 | 61.6041 | 118.3959 | 53.1618 | 145.2518 | 145.2518 | 57.3332 | 202.585 | 0.18797 | 18.8% | 91.6089 | 17.2201 | 12.054 | 169.5716 | 169.5716 | 7.109% | 11.5% | 11.5% | 80% | 9.2% | 8.4279 | 5.9013 | 5.9013 | 49.7355 | 18.6376 | 29.33% | 29.33%
9 | 266 | 23 | 6370 | 10 | 16.6 | 168.94 | 88.75 | 257.69 | 88.75 | 44.38 | 266 | 6370 | 600 | 262.3562 | 0.36431 | -6.9016 | 574.284 | 9.4564 | 38.1544 | 32.8973 | 32.8973 | 47.3708 | 132.6292 | 38.1727 | 244.5292 | 244.5292 | 75.7529 | 320.2821 | 0.42209 | 42.21% | 144.8316 | 61.1322 | 42.7925 | 152.2809 | 152.2809 | 28.1% | 11.44% | 11.44% | 85% | 9.725% | 14.0855 | 5.6539 | 5.6539 | 79.6387 | 31.1489 | 52.3% | 52.3%
9 | 266 | 23 | 6371 | 11 | 17.9 | 227.44 | 103.89 | 331.33 | 103.89 | 51.95 | 266 | 6371 | 660 | 262.3562 | 0.36431 | -6.9016 | 634.284 | 10.4564 | 23.1544 | 39.3669 | 39.3669 | 30.5709 | 149.4291 | 23.1928 | 329.5991 | 329.5991 | 88.6757 | 418.2747 | 0.51852 | 51.85% | 189.1438 | 98.0748 | 68.6524 | 150.8977 | 150.8977 | 45.5% | 11.4% | 11.4% | 85% | 9.687% | 18.3218 | 5.3726 | 5.3726 | 98.4346 | 40.5169 | 65.23% | 65.23%
9 | 266 | 23 | 6372 | 12 | 17.4 | 272.5 | 114.86 | 387.36 | 114.86 | 57.43 | 266 | 6372 | 720 | 262.3562 | 0.36431 | -6.9016 | 694.284 | 11.4564 | 8.1544 | 43.0411 | 43.0411 | 11.1904 | 168.8096 | 8.2744 | 395.098 | 395.098 | 98.0391 | 493.1371 | 0.55959 | 55.96% | 222.9966 | 124.7877 | 87.3514 | 142.7652 | 142.7652 | 61.19% | 11.4% | 11.4% | 85% | 9.686% | 21.6006 | 5.4794 | 5.4794 | 118.3577 | 47.7677 | 82.9% | 82.9%
9 | 266 | 23 | 6373 | 13 | 16.7 | 298.19 | 139.5 | 437.69 | 139.5 | 69.75 | 266 | 6373 | 780 | 262.3562 | 0.36431 | -6.9016 | 754.284 | 12.4564 | -6.8456 | 43.2014 | 43.2014 | 9.4108 | 189.4108 | 6.9887 | 432.3545 | 432.3545 | 119.0707 | 551.4252 | 0.58259 | 58.26% | 249.3545 | 145.2702 | 101.6891 | 141.629 | 141.629 | 71.8% | 11.4% | 11.4% | 90% | 10.26% | 25.5773 | 5.6319 | 5.6319 | 144.0481 | 56.5619 | 101.7% | 101.7%
9 | 266 | 23 | 6374 | 14 | 16.4 | 295.22 | 145.61 | 440.83 | 145.61 | 72.81 | 266 | 6374 | 840 | 262.3562 | 0.36431 | -6.9016 | 814.284 | 13.4564 | -21.8456 | 39.812 | 39.812 | 28.9738 | 208.9738 | 21.8869 | 427.8523 | 427.8523 | 124.2859 | 552.1382 | 0.58165 | 58.17% | 249.6769 | 145.2246 | 101.6572 | 140.4934 | 140.4934 | 72.36% | 11.4% | 11.4% | 90% | 10.26% | 25.6193 | 5.6983 | 5.6983 | 145.9858 | 56.6547 | 103.9% | 103.9%
9 | 266 | 23 | 6375 | 15 | 17.3 | 255.42 | 135.97 | 391.39 | 135.97 | 67.99 | 266 | 6375 | 900 | 262.3562 | 0.36431 | -6.9016 | 874.284 | 14.4564 | -36.8456 | 33.5496 | 33.5496 | 46.0143 | 226.0143 | 36.8651 | 369.7564 | 369.7564 | 116.0577 | 485.814 | 0.55545 | 55.55% | 219.6851 | 122.0241 | 85.4169 | 137.6267 | 137.6267 | 62.06% | 11.4% | 11.4% | 85% | 9.689% | 21.285 | 5.501 | 5.501 | 117.0877 | 47.0698 | 85.08% | 85.08%
9 | 266 | 23 | 6376 | 16 | 17 | 192.17 | 124.86 | 317.03 | 124.86 | 62.43 | 266 | 6376 | 960 | 262.3562 | 0.36431 | -6.9016 | 934.284 | 15.4564 | -51.8456 | 25.3216 | 25.3216 | 60.4485 | 240.4485 | 51.8538 | 277.5261 | 277.5261 | 106.5747 | 384.1008 | 0.48788 | 48.79% | 173.6904 | 84.7406 | 59.3184 | 132.4701 | 132.4701 | 44.78% | 11.42% | 11.42% | 85% | 9.708% | 16.861 | 5.5661 | 5.5661 | 93.8503 | 37.2867 | 70.85% | 70.85%
9 | 266 | 23 | 6377 | 17 | 17.1 | 131.06 | 102.28 | 233.34 | 102.28 | 51.14 | 266 | 6377 | 1020 | 262.3562 | 0.36431 | -6.9016 | 994.284 | 16.4564 | -66.8456 | 15.897 | 15.897 | 72.9387 | 252.9387 | 66.8456 | 188.1434 | 188.1434 | 87.3014 | 275.4448 | 0.364 | 36.4% | 124.5561 | 45.338 | 31.7366 | 126.4796 | 126.4796 | 25.09% | 11.44% | 11.44% | 80% | 9.149% | 11.3951 | 5.5443 | 5.5443 | 63.1778 | 25.1992 | 49.95% | 49.95%
9 | 266 | 23 | 6378 | 18 | 16.8 | 62.08 | 51.33 | 113.41 | 51.33 | 25.67 | 266 | 6378 | 1080 | 262.3562 | 0.36431 | -6.9016 | 1054.284 | 17.4564 | -81.8456 | 5.841 | 5.841 | 84.2884 | 264.2884 | 81.8383 | 0 | 0 | 43.8129 | 43.8129 | -1.9776 | 0% | 19.8122 | 0 | 0 | 158.5494 | 158.5494 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.6099 | 5.6099 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6379 | 19 | 15.3 | 0 | 9.78 | 9.78 | 9.78 | 4.89 | 266 | 6379 | 1140 | 262.3562 | 0.36431 | -6.9016 | 1114.284 | 18.4564 | -96.8456 | -4.4157 | 0 | 90.532 | 270.532 | 90.3762 | 0 | 0 | 8.3478 | 8.3478 | -14.2001 | 0% | 3.7749 | 0 | 0 | 145.5741 | 145.5741 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6380 | 20 | 14.9 | 0 | 0 | 0 | 0 | 0 | 266 | 6380 | 1200 | 262.3562 | 0.36431 | -6.9016 | 1174.284 | 19.4564 | -111.8456 | -14.4888 | 0 | 90.532 | 270.532 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.7756 | 138.7756 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6381 | 21 | 14.3 | 0 | 0 | 0 | 0 | 0 | 266 | 6381 | 1260 | 262.3562 | 0.36431 | -6.9016 | 1234.284 | 20.4564 | -126.8456 | -23.9552 | 0 | 90.532 | 270.532 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5224 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6382 | 22 | 14.1 | 0 | 0 | 0 | 0 | 0 | 266 | 6382 | 1320 | 262.3562 | 0.36431 | -6.9016 | 1294.284 | 21.4564 | -141.8456 | -32.2672 | 0 | 90.532 | 270.532 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.102 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6383 | 23 | 13.4 | 0 | 0 | 0 | 0 | 0 | 266 | 6383 | 1380 | 262.3562 | 0.36431 | -6.9016 | 1354.284 | 22.4564 | -156.8456 | -38.6834 | 0 | 90.532 | 270.532 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7348 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
9 | 266 | 23 | 6384 | 24 | 13.4 | 0 | 0 | 0 | 0 | 0 | 266 | 6384 | 1440 | 262.3562 | 0.36431 | -6.9016 | 1414.284 | 23.4564 | -171.8456 | -42.3189 | 0 | 90.532 | 270.532 | 90.3762 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3009 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6385 | 1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 267 | 6385 | 60 | 263.3425 | -0.032705 | -6.5872 | 34.284 | 0.46161 | 173.0758 | -42.863 | 0 | 89.9522 | 90.0478 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1641 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6386 | 2 | 12.6 | 0 | 0 | 0 | 0 | 0 | 267 | 6386 | 120 | 263.3425 | -0.032705 | -6.5872 | 94.284 | 1.4616 | 158.0758 | -39.4731 | 0 | 89.9522 | 90.0478 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5497 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6387 | 3 | 12.4 | 0 | 0 | 0 | 0 | 0 | 267 | 6387 | 180 | 263.3425 | -0.032705 | -6.5872 | 154.284 | 2.4616 | 143.0758 | -33.2222 | 0 | 89.9522 | 90.0478 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4781 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6388 | 4 | 12.5 | 0 | 0 | 0 | 0 | 0 | 267 | 6388 | 240 | 263.3425 | -0.032705 | -6.5872 | 214.284 | 3.4616 | 128.0758 | -25.0084 | 0 | 89.9522 | 90.0478 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3257 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6389 | 5 | 12.7 | 0 | 0 | 0 | 0 | 0 | 267 | 6389 | 300 | 263.3425 | -0.032705 | -6.5872 | 274.284 | 4.4616 | 113.0758 | -15.5948 | 0 | 89.9522 | 90.0478 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.3412 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6390 | 6 | 12.9 | 0 | 0 | 0 | 0 | 0 | 267 | 6390 | 360 | 263.3425 | -0.032705 | -6.5872 | 334.284 | 5.4616 | 98.0758 | -5.5447 | 0 | 89.9522 | 90.0478 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.7582 | 6.7582 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6391 | 7 | 12.9 | 0 | 1.47 | 1.47 | 1.47 | 0.74 | 267 | 6391 | 420 | 263.3425 | -0.032705 | -6.5872 | 394.284 | 6.4616 | 83.0758 | 4.7118 | 4.7118 | 84.9204 | 95.0796 | 83.0802 | 0 | 0 | 1.2547 | 1.2547 | -103.3802 | 0% | 0.56739 | 0 | 0 | 166.4291 | 166.4291 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6392 | 8 | 13.2 | 18.39 | 26.89 | 45.28 | 26.89 | 13.45 | 267 | 6392 | 480 | 263.3425 | -0.032705 | -6.5872 | 454.284 | 7.4616 | 68.0758 | 14.7904 | 14.7904 | 73.6316 | 106.3684 | 68.088 | 26.883 | 26.883 | 22.9521 | 49.8351 | -1.8053 | 0% | 22.5354 | 0 | 0 | 176.3651 | 176.3651 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6393 | 9 | 13.8 | 75.89 | 73.89 | 149.78 | 73.89 | 36.95 | 267 | 6393 | 540 | 263.3425 | -0.032705 | -6.5872 | 514.284 | 8.4616 | 53.0758 | 24.2676 | 24.2676 | 61.2729 | 118.7271 | 53.0978 | 110.8718 | 110.8718 | 63.0691 | 173.9409 | 0.064316 | 6.432% | 78.6561 | 5.0589 | 3.5412 | 162.4885 | 162.4885 | 2.179% | 11.57% | 11.57% | 80% | 9.252% | 7.2776 | 6.3002 | 6 | 43.6654 | 16.0937 | 26.87% | 26.87%
9 | 267 | 24 | 6394 | 10 | 14.7 | 127.36 | 113.56 | 240.92 | 113.56 | 56.78 | 267 | 6394 | 600 | 263.3425 | -0.032705 | -6.5872 | 574.284 | 9.4616 | 38.0758 | 32.5936 | 32.5936 | 47.0528 | 132.9472 | 38.1127 | 186.0238 | 186.0238 | 96.9295 | 282.9533 | 0.35654 | 35.65% | 127.9515 | 45.6195 | 31.9337 | 145.8814 | 145.8814 | 21.89% | 11.5% | 11.5% | 80% | 9.202% | 11.7743 | 6.0865 | 6 | 70.6459 | 26.0379 | 48.43% | 48.43%
9 | 267 | 24 | 6395 | 11 | 17.3 | 220.69 | 154.11 | 374.8 | 154.11 | 77.06 | 267 | 6395 | 660 | 263.3425 | -0.032705 | -6.5872 | 634.284 | 10.4616 | 23.0758 | 39.0218 | 39.0218 | 30.2981 | 149.7019 | 23.1431 | 322.308 | 322.308 | 131.5411 | 453.8491 | 0.53794 | 53.79% | 205.2306 | 110.4027 | 77.2819 | 150.3704 | 150.3704 | 51.39% | 11.4% | 11.4% | 85% | 9.693% | 19.8928 | 5.501 | 5.501 | 109.4293 | 43.9911 | 72.77% | 72.77%
9 | 267 | 24 | 6396 | 12 | 20.1 | 294.94 | 205.83 | 500.77 | 205.83 | 102.92 | 267 | 6396 | 720 | 263.3425 | -0.032705 | -6.5872 | 694.284 | 11.4616 | 8.0758 | 42.6579 | 42.6579 | 11.0127 | 168.9873 | 8.2751 | 430.7273 | 430.7273 | 175.6869 | 606.4142 | 0.61512 | 61.51% | 274.2205 | 168.6794 | 118.0756 | 151.5177 | 151.5177 | 77.93% | 11.35% | 11.35% | 90% | 10.22% | 28.0139 | 4.9233 | 4.9233 | 137.9214 | 61.9503 | 91.03% | 91.03%
9 | 267 | 24 | 6397 | 13 | 20.4 | 310.5 | 201.25 | 511.75 | 201.25 | 100.63 | 267 | 6397 | 780 | 263.3425 | -0.032705 | -6.5872 | 754.284 | 12.4616 | -6.9242 | 42.798 | 42.798 | 9.4566 | 189.4566 | 7.156 | 453.4503 | 453.4503 | 171.7776 | 625.2279 | 0.62186 | 62.19% | 282.7281 | 175.8176 | 123.0724 | 150.5222 | 150.5222 | 81.76% | 11.35% | 11.35% | 90% | 10.21% | 28.876 | 4.8647 | 4.8647 | 140.4724 | 63.8566 | 93.32% | 93.32%
9 | 267 | 24 | 6398 | 14 | 21.1 | 292.44 | 220.89 | 513.33 | 220.89 | 110.45 | 267 | 6398 | 840 | 263.3425 | -0.032705 | -6.5872 | 814.284 | 13.4616 | -21.9242 | 39.4113 | 39.4113 | 28.8993 | 208.8993 | 21.9954 | 427.0935 | 427.0935 | 188.5414 | 615.6349 | 0.62151 | 62.15% | 278.3901 | 173.0234 | 121.1164 | 151.1948 | 151.1948 | 80.11% | 11.34% | 11.34% | 90% | 10.21% | 28.4146 | 4.7303 | 4.7303 | 134.4101 | 62.8364 | 88.9% | 88.9%
9 | 267 | 24 | 6399 | 15 | 19.2 | 215.83 | 187.72 | 403.55 | 187.72 | 93.86 | 267 | 6399 | 900 | 263.3425 | -0.032705 | -6.5872 | 874.284 | 14.4616 | -36.9242 | 33.1653 | 33.1653 | 45.8623 | 225.8623 | 36.9626 | 315.2407 | 315.2407 | 160.229 | 475.4697 | 0.55893 | 55.89% | 215.0074 | 120.1744 | 84.1221 | 141.2539 | 141.2539 | 59.55% | 11.37% | 11.37% | 85% | 9.661% | 20.7726 | 5.103 | 5.103 | 106.0025 | 45.9367 | 75.04% | 75.04%
9 | 267 | 24 | 6400 | 16 | 19.6 | 220.61 | 152.08 | 372.69 | 152.08 | 76.04 | 267 | 6400 | 960 | 263.3425 | -0.032705 | -6.5872 | 934.284 | 15.4616 | -51.9242 | 24.9558 | 24.9558 | 60.2573 | 240.2573 | 51.9471 | 322.2928 | 322.2928 | 129.8084 | 452.1012 | 0.54822 | 54.82% | 204.4402 | 112.078 | 78.4546 | 139.3781 | 139.3781 | 56.29% | 11.36% | 11.36% | 85% | 9.656% | 19.7401 | 5.0224 | 5.0224 | 99.1437 | 43.6536 | 71.13% | 71.13%
9 | 267 | 24 | 6401 | 17 | 19.8 | 127.22 | 103.75 | 230.97 | 103.75 | 51.88 | 267 | 6401 | 1020 | 263.3425 | -0.032705 | -6.5872 | 994.284 | 16.4616 | -66.9242 | 15.5454 | 15.5454 | 72.7305 | 252.7305 | 66.937 | 185.9599 | 185.9599 | 88.5562 | 274.5161 | 0.38436 | 38.44% | 124.1362 | 47.713 | 33.3991 | 130.6283 | 130.6283 | 25.57% | 11.36% | 11.36% | 80% | 9.086% | 11.2793 | 4.9826 | 4.9826 | 56.2 | 24.9431 | 43.02% | 43.02%
9 | 267 | 24 | 6402 | 18 | 19.6 | 49.58 | 50.42 | 100 | 50.42 | 25.21 | 267 | 6402 | 1080 | 263.3425 | -0.032705 | -6.5872 | 1054.284 | 17.4616 | -81.9242 | 5.4968 | 5.4968 | 84.0744 | 264.0744 | 81.9291 | 0 | 0 | 43.0362 | 43.0362 | -1.883 | 0% | 19.461 | 0 | 0 | 162.0178 | 162.0178 | 0% | 11.37% | 0% | 80% | 0% | 0 | 5.0224 | 5.0224 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6403 | 19 | 17.8 | 0 | 10.83 | 10.83 | 10.83 | 5.42 | 267 | 6403 | 1140 | 263.3425 | -0.032705 | -6.5872 | 1114.284 | 18.4616 | -96.9242 | -4.7596 | 0 | 89.9522 | 269.9522 | 89.9662 | 0 | 0 | 9.244 | 9.244 | -12.1376 | 0% | 4.1801 | 0 | 0 | 149.2246 | 149.2246 | 0% | 11.45% | 0% | 80% | 0% | 0 | 5.3938 | 5.3938 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6404 | 20 | 16.7 | 0 | 0 | 0 | 0 | 0 | 267 | 6404 | 1200 | 263.3425 | -0.032705 | -6.5872 | 1174.284 | 19.4616 | -111.9242 | -14.8397 | 0 | 89.9522 | 269.9522 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.0181 | 141.0181 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6319 | 5.6319 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6405 | 21 | 16.3 | 0 | 0 | 0 | 0 | 0 | 267 | 6405 | 1260 | 263.3425 | -0.032705 | -6.5872 | 1234.284 | 20.4616 | -126.9242 | -24.3199 | 0 | 89.9522 | 269.9522 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.067 | 0 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6406 | 22 | 15.4 | 0 | 0 | 0 | 0 | 0 | 267 | 6406 | 1320 | 263.3425 | -0.032705 | -6.5872 | 1294.284 | 21.4616 | -141.9242 | -32.6502 | 0 | 89.9522 | 269.9522 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.7882 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6407 | 23 | 14.7 | 0 | 0 | 0 | 0 | 0 | 267 | 6407 | 1380 | 263.3425 | -0.032705 | -6.5872 | 1354.284 | 22.4616 | -156.9242 | -39.0832 | 0 | 89.9522 | 269.9522 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4786 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
9 | 267 | 24 | 6408 | 24 | 13.7 | 0 | 0 | 0 | 0 | 0 | 267 | 6408 | 1440 | 263.3425 | -0.032705 | -6.5872 | 1414.284 | 23.4616 | -171.9242 | -42.7227 | 0 | 89.9522 | 269.9522 | 89.9662 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6262 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6409 | 1 | 13.9 | 0 | 0 | 0 | 0 | 0 | 268 | 6409 | 60 | 264.3288 | -0.43035 | -6.271 | 34.284 | 0.46688 | 172.9967 | -43.2491 | 0 | 89.3716 | 90.6284 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1727 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6410 | 2 | 13.1 | 0 | 0 | 0 | 0 | 0 | 268 | 6410 | 120 | 264.3288 | -0.43035 | -6.271 | 94.284 | 1.4669 | 157.9967 | -39.8218 | 0 | 89.3716 | 90.6284 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7899 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6411 | 3 | 13.3 | 0 | 0 | 0 | 0 | 0 | 268 | 6411 | 180 | 264.3288 | -0.43035 | -6.271 | 154.284 | 2.4669 | 142.9967 | -33.5292 | 0 | 89.3716 | 90.6284 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8831 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6412 | 4 | 13.1 | 0 | 0 | 0 | 0 | 0 | 268 | 6412 | 240 | 264.3288 | -0.43035 | -6.271 | 214.284 | 3.4669 | 127.9967 | -25.2806 | 0 | 89.3716 | 90.6284 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1879 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6413 | 5 | 13.2 | 0 | 0 | 0 | 0 | 0 | 268 | 6413 | 300 | 264.3288 | -0.43035 | -6.271 | 274.284 | 4.4669 | 112.9967 | -15.8436 | 0 | 89.3716 | 90.6284 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.8155 | 5.8155 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6414 | 6 | 13.2 | 0 | 0 | 0 | 0 | 0 | 268 | 6414 | 360 | 264.3288 | -0.43035 | -6.271 | 334.284 | 5.4669 | 97.9967 | -5.7819 | 0 | 89.3716 | 90.6284 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 16.935 | 16.935 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6415 | 7 | 13.8 | 0 | 1.19 | 1.19 | 1.19 | 0.6 | 268 | 6415 | 420 | 264.3288 | -0.43035 | -6.271 | 394.284 | 6.4669 | 82.9967 | 4.4749 | 4.4749 | 84.5903 | 95.4097 | 83.0138 | 0 | 0 | 1.0157 | 1.0157 | -125.8649 | 0% | 0.45931 | 0 | 0 | 184.99 | 184.99 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6416 | 8 | 13.8 | 26.89 | 33.06 | 59.95 | 33.06 | 16.53 | 268 | 6416 | 480 | 264.3288 | -0.43035 | -6.271 | 454.284 | 7.4669 | 67.9967 | 14.5424 | 14.5424 | 73.3001 | 106.6999 | 68.0229 | 40.077 | 40.077 | 28.2185 | 68.2955 | -1.0799 | 0% | 30.8832 | 0 | 0 | 198.1636 | 198.1636 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6417 | 9 | 14 | 122 | 74.5 | 196.5 | 74.5 | 37.25 | 268 | 6417 | 540 | 264.3288 | -0.43035 | -6.271 | 514.284 | 8.4669 | 52.9967 | 23.9968 | 23.9968 | 60.9423 | 119.0577 | 53.0355 | 180.3879 | 180.3879 | 63.5897 | 243.9776 | 0.27852 | 27.85% | 110.3267 | 30.7285 | 21.5099 | 185.6133 | 185.6133 | 11.59% | 11.54% | 11.54% | 80% | 9.228% | 10.1814 | 6.2522 | 6 | 61.0883 | 22.5152 | 32.91% | 32.91%
9 | 268 | 25 | 6418 | 10 | 16.8 | 256.39 | 104.86 | 361.25 | 104.86 | 52.43 | 268 | 6418 | 600 | 264.3288 | -0.43035 | -6.271 | 574.284 | 9.4669 | 37.9967 | 32.2888 | 32.2888 | 46.736 | 133.264 | 38.0558 | 377.9286 | 377.9286 | 89.5036 | 467.4322 | 0.54328 | 54.33% | 211.3728 | 114.8345 | 80.3841 | 173.9334 | 173.9334 | 46.22% | 11.41% | 11.41% | 85% | 9.699% | 20.501 | 5.6099 | 5.6099 | 115.0079 | 45.336 | 66.12% | 66.12%
9 | 268 | 25 | 6419 | 11 | 17.3 | 362.44 | 130.42 | 492.86 | 130.42 | 65.21 | 268 | 6419 | 660 | 264.3288 | -0.43035 | -6.271 | 634.284 | 10.4669 | 22.9967 | 38.6756 | 38.6756 | 30.0271 | 149.9729 | 23.0995 | 533.4864 | 533.4864 | 111.3204 | 644.8068 | 0.61674 | 61.67% | 291.5816 | 179.8289 | 125.8802 | 171.2709 | 171.2709 | 73.5% | 11.38% | 11.38% | 90% | 10.24% | 29.8508 | 5.501 | 5.501 | 164.2079 | 66.0124 | 95.88% | 95.88%
9 | 268 | 25 | 6420 | 12 | 20.4 | 401.11 | 155.22 | 556.33 | 155.22 | 77.61 | 268 | 6420 | 720 | 264.3288 | -0.43035 | -6.271 | 694.284 | 11.4669 | 7.9967 | 42.2739 | 42.2739 | 10.8365 | 169.1635 | 8.2951 | 590.0525 | 590.0525 | 132.4886 | 722.541 | 0.64639 | 64.64% | 326.733 | 211.1977 | 147.8384 | 165.0118 | 165.0118 | 89.59% | 11.35% | 11.35% | 90% | 10.22% | 33.3767 | 4.8647 | 4.8647 | 162.3667 | 73.8095 | 98.4% | 98.4%
9 | 268 | 25 | 6421 | 13 | 20.4 | 403 | 159.58 | 562.58 | 159.58 | 79.79 | 268 | 6421 | 780 | 264.3288 | -0.43035 | -6.271 | 754.284 | 12.4669 | -7.0033 | 42.394 | 42.394 | 9.5024 | 189.5024 | 7.3423 | 592.8221 | 592.8221 | 136.2101 | 729.0321 | 0.6478 | 64.78% | 329.6683 | 213.5576 | 149.4903 | 162.078 | 162.078 | 92.23% | 11.35% | 11.35% | 90% | 10.22% | 33.6769 | 4.8647 | 4.8647 | 163.8274 | 74.4735 | 101.1% | 101.1%
9 | 268 | 25 | 6422 | 14 | 21.1 | 431.06 | 165.33 | 596.39 | 165.33 | 82.67 | 268 | 6422 | 840 | 264.3288 | -0.43035 | -6.271 | 814.284 | 13.4669 | -22.0033 | 39.0099 | 39.0099 | 28.8259 | 208.8259 | 22.1109 | 634.4516 | 634.4516 | 141.118 | 775.5696 | 0.65915 | 65.91% | 350.7126 | 231.1707 | 161.8195 | 163.4349 | 163.4349 | 99.01% | 11.35% | 11.35% | 90% | 10.22% | 35.8269 | 4.7303 | 4.7303 | 169.4727 | 79.2281 | 103.7% | 103.7%
9 | 268 | 25 | 6423 | 15 | 21.3 | 390.33 | 136.33 | 526.66 | 136.33 | 68.17 | 268 | 6423 | 900 | 264.3288 | -0.43035 | -6.271 | 874.284 | 14.4669 | -37.0033 | 32.78 | 32.78 | 45.7118 | 225.7118 | 37.0641 | 575.2856 | 575.2856 | 116.3649 | 691.6505 | 0.6422 | 64.22% | 312.7644 | 200.858 | 140.6006 | 157.8458 | 157.8458 | 89.07% | 11.34% | 11.34% | 90% | 10.21% | 31.9327 | 4.6926 | 4.6926 | 149.846 | 70.6163 | 94.93% | 94.93%
9 | 268 | 25 | 6424 | 16 | 21 | 317.83 | 122.28 | 440.11 | 122.28 | 61.14 | 268 | 6424 | 960 | 264.3288 | -0.43035 | -6.271 | 934.284 | 15.4669 | -52.0033 | 24.589 | 24.589 | 60.0672 | 240.0672 | 52.043 | 469.8029 | 469.8029 | 104.3725 | 574.1754 | 0.60796 | 60.8% | 259.6421 | 157.8512 | 110.4958 | 151.9057 | 151.9057 | 72.74% | 11.34% | 11.34% | 90% | 10.21% | 26.4981 | 4.7493 | 4.7493 | 125.8474 | 58.5982 | 82.85% | 82.85%
9 | 268 | 25 | 6425 | 17 | 20.3 | 163 | 81.89 | 244.89 | 81.89 | 40.95 | 268 | 6425 | 1020 | 264.3288 | -0.43035 | -6.271 | 994.284 | 16.4669 | -67.0033 | 15.1927 | 15.1927 | 72.5231 | 252.5231 | 67.0301 | 242.7254 | 242.7254 | 69.8975 | 312.6229 | 0.43903 | 43.9% | 141.3681 | 62.0649 | 43.4454 | 138.1702 | 138.1702 | 31.44% | 11.34% | 11.34% | 85% | 9.642% | 13.6312 | 4.8842 | 4.8842 | 66.577 | 30.1442 | 48.18% | 48.18%
9 | 268 | 25 | 6426 | 18 | 19.3 | 70.06 | 40.14 | 110.2 | 40.14 | 20.07 | 268 | 6426 | 1080 | 264.3288 | -0.43035 | -6.271 | 1054.284 | 17.4669 | -82.0033 | 5.1518 | 5.1518 | 83.8606 | 263.8606 | 82.0208 | 0 | 0 | 34.2616 | 34.2616 | -2.5905 | 0% | 15.4931 | 0 | 0 | 166.7117 | 166.7117 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0828 | 5.0828 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6427 | 19 | 18.3 | 0 | 9.67 | 9.67 | 9.67 | 4.84 | 268 | 6427 | 1140 | 264.3288 | -0.43035 | -6.271 | 1114.284 | 18.4669 | -97.0033 | -5.1043 | 0 | 89.3716 | 269.3716 | 89.5556 | 0 | 0 | 8.2539 | 8.2539 | -13.5552 | 0% | 3.7324 | 0 | 0 | 152.7244 | 152.7244 | 0% | 11.43% | 0% | 80% | 0% | 0 | 5.2884 | 5.2884 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6428 | 20 | 17.6 | 0 | 0 | 0 | 0 | 0 | 268 | 6428 | 1200 | 264.3288 | -0.43035 | -6.271 | 1174.284 | 19.4669 | -112.0033 | -15.1913 | 0 | 89.3716 | 269.3716 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.3239 | 143.3239 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6429 | 21 | 14.5 | 0 | 0 | 0 | 0 | 0 | 268 | 6429 | 1260 | 264.3288 | -0.43035 | -6.271 | 1234.284 | 20.4669 | -127.0033 | -24.6852 | 0 | 89.3716 | 269.3716 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3066 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6430 | 22 | 13.5 | 0 | 0 | 0 | 0 | 0 | 268 | 6430 | 1320 | 264.3288 | -0.43035 | -6.271 | 1294.284 | 21.4669 | -142.0033 | -33.0338 | 0 | 89.3716 | 269.3716 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5882 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6431 | 23 | 12.8 | 0 | 0 | 0 | 0 | 0 | 268 | 6431 | 1380 | 264.3288 | -0.43035 | -6.271 | 1354.284 | 22.4669 | -157.0033 | -39.4836 | 0 | 89.3716 | 269.3716 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.053 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
9 | 268 | 25 | 6432 | 24 | 12.1 | 0 | 0 | 0 | 0 | 0 | 268 | 6432 | 1440 | 264.3288 | -0.43035 | -6.271 | 1414.284 | 23.4669 | -172.0033 | -43.1273 | 0 | 89.3716 | 269.3716 | 89.5556 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5179 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6433 | 1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 269 | 6433 | 60 | 265.3151 | -0.82852 | -5.9532 | 34.284 | 0.47218 | 172.9173 | -43.6354 | 0 | 88.7901 | 91.2099 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.0853 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6434 | 2 | 11.3 | 0 | 0 | 0 | 0 | 0 | 269 | 6434 | 120 | 265.3151 | -0.82852 | -5.9532 | 94.284 | 1.4722 | 157.9173 | -40.1702 | 0 | 88.7901 | 91.2099 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.4061 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6435 | 3 | 11.2 | 0 | 0 | 0 | 0 | 0 | 269 | 6435 | 180 | 265.3151 | -0.82852 | -5.9532 | 154.284 | 2.4722 | 142.9173 | -33.8356 | 0 | 88.7901 | 91.2099 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9649 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6436 | 4 | 10.8 | 0 | 0 | 0 | 0 | 0 | 269 | 6436 | 240 | 265.3151 | -0.82852 | -5.9532 | 214.284 | 3.4722 | 127.9173 | -25.5523 | 0 | 88.7901 | 91.2099 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5745 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6437 | 5 | 10.7 | 0 | 0 | 0 | 0 | 0 | 269 | 6437 | 300 | 265.3151 | -0.82852 | -5.9532 | 274.284 | 4.4722 | 112.9173 | -16.0921 | 0 | 88.7901 | 91.2099 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.4746 | 3.4746 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6438 | 6 | 10.7 | 0 | 0 | 0 | 0 | 0 | 269 | 6438 | 360 | 265.3151 | -0.82852 | -5.9532 | 334.284 | 5.4722 | 97.9173 | -6.019 | 0 | 88.7901 | 91.2099 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 13.4229 | 13.4229 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6439 | 7 | 10.7 | 0 | 1.11 | 1.11 | 1.11 | 0.56 | 269 | 6439 | 420 | 265.3151 | -0.82852 | -5.9532 | 394.284 | 6.4722 | 82.9173 | 4.2377 | 4.2377 | 84.2598 | 95.7402 | 82.9474 | 0 | 0 | 0.94744 | 0.94744 | -142.5356 | 0% | 0.42843 | 0 | 0 | 178.2977 | 178.2977 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6440 | 8 | 11.4 | 30.42 | 28.61 | 59.03 | 28.61 | 14.31 | 269 | 6440 | 480 | 265.3151 | -0.82852 | -5.9532 | 454.284 | 7.4722 | 67.9173 | 14.2937 | 14.2937 | 72.9687 | 107.0313 | 67.9587 | 46.2382 | 46.2382 | 24.4202 | 70.6583 | -1.095 | 0% | 31.9517 | 0 | 0 | 191.661 | 191.661 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6441 | 9 | 11.8 | 119.5 | 64.58 | 184.08 | 64.58 | 32.29 | 269 | 6441 | 540 | 265.3151 | -0.82852 | -5.9532 | 514.284 | 8.4722 | 52.9173 | 23.725 | 23.725 | 60.6125 | 119.3875 | 52.9749 | 178.847 | 178.847 | 55.1225 | 233.9695 | 0.23445 | 23.45% | 105.801 | 24.8056 | 17.3639 | 178.3549 | 178.3549 | 9.736% | 11.61% | 11.61% | 80% | 9.286% | 9.8245 | 6.7954 | 6 | 58.947 | 21.726 | 33.05% | 33.05%
9 | 269 | 26 | 6442 | 10 | 12.3 | 223.47 | 116.72 | 340.19 | 116.72 | 58.36 | 269 | 6442 | 600 | 265.3151 | -0.82852 | -5.9532 | 574.284 | 9.4722 | 37.9173 | 31.9829 | 31.9829 | 46.4208 | 133.5792 | 38.0022 | 332.4581 | 332.4581 | 99.6268 | 432.0849 | 0.49827 | 49.83% | 195.3888 | 97.3559 | 68.1491 | 162.4277 | 162.4277 | 41.96% | 11.51% | 11.51% | 85% | 9.782% | 19.1122 | 6.669 | 6 | 114.6734 | 42.265 | 70.6% | 70.6%
9 | 269 | 26 | 6443 | 11 | 12.9 | 295.42 | 156.67 | 452.09 | 156.67 | 78.34 | 269 | 6443 | 660 | 265.3151 | -0.82852 | -5.9532 | 634.284 | 10.4722 | 22.9173 | 38.3285 | 38.3285 | 29.758 | 150.242 | 23.0623 | 438.2835 | 438.2835 | 133.7262 | 572.0097 | 0.57547 | 57.55% | 258.6628 | 148.8522 | 104.1966 | 159.704 | 159.704 | 65.24% | 11.44% | 11.44% | 90% | 10.3% | 26.6343 | 6.5196 | 6 | 159.8059 | 58.8994 | 100.1% | 100.1%
9 | 269 | 26 | 6444 | 12 | 13.3 | 335.56 | 166.53 | 502.09 | 166.53 | 83.27 | 269 | 6444 | 720 | 265.3151 | -0.82852 | -5.9532 | 694.284 | 11.4722 | 7.9173 | 41.8891 | 41.8891 | 10.6618 | 169.3382 | 8.3344 | 497.26 | 497.26 | 142.1422 | 639.4022 | 0.60099 | 60.1% | 289.1377 | 173.7689 | 121.6382 | 149.8954 | 149.8954 | 81.15% | 11.41% | 11.41% | 90% | 10.27% | 29.6946 | 6.4214 | 6 | 178.1677 | 65.667 | 118.9% | 118.9%
9 | 269 | 26 | 6445 | 13 | 14.7 | 316.72 | 173 | 489.72 | 173 | 86.5 | 269 | 6445 | 780 | 265.3151 | -0.82852 | -5.9532 | 754.284 | 12.4722 | -7.0827 | 41.9894 | 41.9894 | 9.548 | 189.548 | 7.5463 | 469.3276 | 469.3276 | 147.6647 | 616.9923 | 0.59879 | 59.88% | 279.0039 | 167.0657 | 116.946 | 147.8755 | 147.8755 | 79.08% | 11.41% | 11.41% | 90% | 10.26% | 28.6392 | 6.0865 | 6 | 171.8354 | 63.3331 | 116.2% | 116.2%
9 | 269 | 26 | 6446 | 14 | 14.2 | 275.97 | 132.72 | 408.69 | 132.72 | 66.36 | 269 | 6446 | 840 | 265.3151 | -0.82852 | -5.9532 | 814.284 | 13.4722 | -22.0827 | 38.6078 | 38.6078 | 28.7536 | 208.7536 | 22.2333 | 409.3869 | 409.3869 | 113.2836 | 522.6705 | 0.55958 | 55.96% | 236.3516 | 132.2587 | 92.5811 | 141.6938 | 141.6938 | 65.34% | 11.44% | 11.44% | 90% | 10.3% | 24.3358 | 6.2045 | 6 | 146.0145 | 53.8164 | 103% | 103%
9 | 269 | 26 | 6447 | 15 | 13.8 | 223.33 | 104.94 | 328.27 | 104.94 | 52.47 | 269 | 6447 | 900 | 265.3151 | -0.82852 | -5.9532 | 874.284 | 14.4722 | -37.0827 | 32.3939 | 32.3939 | 45.5626 | 225.5626 | 37.1697 | 332.1785 | 332.1785 | 89.5719 | 421.7504 | 0.49894 | 49.89% | 190.7155 | 95.1547 | 66.6083 | 134.1493 | 134.1493 | 49.65% | 11.48% | 11.48% | 85% | 9.759% | 18.6116 | 6.3002 | 6 | 111.6697 | 41.1579 | 83.24% | 83.24%
9 | 269 | 26 | 6448 | 16 | 13.6 | 139.17 | 122.5 | 261.67 | 122.5 | 61.25 | 269 | 6448 | 960 | 265.3151 | -0.82852 | -5.9532 | 934.284 | 15.4722 | -52.0827 | 24.2212 | 24.2212 | 59.8782 | 239.8782 | 52.1414 | 208.1861 | 208.1861 | 104.5603 | 312.7464 | 0.39115 | 39.11% | 141.4239 | 55.3175 | 38.7223 | 128.4433 | 128.4433 | 30.15% | 11.52% | 11.52% | 85% | 9.795% | 13.8525 | 6.3484 | 6 | 83.1147 | 30.6335 | 64.71% | 64.71%
9 | 269 | 26 | 6449 | 17 | 12.7 | 36.39 | 75.83 | 112.22 | 75.83 | 37.92 | 269 | 6449 | 1020 | 265.3151 | -0.82852 | -5.9532 | 994.284 | 16.4722 | -67.0827 | 14.8393 | 14.8393 | 72.3162 | 252.3162 | 67.1248 | 55.2334 | 55.2334 | 64.725 | 119.9583 | -0.28956 | 0% | 54.2451 | 0 | 0 | 158.3464 | 158.3464 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6450 | 18 | 11.2 | 18.83 | 53.39 | 72.22 | 53.39 | 26.7 | 269 | 6450 | 1080 | 265.3151 | -0.82852 | -5.9532 | 1054.284 | 17.4722 | -82.0827 | 4.8061 | 4.8061 | 83.6469 | 263.6469 | 82.1133 | 0 | 0 | 45.5712 | 45.5712 | -2.1506 | 0% | 20.6073 | 0 | 0 | 149.8478 | 149.8478 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6451 | 19 | 10.7 | 0 | 8.75 | 8.75 | 8.75 | 4.38 | 269 | 6451 | 1140 | 265.3151 | -0.82852 | -5.9532 | 1114.284 | 18.4722 | -97.0827 | -5.4495 | 0 | 88.7901 | 268.7901 | 89.1445 | 0 | 0 | 7.4686 | 7.4686 | -17.3797 | 0% | 3.3773 | 0 | 0 | 141.5715 | 141.5715 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6452 | 20 | 10.2 | 0 | 0 | 0 | 0 | 0 | 269 | 6452 | 1200 | 265.3151 | -0.82852 | -5.9532 | 1174.284 | 19.4722 | -112.0827 | -15.5433 | 0 | 88.7901 | 268.7901 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.3186 | 134.3186 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6453 | 21 | 9.9 | 0 | 0 | 0 | 0 | 0 | 269 | 6453 | 1260 | 265.3151 | -0.82852 | -5.9532 | 1234.284 | 20.4722 | -127.0827 | -25.0508 | 0 | 88.7901 | 268.7901 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5704 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6454 | 22 | 9.8 | 0 | 0 | 0 | 0 | 0 | 269 | 6454 | 1320 | 265.3151 | -0.82852 | -5.9532 | 1294.284 | 21.4722 | -142.0827 | -33.4178 | 0 | 88.7901 | 268.7901 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.0665 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6455 | 23 | 9.3 | 0 | 0 | 0 | 0 | 0 | 269 | 6455 | 1380 | 265.3151 | -0.82852 | -5.9532 | 1354.284 | 22.4722 | -157.0827 | -39.8846 | 0 | 88.7901 | 268.7901 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2349 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
9 | 269 | 26 | 6456 | 24 | 9.2 | 0 | 0 | 0 | 0 | 0 | 269 | 6456 | 1440 | 265.3151 | -0.82852 | -5.9532 | 1414.284 | 23.4722 | -172.0827 | -43.5324 | 0 | 88.7901 | 268.7901 | 89.1445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7937 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6457 | 1 | 9.2 | 0 | 0 | 0 | 0 | 0 | 270 | 6457 | 60 | 266.3014 | -1.2271 | -5.6344 | 34.284 | 0.47749 | 172.8376 | -44.0218 | 0 | 88.208 | 91.792 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.341 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6458 | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 270 | 6458 | 120 | 266.3014 | -1.2271 | -5.6344 | 94.284 | 1.4775 | 157.8376 | -40.5183 | 0 | 88.208 | 91.792 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2422 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6459 | 3 | 8.8 | 0 | 0 | 0 | 0 | 0 | 270 | 6459 | 180 | 266.3014 | -1.2271 | -5.6344 | 154.284 | 2.4775 | 142.8376 | -34.1414 | 0 | 88.208 | 91.792 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1434 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6460 | 4 | 8.5 | 0 | 0 | 0 | 0 | 0 | 270 | 6460 | 240 | 266.3014 | -1.2271 | -5.6344 | 214.284 | 3.4775 | 127.8376 | -25.8234 | 0 | 88.208 | 91.792 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6006 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6461 | 5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 270 | 6461 | 300 | 266.3014 | -1.2271 | -5.6344 | 274.284 | 4.4775 | 112.8376 | -16.3402 | 0 | 88.208 | 91.792 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.028 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6462 | 6 | 8.3 | 0 | 0 | 0 | 0 | 0 | 270 | 6462 | 360 | 266.3014 | -1.2271 | -5.6344 | 334.284 | 5.4775 | 97.8376 | -6.256 | 0 | 88.208 | 91.792 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.7418 | 4.7418 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6463 | 7 | 8.2 | 0 | 0 | 0 | 0 | 0 | 270 | 6463 | 420 | 266.3014 | -1.2271 | -5.6344 | 394.284 | 6.4775 | 82.8376 | 4.0003 | 4.0003 | 83.9291 | 96.0709 | 82.8811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 164.7923 | 164.7923 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6464 | 8 | 8.2 | 8.94 | 25.97 | 34.91 | 25.97 | 12.99 | 270 | 6464 | 480 | 266.3014 | -1.2271 | -5.6344 | 454.284 | 7.4775 | 67.8376 | 14.0445 | 14.0445 | 72.6376 | 107.3624 | 67.8953 | 13.8627 | 13.8627 | 22.1668 | 36.0295 | -3.1278 | 0% | 16.2925 | 0 | 0 | 173.3465 | 173.3465 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6465 | 9 | 8.8 | 68.19 | 71.81 | 140 | 71.81 | 35.91 | 270 | 6465 | 540 | 266.3014 | -1.2271 | -5.6344 | 514.284 | 8.4775 | 52.8376 | 23.4524 | 23.4524 | 60.2835 | 119.7165 | 52.9162 | 103.3132 | 103.3132 | 61.2937 | 164.6069 | -0.048025 | 0% | 74.4352 | 0 | 0 | 159.7526 | 159.7526 | 0% | 11.74% | 11.74% | 80% | 9.395% | 6.993 | 7.5907 | 6 | 41.9579 | 15.4644 | 26.26% | 26.26%
9 | 270 | 27 | 6466 | 10 | 9.1 | 155.97 | 106.89 | 262.86 | 106.89 | 53.45 | 270 | 6466 | 600 | 266.3014 | -1.2271 | -5.6344 | 574.284 | 9.4775 | 37.8376 | 31.676 | 31.676 | 46.1071 | 133.8929 | 37.9519 | 234.209 | 234.209 | 91.2363 | 325.4453 | 0.37522 | 37.52% | 147.1664 | 55.2198 | 38.6538 | 143.5719 | 143.5719 | 26.92% | 11.64% | 11.64% | 85% | 9.891% | 14.5563 | 7.5083 | 6 | 87.3375 | 32.1899 | 60.83% | 60.83%
9 | 270 | 27 | 6467 | 11 | 9.4 | 18.06 | 136.53 | 154.59 | 136.53 | 68.27 | 270 | 6467 | 660 | 266.3014 | -1.2271 | -5.6344 | 634.284 | 10.4775 | 22.8376 | 37.9804 | 37.9804 | 29.491 | 150.509 | 23.0316 | 27.0078 | 27.0078 | 116.5356 | 143.5435 | -0.16324 | 0% | 64.9104 | 0 | 0 | 153.7872 | 153.7872 | 0% | 11.73% | 11.73% | 80% | 9.388% | 6.0936 | 7.4266 | 6 | 36.5618 | 13.4755 | 23.77% | 23.77%
9 | 270 | 27 | 6468 | 12 | 9.4 | 293.75 | 142.36 | 436.11 | 142.36 | 71.18 | 270 | 6468 | 720 | 266.3014 | -1.2271 | -5.6344 | 694.284 | 11.4775 | 7.8376 | 41.5037 | 41.5037 | 10.4888 | 169.5112 | 8.393 | 438.5357 | 438.5357 | 121.5119 | 560.0476 | 0.55609 | 55.61% | 253.2535 | 140.832 | 98.5824 | 136.4192 | 136.4192 | 72.26% | 11.49% | 11.49% | 90% | 10.34% | 26.1933 | 7.4266 | 6 | 157.1596 | 57.9241 | 115.2% | 115.2%
9 | 270 | 27 | 6469 | 13 | 10.4 | 299.17 | 158.75 | 457.92 | 158.75 | 79.38 | 270 | 6469 | 780 | 266.3014 | -1.2271 | -5.6344 | 754.284 | 12.4775 | -7.1624 | 41.5844 | 41.5844 | 9.5933 | 189.5933 | 7.7664 | 446.6114 | 446.6114 | 135.5016 | 582.113 | 0.5695 | 56.95% | 263.2315 | 149.9107 | 104.9375 | 136.764 | 136.764 | 76.73% | 11.47% | 11.47% | 90% | 10.32% | 27.1664 | 7.1587 | 6 | 162.9983 | 60.076 | 119.2% | 119.2%
9 | 270 | 27 | 6470 | 14 | 10.2 | 276.89 | 157.92 | 434.81 | 157.92 | 78.96 | 270 | 6470 | 840 | 266.3014 | -1.2271 | -5.6344 | 814.284 | 13.4775 | -22.1624 | 38.2052 | 38.2052 | 28.6823 | 208.6823 | 22.3624 | 414.0258 | 414.0258 | 134.7932 | 548.8189 | 0.55443 | 55.44% | 248.1759 | 137.5953 | 96.3167 | 134.7661 | 134.7661 | 71.47% | 11.49% | 11.49% | 90% | 10.34% | 25.658 | 7.2117 | 6 | 153.9482 | 56.7405 | 114.2% | 114.2%
9 | 270 | 27 | 6471 | 15 | 10.5 | 256.25 | 164.31 | 420.56 | 164.31 | 82.16 | 270 | 6471 | 900 | 266.3014 | -1.2271 | -5.6344 | 874.284 | 14.4775 | -37.1624 | 32.0072 | 32.0072 | 45.4147 | 225.4147 | 37.279 | 384.6923 | 384.6923 | 140.2474 | 524.9396 | 0.54441 | 54.44% | 237.3777 | 129.2296 | 90.4607 | 132.539 | 132.539 | 68.25% | 11.5% | 11.5% | 90% | 10.35% | 24.5594 | 7.1323 | 6 | 147.3567 | 54.311 | 111.2% | 111.2%
9 | 270 | 27 | 6472 | 16 | 10.2 | 190.78 | 101.39 | 292.17 | 101.39 | 50.7 | 270 | 6472 | 960 | 266.3014 | -1.2271 | -5.6344 | 934.284 | 15.4775 | -52.1624 | 23.8528 | 23.8528 | 59.6902 | 239.6902 | 52.2422 | 288.879 | 288.879 | 86.5418 | 375.4207 | 0.43915 | 43.92% | 169.7653 | 74.5531 | 52.1872 | 124.9198 | 124.9198 | 41.78% | 11.58% | 11.58% | 85% | 9.844% | 16.7112 | 7.2117 | 6 | 100.2673 | 36.9554 | 80.27% | 80.27%
9 | 270 | 27 | 6473 | 17 | 10.8 | 118.28 | 55.78 | 174.06 | 55.78 | 27.89 | 270 | 6473 | 1020 | 266.3014 | -1.2271 | -5.6344 | 994.284 | 16.4775 | -67.1624 | 14.4851 | 14.4851 | 72.11 | 252.11 | 67.2209 | 183.0881 | 183.0881 | 47.6112 | 230.6994 | 0.21634 | 21.63% | 104.3222 | 22.5686 | 15.798 | 117.9725 | 117.9725 | 13.39% | 11.64% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6474 | 18 | 10.6 | 38.28 | 32.72 | 71 | 32.72 | 16.36 | 270 | 6474 | 1080 | 266.3014 | -1.2271 | -5.6344 | 1054.284 | 17.4775 | -82.1624 | 4.4598 | 4.4598 | 83.4333 | 263.4333 | 82.2064 | 0 | 0 | 27.9283 | 27.9283 | -4.067 | 0% | 12.6292 | 0 | 0 | 150.5403 | 150.5403 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6475 | 19 | 9.5 | 0 | 8.42 | 8.42 | 8.42 | 4.21 | 270 | 6475 | 1140 | 266.3014 | -1.2271 | -5.6344 | 1114.284 | 18.4775 | -97.1624 | -5.7951 | 0 | 88.208 | 268.208 | 88.733 | 0 | 0 | 7.1869 | 7.1869 | -18.482 | 0% | 3.2499 | 0 | 0 | 140.6091 | 140.6091 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6476 | 20 | 9.5 | 0 | 0 | 0 | 0 | 0 | 270 | 6476 | 1200 | 266.3014 | -1.2271 | -5.6344 | 1174.284 | 19.4775 | -112.1624 | -15.8956 | 0 | 88.208 | 268.208 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.5493 | 134.5493 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6477 | 21 | 9.6 | 0 | 0 | 0 | 0 | 0 | 270 | 6477 | 1260 | 266.3014 | -1.2271 | -5.6344 | 1234.284 | 20.4775 | -127.1624 | -25.4167 | 0 | 88.208 | 268.208 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6753 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6478 | 22 | 9.1 | 0 | 0 | 0 | 0 | 0 | 270 | 6478 | 1320 | 266.3014 | -1.2271 | -5.6344 | 1294.284 | 21.4775 | -142.1624 | -33.802 | 0 | 88.208 | 268.208 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7042 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6479 | 23 | 9 | 0 | 0 | 0 | 0 | 0 | 270 | 6479 | 1380 | 266.3014 | -1.2271 | -5.6344 | 1354.284 | 22.4775 | -157.1624 | -40.286 | 0 | 88.208 | 268.208 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.453 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
9 | 270 | 27 | 6480 | 24 | 8.9 | 0 | 0 | 0 | 0 | 0 | 270 | 6480 | 1440 | 266.3014 | -1.2271 | -5.6344 | 1414.284 | 23.4775 | -172.1624 | -43.938 | 0 | 88.208 | 268.208 | 88.733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2018 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6481 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 271 | 6481 | 60 | 267.2877 | -1.6259 | -5.3148 | 34.284 | 0.48282 | 172.7577 | -44.4083 | 0 | 87.6254 | 92.3746 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7909 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6482 | 2 | 6.9 | 0 | 0 | 0 | 0 | 0 | 271 | 6482 | 120 | 267.2877 | -1.6259 | -5.3148 | 94.284 | 1.4828 | 157.7577 | -40.8659 | 0 | 87.6254 | 92.3746 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8732 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6483 | 3 | 6.1 | 0 | 0 | 0 | 0 | 0 | 271 | 6483 | 180 | 267.2877 | -1.6259 | -5.3148 | 154.284 | 2.4828 | 142.7577 | -34.4465 | 0 | 87.6254 | 92.3746 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4984 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6484 | 4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 271 | 6484 | 240 | 267.2877 | -1.6259 | -5.3148 | 214.284 | 3.4828 | 127.7577 | -26.0939 | 0 | 87.6254 | 92.3746 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5652 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6485 | 5 | 4.8 | 0 | 0 | 0 | 0 | 0 | 271 | 6485 | 300 | 267.2877 | -1.6259 | -5.3148 | 274.284 | 4.4828 | 112.7577 | -16.5878 | 0 | 87.6254 | 92.3746 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.3067 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6486 | 6 | 4.1 | 0 | 0 | 0 | 0 | 0 | 271 | 6486 | 360 | 267.2877 | -1.6259 | -5.3148 | 334.284 | 5.4828 | 97.7577 | -6.4929 | 0 | 87.6254 | 92.3746 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 6.344 | 6.344 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6487 | 7 | 3.7 | 0 | 0 | 0 | 0 | 0 | 271 | 6487 | 420 | 267.2877 | -1.6259 | -5.3148 | 394.284 | 6.4828 | 82.7577 | 3.7626 | 3.7626 | 83.5982 | 96.4018 | 82.815 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 171.7833 | 171.7833 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6488 | 8 | 5.9 | 19.67 | 25.14 | 44.81 | 25.14 | 12.57 | 271 | 6488 | 480 | 267.2877 | -1.6259 | -5.3148 | 454.284 | 7.4828 | 67.7577 | 13.7947 | 13.7947 | 72.3068 | 107.6932 | 67.8329 | 31.1256 | 31.1256 | 21.4583 | 52.5839 | -1.9939 | 0% | 23.7785 | 0 | 0 | 187.1712 | 187.1712 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6489 | 9 | 8.8 | 89.58 | 68.47 | 158.05 | 68.47 | 34.24 | 271 | 6489 | 540 | 267.2877 | -1.6259 | -5.3148 | 514.284 | 8.4828 | 52.7577 | 23.179 | 23.179 | 59.9556 | 120.0444 | 52.8595 | 137.4115 | 137.4115 | 58.4428 | 195.8543 | 0.087911 | 8.791% | 88.5653 | 7.7859 | 5.4501 | 177.5129 | 177.5129 | 3.07% | 11.72% | 11.72% | 80% | 9.379% | 8.3068 | 7.5907 | 6 | 49.841 | 18.3698 | 28.08% | 28.08%
9 | 271 | 28 | 6490 | 10 | 11.5 | 229.86 | 96.81 | 326.67 | 96.81 | 48.41 | 271 | 6490 | 600 | 267.2877 | -1.6259 | -5.3148 | 574.284 | 9.4828 | 37.7577 | 31.3681 | 31.3681 | 45.7952 | 134.2048 | 37.9052 | 348.4225 | 348.4225 | 82.6325 | 431.055 | 0.49325 | 49.33% | 194.9231 | 96.1459 | 67.3021 | 166.4827 | 166.4827 | 40.43% | 11.52% | 11.52% | 85% | 9.796% | 19.0943 | 6.8721 | 6 | 114.5658 | 42.2253 | 68.82% | 68.82%
9 | 271 | 28 | 6491 | 11 | 12.5 | 276.61 | 113.28 | 389.89 | 113.28 | 56.64 | 271 | 6491 | 660 | 267.2877 | -1.6259 | -5.3148 | 634.284 | 10.4828 | 22.7577 | 37.6316 | 37.6316 | 29.2263 | 150.7737 | 23.0075 | 416.9903 | 416.9903 | 96.6905 | 513.6808 | 0.54773 | 54.77% | 232.2865 | 127.2299 | 89.0609 | 161.9541 | 161.9541 | 54.99% | 11.47% | 11.47% | 90% | 10.32% | 23.9792 | 6.6189 | 6 | 143.8749 | 53.0278 | 88.84% | 88.84%
9 | 271 | 28 | 6492 | 12 | 13.8 | 344.03 | 165.97 | 510 | 165.97 | 82.99 | 271 | 6492 | 720 | 267.2877 | -1.6259 | -5.3148 | 694.284 | 11.4828 | 7.7577 | 41.1178 | 41.1178 | 10.3176 | 169.6824 | 8.4706 | 517.4456 | 517.4456 | 141.6643 | 659.1098 | 0.6088 | 60.88% | 298.0495 | 181.4512 | 127.0158 | 156.3613 | 156.3613 | 81.23% | 11.4% | 11.4% | 90% | 10.26% | 30.58 | 6.3002 | 6 | 183.48 | 67.6249 | 117.3% | 117.3%
9 | 271 | 28 | 6493 | 13 | 14 | 420.28 | 189.39 | 609.67 | 189.39 | 94.7 | 271 | 6493 | 780 | 267.2877 | -1.6259 | -5.3148 | 754.284 | 12.4828 | -7.2423 | 41.179 | 41.179 | 9.6382 | 189.6382 | 8.0014 | 632.1082 | 632.1082 | 161.6545 | 793.7626 | 0.64248 | 64.25% | 358.9395 | 230.6132 | 161.4292 | 157.5045 | 157.5045 | 102.5% | 11.35% | 11.35% | 90% | 10.22% | 36.6788 | 6.2522 | 6 | 220.0727 | 81.1118 | 139.7% | 139.7%
9 | 271 | 28 | 6494 | 14 | 14.2 | 409.44 | 174.78 | 584.22 | 174.78 | 87.39 | 271 | 6494 | 840 | 267.2877 | -1.6259 | -5.3148 | 814.284 | 13.4828 | -22.2423 | 37.8023 | 37.8023 | 28.6118 | 208.6118 | 22.498 | 617.1563 | 617.1563 | 149.1841 | 766.3404 | 0.6373 | 63.73% | 346.5391 | 220.8495 | 154.5946 | 155.2964 | 155.2964 | 99.55% | 11.36% | 11.36% | 90% | 10.23% | 35.4387 | 6.2045 | 6 | 212.6322 | 78.3695 | 136.9% | 136.9%
9 | 271 | 28 | 6495 | 15 | 14.3 | 312.44 | 159.94 | 472.38 | 159.94 | 79.97 | 271 | 6495 | 900 | 267.2877 | -1.6259 | -5.3148 | 874.284 | 14.4828 | -37.2423 | 31.62 | 31.62 | 45.2681 | 225.2681 | 37.392 | 473.4718 | 473.4718 | 136.5173 | 609.9891 | 0.59495 | 59.49% | 275.8371 | 164.1081 | 114.8756 | 147.3057 | 147.3057 | 77.98% | 11.41% | 11.41% | 90% | 10.27% | 28.3296 | 6.1808 | 6 | 169.9776 | 62.6484 | 115.4% | 115.4%
9 | 271 | 28 | 6496 | 16 | 13.8 | 229.11 | 139.5 | 368.61 | 139.5 | 69.75 | 271 | 6496 | 960 | 267.2877 | -1.6259 | -5.3148 | 934.284 | 15.4828 | -52.2423 | 23.4838 | 23.4838 | 59.5032 | 239.5032 | 52.3453 | 351.2349 | 351.2349 | 119.0707 | 470.3056 | 0.53043 | 53.04% | 212.6722 | 112.8078 | 78.9655 | 139.7547 | 139.7547 | 56.5% | 11.46% | 11.46% | 85% | 9.745% | 20.7244 | 6.3002 | 6 | 124.3464 | 45.8302 | 88.97% | 88.97%
9 | 271 | 28 | 6497 | 17 | 14.2 | 100.83 | 101.39 | 202.22 | 101.39 | 50.7 | 271 | 6497 | 1020 | 267.2877 | -1.6259 | -5.3148 | 994.284 | 16.4828 | -67.2423 | 14.1305 | 14.1305 | 71.9043 | 251.9043 | 67.3182 | 159.2636 | 159.2636 | 86.5418 | 245.8054 | 0.28429 | 28.43% | 111.1532 | 31.5992 | 22.1195 | 128.7233 | 128.7233 | 17.18% | 11.53% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6498 | 18 | 12.8 | 41.72 | 63.56 | 105.28 | 63.56 | 31.78 | 271 | 6498 | 1080 | 267.2877 | -1.6259 | -5.3148 | 1054.284 | 17.4828 | -82.2423 | 4.1132 | 4.1132 | 83.2199 | 263.2199 | 82.3001 | 0 | 0 | 54.2519 | 54.2519 | -1.6098 | 0% | 24.5327 | 0 | 0 | 158.7916 | 158.7916 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6499 | 19 | 11.3 | 0 | 11.72 | 11.72 | 11.72 | 5.86 | 271 | 6499 | 1140 | 267.2877 | -1.6259 | -5.3148 | 1114.284 | 18.4828 | -97.2423 | -6.141 | 0 | 87.6254 | 267.6254 | 88.3211 | 0 | 0 | 10.0036 | 10.0036 | -12.6324 | 0% | 4.5236 | 0 | 0 | 145.6503 | 145.6503 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6500 | 20 | 10.1 | 0 | 0 | 0 | 0 | 0 | 271 | 6500 | 1200 | 267.2877 | -1.6259 | -5.3148 | 1174.284 | 19.4828 | -112.2423 | -16.248 | 0 | 87.6254 | 267.6254 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.0017 | 136.0017 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6501 | 21 | 8.2 | 0 | 0 | 0 | 0 | 0 | 271 | 6501 | 1260 | 267.2877 | -1.6259 | -5.3148 | 1234.284 | 20.4828 | -127.2423 | -25.7826 | 0 | 87.6254 | 267.6254 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.644 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6502 | 22 | 7.7 | 0 | 0 | 0 | 0 | 0 | 271 | 6502 | 1320 | 267.2877 | -1.6259 | -5.3148 | 1294.284 | 21.4828 | -142.2423 | -34.1864 | 0 | 87.6254 | 267.6254 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0302 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6503 | 23 | 7.5 | 0 | 0 | 0 | 0 | 0 | 271 | 6503 | 1380 | 267.2877 | -1.6259 | -5.3148 | 1354.284 | 22.4828 | -157.2423 | -40.6876 | 0 | 87.6254 | 267.6254 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.741 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
9 | 271 | 28 | 6504 | 24 | 7.5 | 0 | 0 | 0 | 0 | 0 | 271 | 6504 | 1440 | 267.2877 | -1.6259 | -5.3148 | 1414.284 | 23.4828 | -172.2423 | -44.3438 | 0 | 87.6254 | 267.6254 | 88.3211 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1469 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6505 | 1 | 7.6 | 0 | 0 | 0 | 0 | 0 | 272 | 6505 | 60 | 268.274 | -2.025 | -4.9949 | 34.284 | 0.48815 | 172.6777 | -44.7945 | 0 | 87.0424 | 92.9576 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5333 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6506 | 2 | 7.2 | 0 | 0 | 0 | 0 | 0 | 272 | 6506 | 120 | 268.274 | -2.025 | -4.9949 | 94.284 | 1.4882 | 157.6777 | -41.213 | 0 | 87.0424 | 92.9576 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7404 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6507 | 3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 272 | 6507 | 180 | 268.274 | -2.025 | -4.9949 | 154.284 | 2.4882 | 142.6777 | -34.7508 | 0 | 87.0424 | 92.9576 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4903 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6508 | 4 | 6.3 | 0 | 0 | 0 | 0 | 0 | 272 | 6508 | 240 | 268.274 | -2.025 | -4.9949 | 214.284 | 3.4882 | 127.6777 | -26.3637 | 0 | 87.0424 | 92.9576 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7095 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6509 | 5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 272 | 6509 | 300 | 268.274 | -2.025 | -4.9949 | 274.284 | 4.4882 | 112.6777 | -16.835 | 0 | 87.0424 | 92.9576 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.4424 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6510 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 272 | 6510 | 360 | 268.274 | -2.025 | -4.9949 | 334.284 | 5.4882 | 97.6777 | -6.7297 | 0 | 87.0424 | 92.9576 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.332 | 1.332 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6511 | 7 | 6.3 | 0 | 0 | 0 | 0 | 0 | 272 | 6511 | 420 | 268.274 | -2.025 | -4.9949 | 394.284 | 6.4882 | 82.6777 | 3.5247 | 3.5247 | 83.2674 | 96.7326 | 82.7492 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 162.5339 | 162.5339 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6512 | 8 | 6.8 | 16.11 | 34.17 | 50.28 | 34.17 | 17.09 | 272 | 6512 | 480 | 268.274 | -2.025 | -4.9949 | 454.284 | 7.4882 | 67.6777 | 13.5443 | 13.5443 | 71.9767 | 108.0233 | 67.7716 | 26.0226 | 26.0226 | 29.1659 | 55.1885 | -1.823 | 0% | 24.9562 | 0 | 0 | 173.539 | 173.539 | 0% | 11.89% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6513 | 9 | 7.8 | 80.78 | 76.17 | 156.95 | 76.17 | 38.09 | 272 | 6513 | 540 | 268.274 | -2.025 | -4.9949 | 514.284 | 8.4882 | 52.6777 | 22.9048 | 22.9048 | 59.6288 | 120.3712 | 52.8049 | 125.4725 | 125.4725 | 65.0152 | 190.4876 | 0.055359 | 5.536% | 86.1385 | 4.7685 | 3.338 | 160.6265 | 160.6265 | 2.078% | 11.76% | 11.76% | 80% | 9.409% | 8.1046 | 7.8698 | 6 | 48.6275 | 17.9226 | 30.27% | 30.27%
9 | 272 | 29 | 6514 | 10 | 10.6 | 155.83 | 120.28 | 276.11 | 120.28 | 60.14 | 272 | 6514 | 600 | 268.274 | -2.025 | -4.9949 | 574.284 | 9.4882 | 37.6777 | 31.0594 | 31.0594 | 45.4851 | 134.5149 | 37.8621 | 238.4567 | 238.4567 | 102.6654 | 341.1221 | 0.4052 | 40.52% | 154.2554 | 62.5046 | 43.7532 | 148.3942 | 148.3942 | 29.48% | 11.59% | 11.59% | 85% | 9.851% | 15.1955 | 7.1059 | 6 | 91.1729 | 33.6034 | 61.44% | 61.44%
9 | 272 | 29 | 6515 | 11 | 12.5 | 249.03 | 158.67 | 407.7 | 158.67 | 79.34 | 272 | 6515 | 660 | 268.274 | -2.025 | -4.9949 | 634.284 | 10.4882 | 22.6777 | 37.282 | 37.282 | 28.9639 | 151.0361 | 22.9902 | 378.4636 | 378.4636 | 135.4333 | 513.8969 | 0.54784 | 54.78% | 232.3842 | 127.3084 | 89.1159 | 151.2899 | 151.2899 | 58.9% | 11.47% | 11.47% | 90% | 10.32% | 23.9891 | 6.6189 | 6 | 143.9343 | 53.0497 | 95.14% | 95.14%
9 | 272 | 29 | 6516 | 12 | 13.5 | 308.06 | 175.78 | 483.84 | 175.78 | 87.89 | 272 | 6516 | 720 | 268.274 | -2.025 | -4.9949 | 694.284 | 11.4882 | 7.6777 | 40.7315 | 40.7315 | 10.1483 | 169.8517 | 8.5667 | 466.8444 | 466.8444 | 150.0376 | 616.882 | 0.59432 | 59.43% | 278.954 | 165.7883 | 116.0518 | 146.7868 | 146.7868 | 79.06% | 11.42% | 11.42% | 90% | 10.28% | 28.6645 | 6.3727 | 6 | 171.9872 | 63.3891 | 117.2% | 117.2%
9 | 272 | 29 | 6517 | 13 | 13 | 370.14 | 174.11 | 544.25 | 174.11 | 87.06 | 272 | 6517 | 780 | 268.274 | -2.025 | -4.9949 | 754.284 | 12.4882 | -7.3223 | 40.7734 | 40.7734 | 9.6826 | 189.6826 | 8.2497 | 560.9049 | 560.9049 | 148.6122 | 709.5171 | 0.62008 | 62.01% | 320.8436 | 198.9494 | 139.2646 | 146.3989 | 146.3989 | 95.13% | 11.39% | 11.39% | 90% | 10.25% | 32.8805 | 6.4949 | 6 | 197.2833 | 72.7124 | 134.8% | 134.8%
9 | 272 | 29 | 6518 | 14 | 13.2 | 329.86 | 176.72 | 506.58 | 176.72 | 88.36 | 272 | 6518 | 840 | 268.274 | -2.025 | -4.9949 | 814.284 | 13.4882 | -22.3223 | 37.3991 | 37.3991 | 28.542 | 208.542 | 22.6398 | 501.252 | 501.252 | 150.84 | 652.0919 | 0.60459 | 60.46% | 294.876 | 178.2789 | 124.7952 | 144.5941 | 144.5941 | 86.31% | 11.41% | 11.41% | 90% | 10.27% | 30.2737 | 6.4458 | 6 | 181.6422 | 66.9476 | 125.6% | 125.6%
9 | 272 | 29 | 6519 | 15 | 13.3 | 311.61 | 159.39 | 471 | 159.39 | 79.7 | 272 | 6519 | 900 | 268.274 | -2.025 | -4.9949 | 874.284 | 14.4882 | -37.3223 | 31.2325 | 31.2325 | 45.1226 | 225.1226 | 37.5086 | 476.727 | 476.727 | 136.0479 | 612.7749 | 0.59217 | 59.22% | 277.0968 | 164.088 | 114.8616 | 140.9012 | 140.9012 | 81.52% | 11.42% | 11.42% | 90% | 10.28% | 28.4825 | 6.4214 | 6 | 170.8949 | 62.9865 | 121.3% | 121.3%
9 | 272 | 29 | 6520 | 16 | 12.7 | 237.92 | 122 | 359.92 | 122 | 61 | 272 | 6520 | 960 | 268.274 | -2.025 | -4.9949 | 934.284 | 15.4882 | -52.3223 | 23.1145 | 23.1145 | 59.3173 | 239.3173 | 52.4505 | 369.3606 | 369.3606 | 104.1335 | 473.4942 | 0.52695 | 52.69% | 214.1141 | 112.8273 | 78.9791 | 133.7854 | 133.7854 | 59.03% | 11.48% | 11.48% | 85% | 9.761% | 20.8989 | 6.5691 | 6 | 125.3933 | 46.216 | 93.73% | 93.73%
9 | 272 | 29 | 6521 | 17 | 12.8 | 135.97 | 92.78 | 228.75 | 92.78 | 46.39 | 272 | 6521 | 1020 | 268.274 | -2.025 | -4.9949 | 994.284 | 16.4882 | -67.3223 | 13.7756 | 13.7756 | 71.6992 | 251.6992 | 67.4168 | 219.2841 | 219.2841 | 79.1927 | 298.4768 | 0.36527 | 36.53% | 134.9712 | 49.3003 | 34.5102 | 125.1238 | 125.1238 | 27.58% | 11.55% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6522 | 18 | 12.6 | 29.67 | 49.78 | 79.45 | 49.78 | 24.89 | 272 | 6522 | 1080 | 268.274 | -2.025 | -4.9949 | 1054.284 | 17.4882 | -82.3223 | 3.7663 | 3.7663 | 83.0065 | 263.0065 | 82.3942 | 0 | 0 | 42.4899 | 42.4899 | -2.2888 | 0% | 19.2139 | 0 | 0 | 154.5031 | 154.5031 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6523 | 19 | 11.7 | 0 | 7.44 | 7.44 | 7.44 | 3.72 | 272 | 6523 | 1140 | 268.274 | -2.025 | -4.9949 | 1114.284 | 18.4882 | -97.3223 | -6.4869 | 0 | 87.0424 | 267.0424 | 87.9091 | 0 | 0 | 6.3504 | 6.3504 | -20.2162 | 0% | 2.8717 | 0 | 0 | 144.0797 | 144.0797 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6524 | 20 | 10.4 | 0 | 0 | 0 | 0 | 0 | 272 | 6524 | 1200 | 268.274 | -2.025 | -4.9949 | 1174.284 | 19.4882 | -112.3223 | -16.6004 | 0 | 87.0424 | 267.0424 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.4832 | 135.4832 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6525 | 21 | 9.8 | 0 | 0 | 0 | 0 | 0 | 272 | 6525 | 1260 | 268.274 | -2.025 | -4.9949 | 1234.284 | 20.4882 | -127.3223 | -26.1484 | 0 | 87.0424 | 267.0424 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9734 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6526 | 22 | 9.2 | 0 | 0 | 0 | 0 | 0 | 272 | 6526 | 1320 | 268.274 | -2.025 | -4.9949 | 1294.284 | 21.4882 | -142.3223 | -34.5708 | 0 | 87.0424 | 267.0424 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3026 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6527 | 23 | 9.2 | 0 | 0 | 0 | 0 | 0 | 272 | 6527 | 1380 | 268.274 | -2.025 | -4.9949 | 1354.284 | 22.4882 | -157.3223 | -41.0894 | 0 | 87.0424 | 267.0424 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
9 | 272 | 29 | 6528 | 24 | 8.6 | 0 | 0 | 0 | 0 | 0 | 272 | 6528 | 1440 | 268.274 | -2.025 | -4.9949 | 1414.284 | 23.4882 | -172.3223 | -44.7498 | 0 | 87.0424 | 267.0424 | 87.9091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4119 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6529 | 1 | 7.6 | 0 | 0 | 0 | 0 | 0 | 273 | 6529 | 60 | 269.2603 | -2.424 | -4.6751 | 34.284 | 0.49348 | 172.5978 | -45.1806 | 0 | 86.4592 | 93.5408 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7977 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6530 | 2 | 7.4 | 0 | 0 | 0 | 0 | 0 | 273 | 6530 | 120 | 269.2603 | -2.424 | -4.6751 | 94.284 | 1.4935 | 157.5978 | -41.5595 | 0 | 86.4592 | 93.5408 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7641 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6531 | 3 | 6.9 | 0 | 0 | 0 | 0 | 0 | 273 | 6531 | 180 | 269.2603 | -2.424 | -4.6751 | 154.284 | 2.4935 | 142.5978 | -35.0544 | 0 | 86.4592 | 93.5408 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1878 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6532 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 273 | 6532 | 240 | 269.2603 | -2.424 | -4.6751 | 214.284 | 3.4935 | 127.5978 | -26.6327 | 0 | 86.4592 | 93.5408 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0354 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6533 | 5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 273 | 6533 | 300 | 269.2603 | -2.424 | -4.6751 | 274.284 | 4.4935 | 112.5978 | -17.0818 | 0 | 86.4592 | 93.5408 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1361 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6534 | 6 | 6.3 | 0 | 0 | 0 | 0 | 0 | 273 | 6534 | 360 | 269.2603 | -2.424 | -4.6751 | 334.284 | 5.4935 | 97.5978 | -6.9663 | 0 | 86.4592 | 93.5408 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.2613 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6535 | 7 | 6.6 | 0 | 0.92 | 0.92 | 0.92 | 0.46 | 273 | 6535 | 420 | 269.2603 | -2.424 | -4.6751 | 394.284 | 6.4935 | 82.5978 | 3.2866 | 3.2866 | 82.9368 | 97.0632 | 82.6838 | 0 | 0 | 0.78527 | 0.78527 | -184.4242 | 0% | 0.3551 | 0 | 0 | 157.2718 | 157.2718 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6536 | 8 | 6.7 | 7.72 | 34.78 | 42.5 | 34.78 | 17.39 | 273 | 6536 | 480 | 269.2603 | -2.424 | -4.6751 | 454.284 | 7.4935 | 67.5978 | 13.2934 | 13.2934 | 71.6472 | 108.3528 | 67.7115 | 12.7337 | 12.7337 | 29.6866 | 42.4203 | -2.6193 | 0% | 19.1825 | 0 | 0 | 165.9279 | 165.9279 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6537 | 9 | 8.5 | 11.94 | 88.94 | 100.88 | 88.94 | 44.47 | 273 | 6537 | 540 | 269.2603 | -2.424 | -4.6751 | 514.284 | 8.4935 | 52.5978 | 22.6298 | 22.6298 | 59.3034 | 120.6966 | 52.7525 | 18.7818 | 18.7818 | 75.915 | 94.6968 | -0.68449 | 0% | 42.8219 | 0 | 0 | 151.2308 | 151.2308 | 0% | 11.8% | 11.8% | 80% | 9.438% | 4.0417 | 7.6737 | 6 | 24.2504 | 8.9379 | 16.04% | 16.04%
9 | 273 | 30 | 6538 | 10 | 10.8 | 53.56 | 151.67 | 205.23 | 151.67 | 75.84 | 273 | 6538 | 600 | 269.2603 | -2.424 | -4.6751 | 574.284 | 9.4935 | 37.5978 | 30.7499 | 30.7499 | 45.1771 | 134.8229 | 37.8228 | 82.7466 | 82.7466 | 129.4584 | 212.205 | 0.16512 | 16.51% | 95.9591 | 15.8446 | 11.0913 | 138.1982 | 138.1982 | 8.026% | 11.65% | 11.65% | 80% | 9.32% | 8.9429 | 7.0535 | 6 | 53.6577 | 19.7765 | 38.83% | 38.83%
9 | 273 | 30 | 6539 | 11 | 12.7 | 174.03 | 242.83 | 416.86 | 242.83 | 121.42 | 273 | 6539 | 660 | 269.2603 | -2.424 | -4.6751 | 634.284 | 10.4935 | 22.5978 | 36.9318 | 36.9318 | 28.7039 | 151.2961 | 22.9798 | 266.6487 | 266.6487 | 207.2684 | 473.917 | 0.5272 | 52.72% | 214.3053 | 112.981 | 79.0867 | 146.2725 | 146.2725 | 54.07% | 11.48% | 11.48% | 85% | 9.76% | 20.9172 | 6.5691 | 6 | 125.5034 | 46.2566 | 85.8% | 85.8%
9 | 273 | 30 | 6540 | 12 | 13.8 | 189.86 | 252.92 | 442.78 | 252.92 | 126.46 | 273 | 6540 | 720 | 269.2603 | -2.424 | -4.6751 | 694.284 | 11.4935 | 7.5978 | 40.3449 | 40.3449 | 9.981 | 170.019 | 8.6807 | 289.9117 | 289.9117 | 215.8807 | 505.7925 | 0.54962 | 54.96% | 228.7194 | 125.7097 | 87.9968 | 141.3863 | 141.3863 | 62.24% | 11.45% | 11.45% | 90% | 10.31% | 23.5743 | 6.3002 | 6 | 141.4459 | 52.1325 | 100% | 100%
9 | 273 | 30 | 6541 | 13 | 14.1 | 253 | 230.97 | 483.97 | 230.97 | 115.49 | 273 | 6541 | 780 | 269.2603 | -2.424 | -4.6751 | 754.284 | 12.4935 | -7.4022 | 40.3678 | 40.3678 | 9.7264 | 189.7264 | 8.5102 | 386.317 | 386.317 | 197.1452 | 583.4622 | 0.58466 | 58.47% | 263.8416 | 154.2576 | 107.9803 | 141.8432 | 141.8432 | 76.13% | 11.42% | 11.42% | 90% | 10.28% | 27.123 | 6.2283 | 6 | 162.7381 | 59.9801 | 114.7% | 114.7%
9 | 273 | 30 | 6542 | 14 | 15.6 | 184.39 | 207.5 | 391.89 | 207.5 | 103.75 | 273 | 6542 | 840 | 269.2603 | -2.424 | -4.6751 | 814.284 | 13.4935 | -22.4022 | 36.9958 | 36.9958 | 28.4729 | 208.4729 | 22.7876 | 282.5023 | 282.5023 | 177.1123 | 459.6147 | 0.53297 | 53.3% | 207.8378 | 110.7703 | 77.5392 | 139.5871 | 139.5871 | 55.55% | 11.43% | 11.43% | 85% | 9.719% | 20.2002 | 5.8784 | 5.8784 | 118.7457 | 44.6709 | 85.07% | 85.07%
9 | 273 | 30 | 6543 | 15 | 14.9 | 197.72 | 173.28 | 371 | 173.28 | 86.64 | 273 | 6543 | 900 | 269.2603 | -2.424 | -4.6751 | 874.284 | 14.4935 | -37.4022 | 30.8447 | 30.8447 | 44.9783 | 224.9783 | 37.6285 | 305.4171 | 305.4171 | 147.9037 | 453.3208 | 0.52571 | 52.57% | 204.9917 | 107.7652 | 75.4356 | 135.3243 | 135.3243 | 55.74% | 11.45% | 11.45% | 85% | 9.732% | 19.9495 | 6.0398 | 6 | 119.697 | 44.1165 | 88.45% | 88.45%
9 | 273 | 30 | 6544 | 16 | 14.4 | 160.22 | 135 | 295.22 | 135 | 67.5 | 273 | 6544 | 960 | 269.2603 | -2.424 | -4.6751 | 934.284 | 15.4935 | -52.4022 | 22.7449 | 22.7449 | 59.1323 | 239.1323 | 52.5577 | 251.9414 | 251.9414 | 115.2297 | 367.1711 | 0.45731 | 45.73% | 166.0348 | 75.93 | 53.151 | 129.9173 | 129.9173 | 40.91% | 11.49% | 11.49% | 85% | 9.763% | 16.2092 | 6.1571 | 6 | 97.255 | 35.8451 | 74.86% | 74.86%
9 | 273 | 30 | 6545 | 17 | 14.28 | 85.28 | 93.19 | 178.47 | 93.19 | 46.6 | 273 | 6545 | 1020 | 269.2603 | -2.424 | -4.6751 | 994.284 | 16.4935 | -67.4022 | 13.4205 | 13.4205 | 71.4947 | 251.4947 | 67.5164 | 140.5139 | 140.5139 | 79.5426 | 220.0566 | 0.2243 | 22.43% | 99.5096 | 22.3202 | 15.6241 | 121.857 | 121.857 | 12.82% | 11.53% | 0% | 80% | 0% | 0 | 6.1855 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6546 | 18 | 13.11 | 21.94 | 45.89 | 67.83 | 45.89 | 22.95 | 273 | 6546 | 1080 | 269.2603 | -2.424 | -4.6751 | 1054.284 | 17.4935 | -82.4022 | 3.4194 | 3.4194 | 82.7933 | 262.7933 | 82.4886 | 0 | 0 | 39.1696 | 39.1696 | -2.521 | 0% | 17.7125 | 0 | 0 | 152.8014 | 152.8014 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4679 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6547 | 19 | 11.61 | 0 | 5.89 | 5.89 | 5.89 | 2.95 | 273 | 6547 | 1140 | 269.2603 | -2.424 | -4.6751 | 1114.284 | 18.4935 | -97.4022 | -6.8327 | 0 | 86.4592 | 266.4592 | 87.4971 | 0 | 0 | 5.0274 | 5.0274 | -25.7892 | 0% | 2.2734 | 0 | 0 | 142.7525 | 142.7525 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8439 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6548 | 20 | 10.52 | 0 | 0 | 0 | 0 | 0 | 273 | 6548 | 1200 | 269.2603 | -2.424 | -4.6751 | 1174.284 | 19.4935 | -112.4022 | -16.9525 | 0 | 86.4592 | 266.4592 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.2487 | 135.2487 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.127 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6549 | 21 | 9.91 | 0 | 0 | 0 | 0 | 0 | 273 | 6549 | 1260 | 269.2603 | -2.424 | -4.6751 | 1234.284 | 20.4935 | -127.4022 | -26.514 | 0 | 86.4592 | 266.4592 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0448 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2891 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6550 | 22 | 9.19 | 0 | 0 | 0 | 0 | 0 | 273 | 6550 | 1320 | 269.2603 | -2.424 | -4.6751 | 1294.284 | 21.4935 | -142.4022 | -34.955 | 0 | 86.4592 | 266.4592 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3895 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.4837 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6551 | 23 | 8.64 | 0 | 0 | 0 | 0 | 0 | 273 | 6551 | 1380 | 269.2603 | -2.424 | -4.6751 | 1354.284 | 22.4935 | -157.4022 | -41.4911 | 0 | 86.4592 | 266.4592 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8894 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6349 | 6 | 0 | 0 | 0% | 0%
9 | 273 | 30 | 6552 | 24 | 8.41 | 0 | 0 | 0 | 0 | 0 | 273 | 6552 | 1440 | 269.2603 | -2.424 | -4.6751 | 1414.284 | 23.4935 | -172.4022 | -45.1558 | 0 | 86.4592 | 266.4592 | 87.4971 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9016 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6987 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6553 | 1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 274 | 6553 | 60 | 270.2466 | -2.823 | -4.3558 | 34.284 | 0.4988 | 172.5179 | -45.5663 | 0 | 85.8759 | 94.1241 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1337 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6554 | 2 | 8.35 | 0 | 0 | 0 | 0 | 0 | 274 | 6554 | 120 | 270.2466 | -2.823 | -4.3558 | 94.284 | 1.4988 | 157.5179 | -41.9053 | 0 | 85.8759 | 94.1241 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9343 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7154 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6555 | 3 | 8.2 | 0 | 0 | 0 | 0 | 0 | 274 | 6555 | 180 | 270.2466 | -2.823 | -4.3558 | 154.284 | 2.4988 | 142.5179 | -35.3571 | 0 | 85.8759 | 94.1241 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8872 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6556 | 4 | 8.23 | 0 | 0 | 0 | 0 | 0 | 274 | 6556 | 240 | 270.2466 | -2.823 | -4.3558 | 214.284 | 3.4988 | 127.5179 | -26.9009 | 0 | 85.8759 | 94.1241 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8415 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7489 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6557 | 5 | 8.27 | 0 | 0 | 0 | 0 | 0 | 274 | 6557 | 300 | 270.2466 | -2.823 | -4.3558 | 274.284 | 4.4988 | 112.5179 | -17.328 | 0 | 85.8759 | 94.1241 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0599 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7377 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6558 | 6 | 8.42 | 0 | 0 | 0 | 0 | 0 | 274 | 6558 | 360 | 270.2466 | -2.823 | -4.3558 | 334.284 | 5.4988 | 97.5179 | -7.2028 | 0 | 85.8759 | 94.1241 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.3619 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6959 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6559 | 7 | 8.76 | 0 | 0 | 0 | 0 | 0 | 274 | 6559 | 420 | 270.2466 | -2.823 | -4.3558 | 394.284 | 6.4988 | 82.5179 | 3.0483 | 3.0483 | 82.6064 | 97.3936 | 82.619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 156.1943 | 156.1943 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6017 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6560 | 8 | 9.3 | 11.33 | 32.22 | 43.55 | 32.22 | 16.11 | 274 | 6560 | 480 | 270.2466 | -2.823 | -4.3558 | 454.284 | 7.4988 | 67.5179 | 13.0421 | 13.0421 | 71.3186 | 108.6814 | 67.6528 | 19.0895 | 19.0895 | 27.5015 | 46.591 | -2.181 | 0% | 21.0685 | 0 | 0 | 165.4879 | 165.4879 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6561 | 9 | 10.8 | 49.67 | 97.56 | 147.23 | 97.56 | 48.78 | 274 | 6561 | 540 | 270.2466 | -2.823 | -4.3558 | 514.284 | 8.4988 | 52.5179 | 22.3542 | 22.3542 | 58.9795 | 121.0205 | 52.7025 | 79.1356 | 79.1356 | 83.2727 | 162.4083 | -0.030772 | 0% | 73.441 | 0 | 0 | 152.9204 | 152.9204 | 0% | 11.67% | 11.67% | 80% | 9.34% | 6.8592 | 7.0535 | 6 | 41.155 | 15.1684 | 26.91% | 26.91%
10 | 274 | 1 | 6562 | 10 | 11.7 | 99.11 | 138.28 | 237.39 | 138.28 | 69.14 | 274 | 6562 | 600 | 270.2466 | -2.823 | -4.3558 | 574.284 | 9.4988 | 37.5179 | 30.4397 | 30.4397 | 44.8713 | 135.1287 | 37.7873 | 154.6012 | 154.6012 | 118.0294 | 272.6305 | 0.31437 | 31.44% | 123.2835 | 38.757 | 27.1299 | 137.4612 | 137.4612 | 19.74% | 11.59% | 11.59% | 80% | 9.274% | 11.4336 | 6.8209 | 6 | 68.6013 | 25.2843 | 49.91% | 49.91%
10 | 274 | 1 | 6563 | 11 | 12.7 | 145.61 | 169.22 | 314.83 | 169.22 | 84.61 | 274 | 6563 | 660 | 270.2466 | -2.823 | -4.3558 | 634.284 | 10.4988 | 22.5179 | 36.581 | 36.581 | 28.4466 | 151.5534 | 22.9763 | 224.9455 | 224.9455 | 144.4383 | 369.3839 | 0.44886 | 44.89% | 167.0354 | 74.976 | 52.4832 | 138.4655 | 138.4655 | 37.9% | 11.52% | 11.52% | 85% | 9.796% | 16.3631 | 6.5691 | 6 | 98.1783 | 36.1854 | 70.9% | 70.9%
10 | 274 | 1 | 6564 | 12 | 14.1 | 184.31 | 183.61 | 367.92 | 183.61 | 91.81 | 274 | 6564 | 720 | 270.2466 | -2.823 | -4.3558 | 694.284 | 11.4988 | 7.5179 | 39.9581 | 39.9581 | 9.8159 | 170.1841 | 8.8121 | 283.5982 | 283.5982 | 156.7209 | 440.3191 | 0.51335 | 51.34% | 199.1123 | 102.2153 | 71.5507 | 136.3271 | 136.3271 | 52.48% | 11.47% | 11.47% | 85% | 9.748% | 19.4103 | 6.2283 | 6 | 116.4617 | 42.9241 | 85.43% | 85.43%
10 | 274 | 1 | 6565 | 13 | 14.9 | 258.06 | 187.5 | 445.56 | 187.5 | 93.75 | 274 | 6565 | 780 | 270.2466 | -2.823 | -4.3558 | 754.284 | 12.4988 | -7.4821 | 39.9623 | 39.9623 | 9.7695 | 189.7695 | 8.7816 | 397.0757 | 397.0757 | 160.0413 | 557.1169 | 0.57755 | 57.76% | 251.9283 | 145.5022 | 101.8515 | 139.7385 | 139.7385 | 72.89% | 11.42% | 11.42% | 90% | 10.28% | 25.8935 | 6.0398 | 6 | 155.3609 | 57.2611 | 111.2% | 111.2%
10 | 274 | 1 | 6566 | 14 | 15.3 | 255.83 | 183.75 | 439.58 | 183.75 | 91.88 | 274 | 6566 | 840 | 270.2466 | -2.823 | -4.3558 | 814.284 | 13.4988 | -22.4821 | 36.5927 | 36.5927 | 28.4044 | 208.4044 | 22.9412 | 395.2129 | 395.2129 | 156.8404 | 552.0533 | 0.57712 | 57.71% | 249.6385 | 144.0712 | 100.8499 | 139.8909 | 139.8909 | 72.09% | 11.42% | 11.42% | 90% | 10.27% | 25.6491 | 5.9472 | 5.9472 | 152.539 | 56.7206 | 109% | 109%
10 | 274 | 1 | 6567 | 15 | 15.3 | 323.67 | 176.06 | 499.73 | 176.06 | 88.03 | 274 | 6567 | 900 | 270.2466 | -2.823 | -4.3558 | 874.284 | 14.4988 | -37.4821 | 30.457 | 30.457 | 44.8349 | 224.8349 | 37.7517 | 504.8744 | 504.8744 | 150.2766 | 655.151 | 0.61282 | 61.28% | 296.2593 | 181.5543 | 127.088 | 140.8682 | 140.8682 | 90.22% | 11.39% | 11.39% | 90% | 10.25% | 30.3681 | 5.9472 | 5.9472 | 180.6035 | 67.1562 | 128.2% | 128.2%
10 | 274 | 1 | 6568 | 16 | 15.2 | 180.78 | 138 | 318.78 | 138 | 69 | 274 | 6568 | 960 | 270.2466 | -2.823 | -4.3558 | 934.284 | 15.4988 | -52.4821 | 22.3752 | 22.3752 | 58.9481 | 238.9481 | 52.6668 | 288.002 | 288.002 | 117.7904 | 405.7924 | 0.49479 | 49.48% | 183.4993 | 90.7929 | 63.555 | 131.5396 | 131.5396 | 48.32% | 11.46% | 11.46% | 85% | 9.738% | 17.8685 | 5.9702 | 5.9702 | 106.6788 | 39.5147 | 81.1% | 81.1%
10 | 274 | 1 | 6569 | 17 | 15.3 | 126.17 | 106.72 | 232.89 | 106.72 | 53.36 | 274 | 6569 | 1020 | 270.2466 | -2.823 | -4.3558 | 994.284 | 16.4988 | -67.4821 | 13.0654 | 13.0654 | 71.2906 | 251.2906 | 67.617 | 212.5297 | 212.5297 | 91.0912 | 303.6209 | 0.39148 | 39.15% | 137.2974 | 53.7489 | 37.6243 | 125.6664 | 125.6664 | 29.94% | 11.48% | 0% | 85% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6570 | 18 | 15.2 | 27.17 | 44.22 | 71.39 | 44.22 | 22.11 | 274 | 6570 | 1080 | 270.2466 | -2.823 | -4.3558 | 1054.284 | 17.4988 | -82.4821 | 3.0727 | 3.0727 | 82.5801 | 262.5801 | 82.5832 | 0 | 0 | 37.7441 | 37.7441 | -2.5204 | 0% | 17.0679 | 0 | 0 | 155.2698 | 155.2698 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6571 | 19 | 14.5 | 0 | 6.53 | 6.53 | 6.53 | 3.27 | 274 | 6571 | 1140 | 270.2466 | -2.823 | -4.3558 | 1114.284 | 18.4988 | -97.4821 | -7.1782 | 0 | 85.8759 | 265.8759 | 87.0851 | 0 | 0 | 5.5737 | 5.5737 | -21.9934 | 0% | 2.5204 | 0 | 0 | 145.8429 | 145.8429 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1335 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6572 | 20 | 14.3 | 0 | 0 | 0 | 0 | 0 | 274 | 6572 | 1200 | 270.2466 | -2.823 | -4.3558 | 1174.284 | 19.4988 | -112.4821 | -17.3042 | 0 | 85.8759 | 265.8759 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.6837 | 139.6837 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6573 | 21 | 13.7 | 0 | 0 | 0 | 0 | 0 | 274 | 6573 | 1260 | 270.2466 | -2.823 | -4.3558 | 1234.284 | 20.4988 | -127.4821 | -26.8791 | 0 | 85.8759 | 265.8759 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.62 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6574 | 22 | 13.1 | 0 | 0 | 0 | 0 | 0 | 274 | 6574 | 1320 | 270.2466 | -2.823 | -4.3558 | 1294.284 | 21.4988 | -142.4821 | -35.3387 | 0 | 85.8759 | 265.8759 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7979 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6575 | 23 | 13.1 | 0 | 0 | 0 | 0 | 0 | 274 | 6575 | 1380 | 270.2466 | -2.823 | -4.3558 | 1354.284 | 22.4988 | -157.4821 | -41.8927 | 0 | 85.8759 | 265.8759 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5223 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
10 | 274 | 1 | 6576 | 24 | 12.9 | 0 | 0 | 0 | 0 | 0 | 274 | 6576 | 1440 | 270.2466 | -2.823 | -4.3558 | 1414.284 | 23.4988 | -172.4821 | -45.5618 | 0 | 85.8759 | 265.8759 | 87.0851 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5514 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6577 | 1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 275 | 6577 | 60 | 271.2329 | -3.2218 | -4.0373 | 34.284 | 0.50411 | 172.4383 | -45.9516 | 0 | 85.2927 | 94.7073 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8829 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6578 | 2 | 12.6 | 0 | 0 | 0 | 0 | 0 | 275 | 6578 | 120 | 271.2329 | -3.2218 | -4.0373 | 94.284 | 1.5041 | 157.4383 | -42.2502 | 0 | 85.2927 | 94.7073 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.7472 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6579 | 3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 275 | 6579 | 180 | 271.2329 | -3.2218 | -4.0373 | 154.284 | 2.5041 | 142.4383 | -35.6588 | 0 | 85.2927 | 94.7073 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9164 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6580 | 4 | 12.1 | 0 | 0 | 0 | 0 | 0 | 275 | 6580 | 240 | 271.2329 | -3.2218 | -4.0373 | 214.284 | 3.5041 | 127.4383 | -27.1684 | 0 | 85.2927 | 94.7073 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0688 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6581 | 5 | 12.1 | 0 | 0 | 0 | 0 | 0 | 275 | 6581 | 300 | 271.2329 | -3.2218 | -4.0373 | 274.284 | 4.5041 | 112.4383 | -17.5736 | 0 | 85.2927 | 94.7073 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.59169 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6582 | 6 | 12 | 0 | 0 | 0 | 0 | 0 | 275 | 6582 | 360 | 271.2329 | -3.2218 | -4.0373 | 334.284 | 5.5041 | 97.4383 | -7.439 | 0 | 85.2927 | 94.7073 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.5901 | 7.5901 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6583 | 7 | 12 | 0 | 0 | 0 | 0 | 0 | 275 | 6583 | 420 | 271.2329 | -3.2218 | -4.0373 | 394.284 | 6.5041 | 82.4383 | 2.8099 | 2.8099 | 82.2766 | 97.7234 | 82.5548 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 168.3566 | 168.3566 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6584 | 8 | 12.4 | 4.67 | 24.17 | 28.84 | 24.17 | 12.09 | 275 | 6584 | 480 | 271.2329 | -3.2218 | -4.0373 | 454.284 | 7.5041 | 67.4383 | 12.7903 | 12.7903 | 70.991 | 109.009 | 67.5955 | 8.0401 | 8.0401 | 20.6304 | 28.6704 | -3.7956 | 0% | 12.9648 | 0 | 0 | 177.7499 | 177.7499 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6585 | 9 | 12.2 | 47.36 | 81.06 | 128.42 | 81.06 | 40.53 | 275 | 6585 | 540 | 271.2329 | -3.2218 | -4.0373 | 514.284 | 8.5041 | 52.4383 | 22.0779 | 22.0779 | 58.6572 | 121.3428 | 52.6549 | 76.4347 | 76.4347 | 69.189 | 145.6237 | -0.10473 | 0% | 65.851 | 0 | 0 | 162.8677 | 162.8677 | 0% | 11.63% | 11.63% | 80% | 9.306% | 6.1282 | 6.6941 | 6 | 36.7693 | 13.552 | 22.58% | 22.58%
10 | 275 | 2 | 6586 | 10 | 13.1 | 143.39 | 125.83 | 269.22 | 125.83 | 62.92 | 275 | 6586 | 600 | 271.2329 | -3.2218 | -4.0373 | 574.284 | 9.5041 | 37.4383 | 30.1288 | 30.1288 | 44.5678 | 135.4322 | 37.7558 | 225.8577 | 225.8577 | 107.4026 | 333.2603 | 0.41312 | 41.31% | 150.7003 | 62.258 | 43.5806 | 149.2275 | 149.2275 | 29.2% | 11.53% | 11.53% | 85% | 9.8% | 14.7683 | 6.4703 | 6 | 88.6096 | 32.6587 | 59.38% | 59.38%
10 | 275 | 2 | 6587 | 11 | 15 | 238.61 | 167.56 | 406.17 | 167.56 | 83.78 | 275 | 6587 | 660 | 271.2329 | -3.2218 | -4.0373 | 634.284 | 10.5041 | 22.4383 | 36.2298 | 36.2298 | 28.192 | 151.808 | 22.9799 | 371.6838 | 371.6838 | 143.0214 | 514.7052 | 0.55934 | 55.93% | 232.7497 | 130.1852 | 91.1296 | 152.3406 | 152.3406 | 59.82% | 11.43% | 11.43% | 90% | 10.29% | 23.9439 | 6.0165 | 6 | 143.6635 | 52.9498 | 94.3% | 94.3%
10 | 275 | 2 | 6588 | 12 | 17 | 361.44 | 164.03 | 525.47 | 164.03 | 82.02 | 275 | 6588 | 720 | 271.2329 | -3.2218 | -4.0373 | 694.284 | 11.5041 | 7.4383 | 39.5712 | 39.5712 | 9.653 | 170.347 | 8.96 | 560.4534 | 560.4534 | 140.0084 | 700.4617 | 0.63066 | 63.07% | 316.7488 | 199.7595 | 139.8317 | 151.0008 | 151.0008 | 92.6% | 11.37% | 11.37% | 90% | 10.23% | 32.4084 | 5.5661 | 5.5661 | 180.3885 | 71.6683 | 119.5% | 119.5%
10 | 275 | 2 | 6589 | 13 | 20.1 | 259.03 | 171.17 | 430.2 | 171.17 | 85.59 | 275 | 6589 | 780 | 271.2329 | -3.2218 | -4.0373 | 754.284 | 12.5041 | -7.5617 | 39.5569 | 39.5569 | 9.8117 | 189.8117 | 9.0626 | 401.6623 | 401.6623 | 146.1027 | 547.765 | 0.5949 | 59.49% | 247.6993 | 147.3564 | 103.1495 | 149.1226 | 149.1226 | 69.17% | 11.35% | 11.35% | 90% | 10.22% | 25.3039 | 4.9233 | 4.9233 | 124.5788 | 55.9572 | 83.54% | 83.54%
10 | 275 | 2 | 6590 | 14 | 19.8 | 254.03 | 217.36 | 471.39 | 217.36 | 108.68 | 275 | 6590 | 840 | 271.2329 | -3.2218 | -4.0373 | 814.284 | 13.5041 | -22.5617 | 36.1898 | 36.1898 | 28.3364 | 208.3364 | 23.1002 | 395.7274 | 395.7274 | 185.5284 | 581.2557 | 0.60581 | 60.58% | 262.8438 | 159.2339 | 111.4637 | 149.3465 | 149.3465 | 74.63% | 11.35% | 11.35% | 90% | 10.22% | 26.8599 | 4.9826 | 4.9826 | 133.8317 | 59.3983 | 89.61% | 89.61%
10 | 275 | 2 | 6591 | 15 | 20 | 137.5 | 205.97 | 343.47 | 205.97 | 102.99 | 275 | 6591 | 900 | 271.2329 | -3.2218 | -4.0373 | 874.284 | 14.5041 | -37.5617 | 30.0694 | 30.0694 | 44.6926 | 224.6926 | 37.878 | 216.6086 | 216.6086 | 175.8064 | 392.415 | 0.51156 | 51.16% | 177.4501 | 90.7765 | 63.5436 | 140.6647 | 140.6647 | 45.17% | 11.35% | 11.35% | 85% | 9.649% | 17.1225 | 4.943 | 4.943 | 84.6366 | 37.8649 | 60.17% | 60.17%
10 | 275 | 2 | 6592 | 16 | 19.2 | 132.17 | 127.08 | 259.25 | 127.08 | 63.54 | 275 | 6592 | 960 | 271.2329 | -3.2218 | -4.0373 | 934.284 | 15.5041 | -52.5617 | 22.0057 | 22.0057 | 58.7649 | 238.7649 | 52.7776 | 213.3738 | 213.3738 | 108.4696 | 321.8433 | 0.44195 | 44.2% | 145.5376 | 64.3207 | 45.0245 | 133.5889 | 133.5889 | 33.7% | 11.37% | 11.37% | 85% | 9.667% | 14.0692 | 5.103 | 5.103 | 71.7953 | 31.1129 | 53.74% | 53.74%
10 | 275 | 2 | 6593 | 17 | 19.7 | 77 | 96.44 | 173.44 | 96.44 | 48.22 | 275 | 6593 | 1020 | 271.2329 | -3.2218 | -4.0373 | 994.284 | 16.5041 | -67.5617 | 12.7104 | 12.7104 | 71.0871 | 251.0871 | 67.7185 | 132.6911 | 132.6911 | 82.3167 | 215.0078 | 0.26719 | 26.72% | 97.2265 | 25.9779 | 18.1845 | 127.3176 | 127.3176 | 14.28% | 11.36% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6594 | 18 | 19.7 | 16.39 | 39.03 | 55.42 | 39.03 | 19.52 | 275 | 6594 | 1080 | 271.2329 | -3.2218 | -4.0373 | 1054.284 | 17.5041 | -82.5617 | 2.7262 | 2.7262 | 82.367 | 262.367 | 82.6778 | 0 | 0 | 33.3142 | 33.3142 | -2.6605 | 0% | 15.0647 | 0 | 0 | 159.1255 | 159.1255 | 0% | 11.36% | 0% | 80% | 0% | 0 | 5.0025 | 5.0025 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6595 | 19 | 18.5 | 0 | 3.56 | 3.56 | 3.56 | 1.78 | 275 | 6595 | 1140 | 271.2329 | -3.2218 | -4.0373 | 1114.284 | 18.5041 | -97.5617 | -7.5233 | 0 | 85.2927 | 265.2927 | 86.6733 | 0 | 0 | 3.0387 | 3.0387 | -38.0534 | 0% | 1.3741 | 0 | 0 | 150.1651 | 150.1651 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6596 | 20 | 17.9 | 0 | 0 | 0 | 0 | 0 | 275 | 6596 | 1200 | 271.2329 | -3.2218 | -4.0373 | 1174.284 | 19.5041 | -112.5617 | -17.6554 | 0 | 85.2927 | 265.2927 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.286 | 143.286 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6597 | 21 | 17.6 | 0 | 0 | 0 | 0 | 0 | 275 | 6597 | 1260 | 271.2329 | -3.2218 | -4.0373 | 1234.284 | 20.5041 | -127.5617 | -27.2436 | 0 | 85.2927 | 265.2927 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.5805 | 0 | 0% | 11.46% | 0% | 80% | 0% | 0 | 5.4364 | 5.4364 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6598 | 22 | 16.6 | 0 | 0 | 0 | 0 | 0 | 275 | 6598 | 1320 | 271.2329 | -3.2218 | -4.0373 | 1294.284 | 21.5041 | -142.5617 | -35.722 | 0 | 85.2927 | 265.2927 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.4132 | 0 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.6539 | 5.6539 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6599 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 275 | 6599 | 1380 | 271.2329 | -3.2218 | -4.0373 | 1354.284 | 22.5041 | -157.5617 | -42.2938 | 0 | 85.2927 | 265.2927 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.8871 | 0 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.7878 | 5.7878 | 0 | 0 | 0% | 0%
10 | 275 | 2 | 6600 | 24 | 15.7 | 0 | 0 | 0 | 0 | 0 | 275 | 6600 | 1440 | 271.2329 | -3.2218 | -4.0373 | 1414.284 | 23.5041 | -172.5617 | -45.9674 | 0 | 85.2927 | 265.2927 | 86.6733 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9038 | 0 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6601 | 1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 276 | 6601 | 60 | 272.2192 | -3.6202 | -3.7201 | 34.284 | 0.5094 | 172.359 | -46.3363 | 0 | 84.7097 | 95.2903 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1747 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6602 | 2 | 14.9 | 0 | 0 | 0 | 0 | 0 | 276 | 6602 | 120 | 272.2192 | -3.6202 | -3.7201 | 94.284 | 1.5094 | 157.359 | -42.5942 | 0 | 84.7097 | 95.2903 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9044 | 0 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6603 | 3 | 14.4 | 0 | 0 | 0 | 0 | 0 | 276 | 6603 | 180 | 272.2192 | -3.6202 | -3.7201 | 154.284 | 2.5094 | 142.359 | -35.9595 | 0 | 84.7097 | 95.2903 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3961 | 0 | 0% | 11.6% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6604 | 4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 276 | 6604 | 240 | 272.2192 | -3.6202 | -3.7201 | 214.284 | 3.5094 | 127.359 | -27.435 | 0 | 84.7097 | 95.2903 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3105 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6605 | 5 | 12.7 | 0 | 0 | 0 | 0 | 0 | 276 | 6605 | 300 | 272.2192 | -3.6202 | -3.7201 | 274.284 | 4.5094 | 112.359 | -17.8188 | 0 | 84.7097 | 95.2903 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.2896 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6606 | 6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 276 | 6606 | 360 | 272.2192 | -3.6202 | -3.7201 | 334.284 | 5.5094 | 97.359 | -7.675 | 0 | 84.7097 | 95.2903 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.7258 | 2.7258 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6607 | 7 | 12.7 | 0 | 0 | 0 | 0 | 0 | 276 | 6607 | 420 | 272.2192 | -3.6202 | -3.7201 | 394.284 | 6.5094 | 82.359 | 2.5714 | 2.5714 | 81.9474 | 98.0526 | 82.4913 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 157.906 | 157.906 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6608 | 8 | 12.5 | 2.22 | 22.5 | 24.72 | 22.5 | 11.25 | 276 | 6608 | 480 | 272.2192 | -3.6202 | -3.7201 | 454.284 | 7.5094 | 67.359 | 12.5381 | 12.5381 | 70.6646 | 109.3354 | 67.5397 | 3.9069 | 3.9069 | 19.205 | 23.1118 | -4.8919 | 0% | 10.4512 | 0 | 0 | 164.0153 | 164.0153 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6609 | 9 | 12.4 | 22 | 77.64 | 99.64 | 77.64 | 38.82 | 276 | 6609 | 540 | 272.2192 | -3.6202 | -3.7201 | 514.284 | 8.5094 | 52.359 | 21.801 | 21.801 | 58.3367 | 121.6633 | 52.6098 | 35.9716 | 35.9716 | 66.2699 | 102.2414 | -0.48581 | 0% | 46.2336 | 0 | 0 | 147.6117 | 147.6117 | 0% | 11.64% | 11.64% | 80% | 9.315% | 4.3066 | 6.6439 | 6 | 25.8398 | 9.5237 | 17.51% | 17.51%
10 | 276 | 3 | 6610 | 10 | 12.7 | 60.69 | 122.83 | 183.52 | 122.83 | 61.42 | 276 | 6610 | 600 | 272.2192 | -3.6202 | -3.7201 | 574.284 | 9.5094 | 37.359 | 29.8173 | 29.8173 | 44.2668 | 135.7332 | 37.7283 | 96.5359 | 96.5359 | 104.842 | 201.3778 | 0.15258 | 15.26% | 91.0631 | 13.8943 | 9.726 | 151.989 | 151.989 | 6.399% | 11.59% | 11.59% | 80% | 9.274% | 8.4451 | 6.5691 | 6 | 50.6705 | 18.6755 | 33.34% | 33.34%
10 | 276 | 3 | 6611 | 11 | 13.2 | 108.39 | 167.28 | 275.67 | 167.28 | 83.64 | 276 | 6611 | 660 | 272.2192 | -3.6202 | -3.7201 | 634.284 | 10.5094 | 22.359 | 35.8782 | 35.8782 | 27.9403 | 152.0597 | 22.9905 | 170.2552 | 170.2552 | 142.7824 | 313.0376 | 0.38861 | 38.86% | 141.5556 | 55.0093 | 38.5065 | 132.4753 | 132.4753 | 29.07% | 11.53% | 11.53% | 85% | 9.804% | 13.8781 | 6.4458 | 6 | 83.2687 | 30.6902 | 62.86% | 62.86%
10 | 276 | 3 | 6612 | 12 | 14.1 | 182.56 | 251.39 | 433.95 | 251.39 | 125.7 | 276 | 6612 | 720 | 272.2192 | -3.6202 | -3.7201 | 694.284 | 11.5094 | 7.359 | 39.1844 | 39.1844 | 9.4925 | 170.5075 | 9.1237 | 285.2882 | 285.2882 | 214.5748 | 499.863 | 0.54798 | 54.8% | 226.038 | 123.8635 | 86.7045 | 135.1885 | 135.1885 | 64.14% | 11.45% | 11.45% | 85% | 9.732% | 21.998 | 6.2283 | 6 | 131.9879 | 48.6466 | 97.63% | 97.63%
10 | 276 | 3 | 6613 | 13 | 14.8 | 228.67 | 243 | 471.67 | 243 | 121.5 | 276 | 6613 | 780 | 272.2192 | -3.6202 | -3.7201 | 754.284 | 12.5094 | -7.641 | 39.152 | 39.152 | 9.853 | 189.853 | 9.3524 | 357.3611 | 357.3611 | 207.4135 | 564.7746 | 0.58022 | 58.02% | 255.3911 | 148.1836 | 103.7285 | 136.3263 | 136.3263 | 76.09% | 11.42% | 11.42% | 90% | 10.28% | 26.2474 | 6.0631 | 6 | 157.4846 | 58.0438 | 115.5% | 115.5%
10 | 276 | 3 | 6614 | 14 | 15.1 | 214.11 | 227.5 | 441.61 | 227.5 | 113.75 | 276 | 6614 | 840 | 272.2192 | -3.6202 | -3.7201 | 814.284 | 13.5094 | -22.641 | 35.7873 | 35.7873 | 28.2687 | 208.2687 | 23.2646 | 336.3689 | 336.3689 | 194.1834 | 530.5523 | 0.56707 | 56.71% | 239.9158 | 136.0493 | 95.2345 | 134.8809 | 134.8809 | 70.61% | 11.42% | 11.42% | 90% | 10.28% | 24.6685 | 5.9933 | 5.9933 | 147.8462 | 54.5522 | 109.6% | 109.6%
10 | 276 | 3 | 6615 | 15 | 15.4 | 149.67 | 218.11 | 367.78 | 218.11 | 109.06 | 276 | 6615 | 900 | 272.2192 | -3.6202 | -3.7201 | 874.284 | 14.5094 | -37.641 | 29.6821 | 29.6821 | 44.5511 | 224.5511 | 38.0072 | 238.152 | 238.152 | 186.1685 | 424.3206 | 0.50936 | 50.94% | 191.8778 | 97.7339 | 68.4137 | 130.0075 | 130.0075 | 52.62% | 11.45% | 11.45% | 85% | 9.73% | 18.6697 | 5.9242 | 5.9242 | 110.6026 | 41.2863 | 85.07% | 85.07%
10 | 276 | 3 | 6616 | 16 | 14.6 | 84.22 | 144.31 | 228.53 | 144.31 | 72.16 | 276 | 6616 | 960 | 272.2192 | -3.6202 | -3.7201 | 934.284 | 15.5094 | -52.641 | 21.6365 | 21.6365 | 58.5824 | 238.5824 | 52.8901 | 137.8126 | 137.8126 | 123.1763 | 260.9889 | 0.31801 | 31.8% | 118.0192 | 37.5312 | 26.2718 | 120.9932 | 120.9932 | 21.71% | 11.51% | 11.51% | 80% | 9.21% | 10.8692 | 6.1099 | 6 | 65.2151 | 24.0362 | 53.9% | 53.9%
10 | 276 | 3 | 6617 | 17 | 14.3 | 50.14 | 119.94 | 170.08 | 119.94 | 59.97 | 276 | 6617 | 1020 | 272.2192 | -3.6202 | -3.7201 | 994.284 | 16.5094 | -67.641 | 12.3558 | 12.3558 | 70.8841 | 250.8841 | 67.8206 | 88.4572 | 88.4572 | 102.3752 | 190.8324 | 0.13576 | 13.58% | 86.2944 | 11.7158 | 8.201 | 115.6751 | 115.6751 | 7.09% | 11.54% | 0% | 80% | 0% | 0 | 6.1808 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6618 | 18 | 13.6 | 23.06 | 49.31 | 72.37 | 49.31 | 24.66 | 276 | 6618 | 1080 | 272.2192 | -3.6202 | -3.7201 | 1054.284 | 17.5094 | -82.641 | 2.3802 | 2.3802 | 82.154 | 262.154 | 82.7725 | 0 | 0 | 42.0887 | 42.0887 | -2.2638 | 0% | 19.0325 | 0 | 0 | 149.277 | 149.277 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6619 | 19 | 13.1 | 0 | 5.06 | 5.06 | 5.06 | 2.53 | 276 | 6619 | 1140 | 272.2192 | -3.6202 | -3.7201 | 1114.284 | 18.5094 | -97.641 | -7.8679 | 0 | 84.7097 | 264.7097 | 86.2618 | 0 | 0 | 4.319 | 4.319 | -29.3567 | 0% | 1.953 | 0 | 0 | 141.1443 | 141.1443 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4703 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6620 | 20 | 12.7 | 0 | 0 | 0 | 0 | 0 | 276 | 6620 | 1200 | 272.2192 | -3.6202 | -3.7201 | 1174.284 | 19.5094 | -112.641 | -18.0059 | 0 | 84.7097 | 264.7097 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.7876 | 135.7876 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6621 | 21 | 12.5 | 0 | 0 | 0 | 0 | 0 | 276 | 6621 | 1260 | 272.2192 | -3.6202 | -3.7201 | 1234.284 | 20.5094 | -127.641 | -27.6073 | 0 | 84.7097 | 264.7097 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6257 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6622 | 22 | 12.2 | 0 | 0 | 0 | 0 | 0 | 276 | 6622 | 1320 | 272.2192 | -3.6202 | -3.7201 | 1294.284 | 21.5094 | -142.641 | -36.1045 | 0 | 84.7097 | 264.7097 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1005 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6623 | 23 | 12.1 | 0 | 0 | 0 | 0 | 0 | 276 | 6623 | 1380 | 272.2192 | -3.6202 | -3.7201 | 1354.284 | 22.5094 | -157.641 | -42.6945 | 0 | 84.7097 | 264.7097 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9826 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 276 | 3 | 6624 | 24 | 11.8 | 0 | 0 | 0 | 0 | 0 | 276 | 6624 | 1440 | 272.2192 | -3.6202 | -3.7201 | 1414.284 | 23.5094 | -172.641 | -46.3727 | 0 | 84.7097 | 264.7097 | 86.2618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1694 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6625 | 1 | 11.8 | 0 | 0 | 0 | 0 | 0 | 277 | 6625 | 60 | 273.2055 | -4.0182 | -3.4045 | 34.284 | 0.51466 | 172.2801 | -46.7202 | 0 | 84.1271 | 95.8729 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8175 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6626 | 2 | 11.6 | 0 | 0 | 0 | 0 | 0 | 277 | 6626 | 120 | 273.2055 | -4.0182 | -3.4045 | 94.284 | 1.5147 | 157.2801 | -42.9373 | 0 | 84.1271 | 95.8729 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6083 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6627 | 3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 277 | 6627 | 180 | 273.2055 | -4.0182 | -3.4045 | 154.284 | 2.5147 | 142.2801 | -36.2591 | 0 | 84.1271 | 95.8729 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0943 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6628 | 4 | 10.9 | 0 | 0 | 0 | 0 | 0 | 277 | 6628 | 240 | 273.2055 | -4.0182 | -3.4045 | 214.284 | 3.5147 | 127.2801 | -27.7006 | 0 | 84.1271 | 95.8729 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1611 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6629 | 5 | 10.1 | 0 | 0 | 0 | 0 | 0 | 277 | 6629 | 300 | 273.2055 | -4.0182 | -3.4045 | 274.284 | 4.5147 | 112.2801 | -18.0632 | 0 | 84.1271 | 95.8729 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.6112 | 1.6112 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6630 | 6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 277 | 6630 | 360 | 273.2055 | -4.0182 | -3.4045 | 334.284 | 5.5147 | 97.2801 | -7.9108 | 0 | 84.1271 | 95.8729 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 10.2931 | 10.2931 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6631 | 7 | 9.5 | 0 | 0 | 0 | 0 | 0 | 277 | 6631 | 420 | 273.2055 | -4.0182 | -3.4045 | 394.284 | 6.5147 | 82.2801 | 2.3328 | 2.3328 | 81.619 | 98.381 | 82.4286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 172.9996 | 172.9996 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6632 | 8 | 9.2 | 17.17 | 24.44 | 41.61 | 24.44 | 12.22 | 277 | 6632 | 480 | 273.2055 | -4.0182 | -3.4045 | 454.284 | 7.5147 | 67.2801 | 12.2856 | 12.2856 | 70.3395 | 109.6605 | 67.4855 | 30.8983 | 30.8983 | 20.8608 | 51.7591 | -1.8875 | 0% | 23.4055 | 0 | 0 | 183.1575 | 183.1575 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6633 | 9 | 9.3 | 98.61 | 77.44 | 176.05 | 77.44 | 38.72 | 277 | 6633 | 540 | 273.2055 | -4.0182 | -3.4045 | 514.284 | 8.5147 | 52.2801 | 21.5237 | 21.5237 | 58.0182 | 121.9818 | 52.5673 | 163.37 | 163.37 | 66.0992 | 229.4692 | 0.19793 | 19.79% | 103.766 | 20.538 | 14.3766 | 170.0743 | 170.0743 | 8.453% | 11.69% | 11.69% | 80% | 9.35% | 9.7023 | 7.4538 | 6 | 58.214 | 21.4558 | 34.23% | 34.23%
10 | 277 | 4 | 6634 | 10 | 9.7 | 169.17 | 110.61 | 279.78 | 110.61 | 55.31 | 277 | 6634 | 600 | 273.2055 | -4.0182 | -3.4045 | 574.284 | 9.5147 | 37.2801 | 29.5052 | 29.5052 | 43.9684 | 136.0316 | 37.7049 | 271.7595 | 271.7595 | 94.4115 | 366.1711 | 0.42675 | 42.67% | 165.5826 | 70.6621 | 49.4635 | 151.7758 | 151.7758 | 32.59% | 11.6% | 11.6% | 85% | 9.858% | 16.3233 | 7.3455 | 6 | 97.9398 | 36.0975 | 64.53% | 64.53%
10 | 277 | 4 | 6635 | 11 | 10.4 | 203.67 | 139.94 | 343.61 | 139.94 | 69.97 | 277 | 6635 | 660 | 273.2055 | -4.0182 | -3.4045 | 634.284 | 10.5147 | 22.2801 | 35.5264 | 35.5264 | 27.6915 | 152.3085 | 23.0083 | 322.6204 | 322.6204 | 119.4463 | 442.0667 | 0.49521 | 49.52% | 199.9026 | 98.9943 | 69.296 | 147.9335 | 147.9335 | 46.84% | 11.54% | 11.54% | 85% | 9.81% | 19.6101 | 7.1587 | 6 | 117.6607 | 43.366 | 79.54% | 79.54%
10 | 277 | 4 | 6636 | 12 | 11.3 | 176.39 | 156.94 | 333.33 | 156.94 | 78.47 | 277 | 6636 | 720 | 273.2055 | -4.0182 | -3.4045 | 694.284 | 11.5147 | 7.2801 | 38.7978 | 38.7978 | 9.3344 | 170.6656 | 9.3022 | 277.8132 | 277.8132 | 133.9567 | 411.7699 | 0.47757 | 47.76% | 186.2023 | 88.925 | 62.2475 | 137.7038 | 137.7038 | 45.2% | 11.54% | 11.54% | 85% | 9.807% | 18.2611 | 6.9236 | 6 | 109.5663 | 40.3827 | 79.57% | 79.57%
10 | 277 | 4 | 6637 | 13 | 12 | 253.28 | 155.69 | 408.97 | 155.69 | 77.85 | 277 | 6637 | 780 | 273.2055 | -4.0182 | -3.4045 | 754.284 | 12.5147 | -7.7199 | 38.7475 | 38.7475 | 9.8933 | 189.8933 | 9.6498 | 398.9465 | 398.9465 | 132.8897 | 531.8362 | 0.55431 | 55.43% | 240.4963 | 133.3095 | 93.3166 | 139.2341 | 139.2341 | 67.02% | 11.47% | 11.47% | 90% | 10.32% | 24.8264 | 6.7446 | 6 | 148.9585 | 54.9014 | 107% | 107%
10 | 277 | 4 | 6638 | 14 | 12.8 | 266.81 | 165.14 | 431.95 | 165.14 | 82.57 | 277 | 6638 | 840 | 273.2055 | -4.0182 | -3.4045 | 814.284 | 13.5147 | -22.7199 | 35.3853 | 35.3853 | 28.2013 | 208.2013 | 23.4339 | 422.7515 | 422.7515 | 140.9558 | 563.7073 | 0.57169 | 57.17% | 254.9084 | 145.7299 | 102.0109 | 140.2816 | 140.2816 | 72.72% | 11.45% | 11.45% | 90% | 10.3% | 26.2582 | 6.5443 | 6 | 157.5489 | 58.0676 | 112.3% | 112.3%
10 | 277 | 4 | 6639 | 15 | 13.2 | 227.83 | 164.78 | 392.61 | 164.78 | 82.39 | 277 | 6639 | 900 | 273.2055 | -4.0182 | -3.4045 | 874.284 | 14.5147 | -37.7199 | 29.2953 | 29.2953 | 44.4106 | 224.4106 | 38.1392 | 366.211 | 366.211 | 140.6485 | 506.8595 | 0.54745 | 54.75% | 229.2019 | 125.4769 | 87.8338 | 136.6099 | 136.6099 | 64.3% | 11.46% | 11.46% | 90% | 10.32% | 23.6433 | 6.4458 | 6 | 141.8595 | 52.2849 | 103.8% | 103.8%
10 | 277 | 4 | 6640 | 16 | 14 | 136.67 | 117.36 | 254.03 | 117.36 | 58.68 | 277 | 6640 | 960 | 273.2055 | -4.0182 | -3.4045 | 934.284 | 15.5147 | -52.7199 | 21.2677 | 21.2677 | 58.4008 | 238.4008 | 53.0041 | 226.7342 | 226.7342 | 100.173 | 326.9072 | 0.41183 | 41.18% | 147.8274 | 60.8791 | 42.6154 | 129.5031 | 129.5031 | 32.91% | 11.51% | 11.51% | 85% | 9.782% | 14.4603 | 6.2522 | 6 | 86.762 | 31.9777 | 67% | 67%
10 | 277 | 4 | 6641 | 17 | 12.9 | 98.94 | 74.58 | 173.52 | 74.58 | 37.29 | 277 | 6641 | 1020 | 273.2055 | -4.0182 | -3.4045 | 994.284 | 16.5147 | -67.7199 | 12.0017 | 12.0017 | 70.6816 | 250.6816 | 67.9233 | 178.8311 | 178.8311 | 63.658 | 242.4891 | 0.26491 | 26.49% | 109.6536 | 29.0488 | 20.3342 | 121.52 | 121.52 | 16.73% | 11.57% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6642 | 18 | 11.6 | 28.33 | 32.83 | 61.16 | 32.83 | 16.42 | 277 | 6642 | 1080 | 273.2055 | -4.0182 | -3.4045 | 1054.284 | 17.5147 | -82.7199 | 2.0347 | 2.0347 | 81.9411 | 261.9411 | 82.8669 | 0 | 0 | 28.0222 | 28.0222 | -3.9679 | 0% | 12.6716 | 0 | 0 | 151.5354 | 151.5354 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6643 | 19 | 10.8 | 0 | 3.06 | 3.06 | 3.06 | 1.53 | 277 | 6643 | 1140 | 273.2055 | -4.0182 | -3.4045 | 1114.284 | 18.5147 | -97.7199 | -8.2116 | 0 | 84.1271 | 264.1271 | 85.8509 | 0 | 0 | 2.6119 | 2.6119 | -51.1027 | 0% | 1.1811 | 0 | 0 | 142.1756 | 142.1756 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6644 | 20 | 10.1 | 0 | 0 | 0 | 0 | 0 | 277 | 6644 | 1200 | 273.2055 | -4.0182 | -3.4045 | 1174.284 | 19.5147 | -112.7199 | -18.3554 | 0 | 84.1271 | 264.1271 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.86 | 134.86 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6645 | 21 | 10 | 0 | 0 | 0 | 0 | 0 | 277 | 6645 | 1260 | 273.2055 | -4.0182 | -3.4045 | 1234.284 | 20.5147 | -127.7199 | -27.9701 | 0 | 84.1271 | 264.1271 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7506 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6646 | 22 | 9.9 | 0 | 0 | 0 | 0 | 0 | 277 | 6646 | 1320 | 273.2055 | -4.0182 | -3.4045 | 1294.284 | 21.5147 | -142.7199 | -36.4862 | 0 | 84.1271 | 264.1271 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.255 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6647 | 23 | 9.8 | 0 | 0 | 0 | 0 | 0 | 277 | 6647 | 1380 | 273.2055 | -4.0182 | -3.4045 | 1354.284 | 22.5147 | -157.7199 | -43.0945 | 0 | 84.1271 | 264.1271 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8934 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
10 | 277 | 4 | 6648 | 24 | 9.4 | 0 | 0 | 0 | 0 | 0 | 277 | 6648 | 1440 | 273.2055 | -4.0182 | -3.4045 | 1414.284 | 23.5147 | -172.7199 | -46.7775 | 0 | 84.1271 | 264.1271 | 85.8509 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.989 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6649 | 1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 278 | 6649 | 60 | 274.1918 | -4.4156 | -3.091 | 34.284 | 0.51988 | 172.2018 | -47.1034 | 0 | 83.545 | 96.455 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2428 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6650 | 2 | 7.8 | 0 | 0 | 0 | 0 | 0 | 278 | 6650 | 120 | 274.1918 | -4.4156 | -3.091 | 94.284 | 1.5199 | 157.2018 | -43.2792 | 0 | 83.545 | 96.455 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3534 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6651 | 3 | 7.6 | 0 | 0 | 0 | 0 | 0 | 278 | 6651 | 180 | 274.1918 | -4.4156 | -3.091 | 154.284 | 2.5199 | 142.2018 | -36.5575 | 0 | 83.545 | 96.455 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3971 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6652 | 4 | 7.1 | 0 | 0 | 0 | 0 | 0 | 278 | 6652 | 240 | 274.1918 | -4.4156 | -3.091 | 214.284 | 3.5199 | 127.2018 | -27.9653 | 0 | 83.545 | 96.455 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1591 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6653 | 5 | 6.8 | 0 | 0 | 0 | 0 | 0 | 278 | 6653 | 300 | 274.1918 | -4.4156 | -3.091 | 274.284 | 4.5199 | 112.2018 | -18.3071 | 0 | 83.545 | 96.455 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5425 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6654 | 6 | 6.1 | 0 | 0 | 0 | 0 | 0 | 278 | 6654 | 360 | 274.1918 | -4.4156 | -3.091 | 334.284 | 5.5199 | 97.2018 | -8.1463 | 0 | 83.545 | 96.455 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.5256 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6655 | 7 | 6.4 | 0 | 0 | 0 | 0 | 0 | 278 | 6655 | 420 | 274.1918 | -4.4156 | -3.091 | 394.284 | 6.5199 | 82.2018 | 2.0942 | 2.0942 | 81.2915 | 98.7085 | 82.3669 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.1208 | 149.1208 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6656 | 8 | 6.4 | 8.11 | 21.72 | 29.83 | 21.72 | 10.86 | 278 | 6656 | 480 | 274.1918 | -4.4156 | -3.091 | 454.284 | 7.5199 | 67.2018 | 12.0328 | 12.0328 | 70.0158 | 109.9842 | 67.4331 | 14.9293 | 14.9293 | 18.5392 | 33.4684 | -3.5562 | 0% | 15.1344 | 0 | 0 | 155.4261 | 155.4261 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6657 | 9 | 6.6 | 47.92 | 63.19 | 111.11 | 63.19 | 31.6 | 278 | 6657 | 540 | 274.1918 | -4.4156 | -3.091 | 514.284 | 8.5199 | 52.2018 | 21.2458 | 21.2458 | 57.7017 | 122.2983 | 52.5275 | 80.4527 | 80.4527 | 53.936 | 134.3887 | -0.27834 | 0% | 60.7706 | 0 | 0 | 139.4822 | 139.4822 | 0% | 11.84% | 11.84% | 80% | 9.474% | 5.7574 | 8.2139 | 6 | 34.5446 | 12.732 | 24.77% | 24.77%
10 | 278 | 5 | 6658 | 10 | 7.7 | 85.06 | 93.75 | 178.81 | 93.75 | 46.88 | 278 | 6658 | 600 | 274.1918 | -4.4156 | -3.091 | 574.284 | 9.5199 | 37.2018 | 29.1928 | 29.1928 | 43.6728 | 136.3272 | 37.6857 | 138.0101 | 138.0101 | 80.0206 | 218.0308 | 0.14885 | 14.88% | 98.5935 | 14.6754 | 10.2728 | 143.3856 | 143.3856 | 7.164% | 11.75% | 11.75% | 80% | 9.397% | 9.2644 | 7.8981 | 6 | 55.5864 | 20.4874 | 38.77% | 38.77%
10 | 278 | 5 | 6659 | 11 | 8.7 | 127 | 100.5 | 227.5 | 100.5 | 50.25 | 278 | 6659 | 660 | 274.1918 | -4.4156 | -3.091 | 634.284 | 10.5199 | 22.2018 | 35.1745 | 35.1745 | 27.4458 | 152.5542 | 23.0333 | 202.8845 | 202.8845 | 85.7821 | 288.6667 | 0.31733 | 31.73% | 130.5351 | 41.4232 | 28.9962 | 122.2579 | 122.2579 | 23.72% | 11.67% | 11.67% | 80% | 9.336% | 12.1865 | 7.6183 | 6 | 73.1192 | 26.9494 | 59.81% | 59.81%
10 | 278 | 5 | 6660 | 12 | 11.2 | 133.33 | 109.86 | 243.19 | 109.86 | 54.93 | 278 | 6660 | 720 | 274.1918 | -4.4156 | -3.091 | 694.284 | 11.5199 | 7.2018 | 38.4114 | 38.4114 | 9.1788 | 170.8212 | 9.4946 | 211.6572 | 211.6572 | 93.7714 | 305.4286 | 0.36316 | 36.32% | 138.1148 | 50.1578 | 35.1104 | 120.8967 | 120.8967 | 29.04% | 11.59% | 11.59% | 85% | 9.853% | 13.608 | 6.9494 | 6 | 81.6479 | 30.0929 | 67.54% | 67.54%
10 | 278 | 5 | 6661 | 13 | 13.6 | 125.14 | 87.78 | 212.92 | 87.78 | 43.89 | 278 | 6661 | 780 | 274.1918 | -4.4156 | -3.091 | 754.284 | 12.5199 | -7.7982 | 38.3436 | 38.3436 | 9.9325 | 189.9325 | 9.954 | 198.6798 | 198.6798 | 74.9249 | 273.6047 | 0.33208 | 33.21% | 123.724 | 41.0868 | 28.7608 | 121.9118 | 121.9118 | 23.59% | 11.54% | 11.54% | 80% | 9.23% | 11.4195 | 6.3484 | 6 | 68.5171 | 25.2533 | 56.2% | 56.2%
10 | 278 | 5 | 6662 | 14 | 14.3 | 187.44 | 115.42 | 302.86 | 115.42 | 57.71 | 278 | 6662 | 840 | 274.1918 | -4.4156 | -3.091 | 814.284 | 13.5199 | -22.7982 | 34.984 | 34.984 | 28.1342 | 208.1342 | 23.6079 | 299.5611 | 299.5611 | 98.5171 | 398.0783 | 0.48366 | 48.37% | 180.011 | 87.0639 | 60.9447 | 126.354 | 126.354 | 48.23% | 11.48% | 11.48% | 85% | 9.756% | 17.5624 | 6.1808 | 6 | 105.3745 | 38.8377 | 83.4% | 83.4%
10 | 278 | 5 | 6663 | 15 | 15.5 | 150.06 | 94.17 | 244.23 | 94.17 | 47.09 | 278 | 6663 | 900 | 274.1918 | -4.4156 | -3.091 | 874.284 | 14.5199 | -37.7982 | 28.9092 | 28.9092 | 44.2708 | 224.2708 | 38.2737 | 243.6918 | 243.6918 | 80.3791 | 324.0709 | 0.41891 | 41.89% | 146.5449 | 61.3886 | 42.972 | 124.0883 | 124.0883 | 34.63% | 11.47% | 11.47% | 85% | 9.749% | 14.2871 | 5.9013 | 5.9013 | 84.3123 | 31.5947 | 67.95% | 67.95%
10 | 278 | 5 | 6664 | 16 | 16 | 85.61 | 68.28 | 153.89 | 68.28 | 34.14 | 278 | 6664 | 960 | 274.1918 | -4.4156 | -3.091 | 934.284 | 15.5199 | -52.7982 | 20.8995 | 20.8995 | 58.2199 | 238.2199 | 53.1194 | 144.0272 | 144.0272 | 58.2806 | 202.3078 | 0.19271 | 19.27% | 91.4836 | 17.6298 | 12.3409 | 119.6602 | 119.6602 | 10.31% | 11.48% | 11.48% | 80% | 9.187% | 8.4044 | 5.7878 | 5.7878 | 48.643 | 18.5856 | 40.65% | 40.65%
10 | 278 | 5 | 6665 | 17 | 15.4 | 65.06 | 50.56 | 115.62 | 50.56 | 25.28 | 278 | 6665 | 1020 | 274.1918 | -4.4156 | -3.091 | 994.284 | 16.5199 | -67.7982 | 11.6483 | 11.6483 | 70.4795 | 250.4795 | 68.0265 | 120.5723 | 120.5723 | 43.1557 | 163.728 | 0.040393 | 4.039% | 74.0378 | 2.9906 | 2.0934 | 157.4797 | 157.4797 | 1.329% | 11.51% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6666 | 18 | 14.7 | 20.14 | 25.28 | 45.42 | 25.28 | 12.64 | 278 | 6666 | 1080 | 274.1918 | -4.4156 | -3.091 | 1054.284 | 17.5199 | -82.7982 | 1.6901 | 1.6901 | 81.7282 | 261.7282 | 82.9611 | 0 | 0 | 21.5778 | 21.5778 | -5.0636 | 0% | 9.7575 | 0 | 0 | 150.3202 | 150.3202 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6667 | 19 | 13.8 | 0 | 2.92 | 2.92 | 2.92 | 1.46 | 278 | 6667 | 1140 | 274.1918 | -4.4156 | -3.091 | 1114.284 | 18.5199 | -97.7982 | -8.5544 | 0 | 83.545 | 263.545 | 85.4405 | 0 | 0 | 2.4924 | 2.4924 | -50.8179 | 0% | 1.1271 | 0 | 0 | 143.3281 | 143.3281 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.3002 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6668 | 20 | 13 | 0 | 0 | 0 | 0 | 0 | 278 | 6668 | 1200 | 274.1918 | -4.4156 | -3.091 | 1174.284 | 19.5199 | -112.7982 | -18.7039 | 0 | 83.545 | 263.545 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.2726 | 138.2726 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6669 | 21 | 12.2 | 0 | 0 | 0 | 0 | 0 | 278 | 6669 | 1260 | 274.1918 | -4.4156 | -3.091 | 1234.284 | 20.5199 | -127.7982 | -28.3318 | 0 | 83.545 | 263.545 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8555 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6670 | 22 | 12.1 | 0 | 0 | 0 | 0 | 0 | 278 | 6670 | 1320 | 274.1918 | -4.4156 | -3.091 | 1294.284 | 21.5199 | -142.7982 | -36.8668 | 0 | 83.545 | 263.545 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8445 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6671 | 23 | 12.1 | 0 | 0 | 0 | 0 | 0 | 278 | 6671 | 1380 | 274.1918 | -4.4156 | -3.091 | 1354.284 | 22.5199 | -157.7982 | -43.4937 | 0 | 83.545 | 263.545 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5834 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 278 | 5 | 6672 | 24 | 12.1 | 0 | 0 | 0 | 0 | 0 | 278 | 6672 | 1440 | 274.1918 | -4.4156 | -3.091 | 1414.284 | 23.5199 | -172.7982 | -47.1815 | 0 | 83.545 | 263.545 | 85.4405 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3223 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6673 | 1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 279 | 6673 | 60 | 275.1781 | -4.8123 | -2.7799 | 34.284 | 0.52507 | 172.124 | -47.4856 | 0 | 82.9636 | 97.0364 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3249 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6674 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 279 | 6674 | 120 | 275.1781 | -4.8123 | -2.7799 | 94.284 | 1.5251 | 157.124 | -43.62 | 0 | 82.9636 | 97.0364 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0604 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6675 | 3 | 11.8 | 0 | 0 | 0 | 0 | 0 | 279 | 6675 | 180 | 275.1781 | -4.8123 | -2.7799 | 154.284 | 2.5251 | 142.124 | -36.8548 | 0 | 82.9636 | 97.0364 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2531 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6676 | 4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 279 | 6676 | 240 | 275.1781 | -4.8123 | -2.7799 | 214.284 | 3.5251 | 127.124 | -28.229 | 0 | 82.9636 | 97.0364 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0151 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6677 | 5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 279 | 6677 | 300 | 275.1781 | -4.8123 | -2.7799 | 274.284 | 4.5251 | 112.124 | -18.5503 | 0 | 82.9636 | 97.0364 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3182 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6678 | 6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 279 | 6678 | 360 | 275.1781 | -4.8123 | -2.7799 | 334.284 | 5.5251 | 97.124 | -8.3814 | 0 | 82.9636 | 97.0364 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2404 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6679 | 7 | 9.9 | 0 | 0 | 0 | 0 | 0 | 279 | 6679 | 420 | 275.1781 | -4.8123 | -2.7799 | 394.284 | 6.5251 | 82.124 | 1.8555 | 1.8555 | 80.9651 | 99.0349 | 82.3062 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.0025 | 143.0025 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6680 | 8 | 10.1 | 0.61 | 15.5 | 16.11 | 15.5 | 7.75 | 279 | 6680 | 480 | 275.1781 | -4.8123 | -2.7799 | 454.284 | 7.5251 | 67.124 | 11.7796 | 11.7796 | 69.6938 | 110.3062 | 67.3824 | 1.1491 | 1.1491 | 13.2301 | 14.3792 | -8.7378 | 0% | 6.5023 | 0 | 0 | 147.264 | 147.264 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6681 | 9 | 11.9 | 4.39 | 48.33 | 52.72 | 48.33 | 24.17 | 279 | 6681 | 540 | 275.1781 | -4.8123 | -2.7799 | 514.284 | 8.5251 | 52.124 | 20.9675 | 20.9675 | 57.3875 | 122.6125 | 52.4905 | 7.47 | 7.47 | 41.2522 | 48.7222 | -1.9263 | 0% | 22.0322 | 0 | 0 | 131.4812 | 131.4812 | 0% | 11.69% | 11.69% | 80% | 9.349% | 2.0599 | 6.77 | 6 | 12.3592 | 4.5552 | 9.4% | 9.4%
10 | 279 | 6 | 6682 | 10 | 13.5 | 8.56 | 90 | 98.56 | 90 | 45 | 279 | 6682 | 600 | 275.1781 | -4.8123 | -2.7799 | 574.284 | 9.5251 | 37.124 | 28.88 | 28.88 | 43.38 | 136.62 | 37.6708 | 14.0287 | 14.0287 | 76.8198 | 90.8485 | -0.61977 | 0% | 41.0817 | 0 | 0 | 136.4368 | 136.4368 | 0% | 11.61% | 11.61% | 80% | 9.284% | 3.8142 | 6.3727 | 6 | 22.8852 | 8.4348 | 16.77% | 16.77%
10 | 279 | 6 | 6683 | 11 | 15.2 | 37.17 | 156.11 | 193.28 | 156.11 | 78.06 | 279 | 6683 | 660 | 275.1781 | -4.8123 | -2.7799 | 634.284 | 10.5251 | 22.124 | 34.8225 | 34.8225 | 27.2032 | 152.7968 | 23.0654 | 59.8887 | 59.8887 | 133.2482 | 193.1369 | 0.15432 | 15.43% | 87.3365 | 13.478 | 9.4346 | 141.8732 | 141.8732 | 6.65% | 11.51% | 11.51% | 80% | 9.21% | 8.0435 | 5.9702 | 5.9702 | 48.0213 | 17.7875 | 33.85% | 33.85%
10 | 279 | 6 | 6684 | 12 | 16.8 | 40.42 | 172.56 | 212.98 | 172.56 | 86.28 | 279 | 6684 | 720 | 275.1781 | -4.8123 | -2.7799 | 694.284 | 11.5251 | 7.124 | 38.0255 | 38.0255 | 9.0258 | 170.9742 | 9.7001 | 64.6774 | 64.6774 | 147.2892 | 211.9666 | 0.22905 | 22.91% | 95.8513 | 21.9551 | 15.3686 | 121.2809 | 121.2809 | 12.67% | 11.46% | 11.46% | 80% | 9.164% | 8.7842 | 5.6099 | 5.6099 | 49.2783 | 19.4255 | 40.63% | 40.63%
10 | 279 | 6 | 6685 | 13 | 18.5 | 91.17 | 183.47 | 274.64 | 183.47 | 91.74 | 279 | 6685 | 780 | 275.1781 | -4.8123 | -2.7799 | 754.284 | 12.5251 | -7.876 | 37.9406 | 37.9406 | 9.9705 | 189.9705 | 10.2641 | 145.9087 | 145.9087 | 156.6014 | 302.5101 | 0.41369 | 41.37% | 136.7951 | 56.5901 | 39.6131 | 126.5102 | 126.5102 | 31.31% | 11.39% | 11.39% | 85% | 9.684% | 13.2474 | 5.2467 | 5.2467 | 69.5046 | 29.2953 | 54.94% | 54.94%
10 | 279 | 6 | 6686 | 14 | 20 | 45.22 | 184.72 | 229.94 | 184.72 | 92.36 | 279 | 6686 | 840 | 275.1781 | -4.8123 | -2.7799 | 814.284 | 13.5251 | -22.876 | 34.5836 | 34.5836 | 28.0672 | 208.0672 | 23.7864 | 72.9003 | 72.9003 | 157.6684 | 230.5687 | 0.30629 | 30.63% | 104.2632 | 31.9343 | 22.354 | 127.0559 | 127.0559 | 17.59% | 11.35% | 11.35% | 80% | 9.082% | 9.4688 | 4.943 | 4.943 | 46.8041 | 20.9393 | 36.84% | 36.84%
10 | 279 | 6 | 6687 | 15 | 20.1 | 53.47 | 163.94 | 217.41 | 163.94 | 81.97 | 279 | 6687 | 900 | 275.1781 | -4.8123 | -2.7799 | 874.284 | 14.5251 | -37.876 | 28.5238 | 28.5238 | 44.1317 | 224.1317 | 38.4107 | 87.7397 | 87.7397 | 139.9315 | 227.6713 | 0.30092 | 30.09% | 102.9529 | 30.9803 | 21.6862 | 125.5101 | 125.5101 | 17.28% | 11.35% | 11.35% | 80% | 9.079% | 9.3472 | 4.9233 | 4.9233 | 46.0191 | 20.6705 | 36.67% | 36.67%
10 | 279 | 6 | 6688 | 16 | 20.6 | 123.89 | 101.17 | 225.06 | 101.17 | 50.59 | 279 | 6688 | 960 | 275.1781 | -4.8123 | -2.7799 | 934.284 | 15.5251 | -52.876 | 20.5321 | 20.5321 | 58.0398 | 238.0398 | 53.2359 | 211.4171 | 211.4171 | 86.354 | 297.7711 | 0.42304 | 42.3% | 134.6521 | 56.963 | 39.8741 | 126.5663 | 126.5663 | 31.5% | 11.34% | 11.34% | 80% | 9.068% | 12.2107 | 4.8259 | 4.8259 | 58.9282 | 27.0029 | 46.56% | 46.56%
10 | 279 | 6 | 6689 | 17 | 20.6 | 47.78 | 66.44 | 114.22 | 66.44 | 33.22 | 279 | 6689 | 1020 | 275.1781 | -4.8123 | -2.7799 | 994.284 | 16.5251 | -67.876 | 11.2957 | 11.2957 | 70.2778 | 250.2778 | 68.1301 | 90.8655 | 90.8655 | 56.7101 | 147.5756 | 0.035314 | 3.531% | 66.7337 | 2.3566 | 1.6496 | 161.8861 | 161.8861 | 1.019% | 11.33% | 0% | 80% | 0% | 0 | 4.8259 | 4.8259 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6690 | 18 | 20.1 | 3.56 | 39.78 | 43.34 | 39.78 | 19.89 | 279 | 6690 | 1080 | 275.1781 | -4.8123 | -2.7799 | 1054.284 | 17.5251 | -82.876 | 1.3465 | 1.3465 | 81.5153 | 261.5153 | 83.055 | 0 | 0 | 33.9544 | 33.9544 | -2.5693 | 0% | 15.3542 | 0 | 0 | 154.9883 | 154.9883 | 0% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6691 | 19 | 19 | 0 | 3.61 | 3.61 | 3.61 | 1.81 | 279 | 6691 | 1140 | 275.1781 | -4.8123 | -2.7799 | 1114.284 | 18.5251 | -97.876 | -8.8961 | 0 | 82.9636 | 262.9636 | 85.0308 | 0 | 0 | 3.0813 | 3.0813 | -37.1554 | 0% | 1.3934 | 0 | 0 | 148.4657 | 148.4657 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1437 | 5.1437 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6692 | 20 | 15.3 | 0 | 0 | 0 | 0 | 0 | 279 | 6692 | 1200 | 275.1781 | -4.8123 | -2.7799 | 1174.284 | 19.5251 | -112.876 | -19.0512 | 0 | 82.9636 | 262.9636 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.1962 | 139.1962 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9472 | 5.9472 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6693 | 21 | 13.3 | 0 | 0 | 0 | 0 | 0 | 279 | 6693 | 1260 | 275.1781 | -4.8123 | -2.7799 | 1234.284 | 20.5251 | -127.876 | -28.6921 | 0 | 82.9636 | 262.9636 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7354 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6694 | 22 | 12.4 | 0 | 0 | 0 | 0 | 0 | 279 | 6694 | 1320 | 275.1781 | -4.8123 | -2.7799 | 1294.284 | 21.5251 | -142.876 | -37.2462 | 0 | 82.9636 | 262.9636 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8991 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6695 | 23 | 12.1 | 0 | 0 | 0 | 0 | 0 | 279 | 6695 | 1380 | 275.1781 | -4.8123 | -2.7799 | 1354.284 | 22.5251 | -157.876 | -43.8919 | 0 | 82.9636 | 262.9636 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2442 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 279 | 6 | 6696 | 24 | 11.7 | 0 | 0 | 0 | 0 | 0 | 279 | 6696 | 1440 | 275.1781 | -4.8123 | -2.7799 | 1414.284 | 23.5251 | -172.876 | -47.5848 | 0 | 82.9636 | 262.9636 | 85.0308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.7417 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6697 | 1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 280 | 6697 | 60 | 276.1644 | -5.2081 | -2.4716 | 34.284 | 0.53021 | 172.0469 | -47.8668 | 0 | 82.3831 | 97.6169 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5493 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6698 | 2 | 11.5 | 0 | 0 | 0 | 0 | 0 | 280 | 6698 | 120 | 276.1644 | -5.2081 | -2.4716 | 94.284 | 1.5302 | 157.0469 | -43.9594 | 0 | 82.3831 | 97.6169 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7367 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6699 | 3 | 11.8 | 0 | 0 | 0 | 0 | 0 | 280 | 6699 | 180 | 276.1644 | -5.2081 | -2.4716 | 154.284 | 2.5302 | 142.0469 | -37.1507 | 0 | 82.3831 | 97.6169 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1621 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6700 | 4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 280 | 6700 | 240 | 276.1644 | -5.2081 | -2.4716 | 214.284 | 3.5302 | 127.0469 | -28.4916 | 0 | 82.3831 | 97.6169 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9241 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6701 | 5 | 11.1 | 0 | 0 | 0 | 0 | 0 | 280 | 6701 | 300 | 276.1644 | -5.2081 | -2.4716 | 274.284 | 4.5302 | 112.0469 | -18.7928 | 0 | 82.3831 | 97.6169 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.1646 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6702 | 6 | 11.1 | 0 | 0 | 0 | 0 | 0 | 280 | 6702 | 360 | 276.1644 | -5.2081 | -2.4716 | 334.284 | 5.5302 | 97.0469 | -8.6163 | 0 | 82.3831 | 97.6169 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.1174 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6703 | 7 | 11.2 | 0 | 0 | 0 | 0 | 0 | 280 | 6703 | 420 | 276.1644 | -5.2081 | -2.4716 | 394.284 | 6.5302 | 82.0469 | 1.6169 | 1.6169 | 80.6399 | 99.3601 | 82.2467 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.9447 | 145.9447 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6704 | 8 | 11.6 | 2.83 | 21.17 | 24 | 21.17 | 10.59 | 280 | 6704 | 480 | 276.1644 | -5.2081 | -2.4716 | 454.284 | 7.5302 | 67.0469 | 11.5263 | 11.5263 | 69.3735 | 110.6265 | 67.3337 | 5.4579 | 5.4579 | 18.0697 | 23.5276 | -4.8795 | 0% | 10.6392 | 0 | 0 | 151.7667 | 151.7667 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6705 | 9 | 12.7 | 13.28 | 73.39 | 86.67 | 73.39 | 36.7 | 280 | 6705 | 540 | 276.1644 | -5.2081 | -2.4716 | 514.284 | 8.5302 | 52.0469 | 20.6889 | 20.6889 | 57.0757 | 122.9243 | 52.4563 | 22.9055 | 22.9055 | 62.6423 | 85.5478 | -0.72943 | 0% | 38.6847 | 0 | 0 | 136.4056 | 136.4056 | 0% | 11.64% | 11.64% | 80% | 9.311% | 3.602 | 6.5691 | 6 | 21.6118 | 7.9654 | 15.84% | 15.84%
10 | 280 | 7 | 6706 | 10 | 15 | 22.5 | 139.78 | 162.28 | 139.78 | 69.89 | 280 | 6706 | 600 | 276.1644 | -5.2081 | -2.4716 | 574.284 | 9.5302 | 37.0469 | 28.567 | 28.567 | 43.0902 | 136.9098 | 37.6602 | 37.2493 | 37.2493 | 119.3097 | 156.559 | -0.00036134 | 0% | 70.796 | 0 | 0 | 144.4588 | 144.4588 | 0% | 11.53% | 11.53% | 80% | 9.223% | 6.5296 | 6.0165 | 6 | 39.1777 | 14.4397 | 27.12% | 27.12%
10 | 280 | 7 | 6707 | 11 | 17.2 | 28.67 | 170.33 | 199 | 170.33 | 85.17 | 280 | 6707 | 660 | 276.1644 | -5.2081 | -2.4716 | 634.284 | 10.5302 | 22.0469 | 34.4706 | 34.4706 | 26.964 | 153.036 | 23.1047 | 46.5922 | 46.5922 | 145.3857 | 191.9779 | 0.17386 | 17.39% | 86.8124 | 15.0933 | 10.5653 | 147.9919 | 147.9919 | 7.139% | 11.45% | 11.45% | 80% | 9.157% | 7.949 | 5.5226 | 5.5226 | 43.8991 | 17.5785 | 29.66% | 29.66%
10 | 280 | 7 | 6708 | 12 | 18.1 | 28.61 | 195.75 | 224.36 | 195.75 | 97.88 | 280 | 6708 | 720 | 276.1644 | -5.2081 | -2.4716 | 694.284 | 11.5302 | 7.0469 | 37.6402 | 37.6402 | 8.8755 | 171.1245 | 9.9176 | 46.1477 | 46.1477 | 167.0831 | 213.2308 | 0.24609 | 24.61% | 96.423 | 23.7287 | 16.6101 | 126.528 | 126.528 | 13.13% | 11.41% | 11.41% | 80% | 9.131% | 8.804 | 5.3303 | 5.3303 | 46.9284 | 19.4694 | 37.09% | 37.09%
10 | 280 | 7 | 6709 | 13 | 20.4 | 199.86 | 188.94 | 388.8 | 188.94 | 94.47 | 280 | 6709 | 780 | 276.1644 | -5.2081 | -2.4716 | 754.284 | 12.5302 | -7.9531 | 37.5384 | 37.5384 | 10.0072 | 190.0072 | 10.5793 | 322.4438 | 322.4438 | 161.2704 | 483.7142 | 0.56858 | 56.86% | 218.7356 | 124.3677 | 87.0574 | 136.8607 | 136.8607 | 63.61% | 11.35% | 11.35% | 85% | 9.643% | 21.0933 | 4.8647 | 4.8647 | 102.6121 | 46.6459 | 74.98% | 74.98%
10 | 280 | 7 | 6710 | 14 | 20.1 | 220.97 | 168.39 | 389.36 | 168.39 | 84.2 | 280 | 6710 | 840 | 276.1644 | -5.2081 | -2.4716 | 814.284 | 13.5302 | -22.9531 | 34.1842 | 34.1842 | 28.0003 | 208.0003 | 23.9691 | 359.3715 | 359.3715 | 143.7299 | 503.1014 | 0.57634 | 57.63% | 227.5024 | 131.1181 | 91.7827 | 136.6519 | 136.6519 | 67.17% | 11.35% | 11.35% | 90% | 10.22% | 23.2401 | 4.9233 | 4.9233 | 114.4185 | 51.3935 | 83.73% | 83.73%
10 | 280 | 7 | 6711 | 15 | 21.1 | 229.94 | 140.5 | 370.44 | 140.5 | 70.25 | 280 | 6711 | 900 | 276.1644 | -5.2081 | -2.4716 | 874.284 | 14.5302 | -37.9531 | 28.1395 | 28.1395 | 43.9933 | 223.9933 | 38.55 | 381.2988 | 381.2988 | 119.9243 | 501.223 | 0.57986 | 57.99% | 226.6531 | 131.4269 | 91.9988 | 136.3049 | 136.3049 | 67.49% | 11.33% | 11.33% | 90% | 10.2% | 23.1198 | 4.7303 | 4.7303 | 109.364 | 51.1274 | 80.23% | 80.23%
10 | 280 | 7 | 6712 | 16 | 20.8 | 156.06 | 112.64 | 268.7 | 112.64 | 56.32 | 280 | 6712 | 960 | 276.1644 | -5.2081 | -2.4716 | 934.284 | 15.5302 | -52.9531 | 20.1657 | 20.1657 | 57.8603 | 237.8603 | 53.3535 | 270.2021 | 270.2021 | 96.1443 | 366.3464 | 0.49555 | 49.55% | 165.6618 | 82.0931 | 57.4651 | 130.9721 | 130.9721 | 43.88% | 11.33% | 11.33% | 85% | 9.633% | 15.9582 | 4.7875 | 4.7875 | 76.3994 | 35.2901 | 58.33% | 58.33%
10 | 280 | 7 | 6713 | 17 | 21.1 | 76.94 | 91.44 | 168.38 | 91.44 | 45.72 | 280 | 6713 | 1020 | 276.1644 | -5.2081 | -2.4716 | 994.284 | 16.5302 | -67.9531 | 10.9441 | 10.9441 | 70.0766 | 250.0766 | 68.2338 | 150.2794 | 150.2794 | 78.0489 | 228.3283 | 0.31197 | 31.2% | 103.2501 | 32.2109 | 22.5476 | 124.997 | 124.997 | 18.04% | 11.32% | 0% | 80% | 0% | 0 | 4.7303 | 4.7303 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6714 | 18 | 19.8 | 25.06 | 34.22 | 59.28 | 34.22 | 17.11 | 280 | 6714 | 1080 | 276.1644 | -5.2081 | -2.4716 | 1054.284 | 17.5302 | -82.9531 | 1.004 | 1.004 | 81.3025 | 261.3025 | 83.1483 | 0 | 0 | 29.2086 | 29.2086 | -3.14 | 0% | 13.2081 | 0 | 0 | 157.0631 | 157.0631 | 0% | 11.36% | 0% | 80% | 0% | 0 | 4.9826 | 4.9826 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6715 | 19 | 18.9 | 0 | 3.33 | 3.33 | 3.33 | 1.67 | 280 | 6715 | 1140 | 276.1644 | -5.2081 | -2.4716 | 1114.284 | 18.5302 | -97.9531 | -9.2365 | 0 | 82.3831 | 262.3831 | 84.622 | 0 | 0 | 2.8423 | 2.8423 | -40.4251 | 0% | 1.2853 | 0 | 0 | 148.3917 | 148.3917 | 0% | 11.4% | 0% | 80% | 0% | 0 | 5.1642 | 5.1642 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6716 | 20 | 16.9 | 0 | 0 | 0 | 0 | 0 | 280 | 6716 | 1200 | 276.1644 | -5.2081 | -2.4716 | 1174.284 | 19.5302 | -112.9531 | -19.397 | 0 | 82.3831 | 262.3831 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.0536 | 141.0536 | 0% | 11.49% | 0% | 80% | 0% | 0 | 5.588 | 5.588 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6717 | 21 | 15.4 | 0 | 0 | 0 | 0 | 0 | 280 | 6717 | 1260 | 276.1644 | -5.2081 | -2.4716 | 1234.284 | 20.5302 | -127.9531 | -29.051 | 0 | 82.3831 | 262.3831 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.3015 | 0 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6718 | 22 | 14.1 | 0 | 0 | 0 | 0 | 0 | 280 | 6718 | 1320 | 276.1644 | -5.2081 | -2.4716 | 1294.284 | 21.5302 | -142.9531 | -37.6242 | 0 | 82.3831 | 262.3831 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.244 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6719 | 23 | 13.3 | 0 | 0 | 0 | 0 | 0 | 280 | 6719 | 1380 | 276.1644 | -5.2081 | -2.4716 | 1354.284 | 22.5302 | -157.9531 | -44.2889 | 0 | 82.3831 | 262.3831 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3458 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
10 | 280 | 7 | 6720 | 24 | 12.5 | 0 | 0 | 0 | 0 | 0 | 280 | 6720 | 1440 | 276.1644 | -5.2081 | -2.4716 | 1414.284 | 23.5302 | -172.9531 | -47.9872 | 0 | 82.3831 | 262.3831 | 84.622 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4476 | 0 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6721 | 1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 281 | 6721 | 60 | 277.1507 | -5.603 | -2.1665 | 34.284 | 0.53529 | 171.9706 | -48.2468 | 0 | 81.8035 | 98.1965 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.237 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6722 | 2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 281 | 6722 | 120 | 277.1507 | -5.603 | -2.1665 | 94.284 | 1.5353 | 156.9706 | -44.2976 | 0 | 81.8035 | 98.1965 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7071 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6723 | 3 | 12 | 0 | 0 | 0 | 0 | 0 | 281 | 6723 | 180 | 277.1507 | -5.603 | -2.1665 | 154.284 | 2.5353 | 141.9706 | -37.4453 | 0 | 81.8035 | 98.1965 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2628 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6724 | 4 | 12 | 0 | 0 | 0 | 0 | 0 | 281 | 6724 | 240 | 277.1507 | -5.603 | -2.1665 | 214.284 | 3.5353 | 126.9706 | -28.7532 | 0 | 81.8035 | 98.1965 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2628 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6725 | 5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 281 | 6725 | 300 | 277.1507 | -5.603 | -2.1665 | 274.284 | 4.5353 | 111.9706 | -19.0345 | 0 | 81.8035 | 98.1965 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.5465 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6726 | 6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 281 | 6726 | 360 | 277.1507 | -5.603 | -2.1665 | 334.284 | 5.5353 | 96.9706 | -8.8507 | 0 | 81.8035 | 98.1965 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0.74567 | 0.74567 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6727 | 7 | 10.5 | 0 | 0 | 0 | 0 | 0 | 281 | 6727 | 420 | 277.1507 | -5.603 | -2.1665 | 394.284 | 6.5353 | 81.9706 | 1.3783 | 1.3783 | 80.3162 | 99.6838 | 82.1883 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 157.9726 | 157.9726 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6728 | 8 | 10.7 | 6.94 | 23.39 | 30.33 | 23.39 | 11.7 | 281 | 6728 | 480 | 277.1507 | -5.603 | -2.1665 | 454.284 | 7.5353 | 66.9706 | 11.2728 | 11.2728 | 69.0552 | 110.9448 | 67.2869 | 13.7081 | 13.7081 | 19.9646 | 33.6727 | -3.2291 | 0% | 15.2268 | 0 | 0 | 166.3144 | 166.3144 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6729 | 9 | 11.5 | 43.19 | 67.36 | 110.55 | 67.36 | 33.68 | 281 | 6729 | 540 | 277.1507 | -5.603 | -2.1665 | 514.284 | 8.5353 | 51.9706 | 20.41 | 20.41 | 56.7664 | 123.2336 | 52.4251 | 75.5218 | 75.5218 | 57.4954 | 133.0171 | -0.20301 | 0% | 60.1503 | 0 | 0 | 151.8295 | 151.8295 | 0% | 11.66% | 11.66% | 80% | 9.331% | 5.6127 | 6.8721 | 6 | 33.676 | 12.4119 | 22.18% | 22.18%
10 | 281 | 8 | 6730 | 10 | 12.7 | 87.72 | 128.06 | 215.78 | 128.06 | 64.03 | 281 | 6730 | 600 | 277.1507 | -5.603 | -2.1665 | 574.284 | 9.5353 | 36.9706 | 28.2538 | 28.2538 | 42.8035 | 137.1965 | 37.6539 | 146.7099 | 146.7099 | 109.306 | 256.016 | 0.2916 | 29.16% | 115.7704 | 33.759 | 23.6313 | 138.0842 | 138.0842 | 17.11% | 11.57% | 11.57% | 80% | 9.256% | 10.7161 | 6.5691 | 6 | 64.2965 | 23.6977 | 46.56% | 46.56%
10 | 281 | 8 | 6731 | 11 | 14.4 | 174.17 | 160.28 | 334.45 | 160.28 | 80.14 | 281 | 6731 | 660 | 277.1507 | -5.603 | -2.1665 | 634.284 | 10.5353 | 21.9706 | 34.1188 | 34.1188 | 26.7281 | 153.2719 | 23.1511 | 285.5075 | 285.5075 | 136.8075 | 422.3151 | 0.50258 | 50.26% | 190.9709 | 95.9786 | 67.185 | 142.3602 | 142.3602 | 47.19% | 11.47% | 11.47% | 85% | 9.748% | 18.616 | 6.1571 | 6 | 111.6959 | 41.1676 | 78.46% | 78.46%
10 | 281 | 8 | 6732 | 12 | 16 | 285.14 | 168.47 | 453.61 | 168.47 | 84.24 | 281 | 6732 | 720 | 277.1507 | -5.603 | -2.1665 | 694.284 | 11.5353 | 6.9706 | 37.2555 | 37.2555 | 8.7281 | 171.2719 | 10.1463 | 463.651 | 463.651 | 143.7981 | 607.4491 | 0.60041 | 60.04% | 274.6885 | 164.9266 | 115.4486 | 143.3264 | 143.3264 | 80.55% | 11.39% | 11.39% | 90% | 10.25% | 28.1691 | 5.7878 | 5.7878 | 163.0371 | 62.2935 | 113.8% | 113.8%
10 | 281 | 8 | 6733 | 13 | 16.8 | 387.44 | 160.28 | 547.72 | 160.28 | 80.14 | 281 | 6733 | 780 | 277.1507 | -5.603 | -2.1665 | 754.284 | 12.5353 | -8.0294 | 37.1373 | 37.1373 | 10.0425 | 190.0425 | 10.899 | 630.1713 | 630.1713 | 136.8075 | 766.9788 | 0.6451 | 64.51% | 346.8278 | 223.7403 | 156.6182 | 146.6907 | 146.6907 | 106.8% | 11.36% | 11.36% | 90% | 10.22% | 35.4528 | 5.6099 | 5.6099 | 198.8862 | 78.4008 | 135.6% | 135.6%
10 | 281 | 8 | 6734 | 14 | 17.7 | 369.67 | 168.47 | 538.14 | 168.47 | 84.24 | 281 | 6734 | 840 | 277.1507 | -5.603 | -2.1665 | 814.284 | 13.5353 | -23.0294 | 33.7859 | 33.7859 | 27.9334 | 207.9334 | 24.1556 | 606.556 | 606.556 | 143.7981 | 750.3541 | 0.64427 | 64.43% | 339.3101 | 218.6068 | 153.0248 | 147.4633 | 147.4633 | 103.8% | 11.36% | 11.36% | 90% | 10.22% | 34.6858 | 5.4151 | 5.4151 | 187.8263 | 76.7046 | 127.4% | 127.4%
10 | 281 | 8 | 6735 | 15 | 18.5 | 313.75 | 141.17 | 454.92 | 141.17 | 70.59 | 281 | 6735 | 900 | 277.1507 | -5.603 | -2.1665 | 874.284 | 14.5353 | -38.0294 | 27.7562 | 27.7562 | 43.8556 | 223.8556 | 38.6913 | 525.8405 | 525.8405 | 120.4961 | 646.3367 | 0.62132 | 62.13% | 292.2734 | 181.5948 | 127.1163 | 142.8012 | 142.8012 | 89.02% | 11.36% | 11.36% | 90% | 10.23% | 29.8943 | 5.2467 | 5.2467 | 156.8459 | 66.1087 | 109.8% | 109.8%
10 | 281 | 8 | 6736 | 16 | 17.9 | 150 | 146.25 | 296.25 | 146.25 | 73.13 | 281 | 6736 | 960 | 277.1507 | -5.603 | -2.1665 | 934.284 | 15.5353 | -53.0294 | 19.8004 | 19.8004 | 57.6816 | 237.6816 | 53.4721 | 263.5681 | 263.5681 | 124.8322 | 388.4003 | 0.49656 | 49.66% | 175.6346 | 87.2134 | 61.0494 | 133.2733 | 133.2733 | 45.81% | 11.4% | 11.4% | 85% | 9.69% | 17.0183 | 5.3726 | 5.3726 | 91.4318 | 37.6345 | 68.6% | 68.6%
10 | 281 | 8 | 6737 | 17 | 16.1 | 65.89 | 95.89 | 161.78 | 95.89 | 47.95 | 281 | 6737 | 1020 | 277.1507 | -5.603 | -2.1665 | 994.284 | 16.5353 | -68.0294 | 10.5938 | 10.5938 | 69.8758 | 249.8758 | 68.3377 | 132.2984 | 132.2984 | 81.8472 | 214.1456 | 0.22755 | 22.76% | 96.8366 | 22.0356 | 15.4249 | 121.1843 | 121.1843 | 12.73% | 11.48% | 0% | 80% | 0% | 0 | 5.7653 | 5.7653 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6738 | 18 | 15.4 | 20.56 | 42.72 | 63.28 | 42.72 | 21.36 | 281 | 6738 | 1080 | 277.1507 | -5.603 | -2.1665 | 1054.284 | 17.5353 | -83.0294 | 0.66277 | 0.66277 | 81.0898 | 261.0898 | 83.241 | 0 | 0 | 36.4638 | 36.4638 | -2.6247 | 0% | 16.4889 | 0 | 0 | 153.4575 | 153.4575 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6739 | 19 | 16.4 | 0 | 2.64 | 2.64 | 2.64 | 1.32 | 281 | 6739 | 1140 | 277.1507 | -5.603 | -2.1665 | 1114.284 | 18.5353 | -98.0294 | -9.5755 | 0 | 81.8035 | 261.8035 | 84.2142 | 0 | 0 | 2.2534 | 2.2534 | -53.6777 | 0% | 1.019 | 0 | 0 | 146.9781 | 146.9781 | 0% | 11.51% | 0% | 80% | 0% | 0 | 5.6983 | 5.6983 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6740 | 20 | 15.2 | 0 | 0 | 0 | 0 | 0 | 281 | 6740 | 1200 | 277.1507 | -5.603 | -2.1665 | 1174.284 | 19.5353 | -113.0294 | -19.7413 | 0 | 81.8035 | 261.8035 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.7247 | 139.7247 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6741 | 21 | 13.7 | 0 | 0 | 0 | 0 | 0 | 281 | 6741 | 1260 | 277.1507 | -5.603 | -2.1665 | 1234.284 | 20.5353 | -128.0294 | -29.4082 | 0 | 81.8035 | 261.8035 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.9011 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6742 | 22 | 13.9 | 0 | 0 | 0 | 0 | 0 | 281 | 6742 | 1320 | 277.1507 | -5.603 | -2.1665 | 1294.284 | 21.5353 | -143.0294 | -38.0007 | 0 | 81.8035 | 261.8035 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.8267 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6743 | 23 | 13.3 | 0 | 0 | 0 | 0 | 0 | 281 | 6743 | 1380 | 277.1507 | -5.603 | -2.1665 | 1354.284 | 22.5353 | -158.0294 | -44.6847 | 0 | 81.8035 | 261.8035 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4492 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
10 | 281 | 8 | 6744 | 24 | 12 | 0 | 0 | 0 | 0 | 0 | 281 | 6744 | 1440 | 277.1507 | -5.603 | -2.1665 | 1414.284 | 23.5353 | -173.0294 | -48.3884 | 0 | 81.8035 | 261.8035 | 84.2142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1385 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6745 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 282 | 6745 | 60 | 278.137 | -5.9967 | -1.8649 | 34.284 | 0.54032 | 171.8952 | -48.6255 | 0 | 81.2252 | 98.7748 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9056 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6746 | 2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 282 | 6746 | 120 | 278.137 | -5.9967 | -1.8649 | 94.284 | 1.5403 | 156.8952 | -44.6342 | 0 | 81.2252 | 98.7748 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2218 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6747 | 3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 282 | 6747 | 180 | 278.137 | -5.9967 | -1.8649 | 154.284 | 2.5403 | 141.8952 | -37.7385 | 0 | 81.2252 | 98.7748 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9952 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6748 | 4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 282 | 6748 | 240 | 278.137 | -5.9967 | -1.8649 | 214.284 | 3.5403 | 126.8952 | -29.0136 | 0 | 81.2252 | 98.7748 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1476 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6749 | 5 | 11.4 | 0 | 0 | 0 | 0 | 0 | 282 | 6749 | 300 | 278.137 | -5.9967 | -1.8649 | 274.284 | 4.5403 | 111.8952 | -19.2755 | 0 | 81.2252 | 98.7748 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 2.3314 | 2.3314 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6750 | 6 | 11.2 | 0 | 0 | 0 | 0 | 0 | 282 | 6750 | 360 | 278.137 | -5.9967 | -1.8649 | 334.284 | 5.5403 | 96.8952 | -9.0847 | 0 | 81.2252 | 98.7748 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 12.0242 | 12.0242 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6751 | 7 | 11.3 | 0 | 0 | 0 | 0 | 0 | 282 | 6751 | 420 | 278.137 | -5.9967 | -1.8649 | 394.284 | 6.5403 | 81.8952 | 1.1398 | 1.1398 | 79.9939 | 100.0061 | 82.1313 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 176.7952 | 176.7952 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6752 | 8 | 11.2 | 8.94 | 20.5 | 29.44 | 20.5 | 10.25 | 282 | 6752 | 480 | 278.137 | -5.9967 | -1.8649 | 454.284 | 7.5403 | 66.8952 | 11.0191 | 11.0191 | 68.7389 | 111.2611 | 67.2422 | 18.0935 | 18.0935 | 17.4978 | 35.5913 | -2.9791 | 0% | 16.0944 | 0 | 0 | 187.3343 | 187.3343 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6753 | 9 | 11.6 | 86.44 | 59.86 | 146.3 | 59.86 | 29.93 | 282 | 6753 | 540 | 278.137 | -5.9967 | -1.8649 | 514.284 | 8.5403 | 51.8952 | 20.1309 | 20.1309 | 56.4597 | 123.5403 | 52.3969 | 153.2532 | 153.2532 | 51.0937 | 204.3469 | 0.14963 | 14.96% | 92.4057 | 13.8266 | 9.6786 | 174.7092 | 174.7092 | 5.54% | 11.63% | 11.63% | 80% | 9.302% | 8.5953 | 6.8464 | 6 | 51.5721 | 19.0078 | 29.52% | 29.52%
10 | 282 | 9 | 6754 | 10 | 12.2 | 191.94 | 95.83 | 287.77 | 95.83 | 47.92 | 282 | 6754 | 600 | 278.137 | -5.9967 | -1.8649 | 574.284 | 9.5403 | 36.8952 | 27.9405 | 27.9405 | 42.5201 | 137.4799 | 37.6521 | 324.3283 | 324.3283 | 81.796 | 406.1244 | 0.47816 | 47.82% | 183.6494 | 87.8132 | 61.4692 | 159.6835 | 159.6835 | 38.49% | 11.52% | 11.52% | 85% | 9.793% | 17.9845 | 6.6941 | 6 | 107.9068 | 39.7711 | 67.58% | 67.58%
10 | 282 | 9 | 6755 | 11 | 14.2 | 275.83 | 129.11 | 404.94 | 129.11 | 64.56 | 282 | 6755 | 660 | 278.137 | -5.9967 | -1.8649 | 634.284 | 10.5403 | 21.8952 | 33.7674 | 33.7674 | 26.4958 | 153.5042 | 23.2045 | 456.1103 | 456.1103 | 110.2023 | 566.3126 | 0.57842 | 57.84% | 256.0865 | 148.1256 | 103.6879 | 160.1887 | 160.1887 | 64.73% | 11.43% | 11.43% | 90% | 10.28% | 26.3357 | 6.2045 | 6 | 158.014 | 58.239 | 98.64% | 98.64%
10 | 282 | 9 | 6756 | 12 | 16.7 | 393.89 | 119.03 | 512.92 | 119.03 | 59.52 | 282 | 6756 | 720 | 278.137 | -5.9967 | -1.8649 | 694.284 | 11.5403 | 6.8952 | 36.8717 | 36.8717 | 8.5835 | 171.4165 | 10.3852 | 645.702 | 645.702 | 101.5985 | 747.3005 | 0.64062 | 64.06% | 337.9293 | 216.4843 | 151.539 | 156.7197 | 156.7197 | 96.69% | 11.36% | 11.36% | 90% | 10.23% | 34.5546 | 5.6319 | 5.6319 | 194.6075 | 76.4145 | 124.2% | 124.2%
10 | 282 | 9 | 6757 | 13 | 17.5 | 372.28 | 156.81 | 529.09 | 156.81 | 78.41 | 282 | 6757 | 780 | 278.137 | -5.9967 | -1.8649 | 754.284 | 12.5403 | -8.1048 | 36.7374 | 36.7374 | 10.0765 | 190.0765 | 11.2224 | 610.4868 | 610.4868 | 133.8457 | 744.3325 | 0.64238 | 64.24% | 336.5872 | 216.2156 | 151.3509 | 155.7144 | 155.7144 | 97.2% | 11.36% | 11.36% | 90% | 10.22% | 34.4116 | 5.4579 | 5.4579 | 187.8144 | 76.0982 | 120.6% | 120.6%
10 | 282 | 9 | 6758 | 14 | 19.8 | 290.22 | 169.86 | 460.08 | 169.86 | 84.93 | 282 | 6758 | 840 | 278.137 | -5.9967 | -1.8649 | 814.284 | 13.5403 | -23.1048 | 33.389 | 33.389 | 27.8664 | 207.8664 | 24.3458 | 480.4686 | 480.4686 | 144.9846 | 625.4532 | 0.61982 | 61.98% | 282.8299 | 175.3027 | 122.7119 | 155.337 | 155.337 | 79% | 11.35% | 11.35% | 90% | 10.22% | 28.9011 | 4.9826 | 4.9826 | 144.0018 | 63.9121 | 92.7% | 92.7%
10 | 282 | 9 | 6759 | 15 | 20.5 | 269.5 | 148.33 | 417.83 | 148.33 | 74.17 | 282 | 6759 | 900 | 278.137 | -5.9967 | -1.8649 | 874.284 | 14.5403 | -38.1048 | 27.3743 | 27.3743 | 43.7184 | 223.7184 | 38.8346 | 456.5655 | 456.5655 | 126.6076 | 583.173 | 0.6091 | 60.91% | 263.7108 | 160.6271 | 112.4389 | 151.2113 | 151.2113 | 74.36% | 11.35% | 11.35% | 90% | 10.21% | 26.9287 | 4.8453 | 4.8453 | 130.4768 | 59.5503 | 86.29% | 86.29%
10 | 282 | 9 | 6760 | 16 | 20.1 | 220.22 | 120.83 | 341.05 | 120.83 | 60.42 | 282 | 6760 | 960 | 278.137 | -5.9967 | -1.8649 | 934.284 | 15.5403 | -53.1048 | 19.4364 | 19.4364 | 57.5035 | 237.5035 | 53.5914 | 392.8035 | 392.8035 | 103.1349 | 495.9383 | 0.57305 | 57.3% | 224.2633 | 128.5139 | 89.9597 | 145.3706 | 145.3706 | 61.88% | 11.35% | 11.35% | 85% | 9.648% | 21.6364 | 4.9233 | 4.9233 | 106.523 | 47.847 | 73.28% | 73.28%
10 | 282 | 9 | 6761 | 17 | 20.1 | 98.67 | 81.39 | 180.06 | 81.39 | 40.7 | 282 | 6761 | 1020 | 278.137 | -5.9967 | -1.8649 | 994.284 | 16.5403 | -68.1048 | 10.2447 | 10.2447 | 69.6755 | 249.6755 | 68.4416 | 203.8552 | 203.8552 | 69.4707 | 273.3259 | 0.38495 | 38.49% | 123.598 | 47.5789 | 33.3053 | 134.0147 | 134.0147 | 24.85% | 11.35% | 0% | 80% | 0% | 0 | 4.9233 | 4.9233 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6762 | 18 | 19.3 | 22.44 | 34.72 | 57.16 | 34.72 | 17.36 | 282 | 6762 | 1080 | 278.137 | -5.9967 | -1.8649 | 1054.284 | 17.5403 | -83.1048 | 0.32303 | 0.32303 | 80.8771 | 260.8771 | 83.333 | 0 | 0 | 29.6354 | 29.6354 | -3.1204 | 0% | 13.4011 | 0 | 0 | 163.1289 | 163.1289 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0828 | 5.0828 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6763 | 19 | 17.3 | 0 | 1.47 | 1.47 | 1.47 | 0.74 | 282 | 6763 | 1140 | 278.137 | -5.9967 | -1.8649 | 1114.284 | 18.5403 | -98.1048 | -9.9128 | 0 | 81.2252 | 261.2252 | 83.8075 | 0 | 0 | 1.2547 | 1.2547 | -95.4316 | 0% | 0.56739 | 0 | 0 | 151.1181 | 151.1181 | 0% | 11.47% | 0% | 80% | 0% | 0 | 5.501 | 5.501 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6764 | 20 | 15.6 | 0 | 0 | 0 | 0 | 0 | 282 | 6764 | 1200 | 278.137 | -5.9967 | -1.8649 | 1174.284 | 19.5403 | -113.1048 | -20.0838 | 0 | 81.2252 | 261.2252 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.3362 | 141.3362 | 0% | 11.55% | 0% | 80% | 0% | 0 | 5.8784 | 5.8784 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6765 | 21 | 14.6 | 0 | 0 | 0 | 0 | 0 | 282 | 6765 | 1260 | 278.137 | -5.9967 | -1.8649 | 1234.284 | 20.5403 | -128.1048 | -29.7637 | 0 | 81.2252 | 261.2252 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9282 | 0 | 0% | 11.59% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6766 | 22 | 13.9 | 0 | 0 | 0 | 0 | 0 | 282 | 6766 | 1320 | 278.137 | -5.9967 | -1.8649 | 1294.284 | 21.5403 | -143.1048 | -38.3754 | 0 | 81.2252 | 261.2252 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6043 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6767 | 23 | 13.3 | 0 | 0 | 0 | 0 | 0 | 282 | 6767 | 1380 | 278.137 | -5.9967 | -1.8649 | 1354.284 | 22.5403 | -158.1048 | -45.0789 | 0 | 81.2252 | 261.2252 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.9873 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
10 | 282 | 9 | 6768 | 24 | 13.7 | 0 | 0 | 0 | 0 | 0 | 282 | 6768 | 1440 | 278.137 | -5.9967 | -1.8649 | 1414.284 | 23.5403 | -173.1048 | -48.7885 | 0 | 81.2252 | 261.2252 | 83.8075 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8463 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6769 | 1 | 13.3 | 0 | 0 | 0 | 0 | 0 | 283 | 6769 | 60 | 279.1233 | -6.3892 | -1.5672 | 34.284 | 0.54528 | 171.8208 | -49.0028 | 0 | 80.6482 | 99.3518 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5723 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6770 | 2 | 13.2 | 0 | 0 | 0 | 0 | 0 | 283 | 6770 | 120 | 279.1233 | -6.3892 | -1.5672 | 94.284 | 1.5453 | 156.8208 | -44.9693 | 0 | 80.6482 | 99.3518 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2279 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6771 | 3 | 13.4 | 0 | 0 | 0 | 0 | 0 | 283 | 6771 | 180 | 279.1233 | -6.3892 | -1.5672 | 154.284 | 2.5453 | 141.8208 | -38.0302 | 0 | 80.6482 | 99.3518 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.4263 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6772 | 4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 283 | 6772 | 240 | 279.1233 | -6.3892 | -1.5672 | 214.284 | 3.5453 | 126.8208 | -29.2728 | 0 | 80.6482 | 99.3518 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5787 | 0 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6773 | 5 | 13.2 | 0 | 0 | 0 | 0 | 0 | 283 | 6773 | 300 | 279.1233 | -6.3892 | -1.5672 | 274.284 | 4.5453 | 111.8208 | -19.5156 | 0 | 80.6482 | 99.3518 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.1227 | 4.1227 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6774 | 6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 283 | 6774 | 360 | 279.1233 | -6.3892 | -1.5672 | 334.284 | 5.5453 | 96.8208 | -9.3183 | 0 | 80.6482 | 99.3518 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 12.6143 | 12.6143 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6775 | 7 | 12.4 | 0 | 0 | 0 | 0 | 0 | 283 | 6775 | 420 | 279.1233 | -6.3892 | -1.5672 | 394.284 | 6.5453 | 81.8208 | 0.90151 | 0.90151 | 79.6734 | 100.3266 | 82.0757 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 175.1114 | 175.1114 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6776 | 8 | 12.6 | 10.56 | 22.5 | 33.06 | 22.5 | 11.25 | 283 | 6776 | 480 | 279.1233 | -6.3892 | -1.5672 | 454.284 | 7.5453 | 66.8208 | 10.7654 | 10.7654 | 68.4247 | 111.5753 | 67.1996 | 21.9084 | 21.9084 | 19.205 | 41.1134 | -2.3923 | 0% | 18.5915 | 0 | 0 | 185.8432 | 185.8432 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6777 | 9 | 13.1 | 88.47 | 63.47 | 151.94 | 63.47 | 31.74 | 283 | 6777 | 540 | 279.1233 | -6.3892 | -1.5672 | 514.284 | 8.5453 | 51.8208 | 19.8517 | 19.8517 | 56.1558 | 123.8442 | 52.3718 | 159.0581 | 159.0581 | 54.175 | 213.2332 | 0.1931 | 19.31% | 96.424 | 18.6198 | 13.0339 | 173.3703 | 173.3703 | 7.518% | 11.57% | 11.57% | 80% | 9.26% | 8.9286 | 6.4703 | 6 | 53.5717 | 19.7448 | 30.9% | 30.9%
10 | 283 | 10 | 6778 | 10 | 13.8 | 178.94 | 99.67 | 278.61 | 99.67 | 49.84 | 283 | 6778 | 600 | 279.1233 | -6.3892 | -1.5672 | 574.284 | 9.5453 | 36.8208 | 27.6272 | 27.6272 | 42.2401 | 137.7599 | 37.6548 | 305.5049 | 305.5049 | 85.0737 | 390.5785 | 0.47459 | 47.46% | 176.6196 | 83.8216 | 58.6751 | 158.1466 | 158.1466 | 37.1% | 11.49% | 11.49% | 85% | 9.768% | 17.252 | 6.3002 | 6 | 103.5119 | 38.1512 | 65.45% | 65.45%
10 | 283 | 10 | 6779 | 11 | 14.7 | 269.5 | 120.33 | 389.83 | 120.33 | 60.17 | 283 | 6779 | 660 | 279.1233 | -6.3892 | -1.5672 | 634.284 | 10.5453 | 21.8208 | 33.4164 | 33.4164 | 26.267 | 153.733 | 23.265 | 449.5688 | 449.5688 | 102.7081 | 552.2768 | 0.57475 | 57.47% | 249.7396 | 143.5371 | 100.476 | 157.5399 | 157.5399 | 63.78% | 11.42% | 11.42% | 90% | 10.28% | 25.6777 | 6.0865 | 6 | 154.0662 | 56.7839 | 97.8% | 97.8%
10 | 283 | 10 | 6780 | 12 | 14.9 | 393.75 | 122.44 | 516.19 | 122.44 | 61.22 | 283 | 6780 | 720 | 279.1233 | -6.3892 | -1.5672 | 694.284 | 11.5453 | 6.8208 | 36.4888 | 36.4888 | 8.4418 | 171.5582 | 10.6335 | 650.7665 | 650.7665 | 104.5091 | 755.2756 | 0.63697 | 63.7% | 341.5356 | 217.5465 | 152.2825 | 152.4612 | 152.4612 | 99.88% | 11.36% | 11.36% | 90% | 10.23% | 34.9326 | 6.0398 | 6 | 209.5954 | 77.2503 | 137.5% | 137.5%
10 | 283 | 10 | 6781 | 13 | 14.5 | 424.78 | 122 | 546.78 | 122 | 61 | 283 | 6781 | 780 | 279.1233 | -6.3892 | -1.5672 | 754.284 | 12.5453 | -8.1792 | 36.3388 | 36.3388 | 10.1089 | 190.1089 | 11.549 | 702.3427 | 702.3427 | 104.1335 | 806.4762 | 0.64644 | 64.64% | 364.6886 | 235.7505 | 165.0253 | 149.8725 | 149.8725 | 110.1% | 11.35% | 11.35% | 95% | 10.78% | 39.3227 | 6.1335 | 6 | 235.9361 | 86.9586 | 157.4% | 157.4%
10 | 283 | 10 | 6782 | 14 | 15 | 333.83 | 132.64 | 466.47 | 132.64 | 66.32 | 283 | 6782 | 840 | 279.1233 | -6.3892 | -1.5672 | 814.284 | 13.5453 | -23.1792 | 32.9936 | 32.9936 | 27.7992 | 207.7992 | 24.5394 | 557.6711 | 557.6711 | 113.2153 | 670.8865 | 0.61629 | 61.63% | 303.3749 | 186.9678 | 130.8775 | 146.23 | 146.23 | 89.5% | 11.39% | 11.39% | 90% | 10.25% | 31.0921 | 6.0165 | 6 | 186.5529 | 68.7575 | 127.6% | 127.6%
10 | 283 | 10 | 6783 | 15 | 15.3 | 273.56 | 121.39 | 394.95 | 121.39 | 60.7 | 283 | 6783 | 900 | 279.1233 | -6.3892 | -1.5672 | 874.284 | 14.5453 | -38.1792 | 26.9939 | 26.9939 | 43.5818 | 223.5818 | 38.9796 | 468.5168 | 468.5168 | 103.6128 | 572.1296 | 0.58508 | 58.51% | 258.717 | 151.3703 | 105.9592 | 140.1646 | 140.1646 | 75.6% | 11.41% | 11.41% | 90% | 10.27% | 26.5698 | 5.9472 | 5.9472 | 158.0145 | 58.7566 | 112.7% | 112.7%
10 | 283 | 10 | 6784 | 16 | 16.3 | 176.81 | 87.08 | 263.89 | 87.08 | 43.54 | 283 | 6784 | 960 | 279.1233 | -6.3892 | -1.5672 | 934.284 | 15.5453 | -53.1792 | 19.0738 | 19.0738 | 57.326 | 237.326 | 53.7114 | 320.226 | 320.226 | 74.3274 | 394.5534 | 0.49227 | 49.23% | 178.417 | 87.8299 | 61.4809 | 133.6702 | 133.6702 | 45.99% | 11.43% | 11.43% | 85% | 9.719% | 17.3409 | 5.7206 | 5.7206 | 99.1998 | 38.348 | 74.21% | 74.21%
10 | 283 | 10 | 6785 | 17 | 16.3 | 92.08 | 60.61 | 152.69 | 60.61 | 30.31 | 283 | 6785 | 1020 | 279.1233 | -6.3892 | -1.5672 | 994.284 | 16.5453 | -68.1792 | 9.8972 | 9.8972 | 69.4755 | 249.4755 | 68.5453 | 0 | 0 | 51.7339 | 51.7339 | -1.5734 | 0% | 23.3941 | 0 | 0 | 124.9677 | 124.9677 | 0% | 11.5% | 0% | 80% | 0% | 0 | 5.7206 | 5.7206 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6786 | 18 | 15.7 | 19.78 | 28.61 | 48.39 | 28.61 | 14.31 | 283 | 6786 | 1080 | 279.1233 | -6.3892 | -1.5672 | 1054.284 | 17.5453 | -83.1792 | -0.015077 | 0 | 80.6482 | 260.6482 | 83.4021 | 0 | 0 | 24.4202 | 24.4202 | -4.2879 | 0% | 11.0428 | 0 | 0 | 155.699 | 155.699 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.8557 | 5.8557 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6787 | 19 | 14.8 | 0 | 0.97 | 0.97 | 0.97 | 0.49 | 283 | 6787 | 1140 | 279.1233 | -6.3892 | -1.5672 | 1114.284 | 18.5453 | -98.1792 | -10.2484 | 0 | 80.6482 | 260.6482 | 83.4021 | 0 | 0 | 0.82795 | 0.82795 | -151.8433 | 0% | 0.3744 | 0 | 0 | 146.5066 | 146.5066 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6788 | 20 | 13.4 | 0 | 0 | 0 | 0 | 0 | 283 | 6788 | 1200 | 279.1233 | -6.3892 | -1.5672 | 1174.284 | 19.5453 | -113.1792 | -20.4244 | 0 | 80.6482 | 260.6482 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.0542 | 138.0542 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.397 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6789 | 21 | 12.3 | 0 | 0 | 0 | 0 | 0 | 283 | 6789 | 1260 | 279.1233 | -6.3892 | -1.5672 | 1234.284 | 20.5453 | -128.1792 | -30.1171 | 0 | 80.6482 | 260.6482 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1571 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6790 | 22 | 11.9 | 0 | 0 | 0 | 0 | 0 | 283 | 6790 | 1320 | 279.1233 | -6.3892 | -1.5672 | 1294.284 | 21.5453 | -143.1792 | -38.7482 | 0 | 80.6482 | 260.6482 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1962 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6791 | 23 | 10.8 | 0 | 0 | 0 | 0 | 0 | 283 | 6791 | 1380 | 279.1233 | -6.3892 | -1.5672 | 1354.284 | 22.5453 | -158.1792 | -45.4715 | 0 | 80.6482 | 260.6482 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3758 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 283 | 10 | 6792 | 24 | 10.4 | 0 | 0 | 0 | 0 | 0 | 283 | 6792 | 1440 | 279.1233 | -6.3892 | -1.5672 | 1414.284 | 23.5453 | -173.1792 | -49.1871 | 0 | 80.6482 | 260.6482 | 83.4021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4886 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6793 | 1 | 9.8 | 0 | 0 | 0 | 0 | 0 | 284 | 6793 | 60 | 280.1096 | -6.7803 | -1.2739 | 34.284 | 0.55017 | 171.7475 | -49.3786 | 0 | 80.0728 | 99.9272 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1416 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6794 | 2 | 9.9 | 0 | 0 | 0 | 0 | 0 | 284 | 6794 | 120 | 280.1096 | -6.7803 | -1.2739 | 94.284 | 1.5502 | 156.7475 | -45.3027 | 0 | 80.0728 | 99.9272 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7741 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6795 | 3 | 9 | 0 | 0 | 0 | 0 | 0 | 284 | 6795 | 180 | 280.1096 | -6.7803 | -1.2739 | 154.284 | 2.5502 | 141.7475 | -38.3204 | 0 | 80.0728 | 99.9272 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9306 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6796 | 4 | 9.4 | 0 | 0 | 0 | 0 | 0 | 284 | 6796 | 240 | 280.1096 | -6.7803 | -1.2739 | 214.284 | 3.5502 | 126.7475 | -29.5308 | 0 | 80.0728 | 99.9272 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.321 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6797 | 5 | 9.2 | 0 | 0 | 0 | 0 | 0 | 284 | 6797 | 300 | 280.1096 | -6.7803 | -1.2739 | 274.284 | 4.5502 | 111.7475 | -19.7549 | 0 | 80.0728 | 99.9272 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9553 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6798 | 6 | 9.3 | 0 | 0 | 0 | 0 | 0 | 284 | 6798 | 360 | 280.1096 | -6.7803 | -1.2739 | 334.284 | 5.5502 | 96.7475 | -9.5514 | 0 | 80.0728 | 99.9272 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.9969 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6799 | 7 | 9.5 | 0 | 0 | 0 | 0 | 0 | 284 | 6799 | 420 | 280.1096 | -6.7803 | -1.2739 | 394.284 | 6.5502 | 81.7475 | 0.66336 | 0.66336 | 79.3547 | 100.6453 | 82.0215 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 153.7257 | 153.7257 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6800 | 8 | 9.7 | 1.11 | 15.06 | 16.17 | 15.06 | 7.53 | 284 | 6800 | 480 | 280.1096 | -6.7803 | -1.2739 | 454.284 | 7.5502 | 66.7475 | 10.5117 | 10.5117 | 68.113 | 111.887 | 67.1592 | 2.3618 | 2.3618 | 12.8545 | 15.2163 | -8.2743 | 0% | 6.8808 | 0 | 0 | 159.9329 | 159.9329 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6801 | 9 | 10.7 | 14.5 | 65.22 | 79.72 | 65.22 | 32.61 | 284 | 6801 | 540 | 280.1096 | -6.7803 | -1.2739 | 514.284 | 8.5502 | 51.7475 | 19.5724 | 19.5724 | 55.8548 | 124.1452 | 52.3498 | 26.4395 | 26.4395 | 55.6688 | 82.1082 | -0.84999 | 0% | 37.1293 | 0 | 0 | 144.6853 | 144.6853 | 0% | 11.72% | 11.72% | 80% | 9.375% | 3.481 | 7.0797 | 6 | 20.8861 | 7.6979 | 14.44% | 14.44%
10 | 284 | 11 | 6802 | 10 | 12.2 | 64.11 | 124.67 | 188.78 | 124.67 | 62.34 | 284 | 6802 | 600 | 280.1096 | -6.7803 | -1.2739 | 574.284 | 9.5502 | 36.7475 | 27.3141 | 27.3141 | 41.9635 | 138.0365 | 37.6619 | 110.6013 | 110.6013 | 106.4125 | 217.0138 | 0.19421 | 19.42% | 98.1336 | 19.0585 | 13.341 | 152.3283 | 152.3283 | 8.758% | 11.6% | 11.6% | 80% | 9.282% | 9.1085 | 6.6941 | 6 | 54.6507 | 20.1425 | 35.88% | 35.88%
10 | 284 | 11 | 6803 | 11 | 14.8 | 76.06 | 175.14 | 251.2 | 175.14 | 87.57 | 284 | 6803 | 660 | 280.1096 | -6.7803 | -1.2739 | 634.284 | 10.5502 | 21.7475 | 33.0659 | 33.0659 | 26.0419 | 153.9581 | 23.3324 | 128.005 | 128.005 | 149.4913 | 277.4963 | 0.34856 | 34.86% | 125.4838 | 43.7382 | 30.6168 | 134.6959 | 134.6959 | 22.73% | 11.5% | 11.5% | 80% | 9.201% | 11.546 | 6.0631 | 6 | 69.2757 | 25.5329 | 51.43% | 51.43%
10 | 284 | 11 | 6804 | 12 | 16.5 | 164.11 | 206.61 | 370.72 | 206.61 | 103.31 | 284 | 6804 | 720 | 280.1096 | -6.7803 | -1.2739 | 694.284 | 11.5502 | 6.7475 | 36.107 | 36.107 | 8.3031 | 171.6969 | 10.8904 | 273.47 | 273.47 | 176.3527 | 449.8227 | 0.53157 | 53.16% | 203.4098 | 108.1275 | 75.6893 | 137.0613 | 137.0613 | 55.22% | 11.42% | 11.42% | 85% | 9.706% | 19.744 | 5.6761 | 5.6761 | 112.0683 | 43.662 | 81.77% | 81.77%
10 | 284 | 11 | 6805 | 13 | 18.2 | 179.03 | 216.94 | 395.97 | 216.94 | 108.47 | 284 | 6805 | 780 | 280.1096 | -6.7803 | -1.2739 | 754.284 | 12.5502 | -8.2525 | 35.9418 | 35.9418 | 10.1398 | 190.1398 | 11.8782 | 298.4796 | 298.4796 | 185.1699 | 483.6495 | 0.55849 | 55.85% | 218.7063 | 122.1452 | 85.5016 | 140.3035 | 140.3035 | 60.94% | 11.38% | 11.38% | 85% | 9.676% | 21.1616 | 5.3093 | 5.3093 | 112.3534 | 46.7971 | 80.08% | 80.08%
10 | 284 | 11 | 6806 | 14 | 18.3 | 185.61 | 178.67 | 364.28 | 178.67 | 89.34 | 284 | 6806 | 840 | 280.1096 | -6.7803 | -1.2739 | 814.284 | 13.5502 | -23.2525 | 32.5998 | 32.5998 | 27.7319 | 207.7319 | 24.736 | 312.8981 | 312.8981 | 152.5044 | 465.4025 | 0.54934 | 54.93% | 210.455 | 115.6117 | 80.9282 | 139.223 | 139.223 | 58.13% | 11.38% | 11.38% | 85% | 9.676% | 20.3632 | 5.2884 | 5.2884 | 107.6878 | 45.0314 | 77.35% | 77.35%
10 | 284 | 11 | 6807 | 15 | 18.1 | 192.5 | 139.03 | 331.53 | 139.03 | 69.52 | 284 | 6807 | 900 | 280.1096 | -6.7803 | -1.2739 | 874.284 | 14.5502 | -38.2525 | 26.615 | 26.615 | 43.4456 | 223.4456 | 39.1261 | 333.3385 | 333.3385 | 118.6695 | 452.0081 | 0.54081 | 54.08% | 204.3981 | 110.5407 | 77.3785 | 136.2217 | 136.2217 | 56.8% | 11.39% | 11.39% | 85% | 9.68% | 19.786 | 5.3303 | 5.3303 | 105.4654 | 43.7549 | 77.42% | 77.42%
10 | 284 | 11 | 6808 | 16 | 17.1 | 163.75 | 93.75 | 257.5 | 93.75 | 46.88 | 284 | 6808 | 960 | 280.1096 | -6.7803 | -1.2739 | 934.284 | 15.5502 | -53.2525 | 18.7129 | 18.7129 | 57.1491 | 237.1491 | 53.8319 | 301.2158 | 301.2158 | 80.0206 | 381.2364 | 0.4861 | 48.61% | 172.3951 | 83.8005 | 58.6603 | 130.9508 | 130.9508 | 44.8% | 11.42% | 11.42% | 85% | 9.706% | 16.7326 | 5.5443 | 5.5443 | 92.7709 | 37.0027 | 70.84% | 70.84%
10 | 284 | 11 | 6809 | 17 | 15.4 | 111.44 | 62.28 | 173.72 | 62.28 | 31.14 | 284 | 6809 | 1020 | 280.1096 | -6.7803 | -1.2739 | 994.284 | 16.5502 | -68.2525 | 9.5514 | 9.5514 | 69.276 | 249.276 | 68.6487 | 0 | 0 | 53.1593 | 53.1593 | -1.5479 | 0% | 24.0386 | 0 | 0 | 122.9779 | 122.9779 | 0% | 11.54% | 0% | 80% | 0% | 0 | 5.9242 | 5.9242 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6810 | 18 | 15.2 | 20 | 23.19 | 43.19 | 23.19 | 11.6 | 284 | 6810 | 1080 | 280.1096 | -6.7803 | -1.2739 | 1054.284 | 17.5502 | -83.2525 | -0.35137 | 0 | 80.0728 | 260.0728 | 82.9981 | 0 | 0 | 19.7939 | 19.7939 | -5.5352 | 0% | 8.9508 | 0 | 0 | 154.0123 | 154.0123 | 0% | 11.56% | 0% | 80% | 0% | 0 | 5.9702 | 5.9702 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6811 | 19 | 13.7 | 0 | 1.39 | 1.39 | 1.39 | 0.7 | 284 | 6811 | 1140 | 280.1096 | -6.7803 | -1.2739 | 1114.284 | 18.5502 | -98.2525 | -10.582 | 0 | 80.0728 | 260.0728 | 82.9981 | 0 | 0 | 1.1864 | 1.1864 | -107.8318 | 0% | 0.53651 | 0 | 0 | 144.2476 | 144.2476 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6812 | 20 | 11.8 | 0 | 0 | 0 | 0 | 0 | 284 | 6812 | 1200 | 280.1096 | -6.7803 | -1.2739 | 1174.284 | 19.5502 | -113.2525 | -20.7629 | 0 | 80.0728 | 260.0728 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.8577 | 135.8577 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6813 | 21 | 11.2 | 0 | 0 | 0 | 0 | 0 | 284 | 6813 | 1260 | 280.1096 | -6.7803 | -1.2739 | 1234.284 | 20.5502 | -128.2525 | -30.4684 | 0 | 80.0728 | 260.0728 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4239 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6814 | 22 | 10.8 | 0 | 0 | 0 | 0 | 0 | 284 | 6814 | 1320 | 280.1096 | -6.7803 | -1.2739 | 1294.284 | 21.5502 | -143.2525 | -39.119 | 0 | 80.0728 | 260.0728 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2629 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6815 | 23 | 10.4 | 0 | 0 | 0 | 0 | 0 | 284 | 6815 | 1380 | 280.1096 | -6.7803 | -1.2739 | 1354.284 | 22.5502 | -158.2525 | -45.8624 | 0 | 80.0728 | 260.0728 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6574 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
10 | 284 | 11 | 6816 | 24 | 19.3 | 0 | 0 | 0 | 0 | 0 | 284 | 6816 | 1440 | 280.1096 | -6.7803 | -1.2739 | 1414.284 | 23.5502 | -173.2525 | -49.5842 | 0 | 80.0728 | 260.0728 | 82.9981 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.87879 | 0 | 0% | 11.38% | 0% | 80% | 0% | 0 | 5.0828 | 5.0828 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6817 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 285 | 6817 | 60 | 281.0959 | -7.1699 | -0.9851 | 34.284 | 0.55498 | 171.6753 | -49.7527 | 0 | 79.499 | 100.501 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0035 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6818 | 2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 285 | 6818 | 120 | 281.0959 | -7.1699 | -0.9851 | 94.284 | 1.555 | 156.6753 | -45.6344 | 0 | 79.499 | 100.501 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0392 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6819 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 285 | 6819 | 180 | 281.0959 | -7.1699 | -0.9851 | 154.284 | 2.555 | 141.6753 | -38.609 | 0 | 79.499 | 100.501 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0561 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6820 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 285 | 6820 | 240 | 281.0959 | -7.1699 | -0.9851 | 214.284 | 3.555 | 126.6753 | -29.7875 | 0 | 79.499 | 100.501 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2941 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6821 | 5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 285 | 6821 | 300 | 281.0959 | -7.1699 | -0.9851 | 274.284 | 4.555 | 111.6753 | -19.9933 | 0 | 79.499 | 100.501 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.7731 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6822 | 6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 285 | 6822 | 360 | 281.0959 | -7.1699 | -0.9851 | 334.284 | 5.555 | 96.6753 | -9.784 | 0 | 79.499 | 100.501 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.1092 | 5.1092 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6823 | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 285 | 6823 | 420 | 281.0959 | -7.1699 | -0.9851 | 394.284 | 6.555 | 81.6753 | 0.42545 | 0.42545 | 79.038 | 100.962 | 81.969 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 164.7795 | 164.7795 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6824 | 8 | 10.1 | 2.72 | 15.56 | 18.28 | 15.56 | 7.78 | 285 | 6824 | 480 | 281.0959 | -7.1699 | -0.9851 | 454.284 | 7.555 | 66.6753 | 10.258 | 10.258 | 67.8037 | 112.1963 | 67.1211 | 5.9383 | 5.9383 | 13.2813 | 19.2196 | -6.3348 | 0% | 8.6911 | 0 | 0 | 172.4186 | 172.4186 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6825 | 9 | 10.3 | 44.39 | 53.47 | 97.86 | 53.47 | 26.74 | 285 | 6825 | 540 | 281.0959 | -7.1699 | -0.9851 | 514.284 | 8.555 | 51.6753 | 19.2932 | 19.2932 | 55.5569 | 124.4431 | 52.3309 | 82.1022 | 82.1022 | 45.6395 | 127.7417 | -0.26642 | 0% | 57.7648 | 0 | 0 | 157.3385 | 157.3385 | 0% | 11.71% | 11.71% | 80% | 9.369% | 5.4117 | 7.1852 | 6 | 32.4702 | 11.9675 | 20.64% | 20.64%
10 | 285 | 12 | 6826 | 10 | 10.5 | 123.83 | 100.28 | 224.11 | 100.28 | 50.14 | 285 | 6826 | 600 | 281.0959 | -7.1699 | -0.9851 | 574.284 | 9.555 | 36.6753 | 27.0012 | 27.0012 | 41.6905 | 138.3095 | 37.6735 | 215.8819 | 215.8819 | 85.5943 | 301.4762 | 0.35199 | 35.2% | 136.3276 | 47.9853 | 33.5897 | 142.0723 | 142.0723 | 23.64% | 11.61% | 11.61% | 85% | 9.871% | 13.4564 | 7.1323 | 6 | 80.7381 | 29.7575 | 56.83% | 56.83%
10 | 285 | 12 | 6827 | 11 | 10.8 | 200.78 | 154.17 | 354.95 | 154.17 | 77.09 | 285 | 6827 | 660 | 281.0959 | -7.1699 | -0.9851 | 634.284 | 10.555 | 21.6753 | 32.7161 | 32.7161 | 25.8206 | 154.1794 | 23.4066 | 340.9166 | 340.9166 | 131.5923 | 472.5089 | 0.51708 | 51.71% | 213.6685 | 110.483 | 77.3381 | 143.2057 | 143.2057 | 54% | 11.52% | 11.52% | 85% | 9.79% | 20.9183 | 7.0535 | 6 | 125.5096 | 46.2589 | 87.64% | 87.64%
10 | 285 | 12 | 6828 | 12 | 10.8 | 277.56 | 160.28 | 437.84 | 160.28 | 80.14 | 285 | 6828 | 720 | 281.0959 | -7.1699 | -0.9851 | 694.284 | 11.555 | 6.6753 | 35.7264 | 35.7264 | 8.1676 | 171.8324 | 11.155 | 466.3627 | 466.3627 | 136.8075 | 603.1702 | 0.57923 | 57.92% | 272.7536 | 157.9874 | 110.5912 | 138.4123 | 138.4123 | 79.9% | 11.45% | 11.45% | 90% | 10.31% | 28.1112 | 7.0535 | 6 | 168.667 | 62.1654 | 121.9% | 121.9%
10 | 285 | 12 | 6829 | 13 | 11.2 | 243.56 | 139.22 | 382.78 | 139.22 | 69.61 | 285 | 6829 | 780 | 281.0959 | -7.1699 | -0.9851 | 754.284 | 12.555 | -8.3247 | 35.5464 | 35.5464 | 10.169 | 190.169 | 12.2094 | 409.4712 | 409.4712 | 118.8317 | 528.3029 | 0.54914 | 54.91% | 238.8986 | 131.1879 | 91.8315 | 134.8725 | 134.8725 | 68.09% | 11.48% | 11.48% | 90% | 10.34% | 24.6905 | 6.9494 | 6 | 148.1432 | 54.6009 | 109.8% | 109.8%
10 | 285 | 12 | 6830 | 14 | 12 | 276.72 | 117 | 393.72 | 117 | 58.5 | 285 | 6830 | 840 | 281.0959 | -7.1699 | -0.9851 | 814.284 | 13.555 | -23.3247 | 32.2078 | 32.2078 | 27.6643 | 207.6643 | 24.9354 | 470.7863 | 470.7863 | 99.8657 | 570.6521 | 0.57129 | 57.13% | 258.0489 | 147.4217 | 103.1952 | 136.0891 | 136.0891 | 75.83% | 11.45% | 11.45% | 90% | 10.31% | 26.5987 | 6.7446 | 6 | 159.5922 | 58.8207 | 117.3% | 117.3%
10 | 285 | 12 | 6831 | 15 | 12.2 | 283.11 | 72.5 | 355.61 | 72.5 | 36.25 | 285 | 6831 | 900 | 281.0959 | -7.1699 | -0.9851 | 874.284 | 14.555 | -38.3247 | 26.238 | 26.238 | 43.31 | 223.31 | 39.274 | 495.7308 | 495.7308 | 61.8826 | 557.6135 | 0.56668 | 56.67% | 252.1528 | 142.8899 | 100.0229 | 132.7297 | 132.7297 | 75.36% | 11.46% | 11.46% | 90% | 10.31% | 25.9979 | 6.6941 | 6 | 155.9876 | 57.4921 | 117.5% | 117.5%
10 | 285 | 12 | 6832 | 16 | 12 | 177.36 | 78.19 | 255.55 | 78.19 | 39.1 | 285 | 6832 | 960 | 281.0959 | -7.1699 | -0.9851 | 934.284 | 15.555 | -53.3247 | 18.3538 | 18.3538 | 56.9728 | 236.9728 | 53.9528 | 331.4482 | 331.4482 | 66.7393 | 398.1876 | 0.4705 | 47.05% | 180.0604 | 84.719 | 59.3033 | 126.7647 | 126.7647 | 46.78% | 11.53% | 11.53% | 85% | 9.799% | 17.645 | 6.7446 | 6 | 105.8699 | 39.0203 | 83.52% | 83.52%
10 | 285 | 12 | 6833 | 17 | 12 | 108 | 65.14 | 173.14 | 65.14 | 32.57 | 285 | 6833 | 1020 | 281.0959 | -7.1699 | -0.9851 | 994.284 | 16.555 | -68.3247 | 9.2074 | 9.2074 | 69.0769 | 249.0769 | 68.7518 | 0 | 0 | 55.6005 | 55.6005 | -1.5844 | 0% | 25.1425 | 0 | 0 | 120.591 | 120.591 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6834 | 18 | 11.5 | 16.39 | 24.03 | 40.42 | 24.03 | 12.02 | 285 | 6834 | 1080 | 281.0959 | -7.1699 | -0.9851 | 1054.284 | 17.555 | -83.3247 | -0.6857 | 0 | 79.499 | 259.499 | 82.5956 | 0 | 0 | 20.5109 | 20.5109 | -5.7267 | 0% | 9.275 | 0 | 0 | 150.234 | 150.234 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6835 | 19 | 11.4 | 0 | 0 | 0 | 0 | 0 | 285 | 6835 | 1140 | 281.0959 | -7.1699 | -0.9851 | 1114.284 | 18.555 | -98.3247 | -10.9135 | 0 | 79.499 | 259.499 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.7348 | 142.7348 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6836 | 20 | 11.2 | 0 | 0 | 0 | 0 | 0 | 285 | 6836 | 1200 | 281.0959 | -7.1699 | -0.9851 | 1174.284 | 19.555 | -113.3247 | -21.0991 | 0 | 79.499 | 259.499 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.5477 | 136.5477 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6837 | 21 | 11 | 0 | 0 | 0 | 0 | 0 | 285 | 6837 | 1260 | 281.0959 | -7.1699 | -0.9851 | 1234.284 | 20.555 | -128.3247 | -30.8174 | 0 | 79.499 | 259.499 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.2124 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6838 | 22 | 10.7 | 0 | 0 | 0 | 0 | 0 | 285 | 6838 | 1320 | 281.0959 | -7.1699 | -0.9851 | 1294.284 | 21.555 | -143.3247 | -39.4875 | 0 | 79.499 | 259.499 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.0009 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6839 | 23 | 10.6 | 0 | 0 | 0 | 0 | 0 | 285 | 6839 | 1380 | 281.0959 | -7.1699 | -0.9851 | 1354.284 | 22.555 | -158.3247 | -46.2512 | 0 | 79.499 | 259.499 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7986 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
10 | 285 | 12 | 6840 | 24 | 10.8 | 0 | 0 | 0 | 0 | 0 | 285 | 6840 | 1440 | 281.0959 | -7.1699 | -0.9851 | 1414.284 | 23.555 | -173.3247 | -49.9797 | 0 | 79.499 | 259.499 | 82.5956 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.1391 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6841 | 1 | 10.8 | 0 | 0 | 0 | 0 | 0 | 286 | 6841 | 60 | 282.0822 | -7.5578 | -0.70133 | 34.284 | 0.55971 | 171.6043 | -50.1251 | 0 | 78.9271 | 101.0729 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8001 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6842 | 2 | 10.9 | 0 | 0 | 0 | 0 | 0 | 286 | 6842 | 120 | 282.0822 | -7.5578 | -0.70133 | 94.284 | 1.5597 | 156.6043 | -45.9643 | 0 | 78.9271 | 101.0729 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4804 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6843 | 3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 286 | 6843 | 180 | 282.0822 | -7.5578 | -0.70133 | 154.284 | 2.5597 | 141.6043 | -38.8959 | 0 | 78.9271 | 101.0729 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9227 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6844 | 4 | 10.5 | 0 | 0 | 0 | 0 | 0 | 286 | 6844 | 240 | 282.0822 | -7.5578 | -0.70133 | 214.284 | 3.5597 | 126.6043 | -30.0429 | 0 | 78.9271 | 101.0729 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9227 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6845 | 5 | 10.5 | 0 | 0 | 0 | 0 | 0 | 286 | 6845 | 300 | 282.0822 | -7.5578 | -0.70133 | 274.284 | 4.5597 | 111.6043 | -20.2308 | 0 | 78.9271 | 101.0729 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.1641 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6846 | 6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 286 | 6846 | 360 | 282.0822 | -7.5578 | -0.70133 | 334.284 | 5.5597 | 96.6043 | -10.016 | 0 | 78.9271 | 101.0729 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.926 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6847 | 7 | 10.6 | 0 | 0 | 0 | 0 | 0 | 286 | 6847 | 420 | 282.0822 | -7.5578 | -0.70133 | 394.284 | 6.5597 | 81.6043 | 0.18781 | 0.18781 | 78.7234 | 101.2766 | 81.9181 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 151.4266 | 151.4266 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6848 | 8 | 10.8 | 0.89 | 11.33 | 12.22 | 11.33 | 5.67 | 286 | 6848 | 480 | 282.0822 | -7.5578 | -0.70133 | 454.284 | 7.5597 | 66.6043 | 10.0044 | 10.0044 | 67.497 | 112.503 | 67.0854 | 1.9947 | 1.9947 | 9.6708 | 11.6655 | -10.8178 | 0% | 5.2751 | 0 | 0 | 156.3046 | 156.3046 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6849 | 9 | 11 | 22.44 | 58 | 80.44 | 58 | 29 | 286 | 6849 | 540 | 282.0822 | -7.5578 | -0.70133 | 514.284 | 8.5597 | 51.6043 | 19.014 | 19.014 | 55.2622 | 124.7378 | 52.3153 | 42.1054 | 42.1054 | 49.5061 | 91.6115 | -0.67081 | 0% | 41.4267 | 0 | 0 | 140.0955 | 140.0955 | 0% | 11.7% | 11.7% | 80% | 9.362% | 3.8784 | 7.0013 | 6 | 23.2705 | 8.5768 | 16.61% | 16.61%
10 | 286 | 13 | 6850 | 10 | 10.8 | 41.81 | 100.06 | 141.87 | 100.06 | 50.03 | 286 | 6850 | 600 | 282.0822 | -7.5578 | -0.70133 | 574.284 | 9.5597 | 36.6043 | 26.6886 | 26.6886 | 41.4213 | 138.5787 | 37.6896 | 73.6645 | 73.6645 | 85.4066 | 159.071 | -0.048285 | 0% | 71.9319 | 0 | 0 | 142.8403 | 142.8403 | 0% | 11.68% | 11.68% | 80% | 9.341% | 6.7192 | 7.0535 | 6 | 40.3152 | 14.8589 | 28.22% | 28.22%
10 | 286 | 13 | 6851 | 11 | 11 | 50.97 | 137.5 | 188.47 | 137.5 | 68.75 | 286 | 6851 | 660 | 282.0822 | -7.5578 | -0.70133 | 634.284 | 10.5597 | 21.6043 | 32.3671 | 32.3671 | 25.6031 | 154.3969 | 23.4875 | 87.3218 | 87.3218 | 117.3636 | 204.6853 | 0.14392 | 14.39% | 92.5587 | 13.3208 | 9.3246 | 142.8656 | 142.8656 | 6.527% | 11.65% | 11.65% | 80% | 9.317% | 8.624 | 7.0013 | 6 | 51.7441 | 19.0712 | 36.22% | 36.22%
10 | 286 | 13 | 6852 | 12 | 10.8 | 88.33 | 166.44 | 254.77 | 166.44 | 83.22 | 286 | 6852 | 720 | 282.0822 | -7.5578 | -0.70133 | 694.284 | 11.5597 | 6.6043 | 35.3471 | 35.3471 | 8.0351 | 171.9649 | 11.4266 | 149.6542 | 149.6542 | 142.0654 | 291.7196 | 0.33926 | 33.93% | 131.9156 | 44.7537 | 31.3276 | 120.5065 | 120.5065 | 26% | 11.61% | 11.61% | 80% | 9.287% | 12.2515 | 7.0535 | 6 | 73.5088 | 27.093 | 61% | 61%
10 | 286 | 13 | 6853 | 13 | 10.6 | 115.69 | 167.56 | 283.25 | 167.56 | 83.78 | 286 | 6853 | 780 | 282.0822 | -7.5578 | -0.70133 | 754.284 | 12.5597 | -8.3957 | 35.1528 | 35.1528 | 10.1966 | 190.1966 | 12.5422 | 196.1398 | 196.1398 | 143.0214 | 339.1612 | 0.4029 | 40.29% | 153.3687 | 61.7916 | 43.2542 | 121.0042 | 121.0042 | 35.75% | 11.59% | 11.59% | 85% | 9.852% | 15.1094 | 7.1059 | 6 | 90.6567 | 33.4132 | 74.92% | 74.92%
10 | 286 | 13 | 6854 | 14 | 10.3 | 179.44 | 129.03 | 308.47 | 129.03 | 64.52 | 286 | 6854 | 840 | 282.0822 | -7.5578 | -0.70133 | 814.284 | 13.5597 | -23.3957 | 31.8178 | 31.8178 | 27.5964 | 207.5964 | 25.1373 | 308.1177 | 308.1177 | 110.134 | 418.2517 | 0.47707 | 47.71% | 189.1334 | 90.2305 | 63.1614 | 121.4546 | 121.4546 | 52% | 11.56% | 11.56% | 85% | 9.822% | 18.5773 | 7.1852 | 6 | 111.4637 | 41.082 | 91.77% | 91.77%
10 | 286 | 13 | 6855 | 15 | 10.4 | 172.17 | 126.44 | 298.61 | 126.44 | 63.22 | 286 | 6855 | 900 | 282.0822 | -7.5578 | -0.70133 | 874.284 | 14.5597 | -38.3957 | 25.863 | 25.863 | 43.1747 | 223.1747 | 39.4232 | 304.8859 | 304.8859 | 107.9233 | 412.8092 | 0.47333 | 47.33% | 186.6723 | 88.3572 | 61.85 | 120.1143 | 120.1143 | 51.49% | 11.56% | 11.56% | 85% | 9.823% | 18.3368 | 7.1587 | 6 | 110.0206 | 40.5501 | 91.6% | 91.6%
10 | 286 | 13 | 6856 | 16 | 9.7 | 128.67 | 98.61 | 227.28 | 98.61 | 49.31 | 286 | 6856 | 960 | 282.0822 | -7.5578 | -0.70133 | 934.284 | 15.5597 | -53.3957 | 17.9966 | 17.9966 | 56.797 | 236.797 | 54.074 | 244.3538 | 244.3538 | 84.1689 | 328.5227 | 0.38352 | 38.35% | 148.558 | 56.9743 | 39.882 | 115.3944 | 115.3944 | 34.56% | 11.62% | 11.62% | 85% | 9.876% | 14.6719 | 7.3455 | 6 | 88.0315 | 32.4457 | 76.29% | 76.29%
10 | 286 | 13 | 6857 | 17 | 8.5 | 70.78 | 61.11 | 131.89 | 61.11 | 30.56 | 286 | 6857 | 1020 | 282.0822 | -7.5578 | -0.70133 | 994.284 | 16.5597 | -68.3957 | 8.8655 | 8.8655 | 68.8781 | 248.8781 | 68.8544 | 0 | 0 | 52.1606 | 52.1606 | -1.8983 | 0% | 23.587 | 0 | 0 | 149.5817 | 149.5817 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6858 | 18 | 8.6 | 10.89 | 23.06 | 33.95 | 23.06 | 11.53 | 286 | 6858 | 1080 | 282.0822 | -7.5578 | -0.70133 | 1054.284 | 17.5597 | -83.3957 | -1.0179 | 0 | 78.9271 | 258.9271 | 82.1948 | 0 | 0 | 19.6829 | 19.6829 | -6.3453 | 0% | 8.9006 | 0 | 0 | 141.7223 | 141.7223 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6859 | 19 | 8.4 | 0 | 0 | 0 | 0 | 0 | 286 | 6859 | 1140 | 282.0822 | -7.5578 | -0.70133 | 1114.284 | 18.5597 | -98.3957 | -11.2427 | 0 | 78.9271 | 258.9271 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.9609 | 135.9609 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6860 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 286 | 6860 | 1200 | 282.0822 | -7.5578 | -0.70133 | 1174.284 | 19.5597 | -113.3957 | -21.4329 | 0 | 78.9271 | 258.9271 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.35 | 131.35 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6861 | 21 | 7.4 | 0 | 0 | 0 | 0 | 0 | 286 | 6861 | 1260 | 282.0822 | -7.5578 | -0.70133 | 1234.284 | 20.5597 | -128.3957 | -31.1638 | 0 | 78.9271 | 258.9271 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5721 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6862 | 22 | 7.3 | 0 | 0 | 0 | 0 | 0 | 286 | 6862 | 1320 | 282.0822 | -7.5578 | -0.70133 | 1294.284 | 21.5597 | -143.3957 | -39.8536 | 0 | 78.9271 | 258.9271 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6358 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6863 | 23 | 7.3 | 0 | 0 | 0 | 0 | 0 | 286 | 6863 | 1380 | 282.0822 | -7.5578 | -0.70133 | 1354.284 | 22.5597 | -158.3957 | -46.6379 | 0 | 78.9271 | 258.9271 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4685 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
10 | 286 | 13 | 6864 | 24 | 7.3 | 0 | 0 | 0 | 0 | 0 | 286 | 6864 | 1440 | 282.0822 | -7.5578 | -0.70133 | 1414.284 | 23.5597 | -173.3957 | -50.3733 | 0 | 78.9271 | 258.9271 | 82.1948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3013 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6865 | 1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 287 | 6865 | 60 | 283.0685 | -7.9439 | -0.42287 | 34.284 | 0.56435 | 171.5347 | -50.4956 | 0 | 78.3573 | 101.6427 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2026 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6866 | 2 | 6.8 | 0 | 0 | 0 | 0 | 0 | 287 | 6866 | 120 | 283.0685 | -7.9439 | -0.42287 | 94.284 | 1.5644 | 156.5347 | -46.2923 | 0 | 78.3573 | 101.6427 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6054 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6867 | 3 | 6.3 | 0 | 0 | 0 | 0 | 0 | 287 | 6867 | 180 | 283.0685 | -7.9439 | -0.42287 | 154.284 | 2.5644 | 141.5347 | -39.1811 | 0 | 78.3573 | 101.6427 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0082 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6868 | 4 | 6.4 | 0 | 0 | 0 | 0 | 0 | 287 | 6868 | 240 | 283.0685 | -7.9439 | -0.42287 | 214.284 | 3.5644 | 126.5347 | -30.297 | 0 | 78.3573 | 101.6427 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8558 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6869 | 5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 287 | 6869 | 300 | 283.0685 | -7.9439 | -0.42287 | 274.284 | 4.5644 | 111.5347 | -20.4674 | 0 | 78.3573 | 101.6427 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.8374 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6870 | 6 | 6.2 | 0 | 0 | 0 | 0 | 0 | 287 | 6870 | 360 | 283.0685 | -7.9439 | -0.42287 | 334.284 | 5.5644 | 96.5347 | -10.2474 | 0 | 78.3573 | 101.6427 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.3792 | 1.3792 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6871 | 7 | 6.2 | 0 | 0 | 0 | 0 | 0 | 287 | 6871 | 420 | 283.0685 | -7.9439 | -0.42287 | 394.284 | 6.5644 | 81.5347 | -0.049496 | 0 | 78.3573 | 101.6427 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 160.5386 | 160.5386 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6872 | 8 | 6 | 2.5 | 14.58 | 17.08 | 14.58 | 7.29 | 287 | 6872 | 480 | 283.0685 | -7.9439 | -0.42287 | 454.284 | 7.5644 | 66.5347 | 9.751 | 9.751 | 67.1931 | 112.8069 | 67.0521 | 0 | 0 | 12.4448 | 12.4448 | -10.9989 | 0% | 5.6275 | 0 | 0 | 167.606 | 167.606 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6873 | 9 | 6.1 | 53.19 | 77.72 | 130.91 | 77.72 | 38.86 | 287 | 6873 | 540 | 283.0685 | -7.9439 | -0.42287 | 514.284 | 8.5644 | 51.5347 | 18.735 | 18.735 | 54.9708 | 125.0292 | 52.3029 | 101.2632 | 101.2632 | 66.3382 | 167.6014 | -0.070968 | 0% | 75.7894 | 0 | 0 | 154.2522 | 154.2522 | 0% | 11.84% | 11.84% | 80% | 9.468% | 7.176 | 8.3603 | 6 | 43.0561 | 15.8691 | 27.91% | 27.91%
10 | 287 | 14 | 6874 | 10 | 6.3 | 91.81 | 95.33 | 187.14 | 95.33 | 47.67 | 287 | 6874 | 600 | 283.0685 | -7.9439 | -0.42287 | 574.284 | 9.5644 | 36.5347 | 26.3764 | 26.3764 | 41.1559 | 138.8441 | 37.7102 | 163.4883 | 163.4883 | 81.3692 | 244.8575 | 0.20705 | 20.7% | 110.7246 | 22.9251 | 16.0475 | 156.2602 | 156.2602 | 10.27% | 11.77% | 11.77% | 80% | 9.416% | 10.4261 | 8.3016 | 6 | 62.5565 | 23.0564 | 40.03% | 40.03%
10 | 287 | 14 | 6875 | 11 | 7.2 | 210.61 | 142.78 | 353.39 | 142.78 | 71.39 | 287 | 6875 | 660 | 283.0685 | -7.9439 | -0.42287 | 634.284 | 10.5644 | 21.5347 | 32.019 | 32.019 | 25.3895 | 154.6105 | 23.575 | 364.0739 | 364.0739 | 121.8704 | 485.9442 | 0.50761 | 50.76% | 219.744 | 111.5447 | 78.0813 | 139.26 | 139.26 | 56.07% | 11.57% | 11.57% | 85% | 9.837% | 21.6165 | 8.0406 | 6 | 129.699 | 47.803 | 93.13% | 93.13%
10 | 287 | 14 | 6876 | 12 | 8.2 | 247.72 | 161.67 | 409.39 | 161.67 | 80.84 | 287 | 6876 | 720 | 283.0685 | -7.9439 | -0.42287 | 694.284 | 11.5644 | 6.5347 | 34.9694 | 34.9694 | 7.9059 | 172.0941 | 11.7043 | 423.2296 | 423.2296 | 137.994 | 561.2235 | 0.55158 | 55.16% | 253.7853 | 139.9837 | 97.9886 | 134.8805 | 134.8805 | 72.65% | 11.51% | 11.51% | 90% | 10.36% | 26.2827 | 7.7573 | 6 | 157.6961 | 58.1218 | 116.9% | 116.9%
10 | 287 | 14 | 6877 | 13 | 9.4 | 280.14 | 170.33 | 450.47 | 170.33 | 85.17 | 287 | 6877 | 780 | 283.0685 | -7.9439 | -0.42287 | 754.284 | 12.5644 | -8.4653 | 34.7611 | 34.7611 | 10.2224 | 190.2224 | 12.8762 | 478.984 | 478.984 | 145.3857 | 624.3698 | 0.58163 | 58.16% | 282.34 | 164.2175 | 114.9523 | 136.5944 | 136.5944 | 84.16% | 11.45% | 11.45% | 90% | 10.31% | 29.1063 | 7.4266 | 6 | 174.6378 | 64.366 | 127.9% | 127.9%
10 | 287 | 14 | 6878 | 14 | 11.2 | 279.03 | 171.89 | 450.92 | 171.89 | 85.95 | 287 | 6878 | 840 | 283.0685 | -7.9439 | -0.42287 | 814.284 | 13.5644 | -23.4653 | 31.4299 | 31.4299 | 27.5281 | 207.5281 | 25.3414 | 483.6085 | 483.6085 | 146.7173 | 630.3258 | 0.59039 | 59.04% | 285.0333 | 168.2803 | 117.7962 | 138.9667 | 138.9667 | 84.77% | 11.43% | 11.43% | 90% | 10.29% | 29.332 | 6.9494 | 6 | 175.9917 | 64.865 | 126.6% | 126.6%
10 | 287 | 14 | 6879 | 15 | 10.5 | 237.72 | 163.61 | 401.33 | 163.61 | 81.81 | 287 | 6879 | 900 | 283.0685 | -7.9439 | -0.42287 | 874.284 | 14.5644 | -38.4653 | 25.49 | 25.49 | 43.0398 | 223.0398 | 39.5733 | 425.7821 | 425.7821 | 139.6499 | 565.4319 | 0.563 | 56.3% | 255.6883 | 143.9514 | 100.766 | 133.5921 | 133.5921 | 75.43% | 11.47% | 11.47% | 90% | 10.33% | 26.4052 | 7.1323 | 6 | 158.4312 | 58.3928 | 118.6% | 118.6%
10 | 287 | 14 | 6880 | 16 | 10.9 | 149.44 | 96.67 | 246.11 | 96.67 | 48.34 | 287 | 6880 | 960 | 283.0685 | -7.9439 | -0.42287 | 934.284 | 15.5644 | -53.4653 | 17.6416 | 17.6416 | 56.6219 | 236.6219 | 54.1952 | 288.4761 | 288.4761 | 82.513 | 370.9891 | 0.43919 | 43.92% | 167.7613 | 73.6787 | 51.5751 | 125.7229 | 125.7229 | 41.02% | 11.57% | 11.57% | 85% | 9.832% | 16.4938 | 7.0274 | 6 | 98.9628 | 36.4746 | 78.72% | 78.72%
10 | 287 | 14 | 6881 | 17 | 10.5 | 90.69 | 65.69 | 156.38 | 65.69 | 32.85 | 287 | 6881 | 1020 | 283.0685 | -7.9439 | -0.42287 | 994.284 | 16.5644 | -68.4653 | 8.5257 | 8.5257 | 68.6798 | 248.6798 | 68.9563 | 0 | 0 | 56.0699 | 56.0699 | -1.6264 | 0% | 25.3548 | 0 | 0 | 118.524 | 118.524 | 0% | 11.74% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6882 | 18 | 9.8 | 16.44 | 23.89 | 40.33 | 23.89 | 11.95 | 287 | 6882 | 1080 | 283.0685 | -7.9439 | -0.42287 | 1054.284 | 17.5644 | -83.4653 | -1.3478 | 0 | 78.3573 | 258.3573 | 81.7959 | 0 | 0 | 20.3914 | 20.3914 | -5.9589 | 0% | 9.221 | 0 | 0 | 149.1623 | 149.1623 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6883 | 19 | 8.5 | 0 | 0 | 0 | 0 | 0 | 287 | 6883 | 1140 | 283.0685 | -7.9439 | -0.42287 | 1114.284 | 18.5644 | -98.4653 | -11.5695 | 0 | 78.3573 | 258.3573 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.92 | 139.92 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6884 | 20 | 7.1 | 0 | 0 | 0 | 0 | 0 | 287 | 6884 | 1200 | 283.0685 | -7.9439 | -0.42287 | 1174.284 | 19.5644 | -113.4653 | -21.7641 | 0 | 78.3573 | 258.3573 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.1027 | 132.1027 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6885 | 21 | 6.1 | 0 | 0 | 0 | 0 | 0 | 287 | 6885 | 1260 | 283.0685 | -7.9439 | -0.42287 | 1234.284 | 20.5644 | -128.4653 | -31.5076 | 0 | 78.3573 | 258.3573 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.823 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6886 | 22 | 6 | 0 | 0 | 0 | 0 | 0 | 287 | 6886 | 1320 | 283.0685 | -7.9439 | -0.42287 | 1294.284 | 21.5644 | -143.4653 | -40.2171 | 0 | 78.3573 | 258.3573 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2614 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6887 | 23 | 5.2 | 0 | 0 | 0 | 0 | 0 | 287 | 6887 | 1380 | 283.0685 | -7.9439 | -0.42287 | 1354.284 | 22.5644 | -158.4653 | -47.0224 | 0 | 78.3573 | 258.3573 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1214 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
10 | 287 | 14 | 6888 | 24 | 4.2 | 0 | 0 | 0 | 0 | 0 | 287 | 6888 | 1440 | 283.0685 | -7.9439 | -0.42287 | 1414.284 | 23.5644 | -173.4653 | -50.765 | 0 | 78.3573 | 258.3573 | 81.7959 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2862 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6889 | 1 | 3.4 | 0 | 0 | 0 | 0 | 0 | 288 | 6889 | 60 | 284.0548 | -8.3281 | -0.15007 | 34.284 | 0.5689 | 171.4665 | -50.8641 | 0 | 77.7896 | 102.2104 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6149 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6890 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 288 | 6890 | 120 | 284.0548 | -8.3281 | -0.15007 | 94.284 | 1.5689 | 156.4665 | -46.6183 | 0 | 77.7896 | 102.2104 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8452 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6891 | 3 | 2.8 | 0 | 0 | 0 | 0 | 0 | 288 | 6891 | 180 | 284.0548 | -8.3281 | -0.15007 | 154.284 | 2.5689 | 141.4665 | -39.4645 | 0 | 77.7896 | 102.2104 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7708 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6892 | 4 | 2.6 | 0 | 0 | 0 | 0 | 0 | 288 | 6892 | 240 | 284.0548 | -8.3281 | -0.15007 | 214.284 | 3.5689 | 126.4665 | -30.5496 | 0 | 77.7896 | 102.2104 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0756 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6893 | 5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 288 | 6893 | 300 | 284.0548 | -8.3281 | -0.15007 | 274.284 | 4.5689 | 111.4665 | -20.7029 | 0 | 77.7896 | 102.2104 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6283 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6894 | 6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 288 | 6894 | 360 | 284.0548 | -8.3281 | -0.15007 | 334.284 | 5.5689 | 96.4665 | -10.4782 | 0 | 77.7896 | 102.2104 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.686 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6895 | 7 | 1.1 | 0 | 0 | 0 | 0 | 0 | 288 | 6895 | 420 | 284.0548 | -8.3281 | -0.15007 | 394.284 | 6.5689 | 81.4665 | -0.28643 | 0 | 77.7896 | 102.2104 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 153.4028 | 153.4028 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6896 | 8 | 0.8 | 2.56 | 14.17 | 16.73 | 14.17 | 7.09 | 288 | 6896 | 480 | 284.0548 | -8.3281 | -0.15007 | 454.284 | 7.5689 | 66.4665 | 9.4978 | 9.4978 | 66.8921 | 113.1079 | 67.0212 | 0 | 0 | 12.0949 | 12.0949 | -12.3823 | 0% | 5.4693 | 0 | 0 | 160.2737 | 160.2737 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6897 | 9 | 2.7 | 48.28 | 59.31 | 107.59 | 59.31 | 29.66 | 288 | 6897 | 540 | 284.0548 | -8.3281 | -0.15007 | 514.284 | 8.5689 | 51.4665 | 18.4563 | 18.4563 | 54.6828 | 125.3172 | 52.2939 | 93.2732 | 93.2732 | 50.6243 | 143.8975 | -0.27204 | 0% | 65.0704 | 0 | 0 | 148.4272 | 148.4272 | 0% | 11.98% | 11.98% | 80% | 9.581% | 6.2344 | 9.4021 | 6 | 37.4065 | 13.7869 | 25.2% | 25.2%
10 | 288 | 15 | 6898 | 10 | 5.4 | 113 | 108.39 | 221.39 | 108.39 | 54.2 | 288 | 6898 | 600 | 284.0548 | -8.3281 | -0.15007 | 574.284 | 9.5689 | 36.4665 | 26.0647 | 26.0647 | 40.8943 | 139.1057 | 37.7353 | 203.3876 | 203.3876 | 92.5167 | 295.9043 | 0.30276 | 30.28% | 133.8079 | 40.5111 | 28.3578 | 135.9997 | 135.9997 | 20.85% | 11.76% | 11.76% | 80% | 9.405% | 12.5852 | 8.5682 | 6 | 75.5113 | 27.8311 | 55.52% | 55.52%
10 | 288 | 15 | 6899 | 11 | 7.7 | 181.72 | 157.36 | 339.08 | 157.36 | 78.68 | 288 | 6899 | 660 | 284.0548 | -8.3281 | -0.15007 | 634.284 | 10.5689 | 21.4665 | 31.6719 | 31.6719 | 25.18 | 154.82 | 23.6689 | 316.9843 | 316.9843 | 134.3152 | 451.2995 | 0.48748 | 48.75% | 204.0776 | 99.4846 | 69.6392 | 139.5009 | 139.5009 | 49.92% | 11.59% | 11.59% | 85% | 9.85% | 20.1011 | 7.8981 | 6 | 120.6063 | 44.4517 | 86.46% | 86.46%
10 | 288 | 15 | 6900 | 12 | 8.9 | 214.03 | 161.39 | 375.42 | 161.39 | 80.7 | 288 | 6900 | 720 | 284.0548 | -8.3281 | -0.15007 | 694.284 | 11.5689 | 6.4665 | 34.5933 | 34.5933 | 7.7799 | 172.2201 | 11.9876 | 368.7601 | 368.7601 | 137.755 | 506.5151 | 0.52757 | 52.76% | 229.0461 | 120.8387 | 84.5871 | 134.4713 | 134.4713 | 62.9% | 11.53% | 11.53% | 90% | 10.38% | 23.7705 | 7.5632 | 6 | 142.6232 | 52.5664 | 106.1% | 106.1%
10 | 288 | 15 | 6901 | 13 | 9.4 | 255.78 | 187.22 | 443 | 187.22 | 93.61 | 288 | 6901 | 780 | 284.0548 | -8.3281 | -0.15007 | 754.284 | 12.5689 | -8.5335 | 34.3715 | 34.3715 | 10.2464 | 190.2464 | 13.2108 | 441.0735 | 441.0735 | 159.8023 | 600.8757 | 0.57294 | 57.29% | 271.716 | 155.6758 | 108.9731 | 136.1086 | 136.1086 | 80.06% | 11.47% | 11.47% | 90% | 10.32% | 28.0446 | 7.4266 | 6 | 168.2674 | 62.0181 | 123.6% | 123.6%
10 | 288 | 15 | 6902 | 14 | 10.8 | 210.83 | 180.78 | 391.61 | 180.78 | 90.39 | 288 | 6902 | 840 | 284.0548 | -8.3281 | -0.15007 | 814.284 | 13.5689 | -23.5335 | 31.0442 | 31.0442 | 27.4595 | 207.4595 | 25.5475 | 368.8518 | 368.8518 | 154.3054 | 523.1571 | 0.54485 | 54.49% | 236.5717 | 128.8971 | 90.228 | 135.3144 | 135.3144 | 66.68% | 11.49% | 11.49% | 90% | 10.34% | 24.4683 | 7.0535 | 6 | 146.8099 | 54.1095 | 108.5% | 108.5%
10 | 288 | 15 | 6903 | 15 | 11.2 | 238.11 | 161.33 | 399.44 | 161.33 | 80.67 | 288 | 6903 | 900 | 284.0548 | -8.3281 | -0.15007 | 874.284 | 14.5689 | -38.5335 | 25.1194 | 25.1194 | 42.9052 | 222.9052 | 39.7243 | 431.4128 | 431.4128 | 137.7038 | 569.1166 | 0.56741 | 56.74% | 257.3545 | 146.0265 | 102.2185 | 133.977 | 133.977 | 76.3% | 11.46% | 11.46% | 90% | 10.32% | 26.5522 | 6.9494 | 6 | 159.3134 | 58.7179 | 118.9% | 118.9%
10 | 288 | 15 | 6904 | 16 | 11.1 | 128.19 | 132.22 | 260.41 | 132.22 | 66.11 | 288 | 6904 | 960 | 284.0548 | -8.3281 | -0.15007 | 934.284 | 15.5689 | -53.5335 | 17.2889 | 17.2889 | 56.4472 | 236.4472 | 54.3164 | 251.6046 | 251.6046 | 112.8568 | 364.4615 | 0.43393 | 43.39% | 164.8095 | 71.5154 | 50.0608 | 125.8521 | 125.8521 | 39.78% | 11.57% | 11.57% | 85% | 9.83% | 16.2015 | 6.9753 | 6 | 97.2087 | 35.8281 | 77.24% | 77.24%
10 | 288 | 15 | 6905 | 17 | 11.2 | 50.33 | 75.83 | 126.16 | 75.83 | 37.92 | 288 | 6905 | 1020 | 284.0548 | -8.3281 | -0.15007 | 994.284 | 16.5689 | -68.5335 | 8.1883 | 8.1883 | 68.482 | 248.482 | 69.0576 | 0 | 0 | 64.725 | 64.725 | -1.2763 | 0% | 29.2686 | 0 | 0 | 158.7249 | 158.7249 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6906 | 18 | 10.8 | 9.22 | 24.03 | 33.25 | 24.03 | 12.02 | 288 | 6906 | 1080 | 284.0548 | -8.3281 | -0.15007 | 1054.284 | 17.5689 | -83.5335 | -1.6752 | 0 | 77.7896 | 257.7896 | 81.3989 | 0 | 0 | 20.5109 | 20.5109 | -5.8058 | 0% | 9.275 | 0 | 0 | 149.5101 | 149.5101 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6907 | 19 | 10.1 | 0 | 0 | 0 | 0 | 0 | 288 | 6907 | 1140 | 284.0548 | -8.3281 | -0.15007 | 1114.284 | 18.5689 | -98.5335 | -11.8936 | 0 | 77.7896 | 257.7896 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.3529 | 142.3529 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6908 | 20 | 9.8 | 0 | 0 | 0 | 0 | 0 | 288 | 6908 | 1200 | 284.0548 | -8.3281 | -0.15007 | 1174.284 | 19.5689 | -113.5335 | -22.0926 | 0 | 77.7896 | 257.7896 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.5228 | 136.5228 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6909 | 21 | 9.3 | 0 | 0 | 0 | 0 | 0 | 288 | 6909 | 1260 | 284.0548 | -8.3281 | -0.15007 | 1234.284 | 20.5689 | -128.5335 | -31.8486 | 0 | 77.7896 | 257.7896 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5508 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6910 | 22 | 9 | 0 | 0 | 0 | 0 | 0 | 288 | 6910 | 1320 | 284.0548 | -8.3281 | -0.15007 | 1294.284 | 21.5689 | -143.5335 | -40.5778 | 0 | 77.7896 | 257.7896 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2183 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6911 | 23 | 8.6 | 0 | 0 | 0 | 0 | 0 | 288 | 6911 | 1380 | 284.0548 | -8.3281 | -0.15007 | 1354.284 | 22.5689 | -158.5335 | -47.4043 | 0 | 77.7896 | 257.7896 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4487 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
10 | 288 | 15 | 6912 | 24 | 8.5 | 0 | 0 | 0 | 0 | 0 | 288 | 6912 | 1440 | 284.0548 | -8.3281 | -0.15007 | 1414.284 | 23.5689 | -173.5335 | -51.1546 | 0 | 77.7896 | 257.7896 | 81.3989 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2218 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6913 | 1 | 8.3 | 0 | 0 | 0 | 0 | 0 | 289 | 6913 | 60 | 285.0411 | -8.7103 | 0.11675 | 34.284 | 0.57335 | 171.3998 | -51.2304 | 0 | 77.2244 | 102.7756 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.135 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6914 | 2 | 8.4 | 0 | 0 | 0 | 0 | 0 | 289 | 6914 | 120 | 285.0411 | -8.7103 | 0.11675 | 94.284 | 1.5733 | 156.3998 | -46.9422 | 0 | 77.2244 | 102.7756 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4964 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6915 | 3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 289 | 6915 | 180 | 285.0411 | -8.7103 | 0.11675 | 154.284 | 2.5733 | 141.3998 | -39.746 | 0 | 77.2244 | 102.7756 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1627 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6916 | 4 | 8.3 | 0 | 0 | 0 | 0 | 0 | 289 | 6916 | 240 | 285.0411 | -8.7103 | 0.11675 | 214.284 | 3.5733 | 126.3998 | -30.8007 | 0 | 77.2244 | 102.7756 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1627 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6917 | 5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 289 | 6917 | 300 | 285.0411 | -8.7103 | 0.11675 | 274.284 | 4.5733 | 111.3998 | -20.9374 | 0 | 77.2244 | 102.7756 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -0.52267 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6918 | 6 | 8.3 | 0 | 0 | 0 | 0 | 0 | 289 | 6918 | 360 | 285.0411 | -8.7103 | 0.11675 | 334.284 | 5.5733 | 96.3998 | -10.7082 | 0 | 77.2244 | 102.7756 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 8.4185 | 8.4185 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6919 | 7 | 8.4 | 0 | 0 | 0 | 0 | 0 | 289 | 6919 | 420 | 285.0411 | -8.7103 | 0.11675 | 394.284 | 6.5733 | 81.3998 | -0.52292 | 0 | 77.2244 | 102.7756 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 171.204 | 171.204 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6920 | 8 | 8.5 | 2.72 | 10.42 | 13.14 | 10.42 | 5.21 | 289 | 6920 | 480 | 285.0411 | -8.7103 | 0.11675 | 454.284 | 7.5733 | 66.3998 | 9.245 | 9.245 | 66.5941 | 113.4059 | 66.9929 | 0 | 0 | 8.894 | 8.894 | -15.0443 | 0% | 4.0219 | 0 | 0 | 179.5494 | 179.5494 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6921 | 9 | 8.6 | 75.61 | 47.92 | 123.53 | 47.92 | 23.96 | 289 | 6921 | 540 | 285.0411 | -8.7103 | 0.11675 | 514.284 | 8.5733 | 51.3998 | 18.178 | 18.178 | 54.3984 | 125.6016 | 52.2881 | 148.2513 | 148.2513 | 40.9023 | 189.1535 | 0.060056 | 6.006% | 85.5352 | 5.1369 | 3.5958 | 166.5222 | 166.5222 | 2.159% | 11.74% | 11.74% | 80% | 9.388% | 8.03 | 7.6459 | 6 | 48.1803 | 17.7577 | 28.93% | 28.93%
10 | 289 | 16 | 6922 | 10 | 9 | 144.58 | 96.25 | 240.83 | 96.25 | 48.13 | 289 | 6922 | 600 | 285.0411 | -8.7103 | 0.11675 | 574.284 | 9.5733 | 36.3998 | 25.7537 | 25.7537 | 40.6368 | 139.3632 | 37.7648 | 263.0473 | 263.0473 | 82.1545 | 345.2018 | 0.39908 | 39.91% | 156.1003 | 62.2965 | 43.6075 | 149.2435 | 149.2435 | 29.22% | 11.63% | 11.63% | 85% | 9.883% | 15.4275 | 7.5357 | 6 | 92.5651 | 34.1166 | 62.02% | 62.02%
10 | 289 | 16 | 6923 | 11 | 9.6 | 224.5 | 125.89 | 350.39 | 125.89 | 62.95 | 289 | 6923 | 660 | 285.0411 | -8.7103 | 0.11675 | 634.284 | 10.5733 | 21.3998 | 31.3259 | 31.3259 | 24.9745 | 155.0255 | 23.7691 | 395.1819 | 395.1819 | 107.4538 | 502.6357 | 0.52871 | 52.87% | 227.2919 | 120.1706 | 84.1194 | 147.8118 | 147.8118 | 56.91% | 11.52% | 11.52% | 90% | 10.37% | 23.5699 | 7.3724 | 6 | 141.4194 | 52.1227 | 95.68% | 95.68%
10 | 289 | 16 | 6924 | 12 | 10.2 | 202.17 | 153.06 | 355.23 | 153.06 | 76.53 | 289 | 6924 | 720 | 285.0411 | -8.7103 | 0.11675 | 694.284 | 11.5733 | 6.3998 | 34.2189 | 34.2189 | 7.6572 | 172.3428 | 12.2758 | 351.285 | 351.285 | 130.6449 | 481.9298 | 0.51979 | 51.98% | 217.9287 | 113.2765 | 79.2935 | 138.0471 | 138.0471 | 57.44% | 11.52% | 11.52% | 85% | 9.795% | 21.3459 | 7.2117 | 6 | 128.0757 | 47.2047 | 92.78% | 92.78%
10 | 289 | 16 | 6925 | 13 | 11.1 | 208.61 | 169.03 | 377.64 | 169.03 | 84.52 | 289 | 6925 | 780 | 285.0411 | -8.7103 | 0.11675 | 754.284 | 12.5733 | -8.6002 | 33.9842 | 33.9842 | 10.2686 | 190.2686 | 13.5458 | 362.827 | 362.827 | 144.2761 | 507.1032 | 0.53802 | 53.8% | 229.312 | 123.3755 | 86.3628 | 137.9704 | 137.9704 | 62.6% | 11.5% | 11.5% | 90% | 10.35% | 23.7242 | 6.9753 | 6 | 142.3455 | 52.4641 | 103.2% | 103.2%
10 | 289 | 16 | 6926 | 14 | 11.4 | 210.22 | 170.22 | 380.44 | 170.22 | 85.11 | 289 | 6926 | 840 | 285.0411 | -8.7103 | 0.11675 | 814.284 | 13.5733 | -23.6002 | 30.661 | 30.661 | 27.3903 | 207.3903 | 25.7553 | 371.2785 | 371.2785 | 145.2919 | 516.5703 | 0.54425 | 54.42% | 233.5931 | 127.1319 | 88.9923 | 137.5646 | 137.5646 | 64.69% | 11.49% | 11.49% | 90% | 10.34% | 24.1476 | 6.8978 | 6 | 144.8855 | 53.4002 | 105.3% | 105.3%
10 | 289 | 16 | 6927 | 15 | 11.9 | 181.67 | 153.47 | 335.14 | 153.47 | 76.74 | 289 | 6927 | 900 | 285.0411 | -8.7103 | 0.11675 | 874.284 | 14.5733 | -38.6002 | 24.7512 | 24.7512 | 42.771 | 222.771 | 39.8759 | 332.9995 | 332.9995 | 130.9948 | 463.9944 | 0.5173 | 51.73% | 209.8183 | 108.5399 | 75.9779 | 133.6759 | 133.6759 | 56.84% | 11.5% | 11.5% | 85% | 9.776% | 20.5127 | 6.77 | 6 | 123.0765 | 45.3621 | 92.07% | 92.07%
10 | 289 | 16 | 6928 | 16 | 12.3 | 164.17 | 110.69 | 274.86 | 110.69 | 55.35 | 289 | 6928 | 960 | 285.0411 | -8.7103 | 0.11675 | 934.284 | 15.5733 | -53.6002 | 16.9386 | 16.9386 | 56.2731 | 236.2731 | 54.4375 | 327.7187 | 327.7187 | 94.4798 | 422.1985 | 0.49111 | 49.11% | 190.9182 | 93.7615 | 65.633 | 130.0652 | 130.0652 | 50.46% | 11.51% | 11.51% | 85% | 9.785% | 18.6817 | 6.669 | 6 | 112.0903 | 41.313 | 86.18% | 86.18%
10 | 289 | 16 | 6929 | 17 | 12.1 | 65.28 | 68.06 | 133.34 | 68.06 | 34.03 | 289 | 6929 | 1020 | 285.0411 | -8.7103 | 0.11675 | 994.284 | 16.5733 | -68.6002 | 7.8535 | 7.8535 | 68.2845 | 248.2845 | 69.1579 | 0 | 0 | 58.0928 | 58.0928 | -1.4779 | 0% | 26.2696 | 0 | 0 | 161.8709 | 161.8709 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6930 | 18 | 11.7 | 8 | 26.89 | 34.89 | 26.89 | 13.45 | 289 | 6930 | 1080 | 285.0411 | -8.7103 | 0.11675 | 1054.284 | 17.5733 | -83.6002 | -2 | 0 | 77.2244 | 257.2244 | 81.0041 | 0 | 0 | 22.9521 | 22.9521 | -5.0119 | 0% | 10.3789 | 0 | 0 | 151.3205 | 151.3205 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6931 | 19 | 11.3 | 0 | 0 | 0 | 0 | 0 | 289 | 6931 | 1140 | 285.0411 | -8.7103 | 0.11675 | 1114.284 | 18.5733 | -98.6002 | -12.215 | 0 | 77.2244 | 257.2244 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.0795 | 144.0795 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6932 | 20 | 10.4 | 0 | 0 | 0 | 0 | 0 | 289 | 6932 | 1200 | 285.0411 | -8.7103 | 0.11675 | 1174.284 | 19.5733 | -113.6002 | -22.4182 | 0 | 77.2244 | 257.2244 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.4883 | 136.4883 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6933 | 21 | 9.8 | 0 | 0 | 0 | 0 | 0 | 289 | 6933 | 1260 | 285.0411 | -8.7103 | 0.11675 | 1234.284 | 20.5733 | -128.6002 | -32.1865 | 0 | 77.2244 | 257.2244 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.924 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6934 | 22 | 9 | 0 | 0 | 0 | 0 | 0 | 289 | 6934 | 1320 | 285.0411 | -8.7103 | 0.11675 | 1294.284 | 21.5733 | -143.6002 | -40.9356 | 0 | 77.2244 | 257.2244 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5266 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6935 | 23 | 8.8 | 0 | 0 | 0 | 0 | 0 | 289 | 6935 | 1380 | 285.0411 | -8.7103 | 0.11675 | 1354.284 | 22.5733 | -158.6002 | -47.7836 | 0 | 77.2244 | 257.2244 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3452 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
10 | 289 | 16 | 6936 | 24 | 7.7 | 0 | 0 | 0 | 0 | 0 | 289 | 6936 | 1440 | 285.0411 | -8.7103 | 0.11675 | 1414.284 | 23.5733 | -173.6002 | -51.542 | 0 | 77.2244 | 257.2244 | 81.0041 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5355 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6937 | 1 | 6.7 | 0 | 0 | 0 | 0 | 0 | 290 | 6937 | 60 | 286.0274 | -9.0902 | 0.37727 | 34.284 | 0.57769 | 171.3347 | -51.5946 | 0 | 76.6618 | 103.3382 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6245 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6938 | 2 | 5.8 | 0 | 0 | 0 | 0 | 0 | 290 | 6938 | 120 | 286.0274 | -9.0902 | 0.37727 | 94.284 | 1.5777 | 156.3347 | -47.2639 | 0 | 76.6618 | 103.3382 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4814 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6939 | 3 | 5.1 | 0 | 0 | 0 | 0 | 0 | 290 | 6939 | 180 | 286.0274 | -9.0902 | 0.37727 | 154.284 | 2.5777 | 141.3347 | -40.0257 | 0 | 76.6618 | 103.3382 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0336 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6940 | 4 | 4.5 | 0 | 0 | 0 | 0 | 0 | 290 | 6940 | 240 | 286.0274 | -9.0902 | 0.37727 | 214.284 | 3.5777 | 126.3347 | -31.0504 | 0 | 76.6618 | 103.3382 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.948 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6941 | 5 | 3.8 | 0 | 0 | 0 | 0 | 0 | 290 | 6941 | 300 | 286.0274 | -9.0902 | 0.37727 | 274.284 | 4.5777 | 111.3347 | -21.1708 | 0 | 76.6618 | 103.3382 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.207 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6942 | 6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 290 | 6942 | 360 | 286.0274 | -9.0902 | 0.37727 | 334.284 | 5.5777 | 96.3347 | -10.9376 | 0 | 76.6618 | 103.3382 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.3486 | 4.3486 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6943 | 7 | 3.5 | 0 | 0 | 0 | 0 | 0 | 290 | 6943 | 420 | 286.0274 | -9.0902 | 0.37727 | 394.284 | 6.5777 | 81.3347 | -0.75893 | 0 | 76.6618 | 103.3382 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 168.1607 | 168.1607 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6944 | 8 | 4.3 | 5.64 | 9.17 | 14.81 | 9.17 | 4.59 | 290 | 6944 | 480 | 286.0274 | -9.0902 | 0.37727 | 454.284 | 7.5777 | 66.3347 | 8.9925 | 8.9925 | 66.2992 | 113.7008 | 66.9671 | 0 | 0 | 7.8271 | 7.8271 | -18.4835 | 0% | 3.5394 | 0 | 0 | 178.7251 | 178.7251 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6945 | 9 | 4.9 | 76.06 | 71.67 | 147.73 | 71.67 | 35.84 | 290 | 6945 | 540 | 286.0274 | -9.0902 | 0.37727 | 514.284 | 8.5777 | 51.3347 | 17.9001 | 17.9001 | 54.1177 | 125.8823 | 52.2857 | 151.3795 | 151.3795 | 61.1742 | 212.5537 | 0.10055 | 10.06% | 96.1168 | 9.6648 | 6.7654 | 167.4035 | 167.4035 | 4.041% | 11.84% | 11.84% | 80% | 9.472% | 9.1041 | 8.7188 | 6 | 54.6245 | 20.1329 | 32.63% | 32.63%
10 | 290 | 17 | 6946 | 10 | 5.9 | 134.31 | 106.39 | 240.7 | 106.39 | 53.2 | 290 | 6946 | 600 | 286.0274 | -9.0902 | 0.37727 | 574.284 | 9.5777 | 36.3347 | 25.4434 | 25.4434 | 40.3834 | 139.6166 | 37.7988 | 247.0263 | 247.0263 | 90.8095 | 337.8358 | 0.36851 | 36.85% | 152.7694 | 56.2973 | 39.4081 | 149.691 | 149.691 | 26.33% | 11.71% | 11.71% | 85% | 9.954% | 15.2064 | 8.4194 | 6 | 91.2386 | 33.6277 | 60.95% | 60.95%
10 | 290 | 17 | 6947 | 11 | 7.8 | 182.17 | 145.22 | 327.39 | 145.22 | 72.61 | 290 | 6947 | 660 | 286.0274 | -9.0902 | 0.37727 | 634.284 | 10.5777 | 21.3347 | 30.9813 | 30.9813 | 24.7731 | 155.2269 | 23.8754 | 323.6111 | 323.6111 | 123.953 | 447.5642 | 0.48537 | 48.54% | 202.3885 | 98.2335 | 68.7635 | 148.6832 | 148.6832 | 46.25% | 11.59% | 11.59% | 85% | 9.85% | 19.9357 | 7.8698 | 6 | 119.6142 | 44.086 | 80.45% | 80.45%
10 | 290 | 17 | 6948 | 12 | 10.1 | 162 | 222.78 | 384.78 | 222.78 | 111.39 | 290 | 6948 | 720 | 286.0274 | -9.0902 | 0.37727 | 694.284 | 11.5777 | 6.3347 | 33.8465 | 33.8465 | 7.5379 | 172.4621 | 12.5682 | 283.8898 | 283.8898 | 190.1546 | 474.0444 | 0.51457 | 51.46% | 214.3629 | 110.3041 | 77.2129 | 143.35 | 143.35 | 53.86% | 11.53% | 11.53% | 85% | 9.8% | 21.0077 | 7.2383 | 6 | 126.0461 | 46.4566 | 87.93% | 87.93%
10 | 290 | 17 | 6949 | 13 | 12.1 | 241.17 | 184.17 | 425.34 | 184.17 | 92.09 | 290 | 6949 | 780 | 286.0274 | -9.0902 | 0.37727 | 754.284 | 12.5777 | -8.6653 | 33.5992 | 33.5992 | 10.2889 | 190.2889 | 13.8806 | 423.086 | 423.086 | 157.1989 | 580.285 | 0.57555 | 57.56% | 262.4049 | 151.0283 | 105.7198 | 145.5474 | 145.5474 | 72.64% | 11.45% | 11.45% | 90% | 10.3% | 27.0348 | 6.7193 | 6 | 162.209 | 59.7851 | 111.4% | 111.4%
10 | 290 | 17 | 6950 | 14 | 14.2 | 231.53 | 190 | 421.53 | 190 | 95 | 290 | 6950 | 840 | 286.0274 | -9.0902 | 0.37727 | 814.284 | 13.5777 | -23.6653 | 30.2804 | 30.2804 | 27.3207 | 207.3207 | 25.9645 | 412.8271 | 412.8271 | 162.1751 | 575.0022 | 0.58183 | 58.18% | 260.016 | 151.2849 | 105.8994 | 147.7892 | 147.7892 | 71.66% | 11.42% | 11.42% | 90% | 10.28% | 26.7333 | 6.2045 | 6 | 160.3997 | 59.1183 | 108.5% | 108.5%
10 | 290 | 17 | 6951 | 15 | 15.2 | 189.94 | 170.83 | 360.77 | 170.83 | 85.42 | 290 | 6951 | 900 | 286.0274 | -9.0902 | 0.37727 | 874.284 | 14.5777 | -38.6653 | 24.3856 | 24.3856 | 42.6371 | 222.6371 | 40.0281 | 352.2672 | 352.2672 | 145.8125 | 498.0797 | 0.55208 | 55.21% | 225.2317 | 124.3457 | 87.042 | 143.878 | 143.878 | 60.5% | 11.43% | 11.43% | 85% | 9.717% | 21.8856 | 5.9702 | 5.9702 | 130.6617 | 48.3982 | 90.81% | 90.81%
10 | 290 | 17 | 6952 | 16 | 16 | 176.39 | 69.08 | 245.47 | 69.08 | 34.54 | 290 | 6952 | 960 | 286.0274 | -9.0902 | 0.37727 | 934.284 | 15.5777 | -53.6653 | 16.591 | 16.591 | 56.0995 | 236.0995 | 54.5582 | 358.2172 | 358.2172 | 58.9635 | 417.1806 | 0.50756 | 50.76% | 188.6491 | 95.7509 | 67.0256 | 138.2541 | 138.2541 | 48.48% | 11.44% | 11.44% | 85% | 9.721% | 18.3382 | 5.7878 | 5.7878 | 106.1377 | 40.5532 | 76.77% | 76.77%
10 | 290 | 17 | 6953 | 17 | 15.9 | 100.36 | 49.08 | 149.44 | 49.08 | 24.54 | 290 | 6953 | 1020 | 286.0274 | -9.0902 | 0.37727 | 994.284 | 16.5777 | -68.6653 | 7.5213 | 7.5213 | 68.0875 | 248.0875 | 69.2574 | 0 | 0 | 41.8924 | 41.8924 | -2.1534 | 0% | 18.9437 | 0 | 0 | 172.7639 | 172.7639 | 0% | 11.52% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6954 | 18 | 15 | 8 | 19.5 | 27.5 | 19.5 | 9.75 | 290 | 6954 | 1080 | 286.0274 | -9.0902 | 0.37727 | 1054.284 | 17.5777 | -83.6653 | -2.322 | 0 | 76.6618 | 256.6618 | 80.6115 | 0 | 0 | 16.6443 | 16.6443 | -6.762 | 0% | 7.5265 | 0 | 0 | 159.0008 | 159.0008 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6955 | 19 | 13 | 0 | 0 | 0 | 0 | 0 | 290 | 6955 | 1140 | 286.0274 | -9.0902 | 0.37727 | 1114.284 | 18.5777 | -98.6653 | -12.5334 | 0 | 76.6618 | 256.6618 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.8976 | 148.8976 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6956 | 20 | 10.5 | 0 | 0 | 0 | 0 | 0 | 290 | 6956 | 1200 | 286.0274 | -9.0902 | 0.37727 | 1174.284 | 19.5777 | -113.6653 | -22.7406 | 0 | 76.6618 | 256.6618 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.9403 | 137.9403 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6957 | 21 | 8.7 | 0 | 0 | 0 | 0 | 0 | 290 | 6957 | 1260 | 286.0274 | -9.0902 | 0.37727 | 1234.284 | 20.5777 | -128.6653 | -32.5213 | 0 | 76.6618 | 256.6618 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.532 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6958 | 22 | 7.5 | 0 | 0 | 0 | 0 | 0 | 290 | 6958 | 1320 | 286.0274 | -9.0902 | 0.37727 | 1294.284 | 21.5777 | -143.6653 | -41.2903 | 0 | 76.6618 | 256.6618 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9491 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6959 | 23 | 7.2 | 0 | 0 | 0 | 0 | 0 | 290 | 6959 | 1380 | 286.0274 | -9.0902 | 0.37727 | 1354.284 | 22.5777 | -158.6653 | -48.1602 | 0 | 76.6618 | 256.6618 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8917 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
10 | 290 | 17 | 6960 | 24 | 6.8 | 0 | 0 | 0 | 0 | 0 | 290 | 6960 | 1440 | 286.0274 | -9.0902 | 0.37727 | 1414.284 | 23.5777 | -173.6653 | -51.9269 | 0 | 76.6618 | 256.6618 | 80.6115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9867 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6961 | 1 | 6.8 | 0 | 0 | 0 | 0 | 0 | 291 | 6961 | 60 | 287.0137 | -9.4678 | 0.63118 | 34.284 | 0.58192 | 171.2712 | -51.9563 | 0 | 76.1019 | 103.8981 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1774 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6962 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 291 | 6962 | 120 | 287.0137 | -9.4678 | 0.63118 | 94.284 | 1.5819 | 156.2712 | -47.5833 | 0 | 76.1019 | 103.8981 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.364 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6963 | 3 | 6.7 | 0 | 0 | 0 | 0 | 0 | 291 | 6963 | 180 | 287.0137 | -9.4678 | 0.63118 | 154.284 | 2.5819 | 141.2712 | -40.3033 | 0 | 76.1019 | 103.8981 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3125 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6964 | 4 | 6.3 | 0 | 0 | 0 | 0 | 0 | 291 | 6964 | 240 | 287.0137 | -9.4678 | 0.63118 | 214.284 | 3.5819 | 126.2712 | -31.2985 | 0 | 76.1019 | 103.8981 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9221 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6965 | 5 | 6.4 | 0 | 0 | 0 | 0 | 0 | 291 | 6965 | 300 | 287.0137 | -9.4678 | 0.63118 | 274.284 | 4.5819 | 111.2712 | -21.403 | 0 | 76.1019 | 103.8981 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.6733 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6966 | 6 | 7.1 | 0 | 0 | 0 | 0 | 0 | 291 | 6966 | 360 | 287.0137 | -9.4678 | 0.63118 | 334.284 | 5.5819 | 96.2712 | -11.1661 | 0 | 76.1019 | 103.8981 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.6219 | 7.6219 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6967 | 7 | 7.8 | 0 | 0 | 0 | 0 | 0 | 291 | 6967 | 420 | 287.0137 | -9.4678 | 0.63118 | 394.284 | 6.5819 | 81.2712 | -0.9944 | 0 | 76.1019 | 103.8981 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 172.1182 | 172.1182 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6968 | 8 | 7.1 | 7.17 | 11.17 | 18.34 | 11.17 | 5.59 | 291 | 6968 | 480 | 287.0137 | -9.4678 | 0.63118 | 454.284 | 7.5819 | 66.2712 | 8.7405 | 8.7405 | 66.0077 | 113.9923 | 66.9439 | 0 | 0 | 9.5342 | 9.5342 | -14.3274 | 0% | 4.3114 | 0 | 0 | 180.4529 | 180.4529 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6969 | 9 | 7.9 | 79.22 | 66.25 | 145.47 | 66.25 | 33.13 | 291 | 6969 | 540 | 287.0137 | -9.4678 | 0.63118 | 514.284 | 8.5819 | 51.2712 | 17.6228 | 17.6228 | 53.8407 | 126.1593 | 52.2866 | 160.0662 | 160.0662 | 56.5479 | 216.6141 | 0.14675 | 14.67% | 97.9529 | 14.3742 | 10.0619 | 169.1854 | 169.1854 | 5.947% | 11.74% | 11.74% | 80% | 9.392% | 9.1999 | 7.8416 | 6 | 55.1996 | 20.3448 | 32.63% | 32.63%
10 | 291 | 18 | 6970 | 10 | 8.2 | 147.36 | 112.44 | 259.8 | 112.44 | 56.22 | 291 | 6970 | 600 | 287.0137 | -9.4678 | 0.63118 | 574.284 | 9.5819 | 36.2712 | 25.134 | 25.134 | 40.1342 | 139.8658 | 37.8372 | 274.0012 | 274.0012 | 95.9735 | 369.9747 | 0.4211 | 42.11% | 167.3026 | 70.4516 | 49.3161 | 152.0117 | 152.0117 | 32.44% | 11.63% | 11.63% | 85% | 9.886% | 16.5402 | 7.7573 | 6 | 99.2414 | 36.5773 | 65.29% | 65.29%
10 | 291 | 18 | 6971 | 11 | 9 | 220.61 | 137.28 | 357.89 | 137.28 | 68.64 | 291 | 6971 | 660 | 287.0137 | -9.4678 | 0.63118 | 634.284 | 10.5819 | 21.2712 | 30.638 | 30.638 | 24.5759 | 155.4241 | 23.9876 | 395.5098 | 395.5098 | 117.1758 | 512.6856 | 0.53136 | 53.14% | 231.8364 | 123.1883 | 86.2318 | 150.33 | 150.33 | 57.36% | 11.53% | 11.53% | 90% | 10.37% | 24.049 | 7.5357 | 6 | 144.2937 | 53.1821 | 95.98% | 95.98%
10 | 291 | 18 | 6972 | 12 | 9.8 | 286.11 | 123.61 | 409.72 | 123.61 | 61.81 | 291 | 6972 | 720 | 287.0137 | -9.4678 | 0.63118 | 694.284 | 11.5819 | 6.2712 | 33.4761 | 33.4761 | 7.4219 | 172.5781 | 12.8643 | 505.6815 | 505.6815 | 105.5077 | 611.1893 | 0.57837 | 57.84% | 276.3798 | 159.8488 | 111.8942 | 142.5961 | 142.5961 | 78.47% | 11.46% | 11.46% | 90% | 10.31% | 28.5006 | 7.3186 | 6 | 171.0039 | 63.0266 | 119.9% | 119.9%
10 | 291 | 18 | 6973 | 13 | 10.1 | 325.14 | 129.58 | 454.72 | 129.58 | 64.79 | 291 | 6973 | 780 | 287.0137 | -9.4678 | 0.63118 | 754.284 | 12.5819 | -8.7288 | 33.2168 | 33.2168 | 10.3072 | 190.3072 | 14.2151 | 575.3558 | 575.3558 | 110.6034 | 685.9592 | 0.60398 | 60.4% | 310.1908 | 187.3497 | 131.1448 | 141.9639 | 141.9639 | 92.38% | 11.41% | 11.41% | 90% | 10.27% | 31.8649 | 7.2383 | 6 | 191.1895 | 70.4664 | 134.7% | 134.7%
10 | 291 | 18 | 6974 | 14 | 10.8 | 315.42 | 121.11 | 436.53 | 121.11 | 60.56 | 291 | 6974 | 840 | 287.0137 | -9.4678 | 0.63118 | 814.284 | 13.5819 | -23.7288 | 29.9025 | 29.9025 | 27.2505 | 207.2505 | 26.1749 | 567.8232 | 567.8232 | 103.3739 | 671.197 | 0.60201 | 60.2% | 303.5153 | 182.7198 | 127.9039 | 141.231 | 141.231 | 90.56% | 11.42% | 11.42% | 90% | 10.28% | 31.1876 | 7.0535 | 6 | 187.1255 | 68.9686 | 132.5% | 132.5%
10 | 291 | 18 | 6975 | 15 | 11.9 | 264.22 | 129.67 | 393.89 | 129.67 | 64.84 | 291 | 6975 | 900 | 287.0137 | -9.4678 | 0.63118 | 874.284 | 14.5819 | -38.7288 | 24.0228 | 24.0228 | 42.5034 | 222.5034 | 40.1805 | 495.8681 | 495.8681 | 110.6803 | 606.5484 | 0.58468 | 58.47% | 274.2812 | 160.3681 | 112.2577 | 138.1516 | 138.1516 | 81.26% | 11.44% | 11.44% | 90% | 10.29% | 28.2355 | 6.77 | 6 | 169.413 | 62.4403 | 122.6% | 122.6%
10 | 291 | 18 | 6976 | 16 | 12.6 | 163.11 | 100.78 | 263.89 | 100.78 | 50.39 | 291 | 6976 | 960 | 287.0137 | -9.4678 | 0.63118 | 934.284 | 15.5819 | -53.7288 | 16.2461 | 16.2461 | 55.9265 | 235.9265 | 54.6784 | 337.0862 | 337.0862 | 86.0211 | 423.1073 | 0.49341 | 49.34% | 191.3291 | 94.4042 | 66.0829 | 131.317 | 131.317 | 50.32% | 11.51% | 11.51% | 85% | 9.78% | 18.7112 | 6.5939 | 6 | 112.2672 | 41.3781 | 85.49% | 85.49%
10 | 291 | 18 | 6977 | 17 | 12.5 | 84.44 | 64.78 | 149.22 | 64.78 | 32.39 | 291 | 6977 | 1020 | 287.0137 | -9.4678 | 0.63118 | 994.284 | 16.5819 | -68.7288 | 7.1919 | 7.1919 | 67.8909 | 247.8909 | 69.3557 | 0 | 0 | 55.2932 | 55.2932 | -1.5768 | 0% | 25.0036 | 0 | 0 | 164.5586 | 164.5586 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6978 | 18 | 12.3 | 10.28 | 22.92 | 33.2 | 22.92 | 11.46 | 291 | 6978 | 1080 | 287.0137 | -9.4678 | 0.63118 | 1054.284 | 17.5819 | -83.7288 | -2.6411 | 0 | 76.1019 | 256.1019 | 80.2212 | 0 | 0 | 19.5634 | 19.5634 | -5.9485 | 0% | 8.8466 | 0 | 0 | 152.91 | 152.91 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6979 | 19 | 11.8 | 0 | 0 | 0 | 0 | 0 | 291 | 6979 | 1140 | 287.0137 | -9.4678 | 0.63118 | 1114.284 | 18.5819 | -98.7288 | -12.8488 | 0 | 76.1019 | 256.1019 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.2075 | 145.2075 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6980 | 20 | 10.7 | 0 | 0 | 0 | 0 | 0 | 291 | 6980 | 1200 | 287.0137 | -9.4678 | 0.63118 | 1174.284 | 19.5819 | -113.7288 | -23.0599 | 0 | 76.1019 | 256.1019 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.2014 | 137.2014 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6981 | 21 | 9.6 | 0 | 0 | 0 | 0 | 0 | 291 | 6981 | 1260 | 287.0137 | -9.4678 | 0.63118 | 1234.284 | 20.5819 | -128.7288 | -32.8528 | 0 | 76.1019 | 256.1019 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0102 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6982 | 22 | 8.7 | 0 | 0 | 0 | 0 | 0 | 291 | 6982 | 1320 | 287.0137 | -9.4678 | 0.63118 | 1294.284 | 21.5819 | -143.7288 | -41.6418 | 0 | 76.1019 | 256.1019 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8079 | 0 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6983 | 23 | 7.6 | 0 | 0 | 0 | 0 | 0 | 291 | 6983 | 1380 | 287.0137 | -9.4678 | 0.63118 | 1354.284 | 22.5819 | -158.7288 | -48.5338 | 0 | 76.1019 | 256.1019 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9756 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
10 | 291 | 18 | 6984 | 24 | 7.2 | 0 | 0 | 0 | 0 | 0 | 291 | 6984 | 1440 | 287.0137 | -9.4678 | 0.63118 | 1414.284 | 23.5819 | -173.7288 | -52.3093 | 0 | 76.1019 | 256.1019 | 80.2212 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0765 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6985 | 1 | 6.9 | 0 | 0 | 0 | 0 | 0 | 292 | 6985 | 60 | 288 | -9.8429 | 0.87819 | 34.284 | 0.58604 | 171.2095 | -52.3156 | 0 | 75.545 | 104.455 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0738 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6986 | 2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 292 | 6986 | 120 | 288 | -9.8429 | 0.87819 | 94.284 | 1.586 | 156.2095 | -47.9004 | 0 | 75.545 | 104.455 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9015 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6987 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 292 | 6987 | 180 | 288 | -9.8429 | 0.87819 | 154.284 | 2.586 | 141.2095 | -40.5789 | 0 | 75.545 | 104.455 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4911 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6988 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 292 | 6988 | 240 | 288 | -9.8429 | 0.87819 | 214.284 | 3.586 | 126.2095 | -31.545 | 0 | 75.545 | 104.455 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4911 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6989 | 5 | 6.4 | 0 | 0 | 0 | 0 | 0 | 292 | 6989 | 300 | 288 | -9.8429 | 0.87819 | 274.284 | 4.586 | 111.2095 | -21.6341 | 0 | 75.545 | 104.455 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.0228 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6990 | 6 | 6.6 | 0 | 0 | 0 | 0 | 0 | 292 | 6990 | 360 | 288 | -9.8429 | 0.87819 | 334.284 | 5.586 | 96.2095 | -11.3939 | 0 | 75.545 | 104.455 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 4.4961 | 4.4961 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6991 | 7 | 6.9 | 0 | 0 | 0 | 0 | 0 | 292 | 6991 | 420 | 288 | -9.8429 | 0.87819 | 394.284 | 6.586 | 81.2095 | -1.2293 | 0 | 75.545 | 104.455 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 166.9377 | 166.9377 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6992 | 8 | 7.3 | 6.61 | 10.78 | 17.39 | 10.78 | 5.39 | 292 | 6992 | 480 | 288 | -9.8429 | 0.87819 | 454.284 | 7.586 | 66.2095 | 8.489 | 8.489 | 65.7196 | 114.2804 | 66.9234 | 0 | 0 | 9.2013 | 9.2013 | -14.8232 | 0% | 4.1608 | 0 | 0 | 175.7976 | 175.7976 | 0% | 11.9% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 6993 | 9 | 7.7 | 75.14 | 54.5 | 129.64 | 54.5 | 27.25 | 292 | 6993 | 540 | 288 | -9.8429 | 0.87819 | 514.284 | 8.586 | 51.2095 | 17.3461 | 17.3461 | 53.5676 | 126.4324 | 52.2909 | 154.1532 | 154.1532 | 46.5187 | 200.6718 | 0.092174 | 9.217% | 90.7438 | 8.3642 | 5.8549 | 162.868 | 162.868 | 3.595% | 11.76% | 11.76% | 80% | 9.406% | 8.5353 | 7.8981 | 6 | 51.2119 | 18.8751 | 31.44% | 31.44%
10 | 292 | 19 | 6994 | 10 | 8.8 | 131.53 | 73.47 | 205 | 73.47 | 36.74 | 292 | 6994 | 600 | 288 | -9.8429 | 0.87819 | 574.284 | 9.586 | 36.2095 | 24.8256 | 24.8256 | 39.8893 | 140.1107 | 37.8799 | 247.2657 | 247.2657 | 62.7106 | 309.9763 | 0.35155 | 35.15% | 140.1713 | 49.277 | 34.4939 | 144.4302 | 144.4302 | 23.88% | 11.65% | 11.65% | 85% | 9.906% | 13.8851 | 7.5907 | 6 | 83.3103 | 30.7056 | 57.68% | 57.68%
10 | 292 | 19 | 6995 | 11 | 9 | 178 | 80.78 | 258.78 | 80.78 | 40.39 | 292 | 6995 | 660 | 288 | -9.8429 | 0.87819 | 634.284 | 10.586 | 21.2095 | 30.2963 | 30.2963 | 24.383 | 155.617 | 24.1055 | 322.0743 | 322.0743 | 68.95 | 391.0244 | 0.44653 | 44.65% | 176.8212 | 78.9561 | 55.2693 | 139.9911 | 139.9911 | 39.48% | 11.6% | 11.6% | 85% | 9.86% | 17.4337 | 7.5357 | 6 | 104.6023 | 38.5531 | 74.72% | 74.72%
10 | 292 | 19 | 6996 | 12 | 10.2 | 216.06 | 70.89 | 286.95 | 70.89 | 35.45 | 292 | 6996 | 720 | 288 | -9.8429 | 0.87819 | 694.284 | 11.586 | 6.2095 | 33.1079 | 33.1079 | 7.3094 | 172.6906 | 13.1635 | 385.1627 | 385.1627 | 60.5084 | 445.6711 | 0.49666 | 49.67% | 201.5325 | 100.0939 | 70.0657 | 132.615 | 132.615 | 52.83% | 11.54% | 11.54% | 85% | 9.812% | 19.7734 | 7.2117 | 6 | 118.6406 | 43.7272 | 89.46% | 89.46%
10 | 292 | 19 | 6997 | 13 | 11.3 | 234.31 | 90 | 324.31 | 90 | 45 | 292 | 6997 | 780 | 288 | -9.8429 | 0.87819 | 754.284 | 12.586 | -8.7905 | 32.837 | 32.837 | 10.3236 | 190.3236 | 14.5488 | 418.2503 | 418.2503 | 76.8198 | 495.0701 | 0.5325 | 53.25% | 223.8707 | 119.2103 | 83.4472 | 133.2136 | 133.2136 | 62.64% | 11.5% | 11.5% | 85% | 9.773% | 21.8794 | 6.9236 | 6 | 131.2763 | 48.3843 | 98.55% | 98.55%
10 | 292 | 19 | 6998 | 14 | 12.8 | 226.06 | 62.5 | 288.56 | 62.5 | 31.25 | 292 | 6998 | 840 | 288 | -9.8429 | 0.87819 | 814.284 | 13.586 | -23.7905 | 29.5275 | 29.5275 | 27.1798 | 207.1798 | 26.3861 | 410.9011 | 410.9011 | 53.3471 | 464.2482 | 0.52193 | 52.19% | 209.933 | 109.5696 | 76.6987 | 132.824 | 132.824 | 57.74% | 11.48% | 11.48% | 85% | 9.762% | 20.4941 | 6.5443 | 6 | 122.9647 | 45.3209 | 92.58% | 92.58%
10 | 292 | 19 | 6999 | 15 | 13.5 | 192.36 | 65.06 | 257.42 | 65.06 | 32.53 | 292 | 6999 | 900 | 288 | -9.8429 | 0.87819 | 874.284 | 14.586 | -38.7905 | 23.663 | 23.663 | 42.3699 | 222.3699 | 40.3331 | 365.3492 | 365.3492 | 55.5322 | 420.8814 | 0.49668 | 49.67% | 190.3226 | 94.5286 | 66.17 | 130.0883 | 130.0883 | 50.87% | 11.49% | 11.49% | 85% | 9.764% | 18.5839 | 6.3727 | 6 | 111.5032 | 41.0966 | 85.71% | 85.71%
10 | 292 | 19 | 7000 | 16 | 14.4 | 138.06 | 54.22 | 192.28 | 54.22 | 27.11 | 292 | 7000 | 960 | 288 | -9.8429 | 0.87819 | 934.284 | 15.586 | -53.7905 | 15.9042 | 15.9042 | 55.7539 | 235.7539 | 54.7981 | 290.4287 | 290.4287 | 46.2797 | 336.7083 | 0.42595 | 42.59% | 152.2595 | 64.8547 | 45.3983 | 126.8905 | 126.8905 | 35.78% | 11.49% | 11.49% | 85% | 9.77% | 14.8765 | 6.1571 | 6 | 89.259 | 32.8981 | 70.34% | 70.34%
10 | 292 | 19 | 7001 | 17 | 14.6 | 68.33 | 29.86 | 98.19 | 29.86 | 14.93 | 292 | 7001 | 1020 | 288 | -9.8429 | 0.87819 | 994.284 | 16.586 | -68.7905 | 6.8655 | 6.8655 | 67.6948 | 247.6948 | 69.4529 | 0 | 0 | 25.4871 | 25.4871 | -4.1726 | 0% | 11.5253 | 0 | 0 | 162.0821 | 162.0821 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1099 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 7002 | 18 | 13.6 | 6.33 | 10.78 | 17.11 | 10.78 | 5.39 | 292 | 7002 | 1080 | 288 | -9.8429 | 0.87819 | 1054.284 | 17.586 | -83.7905 | -2.957 | 0 | 75.545 | 255.545 | 79.8336 | 0 | 0 | 9.2013 | 9.2013 | -13.2286 | 0% | 4.1608 | 0 | 0 | 151.5913 | 151.5913 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 7003 | 19 | 12.1 | 0 | 0 | 0 | 0 | 0 | 292 | 7003 | 1140 | 288 | -9.8429 | 0.87819 | 1114.284 | 18.586 | -98.7905 | -13.1609 | 0 | 75.545 | 255.545 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.2361 | 144.2361 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 7004 | 20 | 11.5 | 0 | 0 | 0 | 0 | 0 | 292 | 7004 | 1200 | 288 | -9.8429 | 0.87819 | 1174.284 | 19.586 | -113.7905 | -23.3757 | 0 | 75.545 | 255.545 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.974 | 137.974 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 7005 | 21 | 10.8 | 0 | 0 | 0 | 0 | 0 | 292 | 7005 | 1260 | 288 | -9.8429 | 0.87819 | 1234.284 | 20.586 | -128.7905 | -33.1807 | 0 | 75.545 | 255.545 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3709 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 7006 | 22 | 10 | 0 | 0 | 0 | 0 | 0 | 292 | 7006 | 1320 | 288 | -9.8429 | 0.87819 | 1294.284 | 21.586 | -143.7905 | -41.9897 | 0 | 75.545 | 255.545 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.781 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 7007 | 23 | 9.7 | 0 | 0 | 0 | 0 | 0 | 292 | 7007 | 1380 | 288 | -9.8429 | 0.87819 | 1354.284 | 22.586 | -158.7905 | -48.9042 | 0 | 75.545 | 255.545 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.761 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
10 | 292 | 19 | 7008 | 24 | 9.1 | 0 | 0 | 0 | 0 | 0 | 292 | 7008 | 1440 | 288 | -9.8429 | 0.87819 | 1414.284 | 23.586 | -173.7905 | -52.689 | 0 | 75.545 | 255.545 | 79.8336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1982 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7009 | 1 | 9.8 | 0 | 0 | 0 | 0 | 0 | 293 | 7009 | 60 | 288.9863 | -10.2153 | 1.118 | 34.284 | 0.59003 | 171.1495 | -52.6723 | 0 | 74.9912 | 105.0088 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5507 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7010 | 2 | 9.3 | 0 | 0 | 0 | 0 | 0 | 293 | 7010 | 120 | 288.9863 | -10.2153 | 1.118 | 94.284 | 1.59 | 156.1495 | -48.215 | 0 | 74.9912 | 105.0088 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8733 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7011 | 3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 293 | 7011 | 180 | 288.9863 | -10.2153 | 1.118 | 154.284 | 2.59 | 141.1495 | -40.8525 | 0 | 74.9912 | 105.0088 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5196 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7012 | 4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 293 | 7012 | 240 | 288.9863 | -10.2153 | 1.118 | 214.284 | 3.59 | 126.1495 | -31.7899 | 0 | 74.9912 | 105.0088 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9768 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7013 | 5 | 9.6 | 0 | 0 | 0 | 0 | 0 | 293 | 7013 | 300 | 288.9863 | -10.2153 | 1.118 | 274.284 | 4.59 | 111.1495 | -21.864 | 0 | 74.9912 | 105.0088 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.3097 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7014 | 6 | 10.3 | 0 | 0 | 0 | 0 | 0 | 293 | 7014 | 360 | 288.9863 | -10.2153 | 1.118 | 334.284 | 5.59 | 96.1495 | -11.6207 | 0 | 74.9912 | 105.0088 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 7.2587 | 7.2587 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7015 | 7 | 10.7 | 0 | 0 | 0 | 0 | 0 | 293 | 7015 | 420 | 288.9863 | -10.2153 | 1.118 | 394.284 | 6.59 | 81.1495 | -1.4635 | 0 | 74.9912 | 105.0088 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 168.0132 | 168.0132 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7016 | 8 | 11.6 | 3.11 | 8.61 | 11.72 | 8.61 | 4.31 | 293 | 7016 | 480 | 288.9863 | -10.2153 | 1.118 | 454.284 | 7.59 | 66.1495 | 8.2381 | 8.2381 | 65.435 | 114.565 | 66.9056 | 0 | 0 | 7.3491 | 7.3491 | -17.3913 | 0% | 3.3233 | 0 | 0 | 176.4693 | 176.4693 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7017 | 9 | 12.5 | 56.61 | 39.5 | 96.11 | 39.5 | 19.75 | 293 | 7017 | 540 | 288.9863 | -10.2153 | 1.118 | 514.284 | 8.59 | 51.1495 | 17.0701 | 17.0701 | 53.2986 | 126.7014 | 52.2986 | 117.938 | 117.938 | 33.7154 | 151.6534 | -0.064044 | 0% | 68.5777 | 0 | 0 | 162.9133 | 162.9133 | 0% | 11.62% | 11.62% | 80% | 9.296% | 6.3747 | 6.6189 | 6 | 38.248 | 14.097 | 23.48% | 23.48%
10 | 293 | 20 | 7018 | 10 | 13.1 | 130.83 | 72.44 | 203.27 | 72.44 | 36.22 | 293 | 7018 | 600 | 288.9863 | -10.2153 | 1.118 | 574.284 | 9.59 | 36.1495 | 24.5183 | 24.5183 | 39.6488 | 140.3512 | 37.9269 | 248.6796 | 248.6796 | 61.8314 | 310.511 | 0.38449 | 38.45% | 140.4131 | 53.987 | 37.7909 | 146.0774 | 146.0774 | 25.87% | 11.54% | 11.54% | 85% | 9.807% | 13.7704 | 6.4703 | 6 | 82.6227 | 30.4521 | 56.56% | 56.56%
10 | 293 | 20 | 7019 | 11 | 13.7 | 169.78 | 89.44 | 259.22 | 89.44 | 44.72 | 293 | 7019 | 660 | 288.9863 | -10.2153 | 1.118 | 634.284 | 10.59 | 21.1495 | 29.9563 | 29.9563 | 24.1944 | 155.8056 | 24.2288 | 310.059 | 310.059 | 76.3418 | 386.4008 | 0.47044 | 47.04% | 174.7304 | 82.1993 | 57.5395 | 143.111 | 143.111 | 40.21% | 11.5% | 11.5% | 85% | 9.771% | 17.0729 | 6.3243 | 6 | 102.4376 | 37.7553 | 71.58% | 71.58%
10 | 293 | 20 | 7020 | 12 | 14.7 | 213.39 | 106.17 | 319.56 | 106.17 | 53.09 | 293 | 7020 | 720 | 288.9863 | -10.2153 | 1.118 | 694.284 | 11.59 | 6.1495 | 32.7421 | 32.7421 | 7.2004 | 172.7996 | 13.4652 | 383.6941 | 383.6941 | 90.6218 | 474.3159 | 0.53707 | 53.71% | 214.4856 | 115.193 | 80.6351 | 138.0343 | 138.0343 | 58.42% | 11.45% | 11.45% | 85% | 9.73% | 20.8692 | 6.0865 | 6 | 125.2154 | 46.1504 | 90.71% | 90.71%
10 | 293 | 20 | 7021 | 13 | 15.5 | 213 | 112.72 | 325.72 | 112.72 | 56.36 | 293 | 7021 | 780 | 288.9863 | -10.2153 | 1.118 | 754.284 | 12.59 | -8.8505 | 32.4601 | 32.4601 | 10.338 | 190.338 | 14.8814 | 383.55 | 383.55 | 96.2125 | 479.7626 | 0.54388 | 54.39% | 216.9486 | 117.9932 | 82.5952 | 136.8071 | 136.8071 | 60.37% | 11.43% | 11.43% | 85% | 9.717% | 21.08 | 5.9013 | 5.9013 | 124.3987 | 46.6165 | 90.93% | 90.93%
10 | 293 | 20 | 7022 | 14 | 14.1 | 173.28 | 125.5 | 298.78 | 125.5 | 62.75 | 293 | 7022 | 840 | 288.9863 | -10.2153 | 1.118 | 814.284 | 13.59 | -23.8505 | 29.1555 | 29.1555 | 27.1084 | 207.1084 | 26.598 | 318.0366 | 318.0366 | 107.121 | 425.1575 | 0.50299 | 50.3% | 192.2562 | 96.703 | 67.6921 | 132.3667 | 132.3667 | 51.14% | 11.47% | 11.47% | 85% | 9.753% | 18.75 | 6.2283 | 6 | 112.4998 | 41.4639 | 84.99% | 84.99%
10 | 293 | 20 | 7023 | 15 | 12.5 | 128.28 | 127.92 | 256.2 | 127.92 | 63.96 | 293 | 7023 | 900 | 288.9863 | -10.2153 | 1.118 | 874.284 | 14.59 | -38.8505 | 23.3062 | 23.3062 | 42.2367 | 222.2367 | 40.4856 | 246.5996 | 246.5996 | 109.1865 | 355.7861 | 0.434 | 43.4% | 160.8865 | 69.8243 | 48.877 | 125.2809 | 125.2809 | 39.01% | 11.54% | 11.54% | 85% | 9.805% | 15.7748 | 6.6189 | 6 | 94.6491 | 34.8847 | 75.55% | 75.55%
10 | 293 | 20 | 7024 | 16 | 10.8 | 62.56 | 98.67 | 161.23 | 98.67 | 49.34 | 293 | 7024 | 960 | 288.9863 | -10.2153 | 1.118 | 934.284 | 15.59 | -53.8505 | 15.5653 | 15.5653 | 55.5819 | 235.5819 | 54.9171 | 133.9995 | 133.9995 | 84.2201 | 218.2197 | 0.18273 | 18.27% | 98.6789 | 18.0314 | 12.622 | 116.2014 | 116.2014 | 10.86% | 11.65% | 11.65% | 80% | 9.317% | 9.194 | 7.0535 | 6 | 55.1641 | 20.3318 | 47.47% | 47.47%
10 | 293 | 20 | 7025 | 17 | 10.4 | 42.44 | 52.64 | 95.08 | 52.64 | 26.32 | 293 | 7025 | 1020 | 288.9863 | -10.2153 | 1.118 | 994.284 | 16.59 | -68.8505 | 6.5423 | 6.5423 | 67.4992 | 247.4992 | 69.5488 | 0 | 0 | 44.9311 | 44.9311 | -2.2341 | 0% | 20.3178 | 0 | 0 | 152.0898 | 152.0898 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.1587 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7026 | 18 | 10.1 | 3.94 | 15.78 | 19.72 | 15.78 | 7.89 | 293 | 7026 | 1080 | 288.9863 | -10.2153 | 1.118 | 1054.284 | 17.59 | -83.8505 | -3.2697 | 0 | 74.9912 | 254.9912 | 79.4486 | 0 | 0 | 13.4691 | 13.4691 | -9.3826 | 0% | 6.0907 | 0 | 0 | 143.8982 | 143.8982 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2383 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7027 | 19 | 8.5 | 0 | 0 | 0 | 0 | 0 | 293 | 7027 | 1140 | 288.9863 | -10.2153 | 1.118 | 1114.284 | 18.59 | -98.8505 | -13.4696 | 0 | 74.9912 | 254.9912 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.0158 | 137.0158 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7028 | 20 | 8.4 | 0 | 0 | 0 | 0 | 0 | 293 | 7028 | 1200 | 288.9863 | -10.2153 | 1.118 | 1174.284 | 19.59 | -113.8505 | -23.688 | 0 | 74.9912 | 254.9912 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.1638 | 132.1638 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7029 | 21 | 7.4 | 0 | 0 | 0 | 0 | 0 | 293 | 7029 | 1260 | 288.9863 | -10.2153 | 1.118 | 1234.284 | 20.59 | -128.8505 | -33.505 | 0 | 74.9912 | 254.9912 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.478 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7030 | 22 | 6.7 | 0 | 0 | 0 | 0 | 0 | 293 | 7030 | 1320 | 288.9863 | -10.2153 | 1.118 | 1294.284 | 21.59 | -143.8505 | -42.3341 | 0 | 74.9912 | 254.9912 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5931 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7031 | 23 | 6.5 | 0 | 0 | 0 | 0 | 0 | 293 | 7031 | 1380 | 288.9863 | -10.2153 | 1.118 | 1354.284 | 22.59 | -158.8505 | -49.2714 | 0 | 74.9912 | 254.9912 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4585 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
10 | 293 | 20 | 7032 | 24 | 6.3 | 0 | 0 | 0 | 0 | 0 | 293 | 7032 | 1440 | 288.9863 | -10.2153 | 1.118 | 1414.284 | 23.59 | -173.8505 | -53.0659 | 0 | 74.9912 | 254.9912 | 79.4486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.324 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7033 | 1 | 6.3 | 0 | 0 | 0 | 0 | 0 | 294 | 7033 | 60 | 289.9726 | -10.585 | 1.3503 | 34.284 | 0.59391 | 171.0914 | -53.0263 | 0 | 74.4407 | 105.5593 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5313 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7034 | 2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 294 | 7034 | 120 | 289.9726 | -10.585 | 1.3503 | 94.284 | 1.5939 | 156.0914 | -48.5272 | 0 | 74.4407 | 105.5593 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.3026 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7035 | 3 | 5.7 | 0 | 0 | 0 | 0 | 0 | 294 | 7035 | 180 | 289.9726 | -10.585 | 1.3503 | 154.284 | 2.5939 | 141.0914 | -41.1238 | 0 | 74.4407 | 105.5593 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9883 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7036 | 4 | 5.7 | 0 | 0 | 0 | 0 | 0 | 294 | 7036 | 240 | 289.9726 | -10.585 | 1.3503 | 214.284 | 3.5939 | 126.0914 | -32.0331 | 0 | 74.4407 | 105.5593 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9883 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7037 | 5 | 5.8 | 0 | 0 | 0 | 0 | 0 | 294 | 7037 | 300 | 289.9726 | -10.585 | 1.3503 | 274.284 | 4.5939 | 111.0914 | -22.0927 | 0 | 74.4407 | 105.5593 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.2177 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7038 | 6 | 4.9 | 0 | 0 | 0 | 0 | 0 | 294 | 7038 | 360 | 289.9726 | -10.585 | 1.3503 | 334.284 | 5.5939 | 96.0914 | -11.8467 | 0 | 74.4407 | 105.5593 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.6534 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7039 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 294 | 7039 | 420 | 289.9726 | -10.585 | 1.3503 | 394.284 | 6.5939 | 81.0914 | -1.6969 | 0 | 74.4407 | 105.5593 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.7934 | 147.7934 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7040 | 8 | 4.8 | 0.83 | 6.25 | 7.08 | 6.25 | 3.13 | 294 | 7040 | 480 | 289.9726 | -10.585 | 1.3503 | 454.284 | 7.5939 | 66.0914 | 7.9879 | 7.9879 | 65.1541 | 114.8459 | 66.8904 | 0 | 0 | 5.3347 | 5.3347 | -27.2689 | 0% | 2.4124 | 0 | 0 | 152.252 | 152.252 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7041 | 9 | 5.4 | 25.97 | 43.89 | 69.86 | 43.89 | 21.95 | 294 | 7041 | 540 | 289.9726 | -10.585 | 1.3503 | 514.284 | 8.5939 | 51.0914 | 16.7949 | 16.7949 | 53.0336 | 126.9664 | 52.3096 | 54.951 | 54.951 | 37.4625 | 92.4134 | -0.80096 | 0% | 41.7894 | 0 | 0 | 136.6456 | 136.6456 | 0% | 11.92% | 11.92% | 80% | 9.536% | 3.9851 | 8.5682 | 6 | 23.9106 | 8.8127 | 17.5% | 17.5%
10 | 294 | 21 | 7042 | 10 | 6.1 | 49.31 | 77.5 | 126.81 | 77.5 | 38.75 | 294 | 7042 | 600 | 289.9726 | -10.585 | 1.3503 | 574.284 | 9.5939 | 36.0914 | 24.2122 | 24.2122 | 39.4127 | 140.5873 | 37.9782 | 94.7738 | 94.7738 | 66.1504 | 160.9242 | -0.10727 | 0% | 72.7699 | 0 | 0 | 140.1985 | 140.1985 | 0% | 11.84% | 11.84% | 80% | 9.472% | 6.8931 | 8.3603 | 6 | 41.3586 | 15.2435 | 29.5% | 29.5%
10 | 294 | 21 | 7043 | 11 | 7.1 | 82.17 | 125.89 | 208.06 | 125.89 | 62.95 | 294 | 7043 | 660 | 289.9726 | -10.585 | 1.3503 | 634.284 | 10.5939 | 21.0914 | 29.6181 | 29.6181 | 24.0102 | 155.9898 | 24.3575 | 151.464 | 151.464 | 107.4538 | 258.9178 | 0.24681 | 24.68% | 117.0827 | 28.8977 | 20.2284 | 121.4275 | 121.4275 | 16.66% | 11.74% | 11.74% | 80% | 9.389% | 10.9926 | 8.0693 | 6 | 65.9554 | 24.3091 | 54.32% | 54.32%
10 | 294 | 21 | 7044 | 12 | 8.2 | 146.89 | 162.36 | 309.25 | 162.36 | 81.18 | 294 | 7044 | 720 | 289.9726 | -10.585 | 1.3503 | 694.284 | 11.5939 | 6.0914 | 32.3787 | 32.3787 | 7.0949 | 172.9051 | 13.769 | 266.4151 | 266.4151 | 138.5829 | 404.998 | 0.45422 | 45.42% | 183.1401 | 83.185 | 58.2295 | 122.6198 | 122.6198 | 47.49% | 11.61% | 11.61% | 85% | 9.867% | 18.0706 | 7.7573 | 6 | 108.4237 | 39.9616 | 88.42% | 88.42%
10 | 294 | 21 | 7045 | 13 | 9.1 | 165.42 | 149.86 | 315.28 | 149.86 | 74.93 | 294 | 7045 | 780 | 289.9726 | -10.585 | 1.3503 | 754.284 | 12.5939 | -8.9086 | 32.0861 | 32.0861 | 10.3504 | 190.3504 | 15.2127 | 300.4995 | 300.4995 | 127.9135 | 428.413 | 0.47828 | 47.83% | 193.7284 | 92.6556 | 64.8589 | 122.9954 | 122.9954 | 52.73% | 11.57% | 11.57% | 85% | 9.839% | 19.0601 | 7.5083 | 6 | 114.3604 | 42.1496 | 92.98% | 92.98%
10 | 294 | 21 | 7046 | 14 | 10.1 | 180.42 | 132 | 312.42 | 132 | 66 | 294 | 7046 | 840 | 289.9726 | -10.585 | 1.3503 | 814.284 | 13.5939 | -23.9086 | 28.7868 | 28.7868 | 27.0364 | 207.0364 | 26.8103 | 334.3894 | 334.3894 | 112.669 | 447.0585 | 0.4971 | 49.71% | 202.1598 | 100.4928 | 70.345 | 124.0038 | 124.0038 | 56.73% | 11.54% | 11.54% | 85% | 9.813% | 19.837 | 7.2383 | 6 | 119.0222 | 43.8678 | 95.98% | 95.98%
10 | 294 | 21 | 7047 | 15 | 11 | 105.56 | 129.78 | 235.34 | 129.78 | 64.89 | 294 | 7047 | 900 | 289.9726 | -10.585 | 1.3503 | 874.284 | 14.5939 | -38.9086 | 22.9526 | 22.9526 | 42.1037 | 222.1037 | 40.638 | 205.4084 | 205.4084 | 110.7742 | 316.1826 | 0.37669 | 37.67% | 142.9778 | 53.8577 | 37.7004 | 120.1397 | 120.1397 | 31.38% | 11.59% | 11.59% | 85% | 9.853% | 14.0873 | 7.0013 | 6 | 84.5236 | 31.1527 | 70.35% | 70.35%
10 | 294 | 21 | 7048 | 16 | 11.6 | 85.56 | 97.83 | 183.39 | 97.83 | 48.92 | 294 | 7048 | 960 | 289.9726 | -10.585 | 1.3503 | 934.284 | 15.5939 | -53.9086 | 15.2298 | 15.2298 | 55.4104 | 235.4104 | 55.0352 | 186.6535 | 186.6535 | 83.5031 | 270.1566 | 0.30903 | 30.9% | 122.1648 | 37.7529 | 26.4271 | 117.762 | 117.762 | 22.44% | 11.6% | 11.6% | 80% | 9.277% | 11.3338 | 6.8464 | 6 | 68.0025 | 25.0636 | 57.75% | 57.75%
10 | 294 | 21 | 7049 | 17 | 10.2 | 39.58 | 64.11 | 103.69 | 64.11 | 32.06 | 294 | 7049 | 1020 | 289.9726 | -10.585 | 1.3503 | 994.284 | 16.5939 | -68.9086 | 6.2223 | 6.2223 | 67.3041 | 247.3041 | 69.6433 | 0 | 0 | 54.7213 | 54.7213 | -1.6991 | 0% | 24.745 | 0 | 0 | 151.9172 | 151.9172 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7050 | 18 | 9.2 | 4.67 | 16.06 | 20.73 | 16.06 | 8.03 | 294 | 7050 | 1080 | 289.9726 | -10.585 | 1.3503 | 1054.284 | 17.5939 | -83.9086 | -3.579 | 0 | 74.4407 | 254.4407 | 79.0664 | 0 | 0 | 13.7081 | 13.7081 | -9.3586 | 0% | 6.1988 | 0 | 0 | 143.2804 | 143.2804 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7051 | 19 | 8.1 | 0 | 0 | 0 | 0 | 0 | 294 | 7051 | 1140 | 289.9726 | -10.585 | 1.3503 | 1114.284 | 18.5939 | -98.9086 | -13.7748 | 0 | 74.4407 | 254.4407 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.2451 | 137.2451 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7052 | 20 | 7.4 | 0 | 0 | 0 | 0 | 0 | 294 | 7052 | 1200 | 289.9726 | -10.585 | 1.3503 | 1174.284 | 19.5939 | -113.9086 | -23.9966 | 0 | 74.4407 | 254.4407 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.3014 | 132.3014 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7053 | 21 | 5.8 | 0 | 0 | 0 | 0 | 0 | 294 | 7053 | 1260 | 289.9726 | -10.585 | 1.3503 | 1234.284 | 20.5939 | -128.9086 | -33.8255 | 0 | 74.4407 | 254.4407 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0977 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7054 | 22 | 3.9 | 0 | 0 | 0 | 0 | 0 | 294 | 7054 | 1320 | 289.9726 | -10.585 | 1.3503 | 1294.284 | 21.5939 | -143.9086 | -42.6748 | 0 | 74.4407 | 254.4407 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8749 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7055 | 23 | 2.8 | 0 | 0 | 0 | 0 | 0 | 294 | 7055 | 1380 | 289.9726 | -10.585 | 1.3503 | 1354.284 | 22.5939 | -158.9086 | -49.6351 | 0 | 74.4407 | 254.4407 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3226 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
10 | 294 | 21 | 7056 | 24 | 1.8 | 0 | 0 | 0 | 0 | 0 | 294 | 7056 | 1440 | 289.9726 | -10.585 | 1.3503 | 1414.284 | 23.5939 | -173.9086 | -53.4399 | 0 | 74.4407 | 254.4407 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6179 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7057 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 295 | 7057 | 60 | 290.9589 | -10.9518 | 1.5749 | 34.284 | 0.59765 | 171.0353 | -53.3775 | 0 | 73.8938 | 106.1062 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6828 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7058 | 2 | 1.4 | 0 | 0 | 0 | 0 | 0 | 295 | 7058 | 120 | 290.9589 | -10.9518 | 1.5749 | 94.284 | 1.5976 | 156.0353 | -48.8367 | 0 | 73.8938 | 106.1062 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7866 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7059 | 3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 295 | 7059 | 180 | 290.9589 | -10.9518 | 1.5749 | 154.284 | 2.5976 | 141.0353 | -41.393 | 0 | 73.8938 | 106.1062 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0429 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7060 | 4 | 0.6 | 0 | 0 | 0 | 0 | 0 | 295 | 7060 | 240 | 290.9589 | -10.9518 | 1.5749 | 214.284 | 3.5976 | 126.0353 | -32.2746 | 0 | 73.8938 | 106.1062 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8049 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7061 | 5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 295 | 7061 | 300 | 290.9589 | -10.9518 | 1.5749 | 274.284 | 4.5976 | 111.0353 | -22.32 | 0 | 73.8938 | 106.1062 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.218 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7062 | 6 | 0.3 | 0 | 0 | 0 | 0 | 0 | 295 | 7062 | 360 | 290.9589 | -10.9518 | 1.5749 | 334.284 | 5.5976 | 96.0353 | -12.0716 | 0 | 73.8938 | 106.1062 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6361 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7063 | 7 | -0.1 | 0 | 0 | 0 | 0 | 0 | 295 | 7063 | 420 | 290.9589 | -10.9518 | 1.5749 | 394.284 | 6.5976 | 81.0353 | -1.9296 | 0 | 73.8938 | 106.1062 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.2499 | 140.2499 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7064 | 8 | -0.5 | 0.56 | 8.28 | 8.84 | 8.28 | 4.14 | 295 | 7064 | 480 | 290.9589 | -10.9518 | 1.5749 | 454.284 | 7.5976 | 66.0353 | 7.7384 | 7.7384 | 64.877 | 115.123 | 66.878 | 0 | 0 | 7.0674 | 7.0674 | -22.2162 | 0% | 3.1959 | 0 | 0 | 144.3079 | 144.3079 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7065 | 9 | 0.7 | 16.33 | 44.31 | 60.64 | 44.31 | 22.16 | 295 | 7065 | 540 | 290.9589 | -10.9518 | 1.5749 | 514.284 | 8.5976 | 51.0353 | 16.5207 | 16.5207 | 52.7729 | 127.2271 | 52.3239 | 35.0991 | 35.0991 | 37.821 | 72.92 | -1.3865 | 0% | 32.9744 | 0 | 0 | 128.9523 | 128.9523 | 0% | 12.12% | 12.12% | 80% | 9.699% | 3.1982 | 10.0527 | 6 | 19.1892 | 7.0725 | 14.88% | 14.88%
10 | 295 | 22 | 7066 | 10 | 1.9 | 45.14 | 88.67 | 133.81 | 88.67 | 44.34 | 295 | 7066 | 600 | 290.9589 | -10.9518 | 1.5749 | 574.284 | 9.5976 | 36.0353 | 23.9074 | 23.9074 | 39.1812 | 140.8188 | 38.0335 | 87.7326 | 87.7326 | 75.6846 | 163.4171 | -0.15545 | 0% | 73.8972 | 0 | 0 | 134.7611 | 134.7611 | 0% | 11.99% | 11.99% | 80% | 9.589% | 7.0857 | 9.659 | 6 | 42.5141 | 15.6694 | 31.55% | 31.55%
10 | 295 | 22 | 7067 | 11 | 2 | 83.39 | 143.33 | 226.72 | 143.33 | 71.67 | 295 | 7067 | 660 | 290.9589 | -10.9518 | 1.5749 | 634.284 | 10.5976 | 21.0353 | 29.2818 | 29.2818 | 23.8304 | 156.1696 | 24.4912 | 155.1544 | 155.1544 | 122.3398 | 277.4942 | 0.23986 | 23.99% | 125.4829 | 30.098 | 21.0686 | 115.7494 | 115.7494 | 18.2% | 11.87% | 11.87% | 80% | 9.495% | 11.9151 | 9.6266 | 6 | 71.4908 | 26.3493 | 61.76% | 61.76%
10 | 295 | 22 | 7068 | 12 | 3.5 | 181.39 | 160.78 | 342.17 | 160.78 | 80.39 | 295 | 7068 | 720 | 290.9589 | -10.9518 | 1.5749 | 694.284 | 11.5976 | 6.0353 | 32.018 | 32.018 | 6.9929 | 173.0071 | 14.0744 | 331.8553 | 331.8553 | 137.2343 | 469.0896 | 0.47805 | 47.81% | 212.1223 | 101.4058 | 70.9841 | 118.7652 | 118.7652 | 59.77% | 11.65% | 11.65% | 85% | 9.904% | 21.0096 | 9.1497 | 6 | 126.0574 | 46.4608 | 106.1% | 106.1%
10 | 295 | 22 | 7069 | 13 | 4.9 | 209.39 | 145.61 | 355 | 145.61 | 72.81 | 295 | 7069 | 780 | 290.9589 | -10.9518 | 1.5749 | 754.284 | 12.5976 | -8.9647 | 31.7153 | 31.7153 | 10.3607 | 190.3607 | 15.5424 | 383.7428 | 383.7428 | 124.2859 | 508.0287 | 0.50969 | 50.97% | 229.7306 | 117.0903 | 81.9632 | 120.163 | 120.163 | 68.21% | 11.59% | 11.59% | 90% | 10.44% | 23.9725 | 8.7188 | 6 | 143.8348 | 53.013 | 119.7% | 119.7%
10 | 295 | 22 | 7070 | 14 | 6.5 | 166.11 | 138.56 | 304.67 | 138.56 | 69.28 | 295 | 7070 | 840 | 290.9589 | -10.9518 | 1.5749 | 814.284 | 13.5976 | -23.9647 | 28.4214 | 28.4214 | 26.9638 | 206.9638 | 27.0227 | 310.9034 | 310.9034 | 118.2684 | 429.1718 | 0.46453 | 46.45% | 194.0715 | 90.1515 | 63.1061 | 120.1772 | 120.1772 | 52.51% | 11.63% | 11.63% | 85% | 9.883% | 19.1805 | 8.2431 | 6 | 115.0833 | 42.4161 | 95.76% | 95.76%
10 | 295 | 22 | 7071 | 15 | 7.4 | 149.22 | 122.72 | 271.94 | 122.72 | 61.36 | 295 | 7071 | 900 | 290.9589 | -10.9518 | 1.5749 | 874.284 | 14.5976 | -38.9647 | 22.6025 | 22.6025 | 41.9709 | 221.9709 | 40.7899 | 293.9513 | 293.9513 | 104.7481 | 398.6994 | 0.44394 | 44.39% | 180.2919 | 80.0396 | 56.0278 | 118.2914 | 118.2914 | 47.36% | 11.63% | 11.63% | 85% | 9.886% | 17.8229 | 7.9834 | 6 | 106.9375 | 39.4138 | 90.4% | 90.4%
10 | 295 | 22 | 7072 | 16 | 7.8 | 71.17 | 86.25 | 157.42 | 86.25 | 43.13 | 295 | 7072 | 960 | 290.9589 | -10.9518 | 1.5749 | 934.284 | 15.5976 | -53.9647 | 14.8976 | 14.8976 | 55.2394 | 235.2394 | 55.1523 | 158.1776 | 158.1776 | 73.619 | 231.7966 | 0.18878 | 18.88% | 104.8184 | 19.7871 | 13.851 | 112.457 | 112.457 | 12.32% | 11.73% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7073 | 17 | 8.3 | 36.53 | 52.72 | 89.25 | 52.72 | 26.36 | 295 | 7073 | 1020 | 290.9589 | -10.9518 | 1.5749 | 994.284 | 16.5976 | -68.9647 | 5.9059 | 5.9059 | 67.1096 | 247.1096 | 69.7363 | 0 | 0 | 44.9993 | 44.9993 | -2.3389 | 0% | 20.3487 | 0 | 0 | 150.0671 | 150.0671 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7074 | 18 | 7.7 | 3.61 | 15.42 | 19.03 | 15.42 | 7.71 | 295 | 7074 | 1080 | 290.9589 | -10.9518 | 1.5749 | 1054.284 | 17.5976 | -83.9647 | -3.8848 | 0 | 73.8938 | 253.8938 | 78.6872 | 0 | 0 | 13.1618 | 13.1618 | -10.0489 | 0% | 5.9518 | 0 | 0 | 142.6637 | 142.6637 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7075 | 19 | 6.5 | 0 | 0 | 0 | 0 | 0 | 295 | 7075 | 1140 | 290.9589 | -10.9518 | 1.5749 | 1114.284 | 18.5976 | -98.9647 | -14.0762 | 0 | 73.8938 | 253.8938 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.7024 | 136.7024 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7076 | 20 | 4.9 | 0 | 0 | 0 | 0 | 0 | 295 | 7076 | 1200 | 290.9589 | -10.9518 | 1.5749 | 1174.284 | 19.5976 | -113.9647 | -24.3013 | 0 | 73.8938 | 253.8938 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.537 | 130.537 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7077 | 21 | 3.5 | 0 | 0 | 0 | 0 | 0 | 295 | 7077 | 1260 | 290.9589 | -10.9518 | 1.5749 | 1234.284 | 20.5976 | -128.9647 | -34.1421 | 0 | 73.8938 | 253.8938 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5315 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7078 | 22 | 2.8 | 0 | 0 | 0 | 0 | 0 | 295 | 7078 | 1320 | 290.9589 | -10.9518 | 1.5749 | 1294.284 | 21.5976 | -143.9647 | -43.0115 | 0 | 73.8938 | 253.8938 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4569 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7079 | 23 | 2.2 | 0 | 0 | 0 | 0 | 0 | 295 | 7079 | 1380 | 290.9589 | -10.9518 | 1.5749 | 1354.284 | 22.5976 | -158.9647 | -49.9952 | 0 | 73.8938 | 253.8938 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1703 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
10 | 295 | 22 | 7080 | 24 | 1.6 | 0 | 0 | 0 | 0 | 0 | 295 | 7080 | 1440 | 290.9589 | -10.9518 | 1.5749 | 1414.284 | 23.5976 | -173.9647 | -53.8106 | 0 | 73.8938 | 253.8938 | 78.6872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8837 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7081 | 1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 296 | 7081 | 60 | 291.9452 | -11.3156 | 1.7915 | 34.284 | 0.60126 | 170.9811 | -53.7258 | 0 | 73.3506 | 106.6494 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8277 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7082 | 2 | 0.3 | 0 | 0 | 0 | 0 | 0 | 296 | 7082 | 120 | 291.9452 | -11.3156 | 1.7915 | 94.284 | 1.6013 | 155.9811 | -49.1436 | 0 | 73.3506 | 106.6494 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0235 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7083 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 7083 | 180 | 291.9452 | -11.3156 | 1.7915 | 154.284 | 2.6013 | 140.9811 | -41.6599 | 0 | 73.3506 | 106.6494 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1524 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7084 | 4 | -0.4 | 0 | 0 | 0 | 0 | 0 | 296 | 7084 | 240 | 291.9452 | -11.3156 | 1.7915 | 214.284 | 3.6013 | 125.9811 | -32.5142 | 0 | 73.3506 | 106.6494 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.762 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7085 | 5 | -0.7 | 0 | 0 | 0 | 0 | 0 | 296 | 7085 | 300 | 291.9452 | -11.3156 | 1.7915 | 274.284 | 4.6013 | 110.9811 | -22.546 | 0 | 73.3506 | 106.6494 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4794 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7086 | 6 | -1 | 0 | 0 | 0 | 0 | 0 | 296 | 7086 | 360 | 291.9452 | -11.3156 | 1.7915 | 334.284 | 5.6013 | 95.9811 | -12.2955 | 0 | 73.3506 | 106.6494 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.612 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7087 | 7 | -1.1 | 0 | 0 | 0 | 0 | 0 | 296 | 7087 | 420 | 291.9452 | -11.3156 | 1.7915 | 394.284 | 6.6013 | 80.9811 | -2.1614 | 0 | 73.3506 | 106.6494 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.6665 | 147.6665 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7088 | 8 | -1.2 | 0.56 | 6.11 | 6.67 | 6.11 | 3.06 | 296 | 7088 | 480 | 291.9452 | -11.3156 | 1.7915 | 454.284 | 7.6013 | 65.9811 | 7.4898 | 7.4898 | 64.6038 | 115.3962 | 66.8684 | 0 | 0 | 5.2152 | 5.2152 | -30.7249 | 0% | 2.3583 | 0 | 0 | 153.5365 | 153.5365 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7089 | 9 | -0.9 | 24.72 | 51.17 | 75.89 | 51.17 | 25.59 | 296 | 7089 | 540 | 291.9452 | -11.3156 | 1.7915 | 514.284 | 8.6013 | 50.9811 | 16.2476 | 16.2476 | 52.5165 | 127.4835 | 52.3416 | 53.9793 | 53.9793 | 43.6763 | 97.6556 | -0.87215 | 0% | 44.1599 | 0 | 0 | 138.1083 | 138.1083 | 0% | 12.16% | 12.16% | 80% | 9.727% | 4.2956 | 10.5933 | 6 | 25.7738 | 9.4994 | 18.66% | 18.66%
10 | 296 | 23 | 7090 | 10 | -0.4 | 92.28 | 91.33 | 183.61 | 91.33 | 45.67 | 296 | 7090 | 600 | 291.9452 | -11.3156 | 1.7915 | 574.284 | 9.6013 | 35.9811 | 23.6041 | 23.6041 | 38.9542 | 141.0458 | 38.093 | 181.3751 | 181.3751 | 77.955 | 259.3301 | 0.17759 | 17.76% | 117.2691 | 20.8262 | 14.5783 | 144.2978 | 144.2978 | 10.1% | 11.96% | 11.96% | 80% | 9.567% | 11.219 | 10.4224 | 6 | 67.3141 | 24.8099 | 46.65% | 46.65%
10 | 296 | 23 | 7091 | 11 | 3.1 | 176.17 | 107.17 | 283.34 | 107.17 | 53.59 | 296 | 7091 | 660 | 291.9452 | -11.3156 | 1.7915 | 634.284 | 10.6013 | 20.9811 | 28.9477 | 28.9477 | 23.655 | 156.345 | 24.6298 | 330.8647 | 330.8647 | 91.4753 | 422.34 | 0.43968 | 43.97% | 190.9822 | 83.9705 | 58.7794 | 128.9847 | 128.9847 | 45.57% | 11.7% | 11.7% | 85% | 9.948% | 18.9981 | 9.2753 | 6 | 113.9886 | 42.0126 | 88.37% | 88.37%
10 | 296 | 23 | 7092 | 12 | 4.1 | 169.86 | 125.69 | 295.55 | 125.69 | 62.85 | 296 | 7092 | 720 | 291.9452 | -11.3156 | 1.7915 | 694.284 | 11.6013 | 5.9811 | 31.66 | 31.66 | 6.8944 | 173.1056 | 14.3809 | 313.4781 | 313.4781 | 107.2831 | 420.7612 | 0.44406 | 44.41% | 190.2682 | 84.4912 | 59.1438 | 123.9256 | 123.9256 | 47.73% | 11.68% | 11.68% | 85% | 9.931% | 18.8957 | 8.9633 | 6 | 113.3743 | 41.7862 | 91.49% | 91.49%
10 | 296 | 23 | 7093 | 13 | 5.7 | 214.03 | 116.67 | 330.7 | 116.67 | 58.34 | 296 | 7093 | 780 | 291.9452 | -11.3156 | 1.7915 | 754.284 | 12.6013 | -9.0189 | 31.3477 | 31.3477 | 10.3689 | 190.3689 | 15.8701 | 395.732 | 395.732 | 99.5841 | 495.3161 | 0.506 | 50.6% | 223.9819 | 113.3359 | 79.3351 | 125.8649 | 125.8649 | 63.03% | 11.59% | 11.59% | 85% | 9.853% | 22.0687 | 8.4787 | 6 | 132.4122 | 48.8029 | 105.2% | 105.2%
10 | 296 | 23 | 7094 | 14 | 9.9 | 288.67 | 125.56 | 414.23 | 125.56 | 62.78 | 296 | 7094 | 840 | 291.9452 | -11.3156 | 1.7915 | 814.284 | 13.6013 | -24.0189 | 28.0595 | 28.0595 | 26.8905 | 206.8905 | 27.235 | 545.6502 | 545.6502 | 107.1722 | 652.8224 | 0.59311 | 59.31% | 295.2063 | 175.091 | 122.5637 | 135.1235 | 135.1235 | 90.7% | 11.43% | 11.43% | 90% | 10.29% | 30.3779 | 7.2918 | 6 | 182.2671 | 67.1779 | 134.9% | 134.9%
10 | 296 | 23 | 7095 | 15 | 11.5 | 178.83 | 108.33 | 287.16 | 108.33 | 54.17 | 296 | 7095 | 900 | 291.9452 | -11.3156 | 1.7915 | 874.284 | 14.6013 | -39.0189 | 22.2559 | 22.2559 | 41.8383 | 221.8383 | 40.9413 | 356.6652 | 356.6652 | 92.4654 | 449.1306 | 0.50576 | 50.58% | 203.0969 | 102.7177 | 71.9024 | 129.2338 | 129.2338 | 55.64% | 11.52% | 11.52% | 85% | 9.789% | 19.8804 | 6.8721 | 6 | 119.2824 | 43.9637 | 92.3% | 92.3%
10 | 296 | 23 | 7096 | 16 | 11.7 | 74.78 | 110.33 | 185.11 | 110.33 | 55.17 | 296 | 7096 | 960 | 291.9452 | -11.3156 | 1.7915 | 934.284 | 15.6013 | -54.0189 | 14.569 | 14.569 | 55.069 | 235.069 | 55.2684 | 169.3712 | 169.3712 | 94.1725 | 263.5437 | 0.29749 | 29.75% | 119.1745 | 35.4533 | 24.8173 | 122.9584 | 122.9584 | 20.18% | 11.6% | 0% | 80% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7097 | 17 | 11.1 | 28.28 | 61.67 | 89.95 | 61.67 | 30.84 | 296 | 7097 | 1020 | 291.9452 | -11.3156 | 1.7915 | 994.284 | 16.6013 | -69.0189 | 5.593 | 5.593 | 66.9155 | 246.9155 | 69.8278 | 0 | 0 | 52.6386 | 52.6386 | -1.7583 | 0% | 23.8032 | 0 | 0 | 156.5776 | 156.5776 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7098 | 18 | 10.5 | 1.33 | 12.92 | 14.25 | 12.92 | 6.46 | 296 | 7098 | 1080 | 291.9452 | -11.3156 | 1.7915 | 1054.284 | 17.6013 | -84.0189 | -4.1868 | 0 | 73.3506 | 253.3506 | 78.3112 | 0 | 0 | 11.0279 | 11.0279 | -11.553 | 0% | 4.9868 | 0 | 0 | 147.9942 | 147.9942 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7099 | 19 | 8.5 | 0 | 0 | 0 | 0 | 0 | 296 | 7099 | 1140 | 291.9452 | -11.3156 | 1.7915 | 1114.284 | 18.6013 | -99.0189 | -14.3739 | 0 | 73.3506 | 253.3506 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.8497 | 140.8497 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7100 | 20 | 6 | 0 | 0 | 0 | 0 | 0 | 296 | 7100 | 1200 | 291.9452 | -11.3156 | 1.7915 | 1174.284 | 19.6013 | -114.0189 | -24.6021 | 0 | 73.3506 | 253.3506 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.5126 | 132.5126 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7101 | 21 | 4.2 | 0 | 0 | 0 | 0 | 0 | 296 | 7101 | 1260 | 291.9452 | -11.3156 | 1.7915 | 1234.284 | 20.6013 | -129.0189 | -34.4545 | 0 | 73.3506 | 253.3506 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3502 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7102 | 22 | 3 | 0 | 0 | 0 | 0 | 0 | 296 | 7102 | 1320 | 291.9452 | -11.3156 | 1.7915 | 1294.284 | 21.6013 | -144.0189 | -43.3441 | 0 | 73.3506 | 253.3506 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2215 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7103 | 23 | 2.6 | 0 | 0 | 0 | 0 | 0 | 296 | 7103 | 1380 | 291.9452 | -11.3156 | 1.7915 | 1354.284 | 22.6013 | -159.0189 | -50.3516 | 0 | 73.3506 | 253.3506 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5029 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
10 | 296 | 23 | 7104 | 24 | 1.7 | 0 | 0 | 0 | 0 | 0 | 296 | 7104 | 1440 | 291.9452 | -11.3156 | 1.7915 | 1414.284 | 23.6013 | -174.0189 | -54.1782 | 0 | 73.3506 | 253.3506 | 78.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5463 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7105 | 1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 297 | 7105 | 60 | 292.9315 | -11.6762 | 1.9998 | 34.284 | 0.60473 | 170.9291 | -54.071 | 0 | 72.8112 | 107.1888 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0402 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7106 | 2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 297 | 7106 | 120 | 292.9315 | -11.6762 | 1.9998 | 94.284 | 1.6047 | 155.9291 | -49.4476 | 0 | 72.8112 | 107.1888 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9883 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7107 | 3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 297 | 7107 | 180 | 292.9315 | -11.6762 | 1.9998 | 154.284 | 2.6047 | 140.9291 | -41.9245 | 0 | 72.8112 | 107.1888 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0031 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7108 | 4 | 0.1 | 0 | 0 | 0 | 0 | 0 | 297 | 7108 | 240 | 292.9315 | -11.6762 | 1.9998 | 214.284 | 3.6047 | 125.9291 | -32.7521 | 0 | 72.8112 | 107.1888 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.3079 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7109 | 5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 297 | 7109 | 300 | 292.9315 | -11.6762 | 1.9998 | 274.284 | 4.6047 | 110.9291 | -22.7706 | 0 | 72.8112 | 107.1888 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7073 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7110 | 6 | -0.1 | 0 | 0 | 0 | 0 | 0 | 297 | 7110 | 360 | 292.9315 | -11.6762 | 1.9998 | 334.284 | 5.6047 | 95.9291 | -12.5184 | 0 | 72.8112 | 107.1888 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8797 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7111 | 7 | -0.3 | 0 | 0 | 0 | 0 | 0 | 297 | 7111 | 420 | 292.9315 | -11.6762 | 1.9998 | 394.284 | 6.6047 | 80.9291 | -2.3923 | 0 | 72.8112 | 107.1888 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.9516 | 137.9516 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7112 | 8 | -0.6 | 0.42 | 5.56 | 5.98 | 5.56 | 2.78 | 297 | 7112 | 480 | 292.9315 | -11.6762 | 1.9998 | 454.284 | 7.6047 | 65.9291 | 7.2421 | 7.2421 | 64.3345 | 115.6655 | 66.8615 | 0 | 0 | 4.7458 | 4.7458 | -33.5301 | 0% | 2.146 | 0 | 0 | 141.4401 | 141.4401 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7113 | 9 | 0.7 | 8.94 | 35.42 | 44.36 | 35.42 | 17.71 | 297 | 7113 | 540 | 292.9315 | -11.6762 | 1.9998 | 514.284 | 8.6047 | 50.9291 | 15.9755 | 15.9755 | 52.2644 | 127.7356 | 52.3625 | 19.8358 | 19.8358 | 30.2329 | 50.0686 | -2.3863 | 0% | 22.641 | 0 | 0 | 125.2746 | 125.2746 | 0% | 12.15% | 12.15% | 80% | 9.718% | 2.2004 | 10.0527 | 6 | 13.2021 | 4.8659 | 10.54% | 10.54%
10 | 297 | 24 | 7114 | 10 | 3.5 | 15.06 | 55.97 | 71.03 | 55.97 | 27.99 | 297 | 7114 | 600 | 292.9315 | -11.6762 | 1.9998 | 574.284 | 9.6047 | 35.9291 | 23.3024 | 23.3024 | 38.7319 | 141.2681 | 38.1564 | 29.9357 | 29.9357 | 47.7734 | 77.7091 | -1.1636 | 0% | 35.1401 | 0 | 0 | 130.8124 | 130.8124 | 0% | 12.01% | 12.01% | 80% | 9.606% | 3.3755 | 9.1497 | 6 | 20.2533 | 7.4647 | 15.48% | 15.48%
10 | 297 | 24 | 7115 | 11 | 5.2 | 95.83 | 99.39 | 195.22 | 99.39 | 49.7 | 297 | 7115 | 660 | 292.9315 | -11.6762 | 1.9998 | 634.284 | 10.6047 | 20.9291 | 28.6157 | 28.6157 | 23.4842 | 156.5158 | 24.7729 | 181.6777 | 181.6777 | 84.8347 | 266.5123 | 0.24568 | 24.57% | 120.5169 | 29.6083 | 20.7258 | 136.9162 | 136.9162 | 15.14% | 11.79% | 11.79% | 80% | 9.429% | 11.3635 | 8.6282 | 6 | 68.1813 | 25.1295 | 49.8% | 49.8%
10 | 297 | 24 | 7116 | 12 | 6.9 | 86.17 | 116.33 | 202.5 | 116.33 | 58.17 | 297 | 7116 | 720 | 292.9315 | -11.6762 | 1.9998 | 694.284 | 11.6047 | 5.9291 | 31.3049 | 31.3049 | 6.7996 | 173.2004 | 14.6882 | 160.4218 | 160.4218 | 99.2939 | 259.7157 | 0.2467 | 24.67% | 117.4434 | 28.9729 | 20.281 | 114.4175 | 114.4175 | 17.73% | 11.74% | 11.74% | 80% | 9.393% | 11.0315 | 8.127 | 6 | 66.1889 | 24.3951 | 57.85% | 57.85%
10 | 297 | 24 | 7117 | 13 | 9.1 | 168.19 | 107.83 | 276.02 | 107.83 | 53.92 | 297 | 7117 | 780 | 292.9315 | -11.6762 | 1.9998 | 754.284 | 12.6047 | -9.0709 | 30.9836 | 30.9836 | 10.3751 | 190.3751 | 16.1957 | 313.7483 | 313.7483 | 92.0387 | 405.7869 | 0.46011 | 46.01% | 183.4969 | 84.4295 | 59.1006 | 119.6804 | 119.6804 | 49.38% | 11.59% | 11.59% | 85% | 9.85% | 18.0746 | 7.5083 | 6 | 108.4475 | 39.9703 | 90.61% | 90.61%
10 | 297 | 24 | 7118 | 14 | 11.8 | 99.58 | 93.19 | 192.77 | 93.19 | 46.6 | 297 | 7118 | 840 | 292.9315 | -11.6762 | 1.9998 | 814.284 | 13.6047 | -24.0709 | 27.7012 | 27.7012 | 26.8165 | 206.8165 | 27.447 | 190.1023 | 190.1023 | 79.5426 | 269.6449 | 0.30981 | 30.98% | 121.9334 | 37.776 | 26.4432 | 140.7222 | 140.7222 | 18.79% | 11.59% | 11.59% | 80% | 9.273% | 11.3068 | 6.7954 | 6 | 67.841 | 25.004 | 48.21% | 48.21%
10 | 297 | 24 | 7119 | 15 | 13 | 84.67 | 77.78 | 162.45 | 77.78 | 38.89 | 297 | 7119 | 900 | 292.9315 | -11.6762 | 1.9998 | 874.284 | 14.6047 | -39.0709 | 21.913 | 21.913 | 41.7059 | 221.7059 | 41.092 | 170.9867 | 170.9867 | 66.3894 | 237.3761 | 0.25427 | 25.43% | 107.3415 | 27.2937 | 19.1056 | 118.3681 | 118.3681 | 16.14% | 11.57% | 11.57% | 80% | 9.255% | 9.9343 | 6.4949 | 6 | 59.606 | 21.9689 | 50.36% | 50.36%
10 | 297 | 24 | 7120 | 16 | 14 | 57.44 | 48.75 | 106.19 | 48.75 | 24.38 | 297 | 7120 | 960 | 292.9315 | -11.6762 | 1.9998 | 934.284 | 15.6047 | -54.0709 | 14.2441 | 14.2441 | 54.8991 | 234.8991 | 55.3832 | 132.6165 | 132.6165 | 41.6107 | 174.2273 | 0.068152 | 6.815% | 78.7856 | 5.3694 | 3.7586 | 158.3035 | 158.3035 | 2.374% | 11.56% | 0% | 80% | 0% | 0 | 6.2522 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7121 | 17 | 13.2 | 19.5 | 27.36 | 46.86 | 27.36 | 13.68 | 297 | 7121 | 1020 | 292.9315 | -11.6762 | 1.9998 | 994.284 | 16.6047 | -69.0709 | 5.2839 | 5.2839 | 66.7221 | 246.7221 | 69.9175 | 0 | 0 | 23.3532 | 23.3532 | -4.7641 | 0% | 10.5603 | 0 | 0 | 152.3491 | 152.3491 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7122 | 18 | 11.8 | 1.33 | 7.64 | 8.97 | 7.64 | 3.82 | 297 | 7122 | 1080 | 292.9315 | -11.6762 | 1.9998 | 1054.284 | 17.6047 | -84.0709 | -4.4851 | 0 | 72.8112 | 252.8112 | 77.9383 | 0 | 0 | 6.5211 | 6.5211 | -19.6305 | 0% | 2.9489 | 0 | 0 | 145.821 | 145.821 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7123 | 19 | 9.6 | 0 | 0 | 0 | 0 | 0 | 297 | 7123 | 1140 | 292.9315 | -11.6762 | 1.9998 | 1114.284 | 18.6047 | -99.0709 | -14.6675 | 0 | 72.8112 | 252.8112 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.6631 | 139.6631 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7124 | 20 | 6.9 | 0 | 0 | 0 | 0 | 0 | 297 | 7124 | 1200 | 292.9315 | -11.6762 | 1.9998 | 1174.284 | 19.6047 | -114.0709 | -24.8987 | 0 | 72.8112 | 252.8112 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.4899 | 132.4899 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7125 | 21 | 4.8 | 0 | 0 | 0 | 0 | 0 | 297 | 7125 | 1260 | 292.9315 | -11.6762 | 1.9998 | 1234.284 | 20.6047 | -129.0709 | -34.7626 | 0 | 72.8112 | 252.8112 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4667 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7126 | 22 | 4.1 | 0 | 0 | 0 | 0 | 0 | 297 | 7126 | 1320 | 292.9315 | -11.6762 | 1.9998 | 1294.284 | 21.6047 | -144.0709 | -43.6725 | 0 | 72.8112 | 252.8112 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2337 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7127 | 23 | 3.4 | 0 | 0 | 0 | 0 | 0 | 297 | 7127 | 1380 | 292.9315 | -11.6762 | 1.9998 | 1354.284 | 22.6047 | -159.0709 | -50.704 | 0 | 72.8112 | 252.8112 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0961 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
10 | 297 | 24 | 7128 | 24 | 2.7 | 0 | 0 | 0 | 0 | 0 | 297 | 7128 | 1440 | 292.9315 | -11.6762 | 1.9998 | 1414.284 | 23.6047 | -174.0709 | -54.5423 | 0 | 72.8112 | 252.8112 | 77.9383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9586 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7129 | 1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 298 | 7129 | 60 | 293.9178 | -12.0335 | 2.1996 | 34.284 | 0.60806 | 170.8791 | -54.413 | 0 | 72.276 | 107.724 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9248 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7130 | 2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 298 | 7130 | 120 | 293.9178 | -12.0335 | 2.1996 | 94.284 | 1.6081 | 155.8791 | -49.7489 | 0 | 72.276 | 107.724 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9795 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7131 | 3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 298 | 7131 | 180 | 293.9178 | -12.0335 | 2.1996 | 154.284 | 2.6081 | 140.8791 | -42.1866 | 0 | 72.276 | 107.724 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1866 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7132 | 4 | 0.9 | 0 | 0 | 0 | 0 | 0 | 298 | 7132 | 240 | 293.9178 | -12.0335 | 2.1996 | 214.284 | 3.6081 | 125.8791 | -32.9881 | 0 | 72.276 | 107.724 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4058 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7133 | 5 | 0.4 | 0 | 0 | 0 | 0 | 0 | 298 | 7133 | 300 | 293.9178 | -12.0335 | 2.1996 | 274.284 | 4.6081 | 110.8791 | -22.9937 | 0 | 72.276 | 107.724 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.3248 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7134 | 6 | 0.1 | 0 | 0 | 0 | 0 | 0 | 298 | 7134 | 360 | 293.9178 | -12.0335 | 2.1996 | 334.284 | 5.6081 | 95.8791 | -12.74 | 0 | 72.276 | 107.724 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.9701 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7135 | 7 | -0.3 | 0 | 0 | 0 | 0 | 0 | 298 | 7135 | 420 | 293.9178 | -12.0335 | 2.1996 | 394.284 | 6.6081 | 80.8791 | -2.6222 | 0 | 72.276 | 107.724 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 154.4752 | 154.4752 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7136 | 8 | -0.4 | 0.28 | 5.14 | 5.42 | 5.14 | 2.57 | 298 | 7136 | 480 | 293.9178 | -12.0335 | 2.1996 | 454.284 | 7.6081 | 65.8791 | 6.9955 | 6.9955 | 64.0694 | 115.9306 | 66.8573 | 0 | 0 | 4.3873 | 4.3873 | -36.2228 | 0% | 1.9839 | 0 | 0 | 161.1464 | 161.1464 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7137 | 9 | 0.9 | 37.44 | 40.56 | 78 | 40.56 | 20.28 | 298 | 7137 | 540 | 293.9178 | -12.0335 | 2.1996 | 514.284 | 8.6081 | 50.8791 | 15.7047 | 15.7047 | 52.0169 | 127.9831 | 52.3867 | 84.4196 | 84.4196 | 34.6201 | 119.0397 | -0.53371 | 0% | 53.8298 | 0 | 0 | 147.8983 | 147.8983 | 0% | 12.07% | 12.07% | 80% | 9.654% | 5.1967 | 9.9864 | 6 | 31.18 | 11.492 | 21.08% | 21.08%
10 | 298 | 25 | 7138 | 10 | 2.4 | 109.86 | 77.17 | 187.03 | 77.17 | 38.59 | 298 | 7138 | 600 | 293.9178 | -12.0335 | 2.1996 | 574.284 | 9.6081 | 35.8791 | 23.0024 | 23.0024 | 38.5144 | 141.4856 | 38.2237 | 220.8622 | 220.8622 | 65.8687 | 286.7309 | 0.26143 | 26.14% | 129.6597 | 33.8974 | 23.7282 | 154.3934 | 154.3934 | 15.37% | 11.85% | 11.85% | 80% | 9.479% | 12.2905 | 9.4979 | 6 | 73.7433 | 27.1794 | 47.76% | 47.76%
10 | 298 | 25 | 7139 | 11 | 2.3 | 167.64 | 142.92 | 310.56 | 142.92 | 71.46 | 298 | 7139 | 660 | 293.9178 | -12.0335 | 2.1996 | 634.284 | 10.6081 | 20.8791 | 28.2861 | 28.2861 | 23.3178 | 156.6822 | 24.9203 | 320.8273 | 320.8273 | 121.9899 | 442.8171 | 0.45213 | 45.21% | 200.2419 | 90.5353 | 63.3747 | 133.0406 | 133.0406 | 47.64% | 11.7% | 11.7% | 85% | 9.945% | 19.9136 | 9.53 | 6 | 119.4815 | 44.0371 | 89.81% | 89.81%
10 | 298 | 25 | 7140 | 12 | 4.3 | 205.56 | 181.72 | 387.28 | 181.72 | 90.86 | 298 | 7140 | 720 | 293.9178 | -12.0335 | 2.1996 | 694.284 | 11.6081 | 5.8791 | 30.9529 | 30.9529 | 6.7083 | 173.2917 | 14.9958 | 386.0527 | 386.0527 | 155.1077 | 541.1604 | 0.52504 | 52.5% | 244.7127 | 128.4828 | 89.938 | 130.5484 | 130.5484 | 68.89% | 11.58% | 11.58% | 90% | 10.42% | 25.4941 | 8.9018 | 6 | 152.9644 | 56.3779 | 117.2% | 117.2%
10 | 298 | 25 | 7141 | 13 | 11 | 218.61 | 183.11 | 401.72 | 183.11 | 91.56 | 298 | 7141 | 780 | 293.9178 | -12.0335 | 2.1996 | 754.284 | 12.6081 | -9.1209 | 30.623 | 30.623 | 10.3791 | 190.3791 | 16.5188 | 411.4496 | 411.4496 | 156.2942 | 567.7438 | 0.56602 | 56.6% | 256.7337 | 145.3175 | 101.7223 | 139.2322 | 139.2322 | 73.06% | 11.47% | 11.47% | 90% | 10.32% | 26.4956 | 7.0013 | 6 | 158.9737 | 58.5927 | 114.2% | 114.2%
10 | 298 | 25 | 7142 | 14 | 11.2 | 223.75 | 145.97 | 369.72 | 145.97 | 72.99 | 298 | 7142 | 840 | 293.9178 | -12.0335 | 2.1996 | 814.284 | 13.6081 | -24.1209 | 27.3467 | 27.3467 | 26.7418 | 206.7418 | 27.6583 | 431.4182 | 431.4182 | 124.5932 | 556.0114 | 0.56184 | 56.18% | 251.4284 | 141.2619 | 98.8833 | 137.3336 | 137.3336 | 72% | 11.47% | 11.47% | 90% | 10.32% | 25.9552 | 6.9494 | 6 | 155.7309 | 57.3975 | 113.4% | 113.4%
10 | 298 | 25 | 7143 | 15 | 11.6 | 197.22 | 123.56 | 320.78 | 123.56 | 61.78 | 298 | 7143 | 900 | 293.9178 | -12.0335 | 2.1996 | 874.284 | 14.6081 | -39.1209 | 21.574 | 21.574 | 41.5737 | 221.5737 | 41.2418 | 403.3059 | 403.3059 | 105.4651 | 508.7709 | 0.54117 | 54.12% | 230.0662 | 124.5057 | 87.154 | 133.3843 | 133.3843 | 65.34% | 11.49% | 11.49% | 90% | 10.34% | 23.784 | 6.8464 | 6 | 142.704 | 52.5962 | 107% | 107%
10 | 298 | 25 | 7144 | 16 | 11.7 | 127.08 | 108 | 235.08 | 108 | 54 | 298 | 7144 | 960 | 293.9178 | -12.0335 | 2.1996 | 934.284 | 15.6081 | -54.1209 | 13.9231 | 13.9231 | 54.7298 | 234.7298 | 55.4967 | 299.1657 | 299.1657 | 92.1838 | 391.3495 | 0.4629 | 46.29% | 176.9682 | 81.9195 | 57.3436 | 128.1152 | 128.1152 | 44.76% | 11.54% | 0% | 85% | 0% | 0 | 6.8209 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7145 | 17 | 11.2 | 54.22 | 50.42 | 104.64 | 50.42 | 25.21 | 298 | 7145 | 1020 | 293.9178 | -12.0335 | 2.1996 | 994.284 | 16.6081 | -69.1209 | 4.9786 | 4.9786 | 66.5293 | 246.5293 | 70.0055 | 0 | 0 | 43.0362 | 43.0362 | -2.3247 | 0% | 19.461 | 0 | 0 | 160.295 | 160.295 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.9494 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7146 | 18 | 10.8 | 2.36 | 11.11 | 13.47 | 11.11 | 5.56 | 298 | 7146 | 1080 | 293.9178 | -12.0335 | 2.1996 | 1054.284 | 17.6081 | -84.1209 | -4.7793 | 0 | 72.276 | 252.276 | 77.5689 | 0 | 0 | 9.483 | 9.483 | -13.4925 | 0% | 4.2882 | 0 | 0 | 150.0261 | 150.0261 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7147 | 19 | 10.2 | 0 | 0 | 0 | 0 | 0 | 298 | 7147 | 1140 | 293.9178 | -12.0335 | 2.1996 | 1114.284 | 18.6081 | -99.1209 | -14.957 | 0 | 72.276 | 252.276 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.1016 | 144.1016 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7148 | 20 | 9.6 | 0 | 0 | 0 | 0 | 0 | 298 | 7148 | 1200 | 293.9178 | -12.0335 | 2.1996 | 1174.284 | 19.6081 | -114.1209 | -25.191 | 0 | 72.276 | 252.276 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.5039 | 137.5039 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7149 | 21 | 8.5 | 0 | 0 | 0 | 0 | 0 | 298 | 7149 | 1260 | 293.9178 | -12.0335 | 2.1996 | 1234.284 | 20.6081 | -129.1209 | -35.0664 | 0 | 72.276 | 252.276 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5584 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7150 | 22 | 7.8 | 0 | 0 | 0 | 0 | 0 | 298 | 7150 | 1320 | 293.9178 | -12.0335 | 2.1996 | 1294.284 | 21.6081 | -144.1209 | -43.9965 | 0 | 72.276 | 252.276 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9027 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7151 | 23 | 7.7 | 0 | 0 | 0 | 0 | 0 | 298 | 7151 | 1380 | 293.9178 | -12.0335 | 2.1996 | 1354.284 | 22.6081 | -159.1209 | -51.0523 | 0 | 72.276 | 252.276 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6526 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
10 | 298 | 25 | 7152 | 24 | 7.6 | 0 | 0 | 0 | 0 | 0 | 298 | 7152 | 1440 | 293.9178 | -12.0335 | 2.1996 | 1414.284 | 23.6081 | -174.1209 | -54.9029 | 0 | 72.276 | 252.276 | 77.5689 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4025 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7153 | 1 | 7.6 | 0 | 0 | 0 | 0 | 0 | 299 | 7153 | 60 | 294.9041 | -12.3873 | 2.3907 | 34.284 | 0.61124 | 170.8313 | -54.7517 | 0 | 71.7451 | 108.2549 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9329 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7154 | 2 | 7.6 | 0 | 0 | 0 | 0 | 0 | 299 | 7154 | 120 | 294.9041 | -12.3873 | 2.3907 | 94.284 | 1.6112 | 155.8313 | -50.0472 | 0 | 71.7451 | 108.2549 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6853 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7155 | 3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 299 | 7155 | 180 | 294.9041 | -12.3873 | 2.3907 | 154.284 | 2.6112 | 140.8313 | -42.4464 | 0 | 71.7451 | 108.2549 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.5901 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7156 | 4 | 7.4 | 0 | 0 | 0 | 0 | 0 | 299 | 7156 | 240 | 294.9041 | -12.3873 | 2.3907 | 214.284 | 3.6112 | 125.8313 | -33.2221 | 0 | 71.7451 | 108.2549 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7425 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7157 | 5 | 7.1 | 0 | 0 | 0 | 0 | 0 | 299 | 7157 | 300 | 294.9041 | -12.3873 | 2.3907 | 274.284 | 4.6112 | 110.8313 | -23.2154 | 0 | 71.7451 | 108.2549 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.0319 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7158 | 6 | 7.2 | 0 | 0 | 0 | 0 | 0 | 299 | 7158 | 360 | 294.9041 | -12.3873 | 2.3907 | 334.284 | 5.6112 | 95.8313 | -12.9605 | 0 | 71.7451 | 108.2549 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.5806 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7159 | 7 | 7.2 | 0 | 0 | 0 | 0 | 0 | 299 | 7159 | 420 | 294.9041 | -12.3873 | 2.3907 | 394.284 | 6.6112 | 80.8313 | -2.8511 | 0 | 71.7451 | 108.2549 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 152.478 | 152.478 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7160 | 8 | 7.2 | 0.28 | 4.31 | 4.59 | 4.31 | 2.16 | 299 | 7160 | 480 | 294.9041 | -12.3873 | 2.3907 | 454.284 | 7.6112 | 65.8313 | 6.7499 | 6.7499 | 63.8086 | 116.1914 | 66.8559 | 0 | 0 | 3.6788 | 3.6788 | -38.3467 | 0% | 1.6636 | 0 | 0 | 157.279 | 157.279 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7161 | 9 | 7.2 | 24.17 | 32.17 | 56.34 | 32.17 | 16.09 | 299 | 7161 | 540 | 294.9041 | -12.3873 | 2.3907 | 514.284 | 8.6112 | 50.8313 | 15.4353 | 15.4353 | 51.7739 | 128.2261 | 52.4142 | 55.3916 | 55.3916 | 27.4588 | 82.8504 | -0.93441 | 0% | 37.4649 | 0 | 0 | 140.4315 | 140.4315 | 0% | 11.86% | 11.86% | 80% | 9.485% | 3.5537 | 8.0406 | 6 | 21.3224 | 7.8588 | 15.18% | 15.18%
10 | 299 | 26 | 7162 | 10 | 7.5 | 60.97 | 64.22 | 125.19 | 64.22 | 32.11 | 299 | 7162 | 600 | 294.9041 | -12.3873 | 2.3907 | 574.284 | 9.6112 | 35.8313 | 22.7041 | 22.7041 | 38.3016 | 141.6984 | 38.2948 | 123.9757 | 123.9757 | 54.8152 | 178.7909 | 0.0024107 | 0.2411% | 80.8492 | 0.1949 | 0.13643 | 143.8638 | 143.8638 | 0.09483% | 11.78% | 11.78% | 80% | 9.423% | 7.6186 | 7.9549 | 6 | 45.7118 | 16.8479 | 31.77% | 31.77%
10 | 299 | 26 | 7163 | 11 | 7.9 | 89.31 | 102.17 | 191.48 | 102.17 | 51.09 | 299 | 7163 | 660 | 294.9041 | -12.3873 | 2.3907 | 634.284 | 10.6112 | 20.8313 | 27.959 | 27.959 | 23.156 | 156.844 | 25.0718 | 172.5432 | 172.5432 | 87.2075 | 259.7507 | 0.2559 | 25.59% | 117.4593 | 30.0573 | 21.0401 | 144.0004 | 144.0004 | 14.61% | 11.71% | 11.71% | 80% | 9.369% | 11.005 | 7.8416 | 6 | 66.0302 | 24.3366 | 45.85% | 45.85%
10 | 299 | 26 | 7164 | 12 | 8.4 | 114.11 | 136.44 | 250.55 | 136.44 | 68.22 | 299 | 7164 | 720 | 294.9041 | -12.3873 | 2.3907 | 694.284 | 11.6112 | 5.8313 | 30.604 | 30.604 | 6.6206 | 173.3794 | 15.3033 | 216.1922 | 216.1922 | 116.4588 | 332.6511 | 0.37956 | 37.96% | 150.4248 | 57.0951 | 39.9666 | 120.8776 | 120.8776 | 33.06% | 11.65% | 11.65% | 85% | 9.903% | 14.896 | 7.7015 | 6 | 89.3762 | 32.9412 | 73.94% | 73.94%
10 | 299 | 26 | 7165 | 13 | 9 | 139.86 | 161.61 | 301.47 | 161.61 | 80.81 | 299 | 7165 | 780 | 294.9041 | -12.3873 | 2.3907 | 754.284 | 12.6112 | -9.1687 | 30.2661 | 30.2661 | 10.381 | 190.381 | 16.8393 | 265.5919 | 265.5919 | 137.9428 | 403.5347 | 0.45761 | 45.76% | 182.4784 | 83.5045 | 58.4531 | 122.942 | 122.942 | 47.55% | 11.59% | 11.59% | 85% | 9.853% | 17.9797 | 7.5357 | 6 | 107.8785 | 39.7606 | 87.75% | 87.75%
10 | 299 | 26 | 7166 | 14 | 8.9 | 167.92 | 153.19 | 321.11 | 153.19 | 76.6 | 299 | 7166 | 840 | 294.9041 | -12.3873 | 2.3907 | 814.284 | 13.6112 | -24.1687 | 26.9962 | 26.9962 | 26.6664 | 206.6664 | 27.8689 | 327.0198 | 327.0198 | 130.7558 | 457.7756 | 0.49814 | 49.81% | 207.0061 | 103.1186 | 72.183 | 123.2749 | 123.2749 | 58.55% | 11.56% | 11.56% | 85% | 9.827% | 20.3421 | 7.5632 | 6 | 122.0523 | 44.9846 | 99.01% | 99.01%
10 | 299 | 26 | 7167 | 15 | 9.2 | 119.03 | 135.22 | 254.25 | 135.22 | 67.61 | 299 | 7167 | 900 | 294.9041 | -12.3873 | 2.3907 | 874.284 | 14.6112 | -39.1687 | 21.2389 | 21.2389 | 41.4416 | 221.4416 | 41.3905 | 246.5058 | 246.5058 | 115.4175 | 361.9233 | 0.41908 | 41.91% | 163.6617 | 68.5881 | 48.0117 | 118.9691 | 118.9691 | 40.36% | 11.61% | 11.61% | 85% | 9.87% | 16.154 | 7.481 | 6 | 96.9243 | 35.7232 | 81.47% | 81.47%
10 | 299 | 26 | 7168 | 16 | 8.8 | 93.75 | 149.58 | 243.33 | 149.58 | 74.79 | 299 | 7168 | 960 | 294.9041 | -12.3873 | 2.3907 | 934.284 | 15.6112 | -54.1687 | 13.606 | 13.606 | 54.5611 | 234.5611 | 55.6087 | 225.1015 | 225.1015 | 127.6745 | 352.776 | 0.40644 | 40.64% | 159.5253 | 64.8377 | 45.3864 | 117.0585 | 117.0585 | 38.77% | 11.63% | 0% | 85% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7169 | 17 | 8.8 | 30.22 | 77.72 | 107.94 | 77.72 | 38.86 | 299 | 7169 | 1020 | 294.9041 | -12.3873 | 2.3907 | 994.284 | 16.6112 | -69.1687 | 4.6775 | 4.6775 | 66.3372 | 246.3372 | 70.0917 | 0 | 0 | 66.3382 | 66.3382 | -1.3102 | 0% | 29.9981 | 0 | 0 | 150.2974 | 150.2974 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7170 | 18 | 8.6 | 1.39 | 11.31 | 12.7 | 11.31 | 5.66 | 299 | 7170 | 1080 | 294.9041 | -12.3873 | 2.3907 | 1054.284 | 17.6112 | -84.1687 | -5.0694 | 0 | 71.7451 | 251.7451 | 77.203 | 0 | 0 | 9.6537 | 9.6537 | -13.7728 | 0% | 4.3654 | 0 | 0 | 141.8593 | 141.8593 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6459 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7171 | 19 | 8.4 | 0 | 0 | 0 | 0 | 0 | 299 | 7171 | 1140 | 294.9041 | -12.3873 | 2.3907 | 1114.284 | 18.6112 | -99.1687 | -15.2423 | 0 | 71.7451 | 251.7451 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.691 | 137.691 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7172 | 20 | 7.1 | 0 | 0 | 0 | 0 | 0 | 299 | 7172 | 1200 | 294.9041 | -12.3873 | 2.3907 | 1174.284 | 19.6112 | -114.1687 | -25.4789 | 0 | 71.7451 | 251.7451 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.5386 | 131.5386 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7173 | 21 | 6.6 | 0 | 0 | 0 | 0 | 0 | 299 | 7173 | 1260 | 294.9041 | -12.3873 | 2.3907 | 1234.284 | 20.6112 | -129.1687 | -35.3656 | 0 | 71.7451 | 251.7451 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2548 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7174 | 22 | 6.7 | 0 | 0 | 0 | 0 | 0 | 299 | 7174 | 1320 | 294.9041 | -12.3873 | 2.3907 | 1294.284 | 21.6112 | -144.1687 | -44.316 | 0 | 71.7451 | 251.7451 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0472 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7175 | 23 | 6.7 | 0 | 0 | 0 | 0 | 0 | 299 | 7175 | 1380 | 294.9041 | -12.3873 | 2.3907 | 1354.284 | 22.6112 | -159.1687 | -51.3964 | 0 | 71.7451 | 251.7451 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7996 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
10 | 299 | 26 | 7176 | 24 | 6.3 | 0 | 0 | 0 | 0 | 0 | 299 | 7176 | 1440 | 294.9041 | -12.3873 | 2.3907 | 1414.284 | 23.6112 | -174.1687 | -55.2597 | 0 | 71.7451 | 251.7451 | 77.203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1616 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7177 | 1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 300 | 7177 | 60 | 295.8904 | -12.7375 | 2.5728 | 34.284 | 0.61428 | 170.7858 | -55.0871 | 0 | 71.2187 | 108.7813 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8323 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7178 | 2 | 5.1 | 0 | 0 | 0 | 0 | 0 | 300 | 7178 | 120 | 295.8904 | -12.7375 | 2.5728 | 94.284 | 1.6143 | 155.7858 | -50.3425 | 0 | 71.2187 | 108.7813 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0615 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7179 | 3 | 3.4 | 0 | 0 | 0 | 0 | 0 | 300 | 7179 | 180 | 295.8904 | -12.7375 | 2.5728 | 154.284 | 2.6143 | 140.7858 | -42.7036 | 0 | 71.2187 | 108.7813 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4244 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7180 | 4 | 3.8 | 0 | 0 | 0 | 0 | 0 | 300 | 7180 | 240 | 295.8904 | -12.7375 | 2.5728 | 214.284 | 3.6143 | 125.7858 | -33.4542 | 0 | 71.2187 | 108.7813 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.8148 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7181 | 5 | 2.9 | 0 | 0 | 0 | 0 | 0 | 300 | 7181 | 300 | 295.8904 | -12.7375 | 2.5728 | 274.284 | 4.6143 | 110.7858 | -23.4355 | 0 | 71.2187 | 108.7813 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4123 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7182 | 6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 300 | 7182 | 360 | 295.8904 | -12.7375 | 2.5728 | 334.284 | 5.6143 | 95.7858 | -13.1798 | 0 | 71.2187 | 108.7813 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9193 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7183 | 7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 300 | 7183 | 420 | 295.8904 | -12.7375 | 2.5728 | 394.284 | 6.6143 | 80.7858 | -3.0788 | 0 | 71.2187 | 108.7813 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.8389 | 145.8389 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7184 | 8 | 1.7 | 0 | 3.67 | 3.67 | 3.67 | 1.84 | 300 | 7184 | 480 | 295.8904 | -12.7375 | 2.5728 | 454.284 | 7.6143 | 65.7858 | 6.5056 | 6.5056 | 63.552 | 116.448 | 66.8573 | 0 | 0 | 3.1325 | 3.1325 | -49.4043 | 0% | 1.4165 | 0 | 0 | 148.8486 | 148.8486 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7185 | 9 | 2.6 | 18.75 | 33.94 | 52.69 | 33.94 | 16.97 | 300 | 7185 | 540 | 295.8904 | -12.7375 | 2.5728 | 514.284 | 8.6143 | 50.7858 | 15.1673 | 15.1673 | 51.5357 | 128.4643 | 52.4448 | 43.6808 | 43.6808 | 28.9696 | 72.6504 | -1.3307 | 0% | 32.8525 | 0 | 0 | 133.1104 | 133.1104 | 0% | 12.05% | 12.05% | 80% | 9.638% | 3.1665 | 9.4339 | 6 | 18.9989 | 7.0024 | 14.27% | 14.27%
10 | 300 | 27 | 7186 | 10 | 5.2 | 54.94 | 94.44 | 149.38 | 94.44 | 47.22 | 300 | 7186 | 600 | 295.8904 | -12.7375 | 2.5728 | 574.284 | 9.6143 | 35.7858 | 22.4079 | 22.4079 | 38.0937 | 141.9063 | 38.3696 | 112.9972 | 112.9972 | 80.6096 | 193.6068 | 0.035433 | 3.543% | 87.549 | 3.1021 | 2.1715 | 141.6072 | 141.6072 | 1.533% | 11.85% | 11.85% | 80% | 9.476% | 8.2966 | 8.6282 | 6 | 49.7794 | 18.3471 | 35.15% | 35.15%
10 | 300 | 27 | 7187 | 11 | 6.7 | 98.33 | 123.56 | 221.89 | 123.56 | 61.78 | 300 | 7187 | 660 | 295.8904 | -12.7375 | 2.5728 | 634.284 | 10.6143 | 20.7858 | 27.6345 | 27.6345 | 22.9988 | 157.0012 | 25.2271 | 191.7772 | 191.7772 | 105.4651 | 297.2423 | 0.31546 | 31.55% | 134.413 | 42.4014 | 29.681 | 123.0534 | 123.0534 | 24.12% | 11.72% | 11.72% | 80% | 9.376% | 12.6023 | 8.1849 | 6 | 75.6139 | 27.8689 | 61.45% | 61.45%
10 | 300 | 27 | 7188 | 12 | 8.5 | 162.17 | 114.5 | 276.67 | 114.5 | 57.25 | 300 | 7188 | 720 | 295.8904 | -12.7375 | 2.5728 | 694.284 | 11.6143 | 5.7858 | 30.2585 | 30.2585 | 6.5366 | 173.4634 | 15.6105 | 309.9572 | 309.9572 | 97.7319 | 407.689 | 0.45826 | 45.83% | 184.357 | 84.4831 | 59.1382 | 122.9267 | 122.9267 | 48.11% | 11.6% | 11.6% | 85% | 9.86% | 18.1778 | 7.6737 | 6 | 109.0669 | 40.1986 | 88.73% | 88.73%
10 | 300 | 27 | 7189 | 13 | 9.7 | 148.56 | 153.47 | 302.03 | 153.47 | 76.74 | 300 | 7189 | 780 | 295.8904 | -12.7375 | 2.5728 | 754.284 | 12.6143 | -9.2142 | 29.9131 | 29.9131 | 10.3808 | 190.3808 | 17.157 | 284.6463 | 284.6463 | 130.9948 | 415.6411 | 0.47165 | 47.16% | 187.9529 | 88.6479 | 62.0535 | 124.8856 | 124.8856 | 49.69% | 11.57% | 11.57% | 85% | 9.834% | 18.4838 | 7.3455 | 6 | 110.9029 | 40.8753 | 88.8% | 88.8%
10 | 300 | 27 | 7190 | 14 | 9.6 | 108.47 | 159.22 | 267.69 | 159.22 | 79.61 | 300 | 7190 | 840 | 295.8904 | -12.7375 | 2.5728 | 814.284 | 13.6143 | -24.2142 | 26.6498 | 26.6498 | 26.5903 | 206.5903 | 28.0784 | 213.369 | 213.369 | 135.9028 | 349.2718 | 0.40783 | 40.78% | 157.9407 | 64.4122 | 45.0886 | 122.9945 | 122.9945 | 36.66% | 11.61% | 11.61% | 85% | 9.868% | 15.5861 | 7.3724 | 6 | 93.5168 | 34.4673 | 76.03% | 76.03%
10 | 300 | 27 | 7191 | 15 | 9.6 | 88.28 | 100.5 | 188.78 | 100.5 | 50.25 | 300 | 7191 | 900 | 295.8904 | -12.7375 | 2.5728 | 874.284 | 14.6143 | -39.2142 | 20.908 | 20.908 | 41.3097 | 221.3097 | 41.538 | 185.163 | 185.163 | 85.7821 | 270.9451 | 0.2933 | 29.33% | 122.5214 | 35.9351 | 25.1546 | 117.5156 | 117.5156 | 21.41% | 11.65% | 11.65% | 80% | 9.324% | 11.4235 | 7.3724 | 6 | 68.5411 | 25.2621 | 58.33% | 58.33%
10 | 300 | 27 | 7192 | 16 | 8.7 | 93.56 | 95.42 | 188.98 | 95.42 | 47.71 | 300 | 7192 | 960 | 295.8904 | -12.7375 | 2.5728 | 934.284 | 15.6143 | -54.2142 | 13.2931 | 13.2931 | 54.393 | 234.393 | 55.7191 | 229.1869 | 229.1869 | 81.4461 | 310.633 | 0.35175 | 35.17% | 140.4682 | 49.4094 | 34.5866 | 115.5493 | 115.5493 | 29.93% | 11.66% | 0% | 85% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7193 | 17 | 8.3 | 35.5 | 58.39 | 93.89 | 58.39 | 29.2 | 300 | 7193 | 1020 | 295.8904 | -12.7375 | 2.5728 | 994.284 | 16.6143 | -69.2142 | 4.3804 | 4.3804 | 66.1458 | 246.1458 | 70.1759 | 0 | 0 | 49.839 | 49.839 | -2.0337 | 0% | 22.5372 | 0 | 0 | 150.3175 | 150.3175 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7194 | 18 | 7.6 | 0 | 9.39 | 9.39 | 9.39 | 4.7 | 300 | 7194 | 1080 | 295.8904 | -12.7375 | 2.5728 | 1054.284 | 17.6143 | -84.2142 | -5.3552 | 0 | 71.2187 | 251.2187 | 76.8408 | 0 | 0 | 8.0149 | 8.0149 | -17.0478 | 0% | 3.6243 | 0 | 0 | 141.3143 | 141.3143 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7195 | 19 | 6.1 | 0 | 0 | 0 | 0 | 0 | 300 | 7195 | 1140 | 295.8904 | -12.7375 | 2.5728 | 1114.284 | 18.6143 | -99.2142 | -15.5232 | 0 | 71.2187 | 251.2187 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.5536 | 135.5536 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7196 | 20 | 5.7 | 0 | 0 | 0 | 0 | 0 | 300 | 7196 | 1200 | 295.8904 | -12.7375 | 2.5728 | 1174.284 | 19.6143 | -114.2142 | -25.7622 | 0 | 71.2187 | 251.2187 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.8754 | 130.8754 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7197 | 21 | 4.4 | 0 | 0 | 0 | 0 | 0 | 300 | 7197 | 1260 | 295.8904 | -12.7375 | 2.5728 | 1234.284 | 20.6143 | -129.2142 | -35.6601 | 0 | 71.2187 | 251.2187 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.1162 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7198 | 22 | 3.4 | 0 | 0 | 0 | 0 | 0 | 300 | 7198 | 1320 | 295.8904 | -12.7375 | 2.5728 | 1294.284 | 21.6143 | -144.2142 | -44.6307 | 0 | 71.2187 | 251.2187 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.564 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7199 | 23 | 2.5 | 0 | 0 | 0 | 0 | 0 | 300 | 7199 | 1380 | 295.8904 | -12.7375 | 2.5728 | 1354.284 | 22.6143 | -159.2142 | -51.7361 | 0 | 71.2187 | 251.2187 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7076 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
10 | 300 | 27 | 7200 | 24 | 3.1 | 0 | 0 | 0 | 0 | 0 | 300 | 7200 | 1440 | 295.8904 | -12.7375 | 2.5728 | 1414.284 | 23.6143 | -174.2142 | -55.6128 | 0 | 71.2187 | 251.2187 | 76.8408 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5653 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7201 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 301 | 7201 | 60 | 296.8767 | -13.084 | 2.7459 | 34.284 | 0.61716 | 170.7425 | -55.419 | 0 | 70.6969 | 109.3031 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.4021 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7202 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 301 | 7202 | 120 | 296.8767 | -13.084 | 2.7459 | 94.284 | 1.6172 | 155.7425 | -50.6347 | 0 | 70.6969 | 109.3031 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.1026 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7203 | 3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 301 | 7203 | 180 | 296.8767 | -13.084 | 2.7459 | 154.284 | 2.6172 | 140.7425 | -42.9583 | 0 | 70.6969 | 109.3031 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.6507 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7204 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 301 | 7204 | 240 | 296.8767 | -13.084 | 2.7459 | 214.284 | 3.6172 | 125.7425 | -33.6843 | 0 | 70.6969 | 109.3031 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8887 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7205 | 5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 301 | 7205 | 300 | 296.8767 | -13.084 | 2.7459 | 274.284 | 4.6172 | 110.7425 | -23.654 | 0 | 70.6969 | 109.3031 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.159 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7206 | 6 | 2.2 | 0 | 0 | 0 | 0 | 0 | 301 | 7206 | 360 | 296.8767 | -13.084 | 2.7459 | 334.284 | 5.6172 | 95.7425 | -13.3977 | 0 | 70.6969 | 109.3031 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.672 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7207 | 7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 301 | 7207 | 420 | 296.8767 | -13.084 | 2.7459 | 394.284 | 6.6172 | 80.7425 | -3.3052 | 0 | 70.6969 | 109.3031 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.2444 | 143.2444 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7208 | 8 | 3.3 | 0 | 5.5 | 5.5 | 5.5 | 2.75 | 301 | 7208 | 480 | 296.8767 | -13.084 | 2.7459 | 454.284 | 7.6172 | 65.7425 | 6.2625 | 6.2625 | 63.2999 | 116.7001 | 66.8615 | 0 | 0 | 4.6945 | 4.6945 | -31.8686 | 0% | 2.1229 | 0 | 0 | 148.7141 | 148.7141 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7209 | 9 | 4.3 | 5.22 | 51.89 | 57.11 | 51.89 | 25.95 | 301 | 7209 | 540 | 296.8767 | -13.084 | 2.7459 | 514.284 | 8.6172 | 50.7425 | 14.9009 | 14.9009 | 51.3021 | 128.6979 | 52.4786 | 12.3636 | 12.3636 | 44.2909 | 56.6545 | -1.8607 | 0% | 25.6192 | 0 | 0 | 132.8548 | 132.8548 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7210 | 10 | 5.8 | 50.28 | 95 | 145.28 | 95 | 47.5 | 301 | 7210 | 600 | 296.8767 | -13.084 | 2.7459 | 574.284 | 9.6172 | 35.7425 | 22.1137 | 22.1137 | 37.8907 | 142.1093 | 38.4479 | 104.6048 | 104.6048 | 81.0876 | 185.6924 | 0.010415 | 1.041% | 83.9701 | 0.87454 | 0.61218 | 139.9848 | 139.9848 | 0.4373% | 11.83% | 11.83% | 80% | 9.465% | 7.9481 | 8.449 | 6 | 47.6887 | 17.5766 | 34.07% | 34.07%
10 | 301 | 28 | 7211 | 11 | 8.4 | 91.94 | 142.5 | 234.44 | 142.5 | 71.25 | 301 | 7211 | 660 | 296.8767 | -13.084 | 2.7459 | 634.284 | 10.6172 | 20.7425 | 27.3127 | 27.3127 | 22.8463 | 157.1537 | 25.3859 | 181.0241 | 181.0241 | 121.6314 | 302.6555 | 0.33749 | 33.75% | 136.8608 | 46.1897 | 32.3328 | 124.204 | 124.204 | 26.03% | 11.67% | 11.67% | 85% | 9.919% | 13.5751 | 7.7015 | 6 | 81.4506 | 30.0201 | 65.58% | 65.58%
10 | 301 | 28 | 7212 | 12 | 11.3 | 154.03 | 157.92 | 311.95 | 157.92 | 78.96 | 301 | 7212 | 720 | 296.8767 | -13.084 | 2.7459 | 694.284 | 11.6172 | 5.7425 | 29.9164 | 29.9164 | 6.4562 | 173.5438 | 15.9169 | 296.9997 | 296.9997 | 134.7932 | 431.7928 | 0.49271 | 49.27% | 195.2567 | 96.2047 | 67.3433 | 127.1776 | 127.1776 | 52.95% | 11.53% | 11.53% | 85% | 9.799% | 19.1331 | 6.9236 | 6 | 114.7987 | 42.3112 | 90.27% | 90.27%
10 | 301 | 28 | 7213 | 13 | 12.4 | 181.06 | 147.83 | 328.89 | 147.83 | 73.92 | 301 | 7213 | 780 | 296.8767 | -13.084 | 2.7459 | 754.284 | 12.6172 | -9.2575 | 29.564 | 29.564 | 10.3785 | 190.3785 | 17.4716 | 350.0372 | 350.0372 | 126.1808 | 476.218 | 0.52708 | 52.71% | 215.3458 | 113.5055 | 79.4538 | 128.4357 | 128.4357 | 61.86% | 11.49% | 11.49% | 85% | 9.764% | 21.0269 | 6.6439 | 6 | 126.1613 | 46.4991 | 98.23% | 98.23%
10 | 301 | 28 | 7214 | 14 | 13.7 | 164.5 | 135.56 | 300.06 | 135.56 | 67.78 | 301 | 7214 | 840 | 296.8767 | -13.084 | 2.7459 | 814.284 | 13.6172 | -24.2575 | 26.3076 | 26.3076 | 26.5134 | 206.5134 | 28.2866 | 326.8508 | 326.8508 | 115.7077 | 442.5585 | 0.51276 | 51.28% | 200.1249 | 102.6165 | 71.8316 | 128.9837 | 128.9837 | 55.69% | 11.48% | 11.48% | 85% | 9.754% | 19.5211 | 6.3243 | 6 | 117.1268 | 43.1693 | 90.81% | 90.81%
10 | 301 | 28 | 7215 | 15 | 14 | 136.33 | 113.28 | 249.61 | 113.28 | 56.64 | 301 | 7215 | 900 | 296.8767 | -13.084 | 2.7459 | 874.284 | 14.6172 | -39.2575 | 20.5814 | 20.5814 | 41.1781 | 221.1781 | 41.6842 | 289.6249 | 289.6249 | 96.6905 | 386.3154 | 0.47213 | 47.21% | 174.6918 | 82.4781 | 57.7346 | 125.5042 | 125.5042 | 46% | 11.49% | 11.49% | 85% | 9.765% | 17.0591 | 6.2522 | 6 | 102.3544 | 37.7246 | 81.55% | 81.55%
10 | 301 | 28 | 7216 | 16 | 13.9 | 91.94 | 82.64 | 174.58 | 82.64 | 41.32 | 301 | 7216 | 960 | 296.8767 | -13.084 | 2.7459 | 934.284 | 15.6172 | -54.2575 | 12.9845 | 12.9845 | 54.2255 | 234.2255 | 55.8279 | 229.8342 | 229.8342 | 70.5377 | 300.3718 | 0.37642 | 37.64% | 135.8281 | 51.1285 | 35.7899 | 121.0699 | 121.0699 | 29.56% | 11.52% | 0% | 85% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7217 | 17 | 13 | 21.72 | 47.78 | 69.5 | 47.78 | 23.89 | 301 | 7217 | 1020 | 296.8767 | -13.084 | 2.7459 | 994.284 | 16.6172 | -69.2575 | 4.0877 | 4.0877 | 65.9551 | 245.9551 | 70.258 | 0 | 0 | 40.7828 | 40.7828 | -2.3957 | 0% | 18.442 | 0 | 0 | 154.1302 | 154.1302 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4949 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7218 | 18 | 12 | 0 | 12.03 | 12.03 | 12.03 | 6.02 | 301 | 7218 | 1080 | 296.8767 | -13.084 | 2.7459 | 1054.284 | 17.6172 | -84.2575 | -5.6367 | 0 | 70.6969 | 250.6969 | 76.4824 | 0 | 0 | 10.2682 | 10.2682 | -12.1285 | 0% | 4.6433 | 0 | 0 | 146.3589 | 146.3589 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7219 | 19 | 12.1 | 0 | 0 | 0 | 0 | 0 | 301 | 7219 | 1140 | 296.8767 | -13.084 | 2.7459 | 1114.284 | 18.6172 | -99.2575 | -15.7996 | 0 | 70.6969 | 250.6969 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.9106 | 142.9106 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7220 | 20 | 11.8 | 0 | 0 | 0 | 0 | 0 | 301 | 7220 | 1200 | 296.8767 | -13.084 | 2.7459 | 1174.284 | 19.6172 | -114.2575 | -26.0409 | 0 | 70.6969 | 250.6969 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.4279 | 138.4279 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7221 | 21 | 11.8 | 0 | 0 | 0 | 0 | 0 | 301 | 7221 | 1260 | 296.8767 | -13.084 | 2.7459 | 1234.284 | 20.6172 | -129.2575 | -35.9498 | 0 | 70.6969 | 250.6969 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.5786 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7222 | 22 | 11.1 | 0 | 0 | 0 | 0 | 0 | 301 | 7222 | 1320 | 296.8767 | -13.084 | 2.7459 | 1294.284 | 21.6172 | -144.2575 | -44.9407 | 0 | 70.6969 | 250.6969 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5658 | 0 | 0% | 11.74% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7223 | 23 | 10.3 | 0 | 0 | 0 | 0 | 0 | 301 | 7223 | 1380 | 296.8767 | -13.084 | 2.7459 | 1354.284 | 22.6172 | -159.2575 | -52.0712 | 0 | 70.6969 | 250.6969 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5711 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
10 | 301 | 28 | 7224 | 24 | 9.9 | 0 | 0 | 0 | 0 | 0 | 301 | 7224 | 1440 | 296.8767 | -13.084 | 2.7459 | 1414.284 | 23.6172 | -174.2575 | -55.9618 | 0 | 70.6969 | 250.6969 | 76.4824 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9668 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.2918 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7225 | 1 | 10.7 | 0 | 0 | 0 | 0 | 0 | 302 | 7225 | 60 | 297.863 | -13.4267 | 2.9096 | 34.284 | 0.61989 | 170.7016 | -55.7472 | 0 | 70.1801 | 109.8199 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.9929 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0797 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7226 | 2 | 9.6 | 0 | 0 | 0 | 0 | 0 | 302 | 7226 | 120 | 297.863 | -13.4267 | 2.9096 | 94.284 | 1.6199 | 155.7016 | -50.9238 | 0 | 70.1801 | 109.8199 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.4346 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7227 | 3 | 9 | 0 | 0 | 0 | 0 | 0 | 302 | 7227 | 180 | 297.863 | -13.4267 | 2.9096 | 154.284 | 2.6199 | 140.7016 | -43.2104 | 0 | 70.1801 | 109.8199 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1143 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7228 | 4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 302 | 7228 | 240 | 297.863 | -13.4267 | 2.9096 | 214.284 | 3.6199 | 125.7016 | -33.9123 | 0 | 70.1801 | 109.8199 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4191 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7229 | 5 | 13.9 | 0 | 0 | 0 | 0 | 0 | 302 | 7229 | 300 | 297.863 | -13.4267 | 2.9096 | 274.284 | 4.6199 | 110.7016 | -23.8709 | 0 | 70.1801 | 109.8199 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.3404 | 0 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7230 | 6 | 13.9 | 0 | 0 | 0 | 0 | 0 | 302 | 7230 | 360 | 297.863 | -13.4267 | 2.9096 | 334.284 | 5.6199 | 95.7016 | -13.6142 | 0 | 70.1801 | 109.8199 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.2887 | 3.2887 | 0% | 11.62% | 0% | 80% | 0% | 0 | 6.2762 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7231 | 7 | 13.5 | 0 | 0 | 0 | 0 | 0 | 302 | 7231 | 420 | 297.863 | -13.4267 | 2.9096 | 394.284 | 6.6199 | 80.7016 | -3.5304 | 0 | 70.1801 | 109.8199 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 156.6441 | 156.6441 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7232 | 8 | 12.5 | 0 | 4.5 | 4.5 | 4.5 | 2.25 | 302 | 7232 | 480 | 297.863 | -13.4267 | 2.9096 | 454.284 | 7.6199 | 65.7016 | 6.0209 | 6.0209 | 63.0524 | 116.9476 | 66.8684 | 0 | 0 | 3.841 | 3.841 | -33.4689 | 0% | 1.7369 | 0 | 0 | 159.1647 | 159.1647 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6189 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7233 | 9 | 12.2 | 20.69 | 36.89 | 57.58 | 36.89 | 18.45 | 302 | 7233 | 540 | 297.863 | -13.4267 | 2.9096 | 514.284 | 8.6199 | 50.7016 | 14.6362 | 14.6362 | 51.0734 | 128.9266 | 52.5155 | 49.8291 | 49.8291 | 31.4876 | 81.3167 | -0.82338 | 0% | 36.7714 | 0 | 0 | 141.6923 | 141.6923 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7234 | 10 | 12.4 | 50.97 | 79.22 | 130.19 | 79.22 | 39.61 | 302 | 7234 | 600 | 297.863 | -13.4267 | 2.9096 | 574.284 | 9.6199 | 35.7016 | 21.8217 | 21.8217 | 37.6927 | 142.3073 | 38.5296 | 107.2668 | 107.2668 | 67.6185 | 174.8853 | 0.049951 | 4.995% | 79.0832 | 3.9503 | 2.7652 | 144.7257 | 144.7257 | 1.911% | 11.61% | 11.61% | 80% | 9.291% | 7.3473 | 6.6439 | 6 | 44.084 | 16.248 | 30.46% | 30.46%
10 | 302 | 29 | 7235 | 11 | 14.1 | 98.47 | 84.72 | 183.19 | 84.72 | 42.36 | 302 | 7235 | 660 | 297.863 | -13.4267 | 2.9096 | 634.284 | 10.6199 | 20.7016 | 26.9939 | 26.9939 | 22.6983 | 157.3017 | 25.548 | 195.7324 | 195.7324 | 72.313 | 268.0455 | 0.32656 | 32.66% | 121.2102 | 39.5819 | 27.7074 | 146.4608 | 146.4608 | 18.92% | 11.52% | 11.52% | 80% | 9.22% | 11.1752 | 6.2283 | 6 | 67.0512 | 24.713 | 45.78% | 45.78%
10 | 302 | 29 | 7236 | 12 | 14.5 | 100 | 122.17 | 222.17 | 122.17 | 61.09 | 302 | 7236 | 720 | 297.863 | -13.4267 | 2.9096 | 694.284 | 11.6199 | 5.7016 | 29.578 | 29.578 | 6.3794 | 173.6206 | 16.2222 | 194.524 | 194.524 | 104.2786 | 298.8026 | 0.37875 | 37.88% | 135.1185 | 51.1762 | 35.8233 | 122.65 | 122.65 | 29.21% | 11.5% | 11.5% | 80% | 9.203% | 12.4348 | 6.1335 | 6 | 74.6089 | 27.4985 | 60.83% | 60.83%
10 | 302 | 29 | 7237 | 13 | 14 | 67.36 | 147.64 | 215 | 147.64 | 73.82 | 302 | 7237 | 780 | 297.863 | -13.4267 | 2.9096 | 754.284 | 12.6199 | -9.2984 | 29.2191 | 29.2191 | 10.374 | 190.374 | 17.7829 | 131.3971 | 131.3971 | 126.0186 | 257.4157 | 0.30595 | 30.6% | 116.4034 | 35.6142 | 24.9299 | 120.5391 | 120.5391 | 20.68% | 11.53% | 11.53% | 80% | 9.225% | 10.738 | 6.2522 | 6 | 64.4282 | 23.7462 | 53.45% | 53.45%
10 | 302 | 29 | 7238 | 14 | 15 | 14.39 | 146.67 | 161.06 | 146.67 | 73.34 | 302 | 7238 | 840 | 297.863 | -13.4267 | 2.9096 | 814.284 | 13.6199 | -24.2984 | 25.9697 | 25.9697 | 26.4358 | 206.4358 | 28.4933 | 28.8813 | 28.8813 | 125.1907 | 154.0719 | -0.013346 | 0% | 69.6713 | 0 | 0 | 140.0607 | 140.0607 | 0% | 11.53% | 11.53% | 80% | 9.224% | 6.4263 | 6.0165 | 6 | 38.5577 | 14.2111 | 27.53% | 27.53%
10 | 302 | 29 | 7239 | 15 | 15.1 | 20.42 | 124.03 | 144.45 | 124.03 | 62.02 | 302 | 7239 | 900 | 297.863 | -13.4267 | 2.9096 | 874.284 | 14.6199 | -39.2984 | 20.2592 | 20.2592 | 41.0466 | 221.0466 | 41.8289 | 43.9422 | 43.9422 | 105.8662 | 149.8084 | -0.035094 | 0% | 67.7434 | 0 | 0 | 158.5433 | 158.5433 | 0% | 11.53% | 11.53% | 80% | 9.222% | 6.2471 | 5.9933 | 5.9933 | 37.4411 | 13.815 | 23.62% | 23.62%
10 | 302 | 29 | 7240 | 16 | 14.8 | 55.22 | 91.25 | 146.47 | 91.25 | 45.63 | 302 | 7240 | 960 | 297.863 | -13.4267 | 2.9096 | 934.284 | 15.6199 | -54.2984 | 12.6803 | 12.6803 | 54.0586 | 234.0586 | 55.9348 | 140.9072 | 140.9072 | 77.8867 | 218.7939 | 0.22636 | 22.64% | 98.9386 | 22.3959 | 15.6771 | 157.447 | 157.447 | 9.957% | 11.52% | 0% | 80% | 0% | 0 | 6.0631 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7241 | 17 | 12.9 | 21.39 | 43.06 | 64.45 | 43.06 | 21.53 | 302 | 7241 | 1020 | 297.863 | -13.4267 | 2.9096 | 994.284 | 16.6199 | -69.2984 | 3.7995 | 3.7995 | 65.7652 | 245.7652 | 70.3381 | 0 | 0 | 36.754 | 36.754 | -2.7527 | 0% | 16.6202 | 0 | 0 | 148.9499 | 148.9499 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7242 | 18 | 12.4 | 0 | 8.11 | 8.11 | 8.11 | 4.06 | 302 | 7242 | 1080 | 297.863 | -13.4267 | 2.9096 | 1054.284 | 17.6199 | -84.2984 | -5.9137 | 0 | 70.1801 | 250.1801 | 76.1279 | 0 | 0 | 6.9223 | 6.9223 | -18.2463 | 0% | 3.1303 | 0 | 0 | 142.5364 | 142.5364 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7243 | 19 | 11.9 | 0 | 0 | 0 | 0 | 0 | 302 | 7243 | 1140 | 297.863 | -13.4267 | 2.9096 | 1114.284 | 18.6199 | -99.2984 | -16.0713 | 0 | 70.1801 | 250.1801 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.0419 | 139.0419 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7244 | 20 | 11.9 | 0 | 0 | 0 | 0 | 0 | 302 | 7244 | 1200 | 297.863 | -13.4267 | 2.9096 | 1174.284 | 19.6199 | -114.2984 | -26.3148 | 0 | 70.1801 | 250.1801 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.6933 | 135.6933 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7245 | 21 | 11.9 | 0 | 0 | 0 | 0 | 0 | 302 | 7245 | 1260 | 297.863 | -13.4267 | 2.9096 | 1234.284 | 20.6199 | -129.2984 | -36.2346 | 0 | 70.1801 | 250.1801 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1194 | 0 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7246 | 22 | 11.3 | 0 | 0 | 0 | 0 | 0 | 302 | 7246 | 1320 | 297.863 | -13.4267 | 2.9096 | 1294.284 | 21.6199 | -144.2984 | -45.2456 | 0 | 70.1801 | 250.1801 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7826 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7247 | 23 | 11.6 | 0 | 0 | 0 | 0 | 0 | 302 | 7247 | 1380 | 297.863 | -13.4267 | 2.9096 | 1354.284 | 22.6199 | -159.2984 | -52.4017 | 0 | 70.1801 | 250.1801 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0907 | 0 | 0% | 11.72% | 0% | 80% | 0% | 0 | 6.8464 | 6 | 0 | 0 | 0% | 0%
10 | 302 | 29 | 7248 | 24 | 9.4 | 0 | 0 | 0 | 0 | 0 | 302 | 7248 | 1440 | 297.863 | -13.4267 | 2.9096 | 1414.284 | 23.6199 | -174.2984 | -56.3068 | 0 | 70.1801 | 250.1801 | 76.1279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2088 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7249 | 1 | 8.9 | 0 | 0 | 0 | 0 | 0 | 303 | 7249 | 60 | 298.8493 | -13.7653 | 3.0638 | 34.284 | 0.62246 | 170.6631 | -56.0718 | 0 | 69.6683 | 110.3317 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.4244 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7250 | 2 | 8.5 | 0 | 0 | 0 | 0 | 0 | 303 | 7250 | 120 | 298.8493 | -13.7653 | 3.0638 | 94.284 | 1.6225 | 155.6631 | -51.2096 | 0 | 69.6683 | 110.3317 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8773 | 0 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7251 | 3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 303 | 7251 | 180 | 298.8493 | -13.7653 | 3.0638 | 154.284 | 2.6225 | 140.6631 | -43.4599 | 0 | 69.6683 | 110.3317 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2445 | 0 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7252 | 4 | 6.7 | 0 | 0 | 0 | 0 | 0 | 303 | 7252 | 240 | 298.8493 | -13.7653 | 3.0638 | 214.284 | 3.6225 | 125.6631 | -34.1382 | 0 | 69.6683 | 110.3317 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4637 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7253 | 5 | 6.6 | 0 | 0 | 0 | 0 | 0 | 303 | 7253 | 300 | 298.8493 | -13.7653 | 3.0638 | 274.284 | 4.6225 | 110.6631 | -24.086 | 0 | 69.6683 | 110.3317 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.2969 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7254 | 6 | 6.6 | 0 | 0 | 0 | 0 | 0 | 303 | 7254 | 360 | 298.8493 | -13.7653 | 3.0638 | 334.284 | 5.6225 | 95.6631 | -13.8292 | 0 | 69.6683 | 110.3317 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.4716 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7255 | 7 | 6.1 | 0 | 0 | 0 | 0 | 0 | 303 | 7255 | 420 | 298.8493 | -13.7653 | 3.0638 | 394.284 | 6.6225 | 80.6631 | -3.7543 | 0 | 69.6683 | 110.3317 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.6291 | 148.6291 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7256 | 8 | 5.5 | 0 | 3.53 | 3.53 | 3.53 | 1.77 | 303 | 7256 | 480 | 298.8493 | -13.7653 | 3.0638 | 454.284 | 7.6225 | 65.6631 | 5.7806 | 5.7806 | 62.8094 | 117.1906 | 66.878 | 0 | 0 | 3.013 | 3.013 | -48.3425 | 0% | 1.3625 | 0 | 0 | 152.3793 | 152.3793 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7257 | 9 | 6.2 | 12.5 | 24.39 | 36.89 | 24.39 | 12.2 | 303 | 7257 | 540 | 298.8493 | -13.7653 | 3.0638 | 514.284 | 8.6225 | 50.6631 | 14.3732 | 14.3732 | 50.8496 | 129.1504 | 52.5554 | 30.6156 | 30.6156 | 20.8182 | 51.4337 | -2.0425 | 0% | 23.2583 | 0 | 0 | 135.7124 | 135.7124 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7258 | 10 | 7.1 | 44.86 | 67.44 | 112.3 | 67.44 | 33.72 | 303 | 7258 | 600 | 298.8493 | -13.7653 | 3.0638 | 574.284 | 9.6225 | 35.6631 | 21.532 | 21.532 | 37.4996 | 142.5004 | 38.6146 | 95.5037 | 95.5037 | 57.5636 | 153.0674 | -0.1385 | 0% | 69.2171 | 0 | 0 | 141.7837 | 141.7837 | 0% | 11.81% | 11.81% | 80% | 9.449% | 6.5402 | 8.0693 | 6 | 39.2411 | 14.463 | 27.68% | 27.68%
10 | 303 | 30 | 7259 | 11 | 7.4 | 44.86 | 151.39 | 196.25 | 151.39 | 75.7 | 303 | 7259 | 660 | 298.8493 | -13.7653 | 3.0638 | 634.284 | 10.6225 | 20.6631 | 26.678 | 26.678 | 22.555 | 157.445 | 25.7131 | 90.0222 | 90.0222 | 129.2194 | 219.2416 | 0.14923 | 14.92% | 99.1411 | 14.7944 | 10.3561 | 143.7856 | 143.7856 | 7.202% | 11.75% | 11.75% | 80% | 9.404% | 9.3228 | 7.9834 | 6 | 55.9368 | 20.6165 | 38.9% | 38.9%
10 | 303 | 30 | 7260 | 12 | 7.4 | 142.08 | 151.06 | 293.14 | 151.06 | 75.53 | 303 | 7260 | 720 | 298.8493 | -13.7653 | 3.0638 | 694.284 | 11.6225 | 5.6631 | 29.2433 | 29.2433 | 6.3063 | 173.6937 | 16.5262 | 278.8238 | 278.8238 | 128.9378 | 407.7616 | 0.45195 | 45.19% | 184.3898 | 83.3344 | 58.3341 | 123.0131 | 123.0131 | 47.42% | 11.62% | 11.62% | 85% | 9.88% | 18.2182 | 7.9834 | 6 | 109.309 | 40.2879 | 88.86% | 88.86%
10 | 303 | 30 | 7261 | 13 | 7.7 | 203.83 | 145.97 | 349.8 | 145.97 | 72.99 | 303 | 7261 | 780 | 298.8493 | -13.7653 | 3.0638 | 754.284 | 12.6225 | -9.3369 | 28.8784 | 28.8784 | 10.3674 | 190.3674 | 18.0907 | 401.1861 | 401.1861 | 124.5932 | 525.7792 | 0.53232 | 53.23% | 237.7574 | 126.5631 | 88.5942 | 125.5342 | 125.5342 | 70.57% | 11.54% | 11.54% | 90% | 10.38% | 24.6882 | 7.8981 | 6 | 148.1289 | 54.5957 | 118% | 118%
10 | 303 | 30 | 7262 | 14 | 9.5 | 139.94 | 130.97 | 270.91 | 130.97 | 65.49 | 303 | 7262 | 840 | 298.8493 | -13.7653 | 3.0638 | 814.284 | 13.6225 | -24.3369 | 25.6363 | 25.6363 | 26.3575 | 206.3575 | 28.6984 | 283.7109 | 283.7109 | 111.7899 | 395.5008 | 0.45354 | 45.35% | 178.8455 | 81.1138 | 56.7797 | 125.2305 | 125.2305 | 45.34% | 11.59% | 11.59% | 85% | 9.848% | 17.6123 | 7.3995 | 6 | 105.6736 | 38.948 | 84.38% | 84.38%
10 | 303 | 30 | 7263 | 15 | 9.8 | 211.44 | 80.14 | 291.58 | 80.14 | 40.07 | 303 | 7263 | 900 | 298.8493 | -13.7653 | 3.0638 | 874.284 | 14.6225 | -39.3369 | 19.9416 | 19.9416 | 40.9154 | 220.9154 | 41.9719 | 460.9138 | 460.9138 | 68.4038 | 529.3175 | 0.54347 | 54.35% | 239.3574 | 130.0828 | 91.058 | 125.3882 | 125.3882 | 72.62% | 11.5% | 11.5% | 90% | 10.35% | 24.7818 | 7.3186 | 6 | 148.6907 | 54.8027 | 118.6% | 118.6%
10 | 303 | 30 | 7264 | 16 | 9.2 | 158.11 | 80.83 | 238.94 | 80.83 | 40.42 | 303 | 7264 | 960 | 298.8493 | -13.7653 | 3.0638 | 934.284 | 15.6225 | -54.3369 | 12.3807 | 12.3807 | 53.8925 | 233.8925 | 56.0398 | 411.9423 | 411.9423 | 68.9927 | 480.935 | 0.51434 | 51.43% | 217.4788 | 111.8571 | 78.3 | 122.0409 | 122.0409 | 64.16% | 11.54% | 0% | 85% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7265 | 17 | 7.5 | 51.67 | 45.97 | 97.64 | 45.97 | 22.99 | 303 | 7265 | 1020 | 298.8493 | -13.7653 | 3.0638 | 994.284 | 16.6225 | -69.3369 | 3.5157 | 3.5157 | 65.5761 | 245.5761 | 70.416 | 0 | 0 | 39.2378 | 39.2378 | -2.8485 | 0% | 17.7434 | 0 | 0 | 152.0826 | 152.0826 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7266 | 18 | 6.5 | 0 | 10.14 | 10.14 | 10.14 | 5.07 | 303 | 7266 | 1080 | 298.8493 | -13.7653 | 3.0638 | 1054.284 | 17.6225 | -84.3369 | -6.186 | 0 | 69.6683 | 249.6683 | 75.7776 | 0 | 0 | 8.655 | 8.655 | -16.0292 | 0% | 3.9138 | 0 | 0 | 141.163 | 141.163 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7267 | 19 | 5.7 | 0 | 0 | 0 | 0 | 0 | 303 | 7267 | 1140 | 298.8493 | -13.7653 | 3.0638 | 1114.284 | 18.6225 | -99.3369 | -16.3383 | 0 | 69.6683 | 249.6683 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.482 | 135.482 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7268 | 20 | 5.3 | 0 | 0 | 0 | 0 | 0 | 303 | 7268 | 1200 | 298.8493 | -13.7653 | 3.0638 | 1174.284 | 19.6225 | -114.3369 | -26.5837 | 0 | 69.6683 | 249.6683 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.9996 | 129.9996 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7269 | 21 | 3.4 | 0 | 0 | 0 | 0 | 0 | 303 | 7269 | 1260 | 298.8493 | -13.7653 | 3.0638 | 1234.284 | 20.6225 | -129.3369 | -36.5142 | 0 | 69.6683 | 249.6683 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.1483 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7270 | 22 | 3.5 | 0 | 0 | 0 | 0 | 0 | 303 | 7270 | 1320 | 298.8493 | -13.7653 | 3.0638 | 1294.284 | 21.6225 | -144.3369 | -45.5454 | 0 | 69.6683 | 249.6683 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1242 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7271 | 23 | 3.5 | 0 | 0 | 0 | 0 | 0 | 303 | 7271 | 1380 | 298.8493 | -13.7653 | 3.0638 | 1354.284 | 22.6225 | -159.3369 | -52.7273 | 0 | 69.6683 | 249.6683 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9675 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
10 | 303 | 30 | 7272 | 24 | 4.6 | 0 | 0 | 0 | 0 | 0 | 303 | 7272 | 1440 | 298.8493 | -13.7653 | 3.0638 | 1414.284 | 23.6225 | -174.3369 | -56.6475 | 0 | 69.6683 | 249.6683 | 75.7776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1343 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7273 | 1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 304 | 7273 | 60 | 299.8356 | -14.0999 | 3.2083 | 34.284 | 0.62487 | 170.6269 | -56.3925 | 0 | 69.1619 | 110.8381 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2128 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7274 | 2 | 4.4 | 0 | 0 | 0 | 0 | 0 | 304 | 7274 | 120 | 299.8356 | -14.0999 | 3.2083 | 94.284 | 1.6249 | 155.6269 | -51.4921 | 0 | 69.1619 | 110.8381 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4414 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7275 | 3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 304 | 7275 | 180 | 299.8356 | -14.0999 | 3.2083 | 154.284 | 2.6249 | 140.6269 | -43.7066 | 0 | 69.1619 | 110.8381 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1273 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7276 | 4 | 4.7 | 0 | 0 | 0 | 0 | 0 | 304 | 7276 | 240 | 299.8356 | -14.0999 | 3.2083 | 214.284 | 3.6249 | 125.6269 | -34.3619 | 0 | 69.1619 | 110.8381 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3653 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7277 | 5 | 5.2 | 0 | 0 | 0 | 0 | 0 | 304 | 7277 | 300 | 299.8356 | -14.0999 | 3.2083 | 274.284 | 4.6249 | 110.6269 | -24.2995 | 0 | 69.1619 | 110.8381 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.7883 | 1.7883 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7278 | 6 | 5.2 | 0 | 0 | 0 | 0 | 0 | 304 | 7278 | 360 | 299.8356 | -14.0999 | 3.2083 | 334.284 | 5.6249 | 95.6269 | -14.0428 | 0 | 69.1619 | 110.8381 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 12.5173 | 12.5173 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7279 | 7 | 3.7 | 0 | 0 | 0 | 0 | 0 | 304 | 7279 | 420 | 299.8356 | -14.0999 | 3.2083 | 394.284 | 6.6249 | 80.6269 | -3.9766 | 0 | 69.1619 | 110.8381 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 176.8896 | 176.8896 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7280 | 8 | 3 | 0 | 3.47 | 3.47 | 3.47 | 1.74 | 304 | 7280 | 480 | 299.8356 | -14.0999 | 3.2083 | 454.284 | 7.6249 | 65.6269 | 5.542 | 5.542 | 62.5712 | 117.4288 | 66.8903 | 0 | 0 | 2.9618 | 2.9618 | -51.2283 | 0% | 1.3393 | 0 | 0 | 184.7933 | 184.7933 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7281 | 9 | 3.1 | 63.39 | 31.53 | 94.92 | 31.53 | 15.77 | 304 | 7281 | 540 | 299.8356 | -14.0999 | 3.2083 | 514.284 | 8.6249 | 50.6269 | 14.1122 | 14.1122 | 50.6307 | 129.3693 | 52.5982 | 157.9152 | 157.9152 | 26.9125 | 184.8278 | -0.028494 | 0% | 83.5791 | 0 | 0 | 172.2109 | 172.2109 | 0% | 11.92% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7282 | 10 | 3.5 | 172.64 | 51.72 | 224.36 | 51.72 | 25.86 | 304 | 7282 | 600 | 299.8356 | -14.0999 | 3.2083 | 574.284 | 9.6249 | 35.6269 | 21.2448 | 21.2448 | 37.3116 | 142.6884 | 38.7027 | 371.8146 | 371.8146 | 44.1458 | 415.9604 | 0.43642 | 43.64% | 188.0973 | 82.0897 | 57.4628 | 155.4927 | 155.4927 | 36.96% | 11.7% | 11.7% | 85% | 9.945% | 18.7071 | 9.1497 | 6 | 112.2426 | 41.3691 | 72.19% | 72.19%
10 | 304 | 31 | 7283 | 11 | 4.4 | 246.72 | 64.22 | 310.94 | 64.22 | 32.11 | 304 | 7283 | 660 | 299.8356 | -14.0999 | 3.2083 | 634.284 | 10.6249 | 20.6269 | 26.3654 | 26.3654 | 22.4164 | 157.5836 | 25.881 | 499.8369 | 499.8369 | 54.8152 | 554.6521 | 0.53226 | 53.23% | 250.8137 | 133.497 | 93.4479 | 151.5061 | 151.5061 | 61.68% | 11.56% | 11.56% | 90% | 10.41% | 26.1003 | 8.8711 | 6 | 156.6019 | 57.7185 | 103.4% | 103.4%
10 | 304 | 31 | 7284 | 12 | 4.8 | 281.89 | 86.17 | 368.06 | 86.17 | 43.09 | 304 | 7284 | 720 | 299.8356 | -14.0999 | 3.2083 | 694.284 | 11.6249 | 5.6269 | 28.9124 | 28.9124 | 6.2368 | 173.7632 | 16.8284 | 558.0842 | 558.0842 | 73.5507 | 631.6349 | 0.5669 | 56.69% | 285.6253 | 161.921 | 113.3447 | 141.128 | 141.128 | 80.31% | 11.49% | 11.49% | 90% | 10.34% | 29.5436 | 8.7491 | 6 | 177.2615 | 65.333 | 125.6% | 125.6%
10 | 304 | 31 | 7285 | 13 | 6.8 | 254.17 | 132.83 | 387 | 132.83 | 66.42 | 304 | 7285 | 780 | 299.8356 | -14.0999 | 3.2083 | 754.284 | 12.6249 | -9.3731 | 28.5421 | 28.5421 | 10.3586 | 190.3586 | 18.3949 | 504.7728 | 504.7728 | 113.3775 | 618.1503 | 0.56946 | 56.95% | 279.5276 | 159.1811 | 111.4268 | 141.5309 | 141.5309 | 78.73% | 11.48% | 11.48% | 90% | 10.34% | 28.8909 | 8.1559 | 6 | 173.3455 | 63.8897 | 122.5% | 122.5%
10 | 304 | 31 | 7286 | 14 | 7.7 | 183.94 | 115.28 | 299.22 | 115.28 | 57.64 | 304 | 7286 | 840 | 299.8356 | -14.0999 | 3.2083 | 814.284 | 13.6249 | -24.3731 | 25.3076 | 25.3076 | 26.2785 | 206.2785 | 28.9016 | 376.6987 | 376.6987 | 98.3976 | 475.0964 | 0.50334 | 50.33% | 214.8386 | 108.1364 | 75.6955 | 137.4557 | 137.4557 | 55.07% | 11.57% | 11.57% | 85% | 9.836% | 21.1316 | 7.8981 | 6 | 126.7895 | 46.7306 | 92.24% | 92.24%
10 | 304 | 31 | 7287 | 15 | 7.9 | 166.67 | 109.39 | 276.06 | 109.39 | 54.7 | 304 | 7287 | 900 | 299.8356 | -14.0999 | 3.2083 | 874.284 | 14.6249 | -39.3731 | 19.6286 | 19.6286 | 40.7843 | 220.7843 | 42.1131 | 368.0608 | 368.0608 | 93.3702 | 461.431 | 0.49546 | 49.55% | 208.6591 | 103.3819 | 72.3674 | 132.8777 | 132.8777 | 54.46% | 11.58% | 11.58% | 85% | 9.841% | 20.5336 | 7.8416 | 6 | 123.2013 | 45.4081 | 92.72% | 92.72%
10 | 304 | 31 | 7288 | 16 | 7.7 | 141.67 | 74.81 | 216.48 | 74.81 | 37.41 | 304 | 7288 | 960 | 299.8356 | -14.0999 | 3.2083 | 934.284 | 15.6249 | -54.3731 | 12.0857 | 12.0857 | 53.7271 | 233.7271 | 56.1428 | 376.9694 | 376.9694 | 63.8543 | 440.8238 | 0.47996 | 48% | 199.3405 | 95.676 | 66.9732 | 127.7028 | 127.7028 | 52.44% | 11.59% | 0% | 85% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7289 | 17 | 7.17 | 59.72 | 33.89 | 93.61 | 33.89 | 16.95 | 304 | 7289 | 1020 | 299.8356 | -14.0999 | 3.2083 | 994.284 | 16.6249 | -69.3731 | 3.2367 | 3.2367 | 65.3879 | 245.3879 | 70.4916 | 0 | 0 | 28.9269 | 28.9269 | -4.1775 | 0% | 13.0808 | 0 | 0 | 159.2187 | 159.2187 | 0% | 11.9% | 0% | 80% | 0% | 0 | 8.0492 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7290 | 18 | 6.53 | 0 | 5.42 | 5.42 | 5.42 | 2.71 | 304 | 7290 | 1080 | 299.8356 | -14.0999 | 3.2083 | 1054.284 | 17.6249 | -84.3731 | -6.4535 | 0 | 69.1619 | 249.1619 | 75.4314 | 0 | 0 | 4.6263 | 4.6263 | -30.673 | 0% | 2.092 | 0 | 0 | 146.5721 | 146.5721 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2343 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7291 | 19 | 5.91 | 0 | 0 | 0 | 0 | 0 | 304 | 7291 | 1140 | 299.8356 | -14.0999 | 3.2083 | 1114.284 | 18.6249 | -99.3731 | -16.6004 | 0 | 69.1619 | 249.1619 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.6135 | 140.6135 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4164 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7292 | 20 | 5.41 | 0 | 0 | 0 | 0 | 0 | 304 | 7292 | 1200 | 299.8356 | -14.0999 | 3.2083 | 1174.284 | 19.6249 | -114.3731 | -26.8476 | 0 | 69.1619 | 249.1619 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.8631 | 132.8631 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5652 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7293 | 21 | 4.82 | 0 | 0 | 0 | 0 | 0 | 304 | 7293 | 1260 | 299.8356 | -14.0999 | 3.2083 | 1234.284 | 20.6249 | -129.3731 | -36.7887 | 0 | 69.1619 | 249.1619 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7125 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.743 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7294 | 22 | 4.48 | 0 | 0 | 0 | 0 | 0 | 304 | 7294 | 1320 | 299.8356 | -14.0999 | 3.2083 | 1294.284 | 21.6249 | -144.3731 | -45.84 | 0 | 69.1619 | 249.1619 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7955 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8466 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7295 | 23 | 4.17 | 0 | 0 | 0 | 0 | 0 | 304 | 7295 | 1380 | 299.8356 | -14.0999 | 3.2083 | 1354.284 | 22.6249 | -159.3731 | -53.0479 | 0 | 69.1619 | 249.1619 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6489 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9417 | 6 | 0 | 0 | 0% | 0%
10 | 304 | 31 | 7296 | 24 | 5.43 | 0 | 0 | 0 | 0 | 0 | 304 | 7296 | 1440 | 299.8356 | -14.0999 | 3.2083 | 1414.284 | 23.6249 | -174.3731 | -56.9838 | 0 | 69.1619 | 249.1619 | 75.4314 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1097 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5592 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7297 | 1 | 7.06 | 0 | 0 | 0 | 0 | 0 | 305 | 7297 | 60 | 300.8219 | -14.4301 | 3.343 | 34.284 | 0.62712 | 170.5932 | -56.7093 | 0 | 68.6609 | 111.3391 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6209 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0808 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7298 | 2 | 8.14 | 0 | 0 | 0 | 0 | 0 | 305 | 7298 | 120 | 300.8219 | -14.4301 | 3.343 | 94.284 | 1.6271 | 155.5932 | -51.7712 | 0 | 68.6609 | 111.3391 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7114 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7741 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7299 | 3 | 7.37 | 0 | 0 | 0 | 0 | 0 | 305 | 7299 | 180 | 300.8219 | -14.4301 | 3.343 | 154.284 | 2.6271 | 140.5932 | -43.9506 | 0 | 68.6609 | 111.3391 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.6214 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9919 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7300 | 4 | 6.65 | 0 | 0 | 0 | 0 | 0 | 305 | 7300 | 240 | 300.8219 | -14.4301 | 3.343 | 214.284 | 3.6271 | 125.5932 | -34.5835 | 0 | 68.6609 | 111.3391 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7186 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1994 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7301 | 5 | 6.13 | 0 | 0 | 0 | 0 | 0 | 305 | 7301 | 300 | 300.8219 | -14.4301 | 3.343 | 274.284 | 4.6271 | 110.5932 | -24.5111 | 0 | 68.6609 | 111.3391 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1893 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3515 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7302 | 6 | 5.2 | 0 | 0 | 0 | 0 | 0 | 305 | 7302 | 360 | 300.8219 | -14.4301 | 3.343 | 334.284 | 5.6271 | 95.5932 | -14.2548 | 0 | 68.6609 | 111.3391 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9936 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7303 | 7 | 4.37 | 0 | 0 | 0 | 0 | 0 | 305 | 7303 | 420 | 300.8219 | -14.4301 | 3.343 | 394.284 | 6.6271 | 80.5932 | -4.1975 | 0 | 68.6609 | 111.3391 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.6994 | 144.6994 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8803 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7304 | 8 | 4.1 | 0 | 3.61 | 3.61 | 3.61 | 1.81 | 305 | 7304 | 480 | 300.8219 | -14.4301 | 3.343 | 454.284 | 7.6271 | 65.5932 | 5.305 | 5.305 | 62.3378 | 117.6622 | 66.9053 | 0 | 0 | 3.0813 | 3.0813 | -48.346 | 0% | 1.3934 | 0 | 0 | 148.1533 | 148.1533 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7305 | 9 | 6.2 | 19.17 | 27.03 | 46.2 | 27.03 | 13.52 | 305 | 7305 | 540 | 300.8219 | -14.4301 | 3.343 | 514.284 | 8.6271 | 50.5932 | 13.8532 | 13.8532 | 50.4169 | 129.5831 | 52.6439 | 48.5799 | 48.5799 | 23.0715 | 71.6515 | -1.2393 | 0% | 32.4008 | 0 | 0 | 133.7309 | 133.7309 | 0% | 11.9% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7306 | 10 | 8 | 15.56 | 54.81 | 70.37 | 54.81 | 27.41 | 305 | 7306 | 600 | 300.8219 | -14.4301 | 3.343 | 574.284 | 9.6271 | 35.5932 | 20.9602 | 20.9602 | 37.1286 | 142.8714 | 38.7939 | 33.9024 | 33.9024 | 46.7833 | 80.6857 | -0.95758 | 0% | 36.4861 | 0 | 0 | 136.0564 | 136.0564 | 0% | 11.83% | 11.83% | 80% | 9.461% | 3.4521 | 7.8134 | 6 | 20.7126 | 7.634 | 15.22% | 15.22%
11 | 305 | 1 | 7307 | 11 | 9.5 | 63.89 | 82.22 | 146.11 | 82.22 | 41.11 | 305 | 7307 | 660 | 300.8219 | -14.4301 | 3.343 | 634.284 | 10.6271 | 20.5932 | 26.056 | 26.056 | 22.2824 | 157.7176 | 26.0514 | 130.6747 | 130.6747 | 70.1792 | 200.8538 | 0.11391 | 11.39% | 90.8261 | 10.3462 | 7.2424 | 138.5928 | 138.5928 | 5.226% | 11.7% | 11.7% | 80% | 9.358% | 8.4999 | 7.3995 | 6 | 50.9992 | 18.7967 | 36.8% | 36.8%
11 | 305 | 1 | 7308 | 12 | 9.7 | 43.81 | 113.53 | 157.34 | 113.53 | 56.77 | 305 | 7308 | 720 | 300.8219 | -14.4301 | 3.343 | 694.284 | 11.6271 | 5.5932 | 28.5856 | 28.5856 | 6.1709 | 173.8291 | 17.1288 | 87.5012 | 87.5012 | 96.9039 | 184.4051 | 0.054896 | 5.49% | 83.388 | 4.5777 | 3.2044 | 134.113 | 134.113 | 2.389% | 11.7% | 11.7% | 80% | 9.361% | 7.8056 | 7.3455 | 6 | 46.8336 | 17.2614 | 34.92% | 34.92%
11 | 305 | 1 | 7309 | 13 | 12.4 | 39.44 | 159.92 | 199.36 | 159.92 | 79.96 | 305 | 7309 | 780 | 300.8219 | -14.4301 | 3.343 | 754.284 | 12.6271 | -9.4068 | 28.2104 | 28.2104 | 10.3477 | 190.3477 | 18.6952 | 79.0315 | 79.0315 | 136.5003 | 215.5318 | 0.19215 | 19.22% | 97.4635 | 18.7281 | 13.1097 | 138.7964 | 138.7964 | 9.445% | 11.6% | 11.6% | 80% | 9.277% | 9.0417 | 6.6439 | 6 | 54.2504 | 19.995 | 39.09% | 39.09%
11 | 305 | 1 | 7310 | 14 | 14.8 | 34.81 | 157.69 | 192.5 | 157.69 | 78.85 | 305 | 7310 | 840 | 300.8219 | -14.4301 | 3.343 | 814.284 | 13.6271 | -24.4068 | 24.9837 | 24.9837 | 26.1988 | 206.1988 | 29.1026 | 72.0126 | 72.0126 | 134.5968 | 206.6094 | 0.1923 | 19.23% | 93.4288 | 17.9659 | 12.5762 | 141.1566 | 141.1566 | 8.909% | 11.52% | 11.52% | 80% | 9.217% | 8.6117 | 6.0631 | 6 | 51.67 | 19.0439 | 36.6% | 36.6%
11 | 305 | 1 | 7311 | 15 | 13.6 | 21.11 | 115.75 | 136.86 | 115.75 | 57.88 | 305 | 7311 | 900 | 300.8219 | -14.4301 | 3.343 | 874.284 | 14.6271 | -39.4068 | 19.3205 | 19.3205 | 40.6536 | 220.6536 | 42.2523 | 47.228 | 47.228 | 98.7988 | 146.0268 | -0.08021 | 0% | 66.0333 | 0 | 0 | 155.8544 | 155.8544 | 0% | 11.58% | 11.58% | 80% | 9.266% | 6.1185 | 6.3484 | 6 | 36.7109 | 13.5305 | 23.55% | 23.55%
11 | 305 | 1 | 7312 | 16 | 13.6 | 2.78 | 59.81 | 62.59 | 59.81 | 29.91 | 305 | 7312 | 960 | 300.8219 | -14.4301 | 3.343 | 934.284 | 15.6271 | -54.4068 | 11.7956 | 11.7956 | 53.5624 | 233.5624 | 56.2437 | 7.5567 | 7.5567 | 51.051 | 58.6077 | -1.3991 | 0% | 26.5024 | 0 | 0 | 150.8796 | 150.8796 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7313 | 17 | 13.5 | 3.06 | 25.64 | 28.7 | 25.64 | 12.82 | 305 | 7313 | 1020 | 300.8219 | -14.4301 | 3.343 | 994.284 | 16.6271 | -69.4068 | 2.9625 | 2.9625 | 65.2007 | 245.2007 | 70.5649 | 0 | 0 | 21.8851 | 21.8851 | -5.1063 | 0% | 9.8964 | 0 | 0 | 147.6244 | 147.6244 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7314 | 18 | 12.9 | 0 | 6.39 | 6.39 | 6.39 | 3.2 | 305 | 7314 | 1080 | 300.8219 | -14.4301 | 3.343 | 1054.284 | 17.6271 | -84.4068 | -6.7162 | 0 | 68.6609 | 248.6609 | 75.0897 | 0 | 0 | 5.4542 | 5.4542 | -23.1633 | 0% | 2.4664 | 0 | 0 | 143.6907 | 143.6907 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7315 | 19 | 11.8 | 0 | 0 | 0 | 0 | 0 | 305 | 7315 | 1140 | 300.8219 | -14.4301 | 3.343 | 1114.284 | 18.6271 | -99.4068 | -16.8575 | 0 | 68.6609 | 248.6609 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.9335 | 139.9335 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7316 | 20 | 12.2 | 0 | 0 | 0 | 0 | 0 | 305 | 7316 | 1200 | 300.8219 | -14.4301 | 3.343 | 1174.284 | 19.6271 | -114.4068 | -27.1064 | 0 | 68.6609 | 248.6609 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.7085 | 137.7085 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.6941 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7317 | 21 | 12.3 | 0 | 0 | 0 | 0 | 0 | 305 | 7317 | 1260 | 300.8219 | -14.4301 | 3.343 | 1234.284 | 20.6271 | -129.4068 | -37.0578 | 0 | 68.6609 | 248.6609 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.8035 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7318 | 22 | 12.1 | 0 | 0 | 0 | 0 | 0 | 305 | 7318 | 1320 | 300.8219 | -14.4301 | 3.343 | 1294.284 | 21.6271 | -144.4068 | -46.1293 | 0 | 68.6609 | 248.6609 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.7306 | 0 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7193 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7319 | 23 | 10.8 | 0 | 0 | 0 | 0 | 0 | 305 | 7319 | 1380 | 300.8219 | -14.4301 | 3.343 | 1354.284 | 22.6271 | -159.4068 | -53.3634 | 0 | 68.6609 | 248.6609 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.4483 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
11 | 305 | 1 | 7320 | 24 | 10.3 | 0 | 0 | 0 | 0 | 0 | 305 | 7320 | 1440 | 300.8219 | -14.4301 | 3.343 | 1414.284 | 23.6271 | -174.4068 | -57.3156 | 0 | 68.6609 | 248.6609 | 75.0897 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9467 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.1852 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7321 | 1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 306 | 7321 | 60 | 301.8082 | -14.756 | 3.4678 | 34.284 | 0.6292 | 170.562 | -57.0221 | 0 | 68.1656 | 111.8344 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2538 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7322 | 2 | 9.4 | 0 | 0 | 0 | 0 | 0 | 306 | 7322 | 120 | 301.8082 | -14.756 | 3.4678 | 94.284 | 1.6292 | 155.562 | -52.0469 | 0 | 68.1656 | 111.8344 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5427 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7323 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 306 | 7323 | 180 | 301.8082 | -14.756 | 3.4678 | 154.284 | 2.6292 | 140.562 | -44.1917 | 0 | 68.1656 | 111.8344 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2219 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7324 | 4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 306 | 7324 | 240 | 301.8082 | -14.756 | 3.4678 | 214.284 | 3.6292 | 125.562 | -34.8028 | 0 | 68.1656 | 111.8344 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0695 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7325 | 5 | 8.2 | 0 | 0 | 0 | 0 | 0 | 306 | 7325 | 300 | 301.8082 | -14.756 | 3.4678 | 274.284 | 4.6292 | 110.562 | -24.7208 | 0 | 68.1656 | 111.8344 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5043 | 0 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7326 | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 306 | 7326 | 360 | 301.8082 | -14.756 | 3.4678 | 334.284 | 5.6292 | 95.562 | -14.4651 | 0 | 68.1656 | 111.8344 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9269 | 0 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5357 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7327 | 7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 306 | 7327 | 420 | 301.8082 | -14.756 | 3.4678 | 394.284 | 6.6292 | 80.562 | -4.4167 | 0 | 68.1656 | 111.8344 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.4779 | 146.4779 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7328 | 8 | 9.3 | 0 | 1.86 | 1.86 | 1.86 | 0.93 | 306 | 7328 | 480 | 301.8082 | -14.756 | 3.4678 | 454.284 | 7.6292 | 65.562 | 5.0698 | 5.0698 | 62.1093 | 117.8907 | 66.923 | 0 | 0 | 1.5876 | 1.5876 | -86.7964 | 0% | 0.71792 | 0 | 0 | 150.8768 | 150.8768 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7329 | 9 | 11.1 | 0.92 | 26.58 | 27.5 | 26.58 | 13.29 | 306 | 7329 | 540 | 301.8082 | -14.756 | 3.4678 | 514.284 | 8.6292 | 50.562 | 13.5963 | 13.5963 | 50.2081 | 129.7919 | 52.6925 | 2.372 | 2.372 | 22.6874 | 25.0594 | -4.5783 | 0% | 11.3319 | 0 | 0 | 134.983 | 134.983 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9753 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7330 | 10 | 13.9 | 4.17 | 65.64 | 69.81 | 65.64 | 32.82 | 306 | 7330 | 600 | 301.8082 | -14.756 | 3.4678 | 574.284 | 9.6292 | 35.562 | 20.6782 | 20.6782 | 36.9508 | 143.0492 | 38.8879 | 9.1919 | 9.1919 | 56.0272 | 65.2191 | -1.1653 | 0% | 29.4921 | 0 | 0 | 142.4258 | 142.4258 | 0% | 11.6% | 11.6% | 80% | 9.279% | 2.7365 | 6.2762 | 6 | 16.4191 | 6.0516 | 11.53% | 11.53%
11 | 306 | 2 | 7331 | 11 | 18.3 | 74.92 | 122.31 | 197.23 | 122.31 | 61.16 | 306 | 7331 | 660 | 301.8082 | -14.756 | 3.4678 | 634.284 | 10.6292 | 20.562 | 25.7501 | 25.7501 | 22.1531 | 157.8469 | 26.2239 | 154.6997 | 154.6997 | 104.3981 | 259.0978 | 0.34657 | 34.66% | 117.164 | 40.6058 | 28.4241 | 153.5563 | 153.5563 | 18.51% | 11.4% | 11.4% | 80% | 9.122% | 10.6878 | 5.2884 | 5.2884 | 56.5207 | 23.6351 | 36.81% | 36.81%
11 | 306 | 2 | 7332 | 12 | 19.9 | 133.33 | 114.08 | 247.41 | 114.08 | 57.04 | 306 | 7332 | 720 | 301.8082 | -14.756 | 3.4678 | 694.284 | 11.6292 | 5.562 | 28.2629 | 28.2629 | 6.1086 | 173.8914 | 17.4268 | 268.6488 | 268.6488 | 97.3734 | 366.0221 | 0.48987 | 48.99% | 165.5152 | 81.0813 | 56.7569 | 133.3139 | 133.3139 | 42.57% | 11.35% | 11.35% | 85% | 9.651% | 15.9743 | 4.9628 | 4.9628 | 79.2763 | 35.3256 | 59.47% | 59.47%
11 | 306 | 2 | 7333 | 13 | 21.1 | 169.92 | 139.36 | 309.28 | 139.36 | 69.68 | 306 | 7333 | 780 | 301.8082 | -14.756 | 3.4678 | 754.284 | 12.6292 | -9.438 | 27.8833 | 27.8833 | 10.3348 | 190.3348 | 18.9914 | 343.5543 | 343.5543 | 118.9512 | 462.5055 | 0.5611 | 56.11% | 209.145 | 117.3504 | 82.1453 | 137.117 | 137.117 | 59.91% | 11.33% | 11.33% | 85% | 9.632% | 20.1445 | 4.7303 | 4.7303 | 95.2899 | 44.5478 | 69.5% | 69.5%
11 | 306 | 2 | 7334 | 14 | 21.1 | 219.08 | 127.97 | 347.05 | 127.97 | 63.99 | 306 | 7334 | 840 | 301.8082 | -14.756 | 3.4678 | 814.284 | 13.6292 | -24.438 | 24.6646 | 24.6646 | 26.1184 | 206.1184 | 29.3014 | 457.8179 | 457.8179 | 109.2292 | 567.0472 | 0.60588 | 60.59% | 256.4187 | 155.3585 | 108.7509 | 138.7061 | 138.7061 | 78.4% | 11.34% | 11.34% | 90% | 10.2% | 26.1653 | 4.7303 | 4.7303 | 123.7699 | 57.8621 | 89.23% | 89.23%
11 | 306 | 2 | 7335 | 15 | 19.5 | 138.14 | 131.67 | 269.81 | 131.67 | 65.84 | 306 | 7335 | 900 | 301.8082 | -14.756 | 3.4678 | 874.284 | 14.6292 | -39.438 | 19.0173 | 19.0173 | 40.5231 | 220.5231 | 42.3895 | 313.1086 | 313.1086 | 112.3874 | 425.4959 | 0.53171 | 53.17% | 192.4093 | 102.3053 | 71.6137 | 130.9856 | 130.9856 | 54.67% | 11.36% | 11.36% | 85% | 9.658% | 18.5828 | 5.0425 | 5.0425 | 93.7033 | 41.0942 | 71.54% | 71.54%
11 | 306 | 2 | 7336 | 16 | 20 | 93.06 | 95.92 | 188.98 | 95.92 | 47.96 | 306 | 7336 | 960 | 301.8082 | -14.756 | 3.4678 | 934.284 | 15.6292 | -54.438 | 11.5103 | 11.5103 | 53.3985 | 233.3985 | 56.3423 | 258.4717 | 258.4717 | 81.8728 | 340.3445 | 0.46682 | 46.68% | 153.9038 | 71.8453 | 50.2917 | 127.285 | 127.285 | 39.51% | 11.35% | 0% | 85% | 0% | 0 | 4.943 | 4.943 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7337 | 17 | 20.3 | 27.14 | 44.25 | 71.39 | 44.25 | 22.13 | 306 | 7337 | 1020 | 301.8082 | -14.756 | 3.4678 | 994.284 | 16.6292 | -69.438 | 2.6933 | 2.6933 | 65.0144 | 245.0144 | 70.6358 | 0 | 0 | 37.7697 | 37.7697 | -2.2169 | 0% | 17.0795 | 0 | 0 | 161.5885 | 161.5885 | 0% | 11.34% | 0% | 80% | 0% | 0 | 4.8842 | 4.8842 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7338 | 18 | 18.5 | 0 | 6.86 | 6.86 | 6.86 | 3.43 | 306 | 7338 | 1080 | 301.8082 | -14.756 | 3.4678 | 1054.284 | 17.6292 | -84.438 | -6.9739 | 0 | 68.1656 | 248.1656 | 74.7524 | 0 | 0 | 5.8554 | 5.8554 | -19.3611 | 0% | 2.6478 | 0 | 0 | 151.8863 | 151.8863 | 0% | 11.42% | 0% | 80% | 0% | 0 | 5.2467 | 5.2467 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7339 | 19 | 17.9 | 0 | 0 | 0 | 0 | 0 | 306 | 7339 | 1140 | 301.8082 | -14.756 | 3.4678 | 1114.284 | 18.6292 | -99.438 | -17.1095 | 0 | 68.1656 | 248.1656 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.5692 | 147.5692 | 0% | 11.44% | 0% | 80% | 0% | 0 | 5.3726 | 5.3726 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7340 | 20 | 15.9 | 0 | 0 | 0 | 0 | 0 | 306 | 7340 | 1200 | 301.8082 | -14.756 | 3.4678 | 1174.284 | 19.6292 | -114.438 | -27.3599 | 0 | 68.1656 | 248.1656 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.6068 | 140.6068 | 0% | 11.53% | 0% | 80% | 0% | 0 | 5.8104 | 5.8104 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7341 | 21 | 15.1 | 0 | 0 | 0 | 0 | 0 | 306 | 7341 | 1260 | 301.8082 | -14.756 | 3.4678 | 1234.284 | 20.6292 | -129.438 | -37.3215 | 0 | 68.1656 | 248.1656 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.614 | 0 | 0% | 11.57% | 0% | 80% | 0% | 0 | 5.9933 | 5.9933 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7342 | 22 | 13.7 | 0 | 0 | 0 | 0 | 0 | 306 | 7342 | 1320 | 301.8082 | -14.756 | 3.4678 | 1294.284 | 21.6292 | -144.438 | -46.413 | 0 | 68.1656 | 248.1656 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6629 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7343 | 23 | 13.6 | 0 | 0 | 0 | 0 | 0 | 306 | 7343 | 1380 | 301.8082 | -14.756 | 3.4678 | 1354.284 | 22.6292 | -159.438 | -53.6736 | 0 | 68.1656 | 248.1656 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6469 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3484 | 6 | 0 | 0 | 0% | 0%
11 | 306 | 2 | 7344 | 24 | 13.5 | 0 | 0 | 0 | 0 | 0 | 306 | 7344 | 1440 | 301.8082 | -14.756 | 3.4678 | 1414.284 | 23.6292 | -174.438 | -57.6427 | 0 | 68.1656 | 248.1656 | 74.7524 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.631 | 0 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7345 | 1 | 14.2 | 0 | 0 | 0 | 0 | 0 | 307 | 7345 | 60 | 302.7945 | -15.0774 | 3.5825 | 34.284 | 0.63111 | 170.5334 | -57.3308 | 0 | 67.6763 | 112.3237 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.518 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2045 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7346 | 2 | 14.1 | 0 | 0 | 0 | 0 | 0 | 307 | 7346 | 120 | 302.7945 | -15.0774 | 3.5825 | 94.284 | 1.6311 | 155.5334 | -52.3191 | 0 | 67.6763 | 112.3237 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.4112 | 0 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7347 | 3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 307 | 7347 | 180 | 302.7945 | -15.0774 | 3.5825 | 154.284 | 2.6311 | 140.5334 | -44.43 | 0 | 67.6763 | 112.3237 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9807 | 0 | 0% | 11.66% | 0% | 80% | 0% | 0 | 6.5196 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7348 | 4 | 12.7 | 0 | 0 | 0 | 0 | 0 | 307 | 7348 | 240 | 302.7945 | -15.0774 | 3.5825 | 214.284 | 3.6311 | 125.5334 | -35.0197 | 0 | 67.6763 | 112.3237 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.2855 | 0 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7349 | 5 | 12.4 | 0 | 0 | 0 | 0 | 0 | 307 | 7349 | 300 | 302.7945 | -15.0774 | 3.5825 | 274.284 | 4.6311 | 110.5334 | -24.9287 | 0 | 67.6763 | 112.3237 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.4737 | 0 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.6439 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7350 | 6 | 12 | 0 | 0 | 0 | 0 | 0 | 307 | 7350 | 360 | 302.7945 | -15.0774 | 3.5825 | 334.284 | 5.6311 | 95.5334 | -14.6738 | 0 | 67.6763 | 112.3237 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.2675 | 3.2675 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7351 | 7 | 11.8 | 0 | 0 | 0 | 0 | 0 | 307 | 7351 | 420 | 302.7945 | -15.0774 | 3.5825 | 394.284 | 6.6311 | 80.5334 | -4.6343 | 0 | 67.6763 | 112.3237 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 158.133 | 158.133 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.7954 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7352 | 8 | 12.6 | 0 | 2.78 | 2.78 | 2.78 | 1.39 | 307 | 7352 | 480 | 302.7945 | -15.0774 | 3.5825 | 454.284 | 7.6311 | 65.5334 | 4.8365 | 4.8365 | 61.8857 | 118.1143 | 66.9433 | 0 | 0 | 2.3729 | 2.3729 | -54.5768 | 0% | 1.073 | 0 | 0 | 163.9681 | 163.9681 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7353 | 9 | 11 | 19.44 | 41.03 | 60.47 | 41.03 | 20.52 | 307 | 7353 | 540 | 302.7945 | -15.0774 | 3.5825 | 514.284 | 8.6311 | 50.5334 | 13.3416 | 13.3416 | 50.0045 | 129.9955 | 52.7437 | 51 | 51 | 35.0213 | 86.0213 | -0.76665 | 0% | 38.8989 | 0 | 0 | 144.9736 | 144.9736 | 0% | 11.71% | 0% | 80% | 0% | 0 | 7.0013 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7354 | 10 | 10.3 | 54.58 | 86.67 | 141.25 | 86.67 | 43.34 | 307 | 7354 | 600 | 302.7945 | -15.0774 | 3.5825 | 574.284 | 9.6311 | 35.5334 | 20.3991 | 20.3991 | 36.7781 | 143.2219 | 38.9847 | 121.7181 | 121.7181 | 73.9775 | 195.6956 | 0.10527 | 10.53% | 88.4935 | 9.3161 | 6.5212 | 147.0854 | 147.0854 | 4.434% | 11.67% | 11.67% | 80% | 9.34% | 8.2649 | 7.1852 | 6 | 49.5892 | 18.277 | 33.71% | 33.71%
11 | 307 | 3 | 7355 | 11 | 9.4 | 97.14 | 123.25 | 220.39 | 123.25 | 61.63 | 307 | 7355 | 660 | 302.7945 | -15.0774 | 3.5825 | 634.284 | 10.6311 | 20.5334 | 25.4477 | 25.4477 | 22.0285 | 157.9715 | 26.3984 | 202.4976 | 202.4976 | 105.2005 | 307.698 | 0.35278 | 35.28% | 139.141 | 49.0855 | 34.3599 | 124.6463 | 124.6463 | 27.57% | 11.64% | 11.64% | 85% | 9.893% | 13.7654 | 7.4266 | 6 | 82.5927 | 30.4411 | 66.26% | 66.26%
11 | 307 | 3 | 7356 | 12 | 10.2 | 98.33 | 151.86 | 250.19 | 151.86 | 75.93 | 307 | 7356 | 720 | 302.7945 | -15.0774 | 3.5825 | 694.284 | 11.6311 | 5.5334 | 27.9445 | 27.9445 | 6.0499 | 173.9501 | 17.7225 | 199.8723 | 199.8723 | 129.6206 | 329.4929 | 0.3883 | 38.83% | 148.9967 | 57.8552 | 40.4986 | 121.3399 | 121.3399 | 33.38% | 11.61% | 11.61% | 85% | 9.865% | 14.6982 | 7.2117 | 6 | 88.189 | 32.5037 | 72.68% | 72.68%
11 | 307 | 3 | 7357 | 13 | 10.6 | 105.83 | 169.72 | 275.55 | 169.72 | 84.86 | 307 | 7357 | 780 | 302.7945 | -15.0774 | 3.5825 | 754.284 | 12.6311 | -9.4666 | 27.561 | 27.561 | 10.3197 | 190.3197 | 19.2835 | 215.8939 | 215.8939 | 144.8651 | 360.759 | 0.42691 | 42.69% | 163.1352 | 69.6439 | 48.7507 | 121.9302 | 121.9302 | 39.98% | 11.58% | 11.58% | 85% | 9.842% | 16.0561 | 7.1059 | 6 | 96.3368 | 35.5067 | 79.01% | 79.01%
11 | 307 | 3 | 7358 | 14 | 10.8 | 106.39 | 156.31 | 262.7 | 156.31 | 78.16 | 307 | 7358 | 840 | 302.7945 | -15.0774 | 3.5825 | 814.284 | 13.6311 | -24.4666 | 24.3506 | 24.3506 | 26.0373 | 206.0373 | 29.4977 | 224.5813 | 224.5813 | 133.4189 | 358.0002 | 0.4253 | 42.53% | 161.8877 | 68.8513 | 48.1959 | 121.1873 | 121.1873 | 39.77% | 11.58% | 11.58% | 85% | 9.839% | 15.9286 | 7.0535 | 6 | 95.5717 | 35.2247 | 78.86% | 78.86%
11 | 307 | 3 | 7359 | 15 | 11.2 | 114.08 | 155.28 | 269.36 | 155.28 | 77.64 | 307 | 7359 | 900 | 302.7945 | -15.0774 | 3.5825 | 874.284 | 14.6311 | -39.4666 | 18.7191 | 18.7191 | 40.3929 | 220.3929 | 42.5244 | 261.976 | 261.976 | 132.5398 | 394.5158 | 0.46271 | 46.27% | 178.4001 | 82.5471 | 57.783 | 120.5604 | 120.5604 | 47.93% | 11.55% | 11.55% | 85% | 9.816% | 17.5118 | 6.9494 | 6 | 105.0707 | 38.7257 | 87.15% | 87.15%
11 | 307 | 3 | 7360 | 16 | 11.3 | 60.75 | 123.14 | 183.89 | 123.14 | 61.57 | 307 | 7360 | 960 | 302.7945 | -15.0774 | 3.5825 | 934.284 | 15.6311 | -54.4666 | 11.2301 | 11.2301 | 53.2355 | 233.2355 | 56.4387 | 172.4482 | 172.4482 | 105.1066 | 277.5548 | 0.31972 | 31.97% | 125.5103 | 40.1286 | 28.09 | 115.5893 | 115.5893 | 24.3% | 11.6% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7361 | 17 | 11.5 | 33.61 | 61.31 | 94.92 | 61.31 | 30.66 | 307 | 7361 | 1020 | 302.7945 | -15.0774 | 3.5825 | 994.284 | 16.6311 | -69.4666 | 2.429 | 2.429 | 64.8291 | 244.8291 | 70.7043 | 0 | 0 | 52.3314 | 52.3314 | -1.7557 | 0% | 23.6642 | 0 | 0 | 152.08 | 152.08 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7362 | 18 | 10.6 | 0 | 8.42 | 8.42 | 8.42 | 4.21 | 307 | 7362 | 1080 | 302.7945 | -15.0774 | 3.5825 | 1054.284 | 17.6311 | -84.4666 | -7.2265 | 0 | 67.6763 | 247.6763 | 74.4198 | 0 | 0 | 7.1869 | 7.1869 | -18.1247 | 0% | 3.2499 | 0 | 0 | 142.5313 | 142.5313 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7363 | 19 | 9.4 | 0 | 0 | 0 | 0 | 0 | 307 | 7363 | 1140 | 302.7945 | -15.0774 | 3.5825 | 1114.284 | 18.6311 | -99.4666 | -17.3563 | 0 | 67.6763 | 247.6763 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.3697 | 137.3697 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7364 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 307 | 7364 | 1200 | 302.7945 | -15.0774 | 3.5825 | 1174.284 | 19.6311 | -114.4666 | -27.608 | 0 | 67.6763 | 247.6763 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.1649 | 131.1649 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7365 | 21 | 7.2 | 0 | 0 | 0 | 0 | 0 | 307 | 7365 | 1260 | 302.7945 | -15.0774 | 3.5825 | 1234.284 | 20.6311 | -129.4666 | -37.5797 | 0 | 67.6763 | 247.6763 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.0505 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7366 | 22 | 7.2 | 0 | 0 | 0 | 0 | 0 | 307 | 7366 | 1320 | 302.7945 | -15.0774 | 3.5825 | 1294.284 | 21.6311 | -144.4666 | -46.6911 | 0 | 67.6763 | 247.6763 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9636 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7367 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 307 | 7367 | 1380 | 302.7945 | -15.0774 | 3.5825 | 1354.284 | 22.6311 | -159.4666 | -53.9784 | 0 | 67.6763 | 247.6763 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0571 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
11 | 307 | 3 | 7368 | 24 | 4.3 | 0 | 0 | 0 | 0 | 0 | 307 | 7368 | 1440 | 302.7945 | -15.0774 | 3.5825 | 1414.284 | 23.6311 | -174.4666 | -57.965 | 0 | 67.6763 | 247.6763 | 74.4198 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8647 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7369 | 1 | 3.4 | 0 | 0 | 0 | 0 | 0 | 308 | 7369 | 60 | 303.7808 | -15.3942 | 3.6871 | 34.284 | 0.63285 | 170.5072 | -57.6352 | 0 | 67.193 | 112.807 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0569 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7370 | 2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 308 | 7370 | 120 | 303.7808 | -15.3942 | 3.6871 | 94.284 | 1.6329 | 155.5072 | -52.5877 | 0 | 67.193 | 112.807 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4523 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7371 | 3 | 3.2 | 0 | 0 | 0 | 0 | 0 | 308 | 7371 | 180 | 303.7808 | -15.3942 | 3.6871 | 154.284 | 2.6329 | 140.5072 | -44.6653 | 0 | 67.193 | 112.807 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.8956 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7372 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 308 | 7372 | 240 | 303.7808 | -15.3942 | 3.6871 | 214.284 | 3.6329 | 125.5072 | -35.2343 | 0 | 67.193 | 112.807 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2004 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7373 | 5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 308 | 7373 | 300 | 303.7808 | -15.3942 | 3.6871 | 274.284 | 4.6329 | 110.5072 | -25.1346 | 0 | 67.193 | 112.807 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.887 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7374 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 308 | 7374 | 360 | 303.7808 | -15.3942 | 3.6871 | 334.284 | 5.6329 | 95.5072 | -14.8807 | 0 | 67.193 | 112.807 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1272 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7375 | 7 | 1.8 | 0 | 0 | 0 | 0 | 0 | 308 | 7375 | 420 | 303.7808 | -15.3942 | 3.6871 | 394.284 | 6.6329 | 80.5072 | -4.8501 | 0 | 67.193 | 112.807 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.7474 | 145.7474 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7376 | 8 | 1.2 | 0 | 1.47 | 1.47 | 1.47 | 0.74 | 308 | 7376 | 480 | 303.7808 | -15.3942 | 3.6871 | 454.284 | 7.6329 | 65.5072 | 4.6051 | 4.6051 | 61.6672 | 118.3328 | 66.9661 | 0 | 0 | 1.2547 | 1.2547 | -125.5221 | 0% | 0.56739 | 0 | 0 | 149.713 | 149.713 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7377 | 9 | 1 | 12.31 | 34.64 | 46.95 | 34.64 | 17.32 | 308 | 7377 | 540 | 303.7808 | -15.3942 | 3.6871 | 514.284 | 8.6329 | 50.5072 | 13.0893 | 13.0893 | 49.8061 | 130.1939 | 52.7976 | 32.8654 | 32.8654 | 29.5671 | 62.4325 | -1.7427 | 0% | 28.232 | 0 | 0 | 132.2276 | 132.2276 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7378 | 10 | 3 | 50.92 | 79.72 | 130.64 | 79.72 | 39.86 | 308 | 7378 | 600 | 303.7808 | -15.3942 | 3.6871 | 574.284 | 9.6329 | 35.5072 | 20.123 | 20.123 | 36.6105 | 143.3895 | 39.084 | 114.8868 | 114.8868 | 68.0453 | 182.9321 | -0.038448 | 0% | 82.7219 | 0 | 0 | 139.7617 | 139.7617 | 0% | 11.93% | 11.93% | 80% | 9.543% | 7.8943 | 9.3069 | 6 | 47.3657 | 17.4575 | 33.89% | 33.89%
11 | 308 | 4 | 7379 | 11 | 5 | 108.14 | 93.25 | 201.39 | 93.25 | 46.63 | 308 | 7379 | 660 | 303.7808 | -15.3942 | 3.6871 | 634.284 | 10.6329 | 20.5072 | 25.149 | 25.149 | 21.9086 | 158.0914 | 26.5746 | 227.5792 | 227.5792 | 79.5939 | 307.173 | 0.31802 | 31.8% | 138.9037 | 44.1741 | 30.9219 | 121.9657 | 121.9657 | 25.35% | 11.76% | 11.76% | 85% | 9.995% | 13.8831 | 8.6885 | 6 | 83.2988 | 30.7013 | 68.3% | 68.3%
11 | 308 | 4 | 7380 | 12 | 8.4 | 139.92 | 121.94 | 261.86 | 121.94 | 60.97 | 308 | 7380 | 720 | 303.7808 | -15.3942 | 3.6871 | 694.284 | 11.6329 | 5.5072 | 27.6306 | 27.6306 | 5.9948 | 174.0052 | 18.0153 | 286.9109 | 286.9109 | 104.0823 | 390.9932 | 0.44289 | 44.29% | 176.8071 | 78.3065 | 54.8146 | 124.3745 | 124.3745 | 44.07% | 11.61% | 11.61% | 85% | 9.871% | 17.4526 | 7.7015 | 6 | 104.7158 | 38.595 | 84.19% | 84.19%
11 | 308 | 4 | 7381 | 13 | 10.6 | 97.31 | 149.44 | 246.75 | 149.44 | 74.72 | 308 | 7381 | 780 | 303.7808 | -15.3942 | 3.6871 | 754.284 | 12.6329 | -9.4928 | 27.2436 | 27.2436 | 10.3025 | 190.3025 | 19.5712 | 200.2906 | 200.2906 | 127.555 | 327.8456 | 0.38905 | 38.91% | 148.2518 | 57.6776 | 40.3743 | 126.2464 | 126.2464 | 31.98% | 11.6% | 11.6% | 85% | 9.857% | 14.6127 | 7.1059 | 6 | 87.6763 | 32.3147 | 69.45% | 69.45%
11 | 308 | 4 | 7382 | 14 | 11.6 | 113.06 | 119.92 | 232.98 | 119.92 | 59.96 | 308 | 7382 | 840 | 303.7808 | -15.3942 | 3.6871 | 814.284 | 13.6329 | -24.4928 | 24.0417 | 24.0417 | 25.9555 | 205.9555 | 29.6914 | 241.0785 | 241.0785 | 102.3581 | 343.4366 | 0.41465 | 41.46% | 155.302 | 64.3953 | 45.0767 | 126.6837 | 126.6837 | 35.58% | 11.56% | 11.56% | 85% | 9.828% | 15.2638 | 6.8464 | 6 | 91.5831 | 33.7546 | 72.29% | 72.29%
11 | 308 | 4 | 7383 | 15 | 12 | 182.78 | 64.72 | 247.5 | 64.72 | 32.36 | 308 | 7383 | 900 | 303.7808 | -15.3942 | 3.6871 | 874.284 | 14.6329 | -39.4928 | 18.4262 | 18.4262 | 40.2631 | 220.2631 | 42.657 | 425.2706 | 425.2706 | 55.242 | 480.5126 | 0.52764 | 52.76% | 217.2878 | 114.6498 | 80.2549 | 126.2739 | 126.2739 | 63.56% | 11.49% | 11.49% | 85% | 9.769% | 21.2262 | 6.7446 | 6 | 127.357 | 46.9398 | 100.9% | 100.9%
11 | 308 | 4 | 7384 | 16 | 13.2 | 105.92 | 53.69 | 159.61 | 53.69 | 26.85 | 308 | 7384 | 960 | 303.7808 | -15.3942 | 3.6871 | 934.284 | 15.6329 | -54.4928 | 10.9551 | 10.9551 | 53.0733 | 233.0733 | 56.5326 | 307.3604 | 307.3604 | 45.8273 | 353.1877 | 0.43583 | 43.58% | 159.7115 | 69.6066 | 48.7246 | 123.155 | 123.155 | 39.56% | 11.52% | 0% | 85% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7385 | 17 | 12.6 | 45.08 | 35.47 | 80.55 | 35.47 | 17.74 | 308 | 7385 | 1020 | 303.7808 | -15.3942 | 3.6871 | 994.284 | 16.6329 | -69.4928 | 2.17 | 2.17 | 64.645 | 244.645 | 70.7702 | 0 | 0 | 30.2755 | 30.2755 | -3.5365 | 0% | 13.6906 | 0 | 0 | 158.3064 | 158.3064 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7386 | 18 | 10.8 | 0 | 4.72 | 4.72 | 4.72 | 2.36 | 308 | 7386 | 1080 | 303.7808 | -15.3942 | 3.6871 | 1054.284 | 17.6329 | -84.4928 | -7.4739 | 0 | 67.193 | 247.193 | 74.0919 | 0 | 0 | 4.0288 | 4.0288 | -32.8474 | 0% | 1.8218 | 0 | 0 | 146.8874 | 146.8874 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7387 | 19 | 9.6 | 0 | 0 | 0 | 0 | 0 | 308 | 7387 | 1140 | 303.7808 | -15.3942 | 3.6871 | 1114.284 | 18.6329 | -99.4928 | -17.5978 | 0 | 67.193 | 247.193 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.3824 | 141.3824 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3724 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7388 | 20 | 7 | 0 | 0 | 0 | 0 | 0 | 308 | 7388 | 1200 | 303.7808 | -15.3942 | 3.6871 | 1174.284 | 19.6329 | -114.4928 | -27.8507 | 0 | 67.193 | 247.193 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.9021 | 132.9021 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7389 | 21 | 6.4 | 0 | 0 | 0 | 0 | 0 | 308 | 7389 | 1260 | 303.7808 | -15.3942 | 3.6871 | 1234.284 | 20.6329 | -129.4928 | -37.8322 | 0 | 67.193 | 247.193 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1473 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2723 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7390 | 22 | 6 | 0 | 0 | 0 | 0 | 0 | 308 | 7390 | 1320 | 303.7808 | -15.3942 | 3.6871 | 1294.284 | 21.6329 | -144.4928 | -46.9634 | 0 | 67.193 | 247.193 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7938 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7391 | 23 | 5.6 | 0 | 0 | 0 | 0 | 0 | 308 | 7391 | 1380 | 303.7808 | -15.3942 | 3.6871 | 1354.284 | 22.6329 | -159.4928 | -54.2777 | 0 | 67.193 | 247.193 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1703 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
11 | 308 | 4 | 7392 | 24 | 5.2 | 0 | 0 | 0 | 0 | 0 | 308 | 7392 | 1440 | 303.7808 | -15.3942 | 3.6871 | 1414.284 | 23.6329 | -174.4928 | -58.2825 | 0 | 67.193 | 247.193 | 74.0919 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5468 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7393 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 309 | 7393 | 60 | 304.7671 | -15.7062 | 3.7814 | 34.284 | 0.63442 | 170.4837 | -57.9352 | 0 | 66.7161 | 113.2839 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4224 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7394 | 2 | 4.6 | 0 | 0 | 0 | 0 | 0 | 309 | 7394 | 120 | 304.7671 | -15.7062 | 3.7814 | 94.284 | 1.6344 | 155.4837 | -52.8526 | 0 | 66.7161 | 113.2839 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.882 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7395 | 3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 309 | 7395 | 180 | 304.7671 | -15.7062 | 3.7814 | 154.284 | 2.6344 | 140.4837 | -44.8977 | 0 | 66.7161 | 113.2839 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.3416 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7396 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 309 | 7396 | 240 | 304.7671 | -15.7062 | 3.7814 | 214.284 | 3.6344 | 125.4837 | -35.4465 | 0 | 66.7161 | 113.2839 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.6464 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7397 | 5 | 3.8 | 0 | 0 | 0 | 0 | 0 | 309 | 7397 | 300 | 304.7671 | -15.7062 | 3.7814 | 274.284 | 4.6344 | 110.4837 | -25.3384 | 0 | 66.7161 | 113.2839 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7743 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7398 | 6 | 3.7 | 0 | 0 | 0 | 0 | 0 | 309 | 7398 | 360 | 304.7671 | -15.7062 | 3.7814 | 334.284 | 5.6344 | 95.4837 | -15.0857 | 0 | 66.7161 | 113.2839 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.6703 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7399 | 7 | 4.8 | 0 | 0 | 0 | 0 | 0 | 309 | 7399 | 420 | 304.7671 | -15.7062 | 3.7814 | 394.284 | 6.6344 | 80.4837 | -5.064 | 0 | 66.7161 | 113.2839 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.8393 | 139.8393 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7400 | 8 | 5.6 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 309 | 7400 | 480 | 304.7671 | -15.7062 | 3.7814 | 454.284 | 7.6344 | 65.4837 | 4.3758 | 4.3758 | 61.4538 | 118.5462 | 66.9915 | 0 | 0 | 1.6559 | 1.6559 | -88.4778 | 0% | 0.7488 | 0 | 0 | 143.8543 | 143.8543 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7401 | 9 | 6.1 | 2.03 | 32.42 | 34.45 | 32.42 | 16.21 | 309 | 7401 | 540 | 304.7671 | -15.7062 | 3.7814 | 514.284 | 8.6344 | 50.4837 | 12.8395 | 12.8395 | 49.6129 | 130.3871 | 52.8541 | 5.5162 | 5.5162 | 27.6722 | 33.1884 | -3.6146 | 0% | 15.0078 | 0 | 0 | 125.7465 | 125.7465 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7402 | 10 | 6.2 | 13.69 | 109.36 | 123.05 | 109.36 | 54.68 | 309 | 7402 | 600 | 304.7671 | -15.7062 | 3.7814 | 574.284 | 9.6344 | 35.4837 | 19.8499 | 19.8499 | 36.4482 | 143.5518 | 39.1858 | 31.2499 | 31.2499 | 93.3446 | 124.5945 | -0.37107 | 0% | 56.3416 | 0 | 0 | 129.915 | 129.915 | 0% | 11.86% | 11.86% | 80% | 9.492% | 5.3478 | 8.3309 | 6 | 32.0867 | 11.8261 | 24.7% | 24.7%
11 | 309 | 5 | 7403 | 11 | 7.3 | 16.03 | 163.61 | 179.64 | 163.61 | 81.81 | 309 | 7403 | 660 | 304.7671 | -15.7062 | 3.7814 | 634.284 | 10.6344 | 20.4837 | 24.8542 | 24.8542 | 21.7934 | 158.2066 | 26.7521 | 34.0562 | 34.0562 | 139.6499 | 173.7061 | -0.023782 | 0% | 78.5499 | 0 | 0 | 132.2438 | 132.2438 | 0% | 11.79% | 11.79% | 80% | 9.432% | 7.4085 | 8.012 | 6 | 44.4509 | 16.3832 | 33.61% | 33.61%
11 | 309 | 5 | 7404 | 12 | 8.3 | 24.81 | 133.81 | 158.62 | 133.81 | 66.91 | 309 | 7404 | 720 | 304.7671 | -15.7062 | 3.7814 | 694.284 | 11.6344 | 5.4837 | 27.3211 | 27.3211 | 5.9433 | 174.0567 | 18.3053 | 51.3197 | 51.3197 | 114.214 | 165.5336 | -0.050366 | 0% | 74.8543 | 0 | 0 | 129.6711 | 129.6711 | 0% | 11.76% | 11.76% | 80% | 9.408% | 7.0425 | 7.7294 | 6 | 42.2548 | 15.5738 | 32.59% | 32.59%
11 | 309 | 5 | 7405 | 13 | 9.2 | 7.14 | 121.03 | 128.17 | 121.03 | 60.52 | 309 | 7405 | 780 | 304.7671 | -15.7062 | 3.7814 | 754.284 | 12.6344 | -9.5163 | 26.9313 | 26.9313 | 10.2833 | 190.2833 | 19.8544 | 14.8273 | 14.8273 | 103.3056 | 118.1328 | -0.37526 | 0% | 53.4197 | 0 | 0 | 129.1 | 129.1 | 0% | 11.76% | 11.76% | 80% | 9.406% | 5.0245 | 7.481 | 6 | 30.1467 | 11.1111 | 23.35% | 23.35%
11 | 309 | 5 | 7406 | 14 | 9.8 | 41.19 | 183.06 | 224.25 | 183.06 | 91.53 | 309 | 7406 | 840 | 304.7671 | -15.7062 | 3.7814 | 814.284 | 13.6344 | -24.5163 | 23.7381 | 23.7381 | 25.8731 | 205.8731 | 29.8823 | 88.7174 | 88.7174 | 156.2515 | 244.9689 | 0.24105 | 24.11% | 110.7749 | 26.7025 | 18.6918 | 112.9622 | 112.9622 | 16.55% | 11.66% | 11.66% | 80% | 9.331% | 10.3361 | 7.3186 | 6 | 62.0164 | 22.8573 | 54.9% | 54.9%
11 | 309 | 5 | 7407 | 15 | 9.9 | 14.81 | 159.08 | 173.89 | 159.08 | 79.54 | 309 | 7407 | 900 | 304.7671 | -15.7062 | 3.7814 | 874.284 | 14.6344 | -39.5163 | 18.1386 | 18.1386 | 40.1336 | 220.1336 | 42.7871 | 34.9124 | 34.9124 | 135.7833 | 170.6957 | -0.0025291 | 0% | 77.1886 | 0 | 0 | 109.5622 | 109.5622 | 0% | 11.7% | 11.7% | 80% | 9.361% | 7.2258 | 7.2918 | 6 | 43.355 | 15.9793 | 39.57% | 39.57%
11 | 309 | 5 | 7408 | 16 | 9.8 | 6.75 | 92.03 | 98.78 | 92.03 | 46.02 | 309 | 7408 | 960 | 304.7671 | -15.7062 | 3.7814 | 934.284 | 15.6344 | -54.5163 | 10.6854 | 10.6854 | 52.912 | 232.912 | 56.6241 | 20.0272 | 20.0272 | 78.5525 | 98.5798 | -0.59492 | 0% | 44.5778 | 0 | 0 | 146.9974 | 146.9974 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7409 | 17 | 8.8 | 6.31 | 74.64 | 80.95 | 74.64 | 37.32 | 309 | 7409 | 1020 | 304.7671 | -15.7062 | 3.7814 | 994.284 | 16.6344 | -69.5163 | 1.9162 | 1.9162 | 64.4621 | 244.4621 | 70.8336 | 0 | 0 | 63.7092 | 63.7092 | -1.3974 | 0% | 28.8093 | 0 | 0 | 143.6526 | 143.6526 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7410 | 18 | 7.5 | 0 | 8.14 | 8.14 | 8.14 | 4.07 | 309 | 7410 | 1080 | 304.7671 | -15.7062 | 3.7814 | 1054.284 | 17.6344 | -84.5163 | -7.716 | 0 | 66.7161 | 246.7161 | 73.769 | 0 | 0 | 6.9479 | 6.9479 | -19.8233 | 0% | 3.1419 | 0 | 0 | 136.5671 | 136.5671 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7411 | 19 | 6.2 | 0 | 0 | 0 | 0 | 0 | 309 | 7411 | 1140 | 304.7671 | -15.7062 | 3.7814 | 1114.284 | 18.6344 | -99.5163 | -17.8338 | 0 | 66.7161 | 246.7161 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.5215 | 132.5215 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7412 | 20 | 6 | 0 | 0 | 0 | 0 | 0 | 309 | 7412 | 1200 | 304.7671 | -15.7062 | 3.7814 | 1174.284 | 19.6344 | -114.5163 | -28.0878 | 0 | 66.7161 | 246.7161 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.7802 | 129.7802 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7413 | 21 | 5.5 | 0 | 0 | 0 | 0 | 0 | 309 | 7413 | 1260 | 304.7671 | -15.7062 | 3.7814 | 1234.284 | 20.6344 | -129.5163 | -38.079 | 0 | 66.7161 | 246.7161 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5709 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7414 | 22 | 5.3 | 0 | 0 | 0 | 0 | 0 | 309 | 7414 | 1320 | 304.7671 | -15.7062 | 3.7814 | 1294.284 | 21.6344 | -144.5163 | -47.2299 | 0 | 66.7161 | 246.7161 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.415 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7415 | 23 | 5.2 | 0 | 0 | 0 | 0 | 0 | 309 | 7415 | 1380 | 304.7671 | -15.7062 | 3.7814 | 1354.284 | 22.6344 | -159.5163 | -54.5713 | 0 | 66.7161 | 246.7161 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.4175 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
11 | 309 | 5 | 7416 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 309 | 7416 | 1440 | 304.7671 | -15.7062 | 3.7814 | 1414.284 | 23.6344 | -174.5163 | -58.5948 | 0 | 66.7161 | 246.7161 | 73.769 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5723 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7417 | 1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 310 | 7417 | 60 | 305.7534 | -16.0133 | 3.8653 | 34.284 | 0.63582 | 170.4627 | -58.2308 | 0 | 66.2456 | 113.7544 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.242 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7418 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 310 | 7418 | 120 | 305.7534 | -16.0133 | 3.8653 | 94.284 | 1.6358 | 155.4627 | -53.1137 | 0 | 66.2456 | 113.7544 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.233 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7419 | 3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 310 | 7419 | 180 | 305.7534 | -16.0133 | 3.8653 | 154.284 | 2.6358 | 140.4627 | -45.127 | 0 | 66.2456 | 113.7544 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.462 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7420 | 4 | 3.5 | 0 | 0 | 0 | 0 | 0 | 310 | 7420 | 240 | 305.7534 | -16.0133 | 3.8653 | 214.284 | 3.6358 | 125.4627 | -35.6563 | 0 | 66.2456 | 113.7544 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6144 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7421 | 5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 310 | 7421 | 300 | 305.7534 | -16.0133 | 3.8653 | 274.284 | 4.6358 | 110.4627 | -25.5402 | 0 | 66.2456 | 113.7544 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1951 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7422 | 6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 310 | 7422 | 360 | 305.7534 | -16.0133 | 3.8653 | 334.284 | 5.6358 | 95.4627 | -15.2888 | 0 | 66.2456 | 113.7544 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.2493 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7423 | 7 | 1.5 | 0 | 0 | 0 | 0 | 0 | 310 | 7423 | 420 | 305.7534 | -16.0133 | 3.8653 | 394.284 | 6.6358 | 80.4627 | -5.276 | 0 | 66.2456 | 113.7544 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 155.4464 | 155.4464 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7424 | 8 | 1.2 | 0 | 1.67 | 1.67 | 1.67 | 0.84 | 310 | 7424 | 480 | 305.7534 | -16.0133 | 3.8653 | 454.284 | 7.6358 | 65.4627 | 4.1486 | 4.1486 | 61.2456 | 118.7544 | 67.0193 | 0 | 0 | 1.4254 | 1.4254 | -110.3932 | 0% | 0.64458 | 0 | 0 | 161.3114 | 161.3114 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7425 | 9 | 1.8 | 13.97 | 28.25 | 42.22 | 28.25 | 14.13 | 310 | 7425 | 540 | 305.7534 | -16.0133 | 3.8653 | 514.284 | 8.6358 | 50.4627 | 12.5923 | 12.5923 | 49.425 | 130.575 | 52.913 | 38.6414 | 38.6414 | 24.1129 | 62.7543 | -1.6984 | 0% | 28.3775 | 0 | 0 | 145.1024 | 145.1024 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7426 | 10 | 1.8 | 61.03 | 71.11 | 132.14 | 71.11 | 35.56 | 310 | 7426 | 600 | 305.7534 | -16.0133 | 3.8653 | 574.284 | 9.6358 | 35.4627 | 19.58 | 19.58 | 36.291 | 143.709 | 39.2897 | 140.9463 | 140.9463 | 60.6962 | 201.6424 | 0.02522 | 2.522% | 91.1827 | 2.2997 | 1.6098 | 149.3387 | 149.3387 | 1.078% | 11.95% | 11.95% | 80% | 9.561% | 8.7178 | 9.6914 | 6 | 52.3066 | 19.2786 | 35.03% | 35.03%
11 | 310 | 6 | 7427 | 11 | 3.2 | 173.42 | 80.36 | 253.78 | 80.36 | 40.18 | 310 | 7427 | 660 | 305.7534 | -16.0133 | 3.8653 | 634.284 | 10.6358 | 20.4627 | 24.5633 | 24.5633 | 21.6828 | 158.3172 | 26.9308 | 371.9365 | 371.9365 | 68.5916 | 440.5281 | 0.45527 | 45.53% | 199.2068 | 90.6929 | 63.485 | 131.4766 | 131.4766 | 48.29% | 11.68% | 11.68% | 85% | 9.932% | 19.7843 | 9.2438 | 6 | 118.7057 | 43.7512 | 90.29% | 90.29%
11 | 310 | 6 | 7428 | 12 | 5.5 | 234.81 | 79.64 | 314.45 | 79.64 | 39.82 | 310 | 7428 | 720 | 305.7534 | -16.0133 | 3.8653 | 694.284 | 11.6358 | 5.4627 | 27.0163 | 27.0163 | 5.8953 | 174.1047 | 18.592 | 489.9477 | 489.9477 | 67.977 | 557.9247 | 0.53859 | 53.86% | 252.2936 | 135.8819 | 95.1174 | 129.3613 | 129.3613 | 73.53% | 11.55% | 11.55% | 90% | 10.39% | 26.2147 | 8.5383 | 6 | 157.2881 | 57.9714 | 121.6% | 121.6%
11 | 310 | 6 | 7429 | 13 | 7.2 | 203.14 | 135.36 | 338.5 | 135.36 | 67.68 | 310 | 7429 | 780 | 305.7534 | -16.0133 | 3.8653 | 754.284 | 12.6358 | -9.5373 | 26.6241 | 26.6241 | 10.2621 | 190.2621 | 20.1329 | 425.6025 | 425.6025 | 115.537 | 541.1395 | 0.53784 | 53.78% | 244.7033 | 131.6119 | 92.1284 | 130.7827 | 130.7827 | 70.44% | 11.53% | 11.53% | 90% | 10.38% | 25.4022 | 8.0406 | 6 | 152.4131 | 56.1747 | 116.5% | 116.5%
11 | 310 | 6 | 7430 | 14 | 6.8 | 173.97 | 146.39 | 320.36 | 146.39 | 73.2 | 310 | 7430 | 840 | 305.7534 | -16.0133 | 3.8653 | 814.284 | 13.6358 | -24.5373 | 23.4399 | 23.4399 | 25.7901 | 205.7901 | 30.0701 | 378.4833 | 378.4833 | 124.9517 | 503.435 | 0.51602 | 51.6% | 227.6533 | 117.4742 | 82.2319 | 128.44 | 128.44 | 64.02% | 11.57% | 11.57% | 90% | 10.41% | 23.7 | 8.1559 | 6 | 142.2001 | 52.4105 | 110.7% | 110.7%
11 | 310 | 6 | 7431 | 15 | 7 | 139.92 | 111.03 | 250.95 | 111.03 | 55.52 | 310 | 7431 | 900 | 305.7534 | -16.0133 | 3.8653 | 874.284 | 14.6358 | -39.5373 | 17.8564 | 17.8564 | 40.0045 | 220.0045 | 42.9146 | 334.1896 | 334.1896 | 94.77 | 428.9596 | 0.46713 | 46.71% | 193.9755 | 90.6122 | 63.4285 | 122.5501 | 122.5501 | 51.76% | 11.62% | 11.62% | 85% | 9.875% | 19.1545 | 8.0981 | 6 | 114.927 | 42.3585 | 93.78% | 93.78%
11 | 310 | 6 | 7432 | 16 | 7.2 | 81.81 | 94.72 | 176.53 | 94.72 | 47.36 | 310 | 7432 | 960 | 305.7534 | -16.0133 | 3.8653 | 934.284 | 15.6358 | -54.5373 | 10.421 | 10.421 | 52.7517 | 232.7517 | 56.713 | 248.2304 | 248.2304 | 80.8486 | 329.079 | 0.36633 | 36.63% | 148.8095 | 54.5134 | 38.1594 | 117.5834 | 117.5834 | 32.45% | 11.68% | 0% | 85% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7433 | 17 | 7 | 6.94 | 46.75 | 53.69 | 46.75 | 23.38 | 310 | 7433 | 1020 | 305.7534 | -16.0133 | 3.8653 | 994.284 | 16.6358 | -69.5373 | 1.6677 | 1.6677 | 64.2803 | 244.2803 | 70.8943 | 0 | 0 | 39.9036 | 39.9036 | -2.8173 | 0% | 18.0444 | 0 | 0 | 149.3497 | 149.3497 | 0% | 11.9% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7434 | 18 | 6.8 | 0 | 2.92 | 2.92 | 2.92 | 1.46 | 310 | 7434 | 1080 | 305.7534 | -16.0133 | 3.8653 | 1054.284 | 17.6358 | -84.5373 | -7.9528 | 0 | 66.2456 | 246.2456 | 73.4511 | 0 | 0 | 2.4924 | 2.4924 | -57.3646 | 0% | 1.1271 | 0 | 0 | 142.5516 | 142.5516 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7435 | 19 | 6.2 | 0 | 0 | 0 | 0 | 0 | 310 | 7435 | 1140 | 305.7534 | -16.0133 | 3.8653 | 1114.284 | 18.6358 | -99.5373 | -18.0645 | 0 | 66.2456 | 246.2456 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.9711 | 137.9711 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7436 | 20 | 6.2 | 0 | 0 | 0 | 0 | 0 | 310 | 7436 | 1200 | 305.7534 | -16.0133 | 3.8653 | 1174.284 | 19.6358 | -114.5373 | -28.3193 | 0 | 66.2456 | 246.2456 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.9675 | 132.9675 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7437 | 21 | 6.2 | 0 | 0 | 0 | 0 | 0 | 310 | 7437 | 1260 | 305.7534 | -16.0133 | 3.8653 | 1234.284 | 20.6358 | -129.5373 | -38.32 | 0 | 66.2456 | 246.2456 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2596 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7438 | 22 | 5.8 | 0 | 0 | 0 | 0 | 0 | 310 | 7438 | 1320 | 305.7534 | -16.0133 | 3.8653 | 1294.284 | 21.6358 | -144.5373 | -47.4904 | 0 | 66.2456 | 246.2456 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0123 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7439 | 23 | 5.2 | 0 | 0 | 0 | 0 | 0 | 310 | 7439 | 1380 | 305.7534 | -16.0133 | 3.8653 | 1354.284 | 22.6358 | -159.5373 | -54.8591 | 0 | 66.2456 | 246.2456 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5461 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
11 | 310 | 6 | 7440 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 310 | 7440 | 1440 | 305.7534 | -16.0133 | 3.8653 | 1414.284 | 23.6358 | -174.5373 | -58.902 | 0 | 66.2456 | 246.2456 | 73.4511 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.775 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7441 | 1 | 4.4 | 0 | 0 | 0 | 0 | 0 | 311 | 7441 | 60 | 306.7397 | -16.3153 | 3.9388 | 34.284 | 0.63705 | 170.4443 | -58.5219 | 0 | 65.7819 | 114.2181 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9475 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7442 | 2 | 4.5 | 0 | 0 | 0 | 0 | 0 | 311 | 7442 | 120 | 306.7397 | -16.3153 | 3.9388 | 94.284 | 1.637 | 155.4443 | -53.3711 | 0 | 65.7819 | 114.2181 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.5893 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7443 | 3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 311 | 7443 | 180 | 306.7397 | -16.3153 | 3.9388 | 154.284 | 2.637 | 140.4443 | -45.3533 | 0 | 65.7819 | 114.2181 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8408 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7444 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 311 | 7444 | 240 | 306.7397 | -16.3153 | 3.9388 | 214.284 | 3.637 | 125.4443 | -35.8635 | 0 | 65.7819 | 114.2181 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1456 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7445 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 311 | 7445 | 300 | 306.7397 | -16.3153 | 3.9388 | 274.284 | 4.637 | 110.4443 | -25.7398 | 0 | 65.7819 | 114.2181 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8671 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7446 | 6 | 2.2 | 0 | 0 | 0 | 0 | 0 | 311 | 7446 | 360 | 306.7397 | -16.3153 | 3.9388 | 334.284 | 5.637 | 95.4443 | -15.4899 | 0 | 65.7819 | 114.2181 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.8375 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7447 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 311 | 7447 | 420 | 306.7397 | -16.3153 | 3.9388 | 394.284 | 6.637 | 80.4443 | -5.486 | 0 | 65.7819 | 114.2181 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.2556 | 143.2556 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7448 | 8 | 2 | 0 | 0.92 | 0.92 | 0.92 | 0.46 | 311 | 7448 | 480 | 306.7397 | -16.3153 | 3.9388 | 454.284 | 7.637 | 65.4443 | 3.9237 | 3.9237 | 61.0427 | 118.9573 | 67.0496 | 0 | 0 | 0.78527 | 0.78527 | -198.5497 | 0% | 0.3551 | 0 | 0 | 146.9183 | 146.9183 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7449 | 9 | 2.3 | 10.08 | 30.47 | 40.55 | 30.47 | 15.24 | 311 | 7449 | 540 | 306.7397 | -16.3153 | 3.9388 | 514.284 | 8.637 | 50.4443 | 12.3477 | 12.3477 | 49.2425 | 130.7575 | 52.9743 | 28.3847 | 28.3847 | 26.0078 | 54.3925 | -2.0606 | 0% | 24.5963 | 0 | 0 | 129.4827 | 129.4827 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7450 | 10 | 2.4 | 43.53 | 65.08 | 108.61 | 65.08 | 32.54 | 311 | 7450 | 600 | 306.7397 | -16.3153 | 3.9388 | 574.284 | 9.637 | 35.4443 | 19.3135 | 19.3135 | 36.1391 | 143.8609 | 39.3958 | 101.7096 | 101.7096 | 55.5493 | 157.2589 | -0.18526 | 0% | 71.1125 | 0 | 0 | 132.6898 | 132.6898 | 0% | 11.97% | 11.97% | 80% | 9.579% | 6.8121 | 9.4979 | 6 | 40.8726 | 15.0644 | 30.8% | 30.8%
11 | 311 | 7 | 7451 | 11 | 3 | 57.58 | 92.58 | 150.16 | 92.58 | 46.29 | 311 | 7451 | 660 | 306.7397 | -16.3153 | 3.9388 | 634.284 | 10.637 | 20.4443 | 24.2765 | 24.2765 | 21.5769 | 158.4231 | 27.1104 | 124.6624 | 124.6624 | 79.022 | 203.6844 | 0.047384 | 4.738% | 92.1061 | 4.3644 | 3.0551 | 132.4833 | 132.4833 | 2.306% | 11.91% | 11.91% | 80% | 9.528% | 8.7755 | 9.3069 | 6 | 52.6532 | 19.4063 | 39.74% | 39.74%
11 | 311 | 7 | 7452 | 12 | 3.4 | 62.86 | 97.14 | 160 | 97.14 | 48.57 | 311 | 7452 | 720 | 306.7397 | -16.3153 | 3.9388 | 694.284 | 11.637 | 5.4443 | 26.7163 | 26.7163 | 5.8509 | 174.1491 | 18.8754 | 132.3025 | 132.3025 | 82.9142 | 215.2166 | 0.092436 | 9.244% | 97.321 | 8.996 | 6.2972 | 128.9338 | 128.9338 | 4.884% | 11.89% | 11.89% | 80% | 9.509% | 9.254 | 9.181 | 6 | 55.5239 | 20.4644 | 43.06% | 43.06%
11 | 311 | 7 | 7453 | 13 | 4.2 | 60.92 | 119.72 | 180.64 | 119.72 | 59.86 | 311 | 7453 | 780 | 306.7397 | -16.3153 | 3.9388 | 754.284 | 12.637 | -9.5557 | 26.3222 | 26.3222 | 10.2388 | 190.2388 | 20.4066 | 128.7649 | 128.7649 | 102.1874 | 230.9523 | 0.14929 | 14.93% | 104.4366 | 15.5917 | 10.9142 | 130.2662 | 130.2662 | 8.378% | 11.85% | 11.85% | 80% | 9.477% | 9.8977 | 8.9325 | 6 | 59.386 | 21.8878 | 45.59% | 45.59%
11 | 311 | 7 | 7454 | 14 | 3.8 | 42.22 | 108.33 | 150.55 | 108.33 | 54.17 | 311 | 7454 | 840 | 306.7397 | -16.3153 | 3.9388 | 814.284 | 13.637 | -24.5557 | 23.1472 | 23.1472 | 25.7065 | 205.7065 | 30.2548 | 92.7749 | 92.7749 | 92.4654 | 185.2403 | -0.017485 | 0% | 83.7657 | 0 | 0 | 127.8264 | 127.8264 | 0% | 11.9% | 11.9% | 80% | 9.52% | 7.9743 | 9.0562 | 6 | 47.8459 | 17.6345 | 37.43% | 37.43%
11 | 311 | 7 | 7455 | 15 | 3.7 | 99.44 | 94.92 | 194.36 | 94.92 | 47.46 | 311 | 7455 | 900 | 306.7397 | -16.3153 | 3.9388 | 874.284 | 14.637 | -39.5557 | 17.5797 | 17.5797 | 39.8758 | 219.8758 | 43.0394 | 240.634 | 240.634 | 81.0193 | 321.6533 | 0.33015 | 33.02% | 145.4516 | 48.0215 | 33.6151 | 107.3957 | 107.3957 | 31.3% | 11.78% | 11.78% | 85% | 10.01% | 14.5651 | 9.0873 | 6 | 87.3906 | 32.2094 | 81.37% | 81.37%
11 | 311 | 7 | 7456 | 16 | 3.9 | 61.75 | 74.72 | 136.47 | 74.72 | 37.36 | 311 | 7456 | 960 | 306.7397 | -16.3153 | 3.9388 | 934.284 | 15.637 | -54.5557 | 10.1622 | 10.1622 | 52.5924 | 232.5924 | 56.7993 | 191.6435 | 191.6435 | 63.7775 | 255.4211 | 0.20918 | 20.92% | 115.5014 | 24.1602 | 16.9122 | 146.2509 | 146.2509 | 11.56% | 11.83% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7457 | 17 | 3.6 | 19.44 | 62.64 | 82.08 | 62.64 | 31.32 | 311 | 7457 | 1020 | 306.7397 | -16.3153 | 3.9388 | 994.284 | 16.637 | -69.5557 | 1.4248 | 1.4248 | 64.0999 | 244.0999 | 70.9525 | 0 | 0 | 53.4666 | 53.4666 | -2.0512 | 0% | 24.1776 | 0 | 0 | 141.4052 | 141.4052 | 0% | 12.03% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7458 | 18 | 3 | 0 | 3.69 | 3.69 | 3.69 | 1.85 | 311 | 7458 | 1080 | 306.7397 | -16.3153 | 3.9388 | 1054.284 | 17.637 | -84.5557 | -8.184 | 0 | 65.7819 | 245.7819 | 73.1383 | 0 | 0 | 3.1496 | 3.1496 | -48.1261 | 0% | 1.4243 | 0 | 0 | 133.6391 | 133.6391 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7459 | 19 | 2.8 | 0 | 0 | 0 | 0 | 0 | 311 | 7459 | 1140 | 306.7397 | -16.3153 | 3.9388 | 1114.284 | 18.637 | -99.5557 | -18.2895 | 0 | 65.7819 | 245.7819 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.7885 | 130.7885 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7460 | 20 | 3.6 | 0 | 0 | 0 | 0 | 0 | 311 | 7460 | 1200 | 306.7397 | -16.3153 | 3.9388 | 1174.284 | 19.637 | -114.5557 | -28.545 | 0 | 65.7819 | 245.7819 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.7514 | 128.7514 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7461 | 21 | 3.8 | 0 | 0 | 0 | 0 | 0 | 311 | 7461 | 1260 | 306.7397 | -16.3153 | 3.9388 | 1234.284 | 20.637 | -129.5557 | -38.555 | 0 | 65.7819 | 245.7819 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7445 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7462 | 22 | 4.4 | 0 | 0 | 0 | 0 | 0 | 311 | 7462 | 1320 | 306.7397 | -16.3153 | 3.9388 | 1294.284 | 21.637 | -144.5557 | -47.7449 | 0 | 65.7819 | 245.7819 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5648 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7463 | 23 | 4 | 0 | 0 | 0 | 0 | 0 | 311 | 7463 | 1380 | 306.7397 | -16.3153 | 3.9388 | 1354.284 | 22.637 | -159.5557 | -55.141 | 0 | 65.7819 | 245.7819 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.9686 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 311 | 7 | 7464 | 24 | 4 | 0 | 0 | 0 | 0 | 0 | 311 | 7464 | 1440 | 306.7397 | -16.3153 | 3.9388 | 1414.284 | 23.637 | -174.5557 | -59.2039 | 0 | 65.7819 | 245.7819 | 73.1383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7629 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7465 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 312 | 7465 | 60 | 307.726 | -16.6123 | 4.0019 | 34.284 | 0.6381 | 170.4285 | -58.8084 | 0 | 65.3251 | 114.6749 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1452 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7466 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 312 | 7466 | 120 | 307.726 | -16.6123 | 4.0019 | 94.284 | 1.6381 | 155.4285 | -53.6246 | 0 | 65.3251 | 114.6749 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7849 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7467 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 312 | 7467 | 180 | 307.726 | -16.6123 | 4.0019 | 154.284 | 2.6381 | 140.4285 | -45.5764 | 0 | 65.3251 | 114.6749 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4246 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7468 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 312 | 7468 | 240 | 307.726 | -16.6123 | 4.0019 | 214.284 | 3.6381 | 125.4285 | -36.0682 | 0 | 65.3251 | 114.6749 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4246 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7469 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 312 | 7469 | 300 | 307.726 | -16.6123 | 4.0019 | 274.284 | 4.6381 | 110.4285 | -25.9373 | 0 | 65.3251 | 114.6749 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.9202 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7470 | 6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 312 | 7470 | 360 | 307.726 | -16.6123 | 4.0019 | 334.284 | 5.6381 | 95.4285 | -15.689 | 0 | 65.3251 | 114.6749 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -1.3159 | 0 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7471 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 312 | 7471 | 420 | 307.726 | -16.6123 | 4.0019 | 394.284 | 6.6381 | 80.4285 | -5.6939 | 0 | 65.3251 | 114.6749 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 155.3004 | 155.3004 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7472 | 8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 312 | 7472 | 480 | 307.726 | -16.6123 | 4.0019 | 454.284 | 7.6381 | 65.4285 | 3.7011 | 3.7011 | 60.8451 | 119.1549 | 67.0822 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 162.0961 | 162.0961 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7473 | 9 | 2.9 | 20.64 | 22.97 | 43.61 | 22.97 | 11.49 | 312 | 7473 | 540 | 307.726 | -16.6123 | 4.0019 | 514.284 | 8.6381 | 50.4285 | 12.106 | 12.106 | 49.0653 | 130.9347 | 53.0379 | 59.1766 | 59.1766 | 19.6061 | 78.7827 | -1.1552 | 0% | 35.6255 | 0 | 0 | 145.9017 | 145.9017 | 0% | 12.03% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7474 | 10 | 3 | 81.67 | 51.94 | 133.61 | 51.94 | 25.97 | 312 | 7474 | 600 | 307.726 | -16.6123 | 4.0019 | 574.284 | 9.6381 | 35.4285 | 19.0504 | 19.0504 | 35.9924 | 144.0076 | 39.5038 | 193.0611 | 193.0611 | 44.3336 | 237.3947 | 0.15482 | 15.48% | 107.3499 | 16.6204 | 11.6343 | 149.9847 | 149.9847 | 7.757% | 11.88% | 11.88% | 80% | 9.502% | 10.2008 | 9.3069 | 6 | 61.2051 | 22.5583 | 40.81% | 40.81%
11 | 312 | 8 | 7475 | 11 | 3.1 | 145.83 | 64.72 | 210.55 | 64.72 | 32.36 | 312 | 7475 | 660 | 307.726 | -16.6123 | 4.0019 | 634.284 | 10.6381 | 20.4285 | 23.9938 | 23.9938 | 21.4756 | 158.5244 | 27.2907 | 318.7057 | 318.7057 | 55.242 | 373.9477 | 0.39253 | 39.25% | 169.0991 | 66.3766 | 46.4636 | 127.6899 | 127.6899 | 36.39% | 11.75% | 11.75% | 85% | 9.986% | 16.8859 | 9.2753 | 6 | 101.3155 | 37.3417 | 79.35% | 79.35%
11 | 312 | 8 | 7476 | 12 | 3.2 | 189.36 | 77.58 | 266.94 | 77.58 | 38.79 | 312 | 7476 | 720 | 307.726 | -16.6123 | 4.0019 | 694.284 | 11.6381 | 5.4285 | 26.4212 | 26.4212 | 5.8099 | 174.1901 | 19.1551 | 401.9978 | 401.9978 | 66.2187 | 468.2165 | 0.47589 | 47.59% | 211.7275 | 100.7595 | 70.5317 | 122.4362 | 122.4362 | 57.61% | 11.66% | 11.66% | 85% | 9.91% | 20.9817 | 9.2438 | 6 | 125.8904 | 46.3992 | 102.8% | 102.8%
11 | 312 | 8 | 7477 | 13 | 4.5 | 206.11 | 135.08 | 341.19 | 135.08 | 67.54 | 312 | 7477 | 780 | 307.726 | -16.6123 | 4.0019 | 754.284 | 12.6381 | -9.5715 | 26.0257 | 26.0257 | 10.2136 | 190.2136 | 20.6754 | 439.4866 | 439.4866 | 115.298 | 554.7846 | 0.53275 | 53.28% | 250.8736 | 133.6541 | 93.5579 | 125.6651 | 125.6651 | 74.45% | 11.56% | 11.56% | 90% | 10.4% | 26.1033 | 8.8405 | 6 | 156.6195 | 57.725 | 124.6% | 124.6%
11 | 312 | 8 | 7478 | 14 | 5.6 | 151.58 | 136.31 | 287.89 | 136.31 | 68.16 | 312 | 7478 | 840 | 307.726 | -16.6123 | 4.0019 | 814.284 | 13.6381 | -24.5715 | 22.8602 | 22.8602 | 25.6223 | 205.6223 | 30.4362 | 336.4145 | 336.4145 | 116.3479 | 452.7624 | 0.47747 | 47.75% | 204.7392 | 97.7565 | 68.4295 | 124.2354 | 124.2354 | 55.08% | 11.63% | 11.63% | 85% | 9.883% | 20.2343 | 8.5084 | 6 | 121.4057 | 44.7463 | 97.72% | 97.72%
11 | 312 | 8 | 7479 | 15 | 6.9 | 146.58 | 101.67 | 248.25 | 101.67 | 50.84 | 312 | 7479 | 900 | 307.726 | -16.6123 | 4.0019 | 874.284 | 14.6381 | -39.5715 | 17.3087 | 17.3087 | 39.7476 | 219.7476 | 43.1613 | 359.3713 | 359.3713 | 86.7808 | 446.1521 | 0.47958 | 47.96% | 201.75 | 96.7554 | 67.7288 | 121.869 | 121.869 | 55.58% | 11.61% | 11.61% | 85% | 9.866% | 19.9045 | 8.127 | 6 | 119.4268 | 44.0169 | 98% | 98%
11 | 312 | 8 | 7480 | 16 | 7.2 | 84.44 | 85 | 169.44 | 85 | 42.5 | 312 | 7480 | 960 | 307.726 | -16.6123 | 4.0019 | 934.284 | 15.6381 | -54.5715 | 9.9089 | 9.9089 | 52.4342 | 232.4342 | 56.8828 | 0 | 0 | 72.552 | 72.552 | -1.1812 | 0% | 32.808 | 0 | 0 | 117.0816 | 117.0816 | 0% | 11.86% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7481 | 17 | 7.3 | 17.22 | 48.89 | 66.11 | 48.89 | 24.45 | 312 | 7481 | 1020 | 307.726 | -16.6123 | 4.0019 | 994.284 | 16.6381 | -69.5715 | 1.1873 | 1.1873 | 63.9208 | 243.9208 | 71.0078 | 0 | 0 | 41.7302 | 41.7302 | -2.6417 | 0% | 18.8704 | 0 | 0 | 150.8785 | 150.8785 | 0% | 11.88% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7482 | 18 | 6.5 | 0 | 5 | 5 | 5 | 2.5 | 312 | 7482 | 1080 | 307.726 | -16.6123 | 4.0019 | 1054.284 | 17.6381 | -84.5715 | -8.4096 | 0 | 65.3251 | 245.3251 | 72.8308 | 0 | 0 | 4.2678 | 4.2678 | -33.3338 | 0% | 1.9299 | 0 | 0 | 142.3564 | 142.3564 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7483 | 19 | 4.5 | 0 | 0 | 0 | 0 | 0 | 312 | 7483 | 1140 | 307.726 | -16.6123 | 4.0019 | 1114.284 | 18.6381 | -99.5715 | -18.5089 | 0 | 65.3251 | 245.3251 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.6467 | 135.6467 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7484 | 20 | 3 | 0 | 0 | 0 | 0 | 0 | 312 | 7484 | 1200 | 307.726 | -16.6123 | 4.0019 | 1174.284 | 19.6381 | -114.5715 | -28.7649 | 0 | 65.3251 | 245.3251 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.5302 | 128.5302 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7485 | 21 | 1.8 | 0 | 0 | 0 | 0 | 0 | 312 | 7485 | 1260 | 307.726 | -16.6123 | 4.0019 | 1234.284 | 20.6381 | -129.5715 | -38.784 | 0 | 65.3251 | 245.3251 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4812 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7486 | 22 | 1.8 | 0 | 0 | 0 | 0 | 0 | 312 | 7486 | 1320 | 307.726 | -16.6123 | 4.0019 | 1294.284 | 21.6381 | -144.5715 | -47.9932 | 0 | 65.3251 | 245.3251 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5788 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7487 | 23 | 1.7 | 0 | 0 | 0 | 0 | 0 | 312 | 7487 | 1380 | 307.726 | -16.6123 | 4.0019 | 1354.284 | 22.6381 | -159.5715 | -55.4169 | 0 | 65.3251 | 245.3251 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3709 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
11 | 312 | 8 | 7488 | 24 | 0.9 | 0 | 0 | 0 | 0 | 0 | 312 | 7488 | 1440 | 307.726 | -16.6123 | 4.0019 | 1414.284 | 23.6381 | -174.5715 | -59.5004 | 0 | 65.3251 | 245.3251 | 72.8308 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2298 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7489 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 7489 | 60 | 308.7123 | -16.904 | 4.0545 | 34.284 | 0.63898 | 170.4154 | -59.0901 | 0 | 64.8754 | 115.1246 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1827 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7490 | 2 | -1 | 0 | 0 | 0 | 0 | 0 | 313 | 7490 | 120 | 308.7123 | -16.904 | 4.0545 | 94.284 | 1.639 | 155.4154 | -53.8742 | 0 | 64.8754 | 115.1246 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5806 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7491 | 3 | -1.4 | 0 | 0 | 0 | 0 | 0 | 313 | 7491 | 180 | 308.7123 | -16.904 | 4.0545 | 154.284 | 2.639 | 140.4154 | -45.7964 | 0 | 64.8754 | 115.1246 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0642 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7492 | 4 | -2 | 0 | 0 | 0 | 0 | 0 | 313 | 7492 | 240 | 308.7123 | -16.904 | 4.0545 | 214.284 | 3.639 | 125.4154 | -36.2703 | 0 | 64.8754 | 115.1246 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9786 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7493 | 5 | -2.5 | 0 | 0 | 0 | 0 | 0 | 313 | 7493 | 300 | 308.7123 | -16.904 | 4.0545 | 274.284 | 4.639 | 110.4154 | -26.1324 | 0 | 64.8754 | 115.1246 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2939 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7494 | 6 | -2.1 | 0 | 0 | 0 | 0 | 0 | 313 | 7494 | 360 | 308.7123 | -16.904 | 4.0545 | 334.284 | 5.639 | 95.4154 | -15.886 | 0 | 64.8754 | 115.1246 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9516 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7495 | 7 | -1.8 | 0 | 0 | 0 | 0 | 0 | 313 | 7495 | 420 | 308.7123 | -16.904 | 4.0545 | 394.284 | 6.639 | 80.4154 | -5.8996 | 0 | 64.8754 | 115.1246 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.3915 | 131.3915 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7496 | 8 | -2.4 | 0 | 1.11 | 1.11 | 1.11 | 0.56 | 313 | 7496 | 480 | 308.7123 | -16.904 | 4.0545 | 454.284 | 7.639 | 65.4154 | 3.481 | 3.481 | 60.6528 | 119.3472 | 67.1172 | 0 | 0 | 0.94744 | 0.94744 | -175.9048 | 0% | 0.42843 | 0 | 0 | 132.8148 | 132.8148 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7497 | 9 | -1.2 | 0.75 | 20.36 | 21.11 | 20.36 | 10.18 | 313 | 7497 | 540 | 308.7123 | -16.904 | 4.0545 | 514.284 | 8.639 | 50.4154 | 11.8672 | 11.8672 | 48.8936 | 131.1064 | 53.1036 | 2.1896 | 2.1896 | 17.3783 | 19.5679 | -7.599 | 0% | 8.8486 | 0 | 0 | 115.0512 | 115.0512 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7498 | 10 | -1.2 | 2.14 | 60.56 | 62.7 | 60.56 | 30.28 | 313 | 7498 | 600 | 308.7123 | -16.904 | 4.0545 | 574.284 | 9.639 | 35.4154 | 18.7909 | 18.7909 | 35.8509 | 144.1491 | 39.6135 | 5.118 | 5.118 | 51.6912 | 56.8092 | -2.0904 | 0% | 25.6891 | 0 | 0 | 116.8353 | 116.8353 | 0% | 12.22% | 12.22% | 80% | 9.775% | 2.5111 | 10.6967 | 6 | 15.0664 | 5.553 | 12.9% | 12.9%
11 | 313 | 9 | 7499 | 11 | -0.8 | 6.11 | 105.92 | 112.03 | 105.92 | 52.96 | 313 | 7499 | 660 | 308.7123 | -16.904 | 4.0545 | 634.284 | 10.639 | 20.4154 | 23.7155 | 23.7155 | 21.379 | 158.621 | 27.4713 | 13.4786 | 13.4786 | 90.4084 | 103.887 | -0.76922 | 0% | 46.9777 | 0 | 0 | 118.2452 | 118.2452 | 0% | 12.15% | 12.15% | 80% | 9.719% | 4.5656 | 10.559 | 6 | 27.3937 | 10.0964 | 23.17% | 23.17%
11 | 313 | 9 | 7500 | 12 | 0 | 29.81 | 165.19 | 195 | 165.19 | 82.6 | 313 | 7500 | 720 | 308.7123 | -16.904 | 4.0545 | 694.284 | 11.639 | 5.4154 | 26.1312 | 26.1312 | 5.7725 | 174.2275 | 19.4311 | 63.829 | 63.829 | 140.9985 | 204.8275 | 0.015739 | 1.574% | 92.623 | 1.4578 | 1.0205 | 120.8655 | 120.8655 | 0.8443% | 12.01% | 12.01% | 80% | 9.605% | 8.8968 | 10.287 | 6 | 53.3806 | 19.6744 | 44.17% | 44.17%
11 | 313 | 9 | 7501 | 13 | 1.2 | 29.36 | 171.39 | 200.75 | 171.39 | 85.7 | 313 | 7501 | 780 | 308.7123 | -16.904 | 4.0545 | 754.284 | 12.639 | -9.5846 | 25.7348 | 25.7348 | 10.1864 | 190.1864 | 20.939 | 63.1523 | 63.1523 | 146.2905 | 209.4428 | 0.047209 | 4.721% | 94.71 | 4.4712 | 3.1298 | 101.3705 | 101.3705 | 3.088% | 11.96% | 11.96% | 80% | 9.57% | 9.0639 | 9.8874 | 6 | 54.3831 | 20.0439 | 53.65% | 53.65%
11 | 313 | 9 | 7502 | 14 | 2 | 7.22 | 147.78 | 155 | 147.78 | 73.89 | 313 | 7502 | 840 | 308.7123 | -16.904 | 4.0545 | 814.284 | 13.639 | -24.5846 | 22.5788 | 22.5788 | 25.5377 | 205.5377 | 30.6141 | 16.1833 | 16.1833 | 126.1381 | 142.3215 | -0.29595 | 0% | 64.3578 | 0 | 0 | 121.0745 | 121.0745 | 0% | 12% | 12% | 80% | 9.602% | 6.1799 | 9.6266 | 6 | 37.0797 | 13.6664 | 30.63% | 30.63%
11 | 313 | 9 | 7503 | 15 | 2.2 | 2.78 | 106.47 | 109.25 | 106.47 | 53.24 | 313 | 7503 | 900 | 308.7123 | -16.904 | 4.0545 | 874.284 | 14.639 | -39.5846 | 17.0434 | 17.0434 | 39.6198 | 219.6198 | 43.2803 | 6.9051 | 6.9051 | 90.8778 | 97.7829 | -0.79196 | 0% | 44.2174 | 0 | 0 | 139.0747 | 139.0747 | 0% | 12.04% | 12.04% | 80% | 9.632% | 4.2588 | 9.5621 | 6 | 25.553 | 9.418 | 18.37% | 18.37%
11 | 313 | 9 | 7504 | 16 | 2.6 | 1.86 | 48.97 | 50.83 | 48.97 | 24.49 | 313 | 7504 | 960 | 308.7123 | -16.904 | 4.0545 | 934.284 | 15.639 | -54.5846 | 9.6614 | 9.6614 | 52.2771 | 232.2771 | 56.9635 | 0 | 0 | 41.7985 | 41.7985 | -2.9063 | 0% | 18.9013 | 0 | 0 | 136.1562 | 136.1562 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7505 | 17 | 2.2 | 0.75 | 19.25 | 20 | 19.25 | 9.63 | 313 | 7505 | 1020 | 308.7123 | -16.904 | 4.0545 | 994.284 | 16.639 | -69.5846 | 0.95557 | 0.95557 | 63.7432 | 243.7432 | 71.0605 | 0 | 0 | 16.4309 | 16.4309 | -8.6938 | 0% | 7.4301 | 0 | 0 | 133.1444 | 133.1444 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7506 | 18 | 1.5 | 0 | 0 | 0 | 0 | 0 | 313 | 7506 | 1080 | 308.7123 | -16.904 | 4.0545 | 1054.284 | 17.639 | -84.5846 | -8.6296 | 0 | 64.8754 | 244.8754 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.9958 | 129.9958 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7507 | 19 | 1.8 | 0 | 0 | 0 | 0 | 0 | 313 | 7507 | 1140 | 308.7123 | -16.904 | 4.0545 | 1114.284 | 18.639 | -99.5846 | -18.7225 | 0 | 64.8754 | 244.8754 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.1045 | 129.1045 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7508 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 313 | 7508 | 1200 | 308.7123 | -16.904 | 4.0545 | 1174.284 | 19.639 | -114.5846 | -28.979 | 0 | 64.8754 | 244.8754 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.4105 | 127.4105 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7509 | 21 | 2.2 | 0 | 0 | 0 | 0 | 0 | 313 | 7509 | 1260 | 308.7123 | -16.904 | 4.0545 | 1234.284 | 20.639 | -129.5846 | -39.0069 | 0 | 64.8754 | 244.8754 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.766 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7510 | 22 | 1.9 | 0 | 0 | 0 | 0 | 0 | 313 | 7510 | 1320 | 308.7123 | -16.904 | 4.0545 | 1294.284 | 21.639 | -144.5846 | -48.2353 | 0 | 64.8754 | 244.8754 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.6651 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7511 | 23 | 1.8 | 0 | 0 | 0 | 0 | 0 | 313 | 7511 | 1380 | 308.7123 | -16.904 | 4.0545 | 1354.284 | 22.639 | -159.5846 | -55.6866 | 0 | 64.8754 | 244.8754 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.6915 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 313 | 9 | 7512 | 24 | 1.7 | 0 | 0 | 0 | 0 | 0 | 313 | 7512 | 1440 | 308.7123 | -16.904 | 4.0545 | 1414.284 | 23.639 | -174.5846 | -59.7913 | 0 | 64.8754 | 244.8754 | 72.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.7179 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7513 | 1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 314 | 7513 | 60 | 309.6986 | -17.1904 | 4.0966 | 34.284 | 0.63968 | 170.4048 | -59.367 | 0 | 64.4331 | 115.5669 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5088 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7514 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 314 | 7514 | 120 | 309.6986 | -17.1904 | 4.0966 | 94.284 | 1.6397 | 155.4048 | -54.1198 | 0 | 64.4331 | 115.5669 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.8765 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7515 | 3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 314 | 7515 | 180 | 309.6986 | -17.1904 | 4.0966 | 154.284 | 2.6397 | 140.4048 | -46.0131 | 0 | 64.4331 | 115.5669 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0918 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7516 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 314 | 7516 | 240 | 309.6986 | -17.1904 | 4.0966 | 214.284 | 3.6397 | 125.4048 | -36.4697 | 0 | 64.4331 | 115.5669 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7014 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7517 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 7517 | 300 | 309.6986 | -17.1904 | 4.0966 | 274.284 | 4.6397 | 110.4048 | -26.3253 | 0 | 64.4331 | 115.5669 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.3742 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7518 | 6 | -0.5 | 0 | 0 | 0 | 0 | 0 | 314 | 7518 | 360 | 309.6986 | -17.1904 | 4.0966 | 334.284 | 5.6397 | 95.4048 | -16.0807 | 0 | 64.4331 | 115.5669 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.931 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7519 | 7 | -0.9 | 0 | 0 | 0 | 0 | 0 | 314 | 7519 | 420 | 309.6986 | -17.1904 | 4.0966 | 394.284 | 6.6397 | 80.4048 | -6.103 | 0 | 64.4331 | 115.5669 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.4397 | 144.4397 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7520 | 8 | -1.4 | 0 | 0 | 0 | 0 | 0 | 314 | 7520 | 480 | 309.6986 | -17.1904 | 4.0966 | 454.284 | 7.6397 | 65.4048 | 3.2635 | 3.2635 | 60.466 | 119.534 | 67.1544 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.0628 | 148.0628 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7521 | 9 | -1.6 | 2.5 | 20.97 | 23.47 | 20.97 | 10.49 | 314 | 7521 | 540 | 309.6986 | -17.1904 | 4.0966 | 514.284 | 8.6397 | 50.4048 | 11.6314 | 11.6314 | 48.7273 | 131.2727 | 53.1714 | 7.4328 | 7.4328 | 17.899 | 25.3318 | -5.7263 | 0% | 11.455 | 0 | 0 | 128.8108 | 128.8108 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7522 | 10 | -1.5 | 48.69 | 72.97 | 121.66 | 72.97 | 36.49 | 314 | 7522 | 600 | 309.6986 | -17.1904 | 4.0966 | 574.284 | 9.6397 | 35.4048 | 18.5351 | 18.5351 | 35.7147 | 144.2853 | 39.7248 | 117.8053 | 117.8053 | 62.2838 | 180.0891 | -0.11319 | 0% | 81.4363 | 0 | 0 | 133.7906 | 133.7906 | 0% | 12.09% | 12.09% | 80% | 9.668% | 7.8733 | 10.8007 | 6 | 47.2397 | 17.4111 | 35.31% | 35.31%
11 | 314 | 10 | 7523 | 11 | -0.6 | 44.17 | 129.92 | 174.09 | 129.92 | 64.96 | 314 | 7523 | 660 | 309.6986 | -17.1904 | 4.0966 | 634.284 | 10.6397 | 20.4048 | 23.4417 | 23.4417 | 21.287 | 158.713 | 27.652 | 98.3496 | 98.3496 | 110.8937 | 209.2433 | 0.025283 | 2.528% | 94.6198 | 2.3923 | 1.6746 | 133.7408 | 133.7408 | 1.252% | 12.02% | 12.02% | 80% | 9.617% | 9.0996 | 10.4906 | 6 | 54.5979 | 20.1231 | 40.82% | 40.82%
11 | 314 | 10 | 7524 | 12 | -0.2 | 77.78 | 156.19 | 233.97 | 156.19 | 78.1 | 314 | 7524 | 720 | 309.6986 | -17.1904 | 4.0966 | 694.284 | 11.6397 | 5.4048 | 25.8463 | 25.8463 | 5.7384 | 174.2616 | 19.703 | 167.966 | 167.966 | 133.3165 | 301.2825 | 0.26646 | 26.65% | 136.24 | 36.3024 | 25.4117 | 110.6227 | 110.6227 | 22.97% | 11.91% | 11.91% | 85% | 10.12% | 13.7877 | 10.3546 | 6 | 82.7262 | 30.4903 | 74.78% | 74.78%
11 | 314 | 10 | 7525 | 13 | 1.2 | 58.69 | 123.14 | 181.83 | 123.14 | 61.57 | 314 | 7525 | 780 | 309.6986 | -17.1904 | 4.0966 | 754.284 | 12.6397 | -9.5952 | 25.4494 | 25.4494 | 10.1573 | 190.1573 | 21.1975 | 127.3381 | 127.3381 | 105.1066 | 232.4446 | 0.1221 | 12.21% | 105.1115 | 12.8339 | 8.9838 | 130.4964 | 130.4964 | 6.884% | 11.94% | 11.94% | 80% | 9.551% | 10.0393 | 9.8874 | 6 | 60.2357 | 22.201 | 46.16% | 46.16%
11 | 314 | 10 | 7526 | 14 | 3 | 90.75 | 122.5 | 213.25 | 122.5 | 61.25 | 314 | 7526 | 840 | 309.6986 | -17.1904 | 4.0966 | 814.284 | 13.6397 | -24.5952 | 22.3033 | 22.3033 | 25.4525 | 205.4525 | 30.7883 | 205.4233 | 205.4233 | 104.5603 | 309.9836 | 0.30684 | 30.68% | 140.1746 | 43.0115 | 30.108 | 113.2665 | 113.2665 | 26.58% | 11.81% | 11.81% | 85% | 10.04% | 14.0716 | 9.3069 | 6 | 84.4297 | 31.1181 | 74.54% | 74.54%
11 | 314 | 10 | 7527 | 15 | 4.8 | 86.39 | 113.97 | 200.36 | 113.97 | 56.99 | 314 | 7527 | 900 | 309.6986 | -17.1904 | 4.0966 | 874.284 | 14.6397 | -39.5952 | 16.784 | 16.784 | 39.4927 | 219.4927 | 43.3962 | 217.3839 | 217.3839 | 97.2795 | 314.6634 | 0.32806 | 32.81% | 142.2908 | 46.68 | 32.676 | 113.9686 | 113.9686 | 28.67% | 11.76% | 11.76% | 85% | 9.994% | 14.2207 | 8.7491 | 6 | 85.3239 | 31.4477 | 74.87% | 74.87%
11 | 314 | 10 | 7528 | 16 | 3.5 | 83.97 | 80.92 | 164.89 | 80.92 | 40.46 | 314 | 7528 | 960 | 309.6986 | -17.1904 | 4.0966 | 934.284 | 15.6397 | -54.5952 | 9.4196 | 9.4196 | 52.1211 | 232.1211 | 57.0414 | 0 | 0 | 69.0695 | 69.0695 | -1.4097 | 0% | 31.2332 | 0 | 0 | 109.8909 | 109.8909 | 0% | 12.02% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7529 | 17 | 4.2 | 11.75 | 40.36 | 52.11 | 40.36 | 20.18 | 314 | 7529 | 1020 | 309.6986 | -17.1904 | 4.0966 | 994.284 | 16.6397 | -69.5952 | 0.72954 | 0.72954 | 63.5671 | 243.5671 | 71.1104 | 0 | 0 | 34.4494 | 34.4494 | -3.5852 | 0% | 15.578 | 0 | 0 | 144.7902 | 144.7902 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7530 | 18 | 3.5 | 0 | 6.67 | 6.67 | 6.67 | 3.34 | 314 | 7530 | 1080 | 309.6986 | -17.1904 | 4.0966 | 1054.284 | 17.6397 | -84.5952 | -8.8439 | 0 | 64.4331 | 244.4331 | 72.232 | 0 | 0 | 5.6932 | 5.6932 | -26.0523 | 0% | 2.5745 | 0 | 0 | 138.099 | 138.099 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7531 | 19 | 3 | 0 | 0 | 0 | 0 | 0 | 314 | 7531 | 1140 | 309.6986 | -17.1904 | 4.0966 | 1114.284 | 18.6397 | -99.5952 | -18.9303 | 0 | 64.4331 | 244.4331 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.0129 | 134.0129 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7532 | 20 | 2.2 | 0 | 0 | 0 | 0 | 0 | 314 | 7532 | 1200 | 309.6986 | -17.1904 | 4.0966 | 1174.284 | 19.6397 | -114.5952 | -29.187 | 0 | 64.4331 | 244.4331 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.6363 | 128.6363 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7533 | 21 | 2.2 | 0 | 0 | 0 | 0 | 0 | 314 | 7533 | 1260 | 309.6986 | -17.1904 | 4.0966 | 1234.284 | 20.6397 | -129.5952 | -39.2237 | 0 | 64.4331 | 244.4331 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.3872 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7534 | 22 | 2 | 0 | 0 | 0 | 0 | 0 | 314 | 7534 | 1320 | 309.6986 | -17.1904 | 4.0966 | 1294.284 | 21.6397 | -144.5952 | -48.471 | 0 | 64.4331 | 244.4331 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.625 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7535 | 23 | 1.6 | 0 | 0 | 0 | 0 | 0 | 314 | 7535 | 1380 | 309.6986 | -17.1904 | 4.0966 | 1354.284 | 22.6397 | -159.5952 | -55.9501 | 0 | 64.4331 | 244.4331 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.9926 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
11 | 314 | 10 | 7536 | 24 | 1.3 | 0 | 0 | 0 | 0 | 0 | 314 | 7536 | 1440 | 309.6986 | -17.1904 | 4.0966 | 1414.284 | 23.6397 | -174.5952 | -60.0766 | 0 | 64.4331 | 244.4331 | 72.232 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2079 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7537 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 315 | 7537 | 60 | 310.6849 | -17.4713 | 4.1282 | 34.284 | 0.6402 | 170.397 | -59.639 | 0 | 63.9982 | 116.0018 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5706 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7538 | 2 | -0.4 | 0 | 0 | 0 | 0 | 0 | 315 | 7538 | 120 | 310.6849 | -17.4713 | 4.1282 | 94.284 | 1.6402 | 155.397 | -54.3613 | 0 | 63.9982 | 116.0018 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.491 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7539 | 3 | -0.8 | 0 | 0 | 0 | 0 | 0 | 315 | 7539 | 180 | 310.6849 | -17.4713 | 4.1282 | 154.284 | 2.6402 | 140.397 | -46.2266 | 0 | 63.9982 | 116.0018 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4969 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7540 | 4 | -1.2 | 0 | 0 | 0 | 0 | 0 | 315 | 7540 | 240 | 310.6849 | -17.4713 | 4.1282 | 214.284 | 3.6402 | 125.397 | -36.6664 | 0 | 63.9982 | 116.0018 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.1065 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7541 | 5 | -1.6 | 0 | 0 | 0 | 0 | 0 | 315 | 7541 | 300 | 310.6849 | -17.4713 | 4.1282 | 274.284 | 4.6402 | 110.397 | -26.5158 | 0 | 63.9982 | 116.0018 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.0371 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7542 | 6 | -2 | 0 | 0 | 0 | 0 | 0 | 315 | 7542 | 360 | 310.6849 | -17.4713 | 4.1282 | 334.284 | 5.6402 | 95.397 | -16.2732 | 0 | 63.9982 | 116.0018 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 5.3097 | 5.3097 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7543 | 7 | -1.6 | 0 | 0 | 0 | 0 | 0 | 315 | 7543 | 420 | 310.6849 | -17.4713 | 4.1282 | 394.284 | 6.6402 | 80.397 | -6.304 | 0 | 63.9982 | 116.0018 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 173.0956 | 173.0956 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7544 | 8 | -1 | 0 | 0 | 0 | 0 | 0 | 315 | 7544 | 480 | 310.6849 | -17.4713 | 4.1282 | 454.284 | 7.6402 | 65.397 | 3.0486 | 3.0486 | 60.2847 | 119.7153 | 67.1937 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 183.3701 | 183.3701 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7545 | 9 | -0.6 | 30.92 | 22.42 | 53.34 | 22.42 | 11.21 | 315 | 7545 | 540 | 310.6849 | -17.4713 | 4.1282 | 514.284 | 8.6402 | 50.397 | 11.3988 | 11.3988 | 48.5664 | 131.4336 | 53.2411 | 93.6267 | 93.6267 | 19.1367 | 112.7634 | -0.64098 | 0% | 50.9916 | 0 | 0 | 169.2585 | 169.2585 | 0% | 12.13% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7546 | 10 | 0 | 150.28 | 47.03 | 197.31 | 47.03 | 23.52 | 315 | 7546 | 600 | 310.6849 | -17.4713 | 4.1282 | 574.284 | 9.6402 | 35.397 | 18.2831 | 18.2831 | 35.5837 | 144.4163 | 39.8375 | 367.836 | 367.836 | 40.1426 | 407.9786 | 0.40825 | 40.83% | 184.4879 | 75.3172 | 52.722 | 176.3889 | 176.3889 | 29.89% | 11.78% | 11.78% | 85% | 10.02% | 18.4778 | 10.287 | 6 | 110.867 | 40.8621 | 62.85% | 62.85%
11 | 315 | 11 | 7547 | 11 | 1.1 | 235.19 | 82.5 | 317.69 | 82.5 | 41.25 | 315 | 7547 | 660 | 310.6849 | -17.4713 | 4.1282 | 634.284 | 10.6402 | 20.397 | 23.1724 | 23.1724 | 21.1996 | 158.8004 | 27.8327 | 528.5448 | 528.5448 | 70.4182 | 598.963 | 0.53896 | 53.9% | 270.8511 | 145.9776 | 102.1843 | 153.6928 | 153.6928 | 66.49% | 11.56% | 11.56% | 90% | 10.4% | 28.1817 | 9.9203 | 6 | 169.0904 | 62.3214 | 110% | 110%
11 | 315 | 11 | 7548 | 12 | 1.8 | 299.25 | 87.03 | 386.28 | 87.03 | 43.52 | 315 | 7548 | 720 | 310.6849 | -17.4713 | 4.1282 | 694.284 | 11.6402 | 5.397 | 25.5667 | 25.5667 | 5.7078 | 174.2922 | 19.9708 | 651.7158 | 651.7158 | 74.2848 | 726.0005 | 0.5877 | 58.77% | 328.2974 | 192.9399 | 135.0579 | 144.3549 | 144.3549 | 93.56% | 11.43% | 11.43% | 90% | 10.28% | 33.7604 | 9.6914 | 6 | 202.5621 | 74.658 | 140.3% | 140.3%
11 | 315 | 11 | 7549 | 13 | 2.1 | 280.08 | 101.39 | 381.47 | 101.39 | 50.7 | 315 | 7549 | 780 | 310.6849 | -17.4713 | 4.1282 | 754.284 | 12.6402 | -9.603 | 25.1699 | 25.1699 | 10.1263 | 190.1263 | 21.4506 | 612.927 | 612.927 | 86.5418 | 699.4688 | 0.58054 | 58.05% | 316.2998 | 183.6252 | 128.5376 | 141.0879 | 141.0879 | 91.1% | 11.45% | 11.45% | 90% | 10.31% | 32.5975 | 9.5943 | 6 | 195.5848 | 72.0864 | 138.6% | 138.6%
11 | 315 | 11 | 7550 | 14 | 2.7 | 331.19 | 73.69 | 404.88 | 73.69 | 36.85 | 315 | 7550 | 840 | 310.6849 | -17.4713 | 4.1282 | 814.284 | 13.6402 | -24.603 | 22.0337 | 22.0337 | 25.3669 | 205.3669 | 30.9588 | 757.0465 | 757.0465 | 62.8983 | 819.9448 | 0.61516 | 61.52% | 370.779 | 228.0877 | 159.6614 | 141.7401 | 141.7401 | 112.6% | 11.33% | 11.33% | 95% | 10.77% | 39.9194 | 9.4021 | 6 | 239.5167 | 88.2783 | 169% | 169%
11 | 315 | 11 | 7551 | 15 | 2.6 | 258.42 | 70.28 | 328.7 | 70.28 | 35.14 | 315 | 7551 | 900 | 310.6849 | -17.4713 | 4.1282 | 874.284 | 14.6402 | -39.603 | 16.5305 | 16.5305 | 39.3661 | 219.3661 | 43.509 | 658.7211 | 658.7211 | 59.9877 | 718.7088 | 0.58822 | 58.82% | 325.0001 | 191.1714 | 133.82 | 134.4343 | 134.4343 | 99.54% | 11.43% | 11.43% | 90% | 10.29% | 33.4322 | 9.4339 | 6 | 200.593 | 73.9323 | 149.2% | 149.2%
11 | 315 | 11 | 7552 | 16 | 2.5 | 160.19 | 51.75 | 211.94 | 51.75 | 25.88 | 315 | 7552 | 960 | 310.6849 | -17.4713 | 4.1282 | 934.284 | 15.6402 | -54.603 | 9.1837 | 9.1837 | 51.9664 | 231.9664 | 57.1163 | 0 | 0 | 44.1714 | 44.1714 | -2.7125 | 0% | 19.9743 | 0 | 0 | 126.6643 | 126.6643 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7553 | 17 | 2.4 | 23.61 | 37.31 | 60.92 | 37.31 | 18.66 | 315 | 7553 | 1020 | 310.6849 | -17.4713 | 4.1282 | 994.284 | 16.6402 | -69.603 | 0.50932 | 0.50932 | 63.3925 | 243.3925 | 71.1574 | 0 | 0 | 31.8461 | 31.8461 | -4.0811 | 0% | 14.4008 | 0 | 0 | 155.1202 | 155.1202 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7554 | 18 | 1.7 | 0 | 2.97 | 2.97 | 2.97 | 1.49 | 315 | 7554 | 1080 | 310.6849 | -17.4713 | 4.1282 | 1054.284 | 17.6402 | -84.603 | -9.0524 | 0 | 63.9982 | 243.9982 | 71.9411 | 0 | 0 | 2.5351 | 2.5351 | -61.2379 | 0% | 1.1464 | 0 | 0 | 144.0442 | 144.0442 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7555 | 19 | 1.3 | 0 | 0 | 0 | 0 | 0 | 315 | 7555 | 1140 | 310.6849 | -17.4713 | 4.1282 | 1114.284 | 18.6402 | -99.603 | -19.1323 | 0 | 63.9982 | 243.9982 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.8945 | 137.8945 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7556 | 20 | -0.5 | 0 | 0 | 0 | 0 | 0 | 315 | 7556 | 1200 | 310.6849 | -17.4713 | 4.1282 | 1174.284 | 19.6402 | -114.603 | -29.3891 | 0 | 63.9982 | 243.9982 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.5369 | 127.5369 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7557 | 21 | -0.6 | 0 | 0 | 0 | 0 | 0 | 315 | 7557 | 1260 | 310.6849 | -17.4713 | 4.1282 | 1234.284 | 20.6402 | -129.603 | -39.4342 | 0 | 63.9982 | 243.9982 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4779 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7558 | 22 | -1 | 0 | 0 | 0 | 0 | 0 | 315 | 7558 | 1320 | 310.6849 | -17.4713 | 4.1282 | 1294.284 | 21.6402 | -144.603 | -48.7002 | 0 | 63.9982 | 243.9982 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8199 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7559 | 23 | -1.2 | 0 | 0 | 0 | 0 | 0 | 315 | 7559 | 1380 | 310.6849 | -17.4713 | 4.1282 | 1354.284 | 22.6402 | -159.603 | -56.2072 | 0 | 63.9982 | 243.9982 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5211 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
11 | 315 | 11 | 7560 | 24 | -1.2 | 0 | 0 | 0 | 0 | 0 | 315 | 7560 | 1440 | 310.6849 | -17.4713 | 4.1282 | 1414.284 | 23.6402 | -174.603 | -60.3561 | 0 | 63.9982 | 243.9982 | 71.9411 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9174 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7561 | 1 | -1.5 | 0 | 0 | 0 | 0 | 0 | 316 | 7561 | 60 | 311.6712 | -17.7466 | 4.1493 | 34.284 | 0.64055 | 170.3917 | -59.906 | 0 | 63.5711 | 116.4289 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.9724 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7562 | 2 | -1 | 0 | 0 | 0 | 0 | 0 | 316 | 7562 | 120 | 311.6712 | -17.7466 | 4.1493 | 94.284 | 1.6406 | 155.3917 | -54.5987 | 0 | 63.5711 | 116.4289 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9035 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7563 | 3 | -1.2 | 0 | 0 | 0 | 0 | 0 | 316 | 7563 | 180 | 311.6712 | -17.7466 | 4.1493 | 154.284 | 2.6406 | 140.3917 | -46.4367 | 0 | 63.5711 | 116.4289 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9014 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7564 | 4 | -1.4 | 0 | 0 | 0 | 0 | 0 | 316 | 7564 | 240 | 311.6712 | -17.7466 | 4.1493 | 214.284 | 3.6406 | 125.3917 | -36.8604 | 0 | 63.5711 | 116.4289 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2062 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7565 | 5 | -1.4 | 0 | 0 | 0 | 0 | 0 | 316 | 7565 | 300 | 311.6712 | -17.7466 | 4.1493 | 274.284 | 4.6406 | 110.3917 | -26.7038 | 0 | 63.5711 | 116.4289 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.1279 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7566 | 6 | -1.4 | 0 | 0 | 0 | 0 | 0 | 316 | 7566 | 360 | 311.6712 | -17.7466 | 4.1493 | 334.284 | 5.6406 | 95.3917 | -16.4633 | 0 | 63.5711 | 116.4289 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.3309 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7567 | 7 | -1.3 | 0 | 0 | 0 | 0 | 0 | 316 | 7567 | 420 | 311.6712 | -17.7466 | 4.1493 | 394.284 | 6.6406 | 80.3917 | -6.5026 | 0 | 63.5711 | 116.4289 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 147.4764 | 147.4764 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7568 | 8 | -1.6 | 0 | 0 | 0 | 0 | 0 | 316 | 7568 | 480 | 311.6712 | -17.7466 | 4.1493 | 454.284 | 7.6406 | 65.3917 | 2.8365 | 2.8365 | 60.1089 | 119.8911 | 67.2352 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 152.151 | 152.151 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7569 | 9 | -1 | 11.31 | 23.53 | 34.84 | 23.53 | 11.77 | 316 | 7569 | 540 | 311.6712 | -17.7466 | 4.1493 | 514.284 | 8.6406 | 50.3917 | 11.1694 | 11.1694 | 48.4111 | 131.5889 | 53.3126 | 34.8826 | 34.8826 | 20.0841 | 54.9667 | -2.1784 | 0% | 24.856 | 0 | 0 | 135.5556 | 135.5556 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7570 | 10 | 0.6 | 66.86 | 72.22 | 139.08 | 72.22 | 36.11 | 316 | 7570 | 600 | 311.6712 | -17.7466 | 4.1493 | 574.284 | 9.6406 | 35.3917 | 18.035 | 18.035 | 35.4579 | 144.5421 | 39.9515 | 165.5504 | 165.5504 | 61.6436 | 227.1941 | 0.099851 | 9.985% | 102.7372 | 10.2584 | 7.1809 | 143.309 | 143.309 | 5.011% | 11.96% | 11.96% | 80% | 9.571% | 9.8325 | 10.0859 | 6 | 58.995 | 21.7437 | 41.17% | 41.17%
11 | 316 | 12 | 7571 | 11 | 2.6 | 102.31 | 97.69 | 200 | 97.69 | 48.85 | 316 | 7571 | 660 | 311.6712 | -17.7466 | 4.1493 | 634.284 | 10.6406 | 20.3917 | 22.9078 | 22.9078 | 21.1167 | 158.8833 | 28.0129 | 232.0451 | 232.0451 | 83.3836 | 315.4287 | 0.31234 | 31.23% | 142.6369 | 44.5513 | 31.1859 | 144.9945 | 144.9945 | 21.51% | 11.82% | 11.82% | 85% | 10.04% | 14.3256 | 9.4339 | 6 | 85.9533 | 31.6797 | 59.28% | 59.28%
11 | 316 | 12 | 7572 | 12 | 3.6 | 168.33 | 99.81 | 268.14 | 99.81 | 49.91 | 316 | 7572 | 720 | 311.6712 | -17.7466 | 4.1493 | 694.284 | 11.6406 | 5.3917 | 25.2924 | 25.2924 | 5.6805 | 174.3195 | 20.2343 | 369.6807 | 369.6807 | 85.1932 | 454.8739 | 0.4684 | 46.84% | 205.694 | 96.3469 | 67.4429 | 122.0662 | 122.0662 | 55.25% | 11.66% | 11.66% | 85% | 9.914% | 20.3921 | 9.1184 | 6 | 122.3526 | 45.0953 | 100.2% | 100.2%
11 | 316 | 12 | 7573 | 13 | 4.2 | 191.94 | 89.44 | 281.38 | 89.44 | 44.72 | 316 | 7573 | 780 | 311.6712 | -17.7466 | 4.1493 | 754.284 | 12.6406 | -9.6083 | 24.8961 | 24.8961 | 10.0935 | 190.0935 | 21.6982 | 423.6361 | 423.6361 | 76.3418 | 499.9779 | 0.50157 | 50.16% | 226.09 | 113.4011 | 79.3808 | 121.5339 | 121.5339 | 65.32% | 11.61% | 11.61% | 85% | 9.871% | 22.3169 | 8.9325 | 6 | 133.9015 | 49.3519 | 110.2% | 110.2%
11 | 316 | 12 | 7574 | 14 | 4.3 | 198.25 | 78.69 | 276.94 | 78.69 | 39.35 | 316 | 7574 | 840 | 311.6712 | -17.7466 | 4.1493 | 814.284 | 13.6406 | -24.6083 | 21.7702 | 21.7702 | 25.2808 | 205.2808 | 31.1254 | 457.5799 | 457.5799 | 67.1661 | 524.746 | 0.51631 | 51.63% | 237.2901 | 122.515 | 85.7605 | 120.8064 | 120.8064 | 70.99% | 11.59% | 11.59% | 90% | 10.43% | 24.7511 | 8.9018 | 6 | 148.5063 | 54.7347 | 122.9% | 122.9%
11 | 316 | 12 | 7575 | 15 | 5.6 | 136.67 | 74.08 | 210.75 | 74.08 | 37.04 | 316 | 7575 | 900 | 311.6712 | -17.7466 | 4.1493 | 874.284 | 14.6406 | -39.6083 | 16.2831 | 16.2831 | 39.2401 | 219.2401 | 43.6185 | 352.8814 | 352.8814 | 63.2312 | 416.1126 | 0.44871 | 44.87% | 188.1661 | 84.4318 | 59.1022 | 117.413 | 117.413 | 50.34% | 11.66% | 11.66% | 85% | 9.908% | 18.6428 | 8.5084 | 6 | 111.8568 | 41.2269 | 95.27% | 95.27%
11 | 316 | 12 | 7576 | 16 | 5 | 57.78 | 58.14 | 115.92 | 58.14 | 29.07 | 316 | 7576 | 960 | 311.6712 | -17.7466 | 4.1493 | 934.284 | 15.6406 | -54.6083 | 8.9538 | 8.9538 | 51.813 | 231.813 | 57.1883 | 0 | 0 | 49.6256 | 49.6256 | -2.2041 | 0% | 22.4407 | 0 | 0 | 152.3316 | 152.3316 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7577 | 17 | 3.8 | 17.86 | 20.83 | 38.69 | 20.83 | 10.42 | 316 | 7577 | 1020 | 311.6712 | -17.7466 | 4.1493 | 994.284 | 16.6406 | -69.6083 | 0.295 | 0.295 | 63.2197 | 243.2197 | 71.2017 | 0 | 0 | 17.7795 | 17.7795 | -7.7548 | 0% | 8.0399 | 0 | 0 | 144.0935 | 144.0935 | 0% | 12.05% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7578 | 18 | 2.6 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 316 | 7578 | 1080 | 311.6712 | -17.7466 | 4.1493 | 1054.284 | 17.6406 | -84.6083 | -9.255 | 0 | 63.5711 | 243.5711 | 71.6559 | 0 | 0 | 1.6559 | 1.6559 | -92.8514 | 0% | 0.7488 | 0 | 0 | 136.3864 | 136.3864 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7579 | 19 | 1.8 | 0 | 0 | 0 | 0 | 0 | 316 | 7579 | 1140 | 311.6712 | -17.7466 | 4.1493 | 1114.284 | 18.6406 | -99.6083 | -19.3283 | 0 | 63.5711 | 243.5711 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.175 | 132.175 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7580 | 20 | 1.4 | 0 | 0 | 0 | 0 | 0 | 316 | 7580 | 1200 | 311.6712 | -17.7466 | 4.1493 | 1174.284 | 19.6406 | -114.6083 | -29.5851 | 0 | 63.5711 | 243.5711 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.4755 | 127.4755 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7581 | 21 | 0.6 | 0 | 0 | 0 | 0 | 0 | 316 | 7581 | 1260 | 311.6712 | -17.7466 | 4.1493 | 1234.284 | 20.6406 | -129.6083 | -39.6384 | 0 | 63.5711 | 243.5711 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7525 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7582 | 22 | -0.2 | 0 | 0 | 0 | 0 | 0 | 316 | 7582 | 1320 | 311.6712 | -17.7466 | 4.1493 | 1294.284 | 21.6406 | -144.6083 | -48.923 | 0 | 63.5711 | 243.5711 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9121 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7583 | 23 | -0.9 | 0 | 0 | 0 | 0 | 0 | 316 | 7583 | 1380 | 311.6712 | -17.7466 | 4.1493 | 1354.284 | 22.6406 | -159.6083 | -56.4578 | 0 | 63.5711 | 243.5711 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6719 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
11 | 316 | 12 | 7584 | 24 | -1.1 | 0 | 0 | 0 | 0 | 0 | 316 | 7584 | 1440 | 311.6712 | -17.7466 | 4.1493 | 1414.284 | 23.6406 | -174.6083 | -60.6297 | 0 | 63.5711 | 243.5711 | 71.6559 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6698 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7585 | 1 | -2.4 | 0 | 0 | 0 | 0 | 0 | 317 | 7585 | 60 | 312.6575 | -18.0162 | 4.1599 | 34.284 | 0.64073 | 170.389 | -60.1679 | 0 | 63.1519 | 116.8481 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8575 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7586 | 2 | -2.5 | 0 | 0 | 0 | 0 | 0 | 317 | 7586 | 120 | 312.6575 | -18.0162 | 4.1599 | 94.284 | 1.6407 | 155.389 | -54.8319 | 0 | 63.1519 | 116.8481 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.738 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7587 | 3 | -2.8 | 0 | 0 | 0 | 0 | 0 | 317 | 7587 | 180 | 312.6575 | -18.0162 | 4.1599 | 154.284 | 2.6407 | 140.389 | -46.6434 | 0 | 63.1519 | 116.8481 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9233 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7588 | 4 | -3 | 0 | 0 | 0 | 0 | 0 | 317 | 7588 | 240 | 312.6575 | -18.0162 | 4.1599 | 214.284 | 3.6407 | 125.389 | -37.0515 | 0 | 63.1519 | 116.8481 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2281 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7589 | 5 | -3.2 | 0 | 0 | 0 | 0 | 0 | 317 | 7589 | 300 | 312.6575 | -18.0162 | 4.1599 | 274.284 | 4.6407 | 110.389 | -26.8893 | 0 | 63.1519 | 116.8481 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7746 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7590 | 6 | -3.3 | 0 | 0 | 0 | 0 | 0 | 317 | 7590 | 360 | 312.6575 | -18.0162 | 4.1599 | 334.284 | 5.6407 | 95.389 | -16.6511 | 0 | 63.1519 | 116.8481 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2333 | 0 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7591 | 7 | -4.4 | 0 | 0 | 0 | 0 | 0 | 317 | 7591 | 420 | 312.6575 | -18.0162 | 4.1599 | 394.284 | 6.6407 | 80.389 | -6.6986 | 0 | 63.1519 | 116.8481 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.0798 | 142.0798 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7592 | 8 | -4.6 | 0 | 0 | 0 | 0 | 0 | 317 | 7592 | 480 | 312.6575 | -18.0162 | 4.1599 | 454.284 | 7.6407 | 65.389 | 2.6272 | 2.6272 | 59.9386 | 120.0614 | 67.2787 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.8751 | 146.8751 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7593 | 9 | -3.2 | 12.86 | 24.44 | 37.3 | 24.44 | 12.22 | 317 | 7593 | 540 | 312.6575 | -18.0162 | 4.1599 | 514.284 | 8.6407 | 50.389 | 10.9434 | 10.9434 | 48.2612 | 131.7388 | 53.3859 | 40.4025 | 40.4025 | 20.8608 | 61.2633 | -1.9616 | 0% | 27.7033 | 0 | 0 | 131.8409 | 131.8409 | 0% | 12.29% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7594 | 10 | -0.6 | 54.92 | 50.08 | 105 | 50.08 | 25.04 | 317 | 7594 | 600 | 312.6575 | -18.0162 | 4.1599 | 574.284 | 9.6407 | 35.389 | 17.791 | 17.791 | 35.3374 | 144.6626 | 40.0665 | 137.5577 | 137.5577 | 42.746 | 180.3037 | -0.099705 | 0% | 81.5333 | 0 | 0 | 139.3325 | 139.3325 | 0% | 12.05% | 12.05% | 80% | 9.643% | 7.8625 | 10.4906 | 6 | 47.175 | 17.3872 | 33.86% | 33.86%
11 | 317 | 13 | 7595 | 11 | 0.8 | 92.97 | 78.89 | 171.86 | 78.89 | 39.45 | 317 | 7595 | 660 | 312.6575 | -18.0162 | 4.1599 | 634.284 | 10.6407 | 20.389 | 22.6481 | 22.6481 | 21.0384 | 158.9616 | 28.1926 | 212.7939 | 212.7939 | 67.3368 | 280.1307 | 0.23467 | 23.47% | 126.6751 | 29.727 | 20.8089 | 140.9097 | 140.9097 | 14.77% | 11.9% | 11.9% | 80% | 9.521% | 12.0605 | 10.0195 | 6 | 72.3628 | 26.6706 | 51.35% | 51.35%
11 | 317 | 13 | 7596 | 12 | 1.8 | 186.19 | 138.25 | 324.44 | 138.25 | 69.13 | 317 | 7596 | 720 | 312.6575 | -18.0162 | 4.1599 | 694.284 | 11.6407 | 5.389 | 25.0237 | 25.0237 | 5.6565 | 174.3435 | 20.4932 | 412.3164 | 412.3164 | 118.0038 | 530.3201 | 0.50789 | 50.79% | 239.8108 | 121.7966 | 85.2576 | 122.4667 | 122.4667 | 69.62% | 11.62% | 11.62% | 90% | 10.46% | 25.0836 | 9.6914 | 6 | 150.5017 | 55.4702 | 122.9% | 122.9%
11 | 317 | 13 | 7597 | 13 | 3.2 | 133.53 | 130.19 | 263.72 | 130.19 | 65.1 | 317 | 7597 | 780 | 312.6575 | -18.0162 | 4.1599 | 754.284 | 12.6407 | -9.611 | 24.6283 | 24.6283 | 10.0589 | 190.0589 | 21.9403 | 297.2161 | 297.2161 | 111.1241 | 408.3402 | 0.42778 | 42.78% | 184.6514 | 78.9904 | 55.2933 | 120.3682 | 120.3682 | 45.94% | 11.71% | 11.71% | 85% | 9.957% | 18.3854 | 9.2438 | 6 | 110.3124 | 40.6577 | 91.65% | 91.65%
11 | 317 | 13 | 7598 | 14 | 5.2 | 127.42 | 124.72 | 252.14 | 124.72 | 62.36 | 317 | 7598 | 840 | 312.6575 | -18.0162 | 4.1599 | 814.284 | 13.6407 | -24.611 | 21.5128 | 21.5128 | 25.1944 | 205.1944 | 31.288 | 296.9354 | 296.9354 | 106.4552 | 403.3906 | 0.43513 | 43.51% | 182.4132 | 79.3729 | 55.561 | 122.2899 | 122.2899 | 45.43% | 11.67% | 11.67% | 85% | 9.924% | 18.102 | 8.6282 | 6 | 108.6119 | 40.0309 | 88.82% | 88.82%
11 | 317 | 13 | 7599 | 15 | 6 | 109.36 | 110.36 | 219.72 | 110.36 | 55.18 | 317 | 7599 | 900 | 312.6575 | -18.0162 | 4.1599 | 874.284 | 14.6407 | -39.611 | 16.0418 | 16.0418 | 39.1148 | 219.1148 | 43.7247 | 285.9938 | 285.9938 | 94.1982 | 380.192 | 0.41766 | 41.77% | 171.9228 | 71.8047 | 50.2633 | 119.6799 | 119.6799 | 42% | 11.68% | 11.68% | 85% | 9.924% | 17.0616 | 8.3898 | 6 | 102.3694 | 37.7301 | 85.54% | 85.54%
11 | 317 | 13 | 7600 | 16 | 6.2 | 80.08 | 73.25 | 153.33 | 73.25 | 36.63 | 317 | 7600 | 960 | 312.6575 | -18.0162 | 4.1599 | 934.284 | 15.6407 | -54.611 | 8.7299 | 8.7299 | 51.6609 | 231.6609 | 57.2572 | 0 | 0 | 62.5228 | 62.5228 | -1.5377 | 0% | 28.2728 | 0 | 0 | 115.8461 | 115.8461 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7601 | 17 | 5 | 25.19 | 40.36 | 65.55 | 40.36 | 20.18 | 317 | 7601 | 1020 | 312.6575 | -18.0162 | 4.1599 | 994.284 | 16.6407 | -69.611 | 0.086647 | 0.086647 | 63.0485 | 243.0485 | 71.243 | 0 | 0 | 34.4494 | 34.4494 | -3.5293 | 0% | 15.578 | 0 | 0 | 149.1457 | 149.1457 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7602 | 18 | 4 | 0 | 2.86 | 2.86 | 2.86 | 1.43 | 317 | 7602 | 1080 | 312.6575 | -18.0162 | 4.1599 | 1054.284 | 17.6407 | -84.611 | -9.4516 | 0 | 63.1519 | 243.1519 | 71.3765 | 0 | 0 | 2.4412 | 2.4412 | -61.3339 | 0% | 1.1039 | 0 | 0 | 139.9927 | 139.9927 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7603 | 19 | 3 | 0 | 0 | 0 | 0 | 0 | 317 | 7603 | 1140 | 312.6575 | -18.0162 | 4.1599 | 1114.284 | 18.6407 | -99.611 | -19.5184 | 0 | 63.1519 | 243.1519 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.089 | 135.089 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7604 | 20 | 0.6 | 0 | 0 | 0 | 0 | 0 | 317 | 7604 | 1200 | 312.6575 | -18.0162 | 4.1599 | 1174.284 | 19.6407 | -114.611 | -29.7749 | 0 | 63.1519 | 243.1519 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.0151 | 127.0151 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7605 | 21 | -0.2 | 0 | 0 | 0 | 0 | 0 | 317 | 7605 | 1260 | 312.6575 | -18.0162 | 4.1599 | 1234.284 | 20.6407 | -129.611 | -39.8363 | 0 | 63.1519 | 243.1519 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3053 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7606 | 22 | -0.7 | 0 | 0 | 0 | 0 | 0 | 317 | 7606 | 1320 | 312.6575 | -18.0162 | 4.1599 | 1294.284 | 21.6407 | -144.611 | -49.1393 | 0 | 63.1519 | 243.1519 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0826 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7607 | 23 | -1.6 | 0 | 0 | 0 | 0 | 0 | 317 | 7607 | 1380 | 312.6575 | -18.0162 | 4.1599 | 1354.284 | 22.6407 | -159.611 | -56.7019 | 0 | 63.1519 | 243.1519 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.1822 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
11 | 317 | 13 | 7608 | 24 | -2 | 0 | 0 | 0 | 0 | 0 | 317 | 7608 | 1440 | 312.6575 | -18.0162 | 4.1599 | 1414.284 | 23.6407 | -174.611 | -60.8973 | 0 | 63.1519 | 243.1519 | 71.3765 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.5199 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7609 | 1 | -2.3 | 0 | 0 | 0 | 0 | 0 | 318 | 7609 | 60 | 313.6438 | -18.28 | 4.16 | 34.284 | 0.64073 | 170.389 | -60.4246 | 0 | 62.7409 | 117.2591 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9615 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7610 | 2 | -2.2 | 0 | 0 | 0 | 0 | 0 | 318 | 7610 | 120 | 313.6438 | -18.28 | 4.16 | 94.284 | 1.6407 | 155.389 | -55.0609 | 0 | 62.7409 | 117.2591 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.5567 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7611 | 3 | -2.4 | 0 | 0 | 0 | 0 | 0 | 318 | 7611 | 180 | 313.6438 | -18.28 | 4.16 | 154.284 | 2.6407 | 140.389 | -46.8467 | 0 | 62.7409 | 117.2591 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6091 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7612 | 4 | -2.3 | 0 | 0 | 0 | 0 | 0 | 318 | 7612 | 240 | 313.6438 | -18.28 | 4.16 | 214.284 | 3.6407 | 125.389 | -37.2398 | 0 | 62.7409 | 117.2591 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.4567 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7613 | 5 | -2.2 | 0 | 0 | 0 | 0 | 0 | 318 | 7613 | 300 | 313.6438 | -18.28 | 4.16 | 274.284 | 4.6407 | 110.389 | -27.0723 | 0 | 62.7409 | 117.2591 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8281 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7614 | 6 | -3.6 | 0 | 0 | 0 | 0 | 0 | 318 | 7614 | 360 | 313.6438 | -18.28 | 4.16 | 334.284 | 5.6407 | 95.389 | -16.8363 | 0 | 62.7409 | 117.2591 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2162 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7615 | 7 | -4.5 | 0 | 0 | 0 | 0 | 0 | 318 | 7615 | 420 | 313.6438 | -18.28 | 4.16 | 394.284 | 6.6407 | 80.389 | -6.8921 | 0 | 62.7409 | 117.2591 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.6845 | 137.6845 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7616 | 8 | -4.2 | 0 | 0 | 0 | 0 | 0 | 318 | 7616 | 480 | 313.6438 | -18.28 | 4.16 | 454.284 | 7.6407 | 65.389 | 2.4209 | 2.4209 | 59.774 | 120.226 | 67.3242 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.2702 | 142.2702 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7617 | 9 | -3.2 | 7.58 | 20.47 | 28.05 | 20.47 | 10.24 | 318 | 7617 | 540 | 313.6438 | -18.28 | 4.16 | 514.284 | 8.6407 | 50.389 | 10.7209 | 10.7209 | 48.1169 | 131.8831 | 53.4607 | 24.2598 | 24.2598 | 17.4722 | 41.732 | -3.2559 | 0% | 18.8712 | 0 | 0 | 125.5174 | 125.5174 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7618 | 10 | -1.1 | 42.97 | 60.28 | 103.25 | 60.28 | 30.14 | 318 | 7618 | 600 | 313.6438 | -18.28 | 4.16 | 574.284 | 9.6407 | 35.389 | 17.5511 | 17.5511 | 35.2221 | 144.7779 | 40.1825 | 108.8645 | 108.8645 | 51.4522 | 160.3167 | -0.22011 | 0% | 72.4952 | 0 | 0 | 132.3236 | 132.3236 | 0% | 12.09% | 12.09% | 80% | 9.675% | 7.0143 | 10.6622 | 6 | 42.0856 | 15.5114 | 31.81% | 31.81%
11 | 318 | 14 | 7619 | 11 | 2.1 | 78.61 | 91.75 | 170.36 | 91.75 | 45.88 | 318 | 7619 | 660 | 313.6438 | -18.28 | 4.16 | 634.284 | 10.6407 | 20.389 | 22.3932 | 22.3932 | 20.9646 | 159.0354 | 28.3715 | 181.5615 | 181.5615 | 78.3135 | 259.875 | 0.20255 | 20.25% | 117.5155 | 23.8026 | 16.6618 | 137.068 | 137.068 | 12.16% | 11.88% | 11.88% | 80% | 9.507% | 11.1722 | 9.5943 | 6 | 67.0332 | 24.7063 | 48.91% | 48.91%
11 | 318 | 14 | 7620 | 12 | 2.5 | 126.31 | 108.25 | 234.56 | 108.25 | 54.13 | 318 | 7620 | 720 | 313.6438 | -18.28 | 4.16 | 694.284 | 11.6407 | 5.389 | 24.7605 | 24.7605 | 5.6359 | 174.3641 | 20.7475 | 282.0236 | 282.0236 | 92.3972 | 374.4208 | 0.38915 | 38.92% | 169.3131 | 65.8889 | 46.1222 | 114.3672 | 114.3672 | 40.33% | 11.76% | 11.76% | 85% | 9.997% | 16.9269 | 9.4659 | 6 | 101.5612 | 37.4323 | 88.8% | 88.8%
11 | 318 | 14 | 7621 | 13 | 3.3 | 120.08 | 131.75 | 251.83 | 131.75 | 65.88 | 318 | 7621 | 780 | 313.6438 | -18.28 | 4.16 | 754.284 | 12.6407 | -9.611 | 24.3666 | 24.3666 | 10.0225 | 190.0225 | 22.1766 | 269.5207 | 269.5207 | 112.4557 | 381.9763 | 0.40245 | 40.24% | 172.7297 | 69.515 | 48.6605 | 114.7862 | 114.7862 | 42.39% | 11.74% | 11.74% | 85% | 9.976% | 17.2308 | 9.2124 | 6 | 103.3845 | 38.1043 | 90.07% | 90.07%
11 | 318 | 14 | 7622 | 14 | 4.9 | 54.17 | 134.44 | 188.61 | 134.44 | 67.22 | 318 | 7622 | 840 | 313.6438 | -18.28 | 4.16 | 814.284 | 13.6407 | -24.611 | 21.2617 | 21.2617 | 25.1077 | 205.1077 | 31.4465 | 127.4418 | 127.4418 | 114.7517 | 242.1936 | 0.18664 | 18.66% | 109.5199 | 20.441 | 14.3087 | 134.6123 | 134.6123 | 10.63% | 11.82% | 11.82% | 80% | 9.452% | 10.352 | 8.7188 | 6 | 62.1123 | 22.8926 | 46.14% | 46.14%
11 | 318 | 14 | 7623 | 15 | 5.2 | 60.19 | 125.75 | 185.94 | 125.75 | 62.88 | 318 | 7623 | 900 | 313.6438 | -18.28 | 4.16 | 874.284 | 14.6407 | -39.611 | 15.8067 | 15.8067 | 38.9903 | 218.9903 | 43.8274 | 159.4122 | 159.4122 | 107.3343 | 266.7466 | 0.24617 | 24.62% | 120.6228 | 29.6934 | 20.7854 | 111.7683 | 111.7683 | 18.6% | 11.79% | 11.79% | 80% | 9.429% | 11.3733 | 8.6282 | 6 | 68.2401 | 25.1511 | 61.05% | 61.05%
11 | 318 | 14 | 7624 | 16 | 5.6 | 31.86 | 85.08 | 116.94 | 85.08 | 42.54 | 318 | 7624 | 960 | 313.6438 | -18.28 | 4.16 | 934.284 | 15.6407 | -54.611 | 8.5121 | 8.5121 | 51.5103 | 231.5103 | 57.323 | 0 | 0 | 72.6203 | 72.6203 | -1.2318 | 0% | 32.8389 | 0 | 0 | 149.7613 | 149.7613 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.5084 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7625 | 17 | 4.7 | 7.03 | 47.31 | 54.34 | 47.31 | 23.66 | 318 | 7625 | 1020 | 313.6438 | -18.28 | 4.16 | 994.284 | 16.6407 | -69.611 | -0.11567 | 0 | 62.7409 | 242.7409 | 71.1031 | 0 | 0 | 40.3816 | 40.3816 | -2.9106 | 0% | 18.2606 | 0 | 0 | 143.2042 | 143.2042 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7626 | 18 | 3.7 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 318 | 7626 | 1080 | 313.6438 | -18.28 | 4.16 | 1054.284 | 17.6407 | -84.611 | -9.6422 | 0 | 62.7409 | 242.7409 | 71.1031 | 0 | 0 | 1.6559 | 1.6559 | -91.2393 | 0% | 0.7488 | 0 | 0 | 136.459 | 136.459 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7627 | 19 | 2.2 | 0 | 0 | 0 | 0 | 0 | 318 | 7627 | 1140 | 313.6438 | -18.28 | 4.16 | 1114.284 | 18.6407 | -99.611 | -19.7024 | 0 | 62.7409 | 242.7409 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.8863 | 131.8863 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7628 | 20 | 0.4 | 0 | 0 | 0 | 0 | 0 | 318 | 7628 | 1200 | 313.6438 | -18.28 | 4.16 | 1174.284 | 19.6407 | -114.611 | -29.9586 | 0 | 62.7409 | 242.7409 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.9156 | 125.9156 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7629 | 21 | -0.4 | 0 | 0 | 0 | 0 | 0 | 318 | 7629 | 1260 | 313.6438 | -18.28 | 4.16 | 1234.284 | 20.6407 | -129.611 | -40.0278 | 0 | 62.7409 | 242.7409 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0895 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7630 | 22 | -1.5 | 0 | 0 | 0 | 0 | 0 | 318 | 7630 | 1320 | 313.6438 | -18.28 | 4.16 | 1294.284 | 21.6407 | -144.611 | -49.3488 | 0 | 62.7409 | 242.7409 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.4996 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7631 | 23 | -1.7 | 0 | 0 | 0 | 0 | 0 | 318 | 7631 | 1380 | 313.6438 | -18.28 | 4.16 | 1354.284 | 22.6407 | -159.611 | -56.9394 | 0 | 62.7409 | 242.7409 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.552 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
11 | 318 | 14 | 7632 | 24 | -2.1 | 0 | 0 | 0 | 0 | 0 | 318 | 7632 | 1440 | 313.6438 | -18.28 | 4.16 | 1414.284 | 23.6407 | -174.611 | -61.1588 | 0 | 62.7409 | 242.7409 | 71.1031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9092 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7633 | 1 | -2.5 | 0 | 0 | 0 | 0 | 0 | 319 | 7633 | 60 | 314.6301 | -18.5379 | 4.1498 | 34.284 | 0.64056 | 170.3915 | -60.676 | 0 | 62.3382 | 117.6618 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.1878 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7634 | 2 | -2.5 | 0 | 0 | 0 | 0 | 0 | 319 | 7634 | 120 | 314.6301 | -18.5379 | 4.1498 | 94.284 | 1.6406 | 155.3915 | -55.2856 | 0 | 62.3382 | 117.6618 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9424 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7635 | 3 | -2.5 | 0 | 0 | 0 | 0 | 0 | 319 | 7635 | 180 | 314.6301 | -18.5379 | 4.1498 | 154.284 | 2.6406 | 140.3915 | -47.0465 | 0 | 62.3382 | 117.6618 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6971 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7636 | 4 | -2.5 | 0 | 0 | 0 | 0 | 0 | 319 | 7636 | 240 | 314.6301 | -18.5379 | 4.1498 | 214.284 | 3.6406 | 125.3915 | -37.4252 | 0 | 62.3382 | 117.6618 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6971 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7637 | 5 | -2.3 | 0 | 0 | 0 | 0 | 0 | 319 | 7637 | 300 | 314.6301 | -18.5379 | 4.1498 | 274.284 | 4.6406 | 110.3915 | -27.2526 | 0 | 62.3382 | 117.6618 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.4731 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7638 | 6 | -2.4 | 0 | 0 | 0 | 0 | 0 | 319 | 7638 | 360 | 314.6301 | -18.5379 | 4.1498 | 334.284 | 5.6406 | 95.3915 | -17.0189 | 0 | 62.3382 | 117.6618 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.5177 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7639 | 7 | -2.9 | 0 | 0 | 0 | 0 | 0 | 319 | 7639 | 420 | 314.6301 | -18.5379 | 4.1498 | 394.284 | 6.6406 | 80.3915 | -7.0828 | 0 | 62.3382 | 117.6618 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.612 | 141.612 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7640 | 8 | -3.3 | 0 | 0 | 0 | 0 | 0 | 319 | 7640 | 480 | 314.6301 | -18.5379 | 4.1498 | 454.284 | 7.6406 | 65.3915 | 2.2177 | 2.2177 | 59.6151 | 120.3849 | 67.3715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.6795 | 145.6795 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7641 | 9 | -2 | 8.81 | 9.92 | 18.73 | 9.92 | 4.96 | 319 | 7641 | 540 | 314.6301 | -18.5379 | 4.1498 | 514.284 | 8.6406 | 50.3915 | 10.502 | 10.502 | 47.9781 | 132.0219 | 53.5371 | 28.7256 | 28.7256 | 8.4672 | 37.1928 | -3.6706 | 0% | 16.8186 | 0 | 0 | 129.3631 | 129.3631 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7642 | 10 | -1.1 | 46.31 | 31.11 | 77.42 | 31.11 | 15.56 | 319 | 7642 | 600 | 314.6301 | -18.5379 | 4.1498 | 574.284 | 9.6406 | 35.3915 | 17.3155 | 17.3155 | 35.112 | 144.888 | 40.2991 | 118.6681 | 118.6681 | 26.554 | 145.2222 | -0.32655 | 0% | 65.6695 | 0 | 0 | 134.2102 | 134.2102 | 0% | 12.11% | 12.11% | 80% | 9.689% | 6.363 | 10.6622 | 6 | 38.1782 | 14.0713 | 28.45% | 28.45%
11 | 319 | 15 | 7643 | 11 | 0.3 | 78.81 | 67.78 | 146.59 | 67.78 | 33.89 | 319 | 7643 | 660 | 314.6301 | -18.5379 | 4.1498 | 634.284 | 10.6406 | 20.3915 | 22.1434 | 22.1434 | 20.8953 | 159.1047 | 28.5493 | 183.6628 | 183.6628 | 57.8538 | 241.5167 | 0.13855 | 13.85% | 109.2138 | 15.1315 | 10.5921 | 136.4585 | 136.4585 | 7.762% | 11.96% | 11.96% | 80% | 9.566% | 10.4471 | 10.1862 | 6 | 62.6824 | 23.1027 | 45.94% | 45.94%
11 | 319 | 15 | 7644 | 12 | 1.8 | 109.81 | 119.08 | 228.89 | 119.08 | 59.54 | 319 | 7644 | 720 | 314.6301 | -18.5379 | 4.1498 | 694.284 | 11.6406 | 5.3915 | 24.5031 | 24.5031 | 5.6185 | 174.3815 | 20.9969 | 247.1865 | 247.1865 | 101.6411 | 348.8277 | 0.35382 | 35.38% | 157.7399 | 55.8116 | 39.0681 | 116.2995 | 116.2995 | 33.59% | 11.8% | 11.8% | 85% | 10.03% | 15.8262 | 9.6914 | 6 | 94.957 | 34.9982 | 81.65% | 81.65%
11 | 319 | 15 | 7645 | 13 | 2.2 | 168.42 | 126.39 | 294.81 | 126.39 | 63.2 | 319 | 7645 | 780 | 314.6301 | -18.5379 | 4.1498 | 754.284 | 12.6406 | -9.6085 | 24.111 | 24.111 | 9.9844 | 189.9844 | 22.4072 | 381.1549 | 381.1549 | 107.8806 | 489.0355 | 0.48489 | 48.49% | 221.1419 | 107.2286 | 75.06 | 118.3964 | 118.3964 | 63.4% | 11.66% | 11.66% | 85% | 9.908% | 21.9107 | 9.5621 | 6 | 131.464 | 48.4535 | 111% | 111%
11 | 319 | 15 | 7646 | 14 | 3.1 | 187.5 | 92.97 | 280.47 | 92.97 | 46.49 | 319 | 7646 | 840 | 314.6301 | -18.5379 | 4.1498 | 814.284 | 13.6406 | -24.6085 | 21.0168 | 21.0168 | 25.0207 | 205.0207 | 31.6006 | 445.2843 | 445.2843 | 79.3549 | 524.6392 | 0.51072 | 51.07% | 237.2418 | 121.1633 | 84.8143 | 118.5706 | 118.5706 | 71.53% | 11.61% | 11.61% | 90% | 10.45% | 24.785 | 9.2753 | 6 | 148.7101 | 54.8099 | 125.4% | 125.4%
11 | 319 | 15 | 7647 | 15 | 3.1 | 127.03 | 79.44 | 206.47 | 79.44 | 39.72 | 319 | 7647 | 900 | 314.6301 | -18.5379 | 4.1498 | 874.284 | 14.6406 | -39.6085 | 15.5779 | 15.5779 | 38.8666 | 218.8666 | 43.9266 | 340.685 | 340.685 | 67.8063 | 408.4913 | 0.42733 | 42.73% | 184.7197 | 78.9356 | 55.2549 | 112.9921 | 112.9921 | 48.9% | 11.72% | 11.72% | 85% | 9.959% | 18.3954 | 9.2753 | 6 | 110.3721 | 40.6797 | 97.68% | 97.68%
11 | 319 | 15 | 7648 | 16 | 3.3 | 62.03 | 49.81 | 111.84 | 49.81 | 24.91 | 319 | 7648 | 960 | 314.6301 | -18.5379 | 4.1498 | 934.284 | 15.6406 | -54.6085 | 8.3006 | 8.3006 | 51.3611 | 231.3611 | 57.3857 | 0 | 0 | 42.5155 | 42.5155 | -2.8037 | 0% | 19.2255 | 0 | 0 | 149.4995 | 149.4995 | 0% | 12.05% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7649 | 17 | 2.8 | 17.42 | 28.14 | 45.56 | 28.14 | 14.07 | 319 | 7649 | 1020 | 314.6301 | -18.5379 | 4.1498 | 994.284 | 16.6406 | -69.6085 | -0.31188 | 0 | 62.3382 | 242.3382 | 70.8358 | 0 | 0 | 24.019 | 24.019 | -5.6324 | 0% | 10.8614 | 0 | 0 | 142.9322 | 142.9322 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7650 | 18 | 2.9 | 0 | 1.25 | 1.25 | 1.25 | 0.63 | 319 | 7650 | 1080 | 314.6301 | -18.5379 | 4.1498 | 1054.284 | 17.6406 | -84.6085 | -9.8268 | 0 | 62.3382 | 242.3382 | 70.8358 | 0 | 0 | 1.0669 | 1.0669 | -143.8653 | 0% | 0.48247 | 0 | 0 | 137.025 | 137.025 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7651 | 19 | 2.7 | 0 | 0 | 0 | 0 | 0 | 319 | 7651 | 1140 | 314.6301 | -18.5379 | 4.1498 | 1114.284 | 18.6406 | -99.6085 | -19.8803 | 0 | 62.3382 | 242.3382 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.7903 | 133.7903 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7652 | 20 | 2.5 | 0 | 0 | 0 | 0 | 0 | 319 | 7652 | 1200 | 314.6301 | -18.5379 | 4.1498 | 1174.284 | 19.6406 | -114.6085 | -30.136 | 0 | 62.3382 | 242.3382 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.5794 | 129.5794 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7653 | 21 | 2.5 | 0 | 0 | 0 | 0 | 0 | 319 | 7653 | 1260 | 314.6301 | -18.5379 | 4.1498 | 1234.284 | 20.6406 | -129.6085 | -40.2128 | 0 | 62.3382 | 242.3382 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3983 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7654 | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 319 | 7654 | 1320 | 314.6301 | -18.5379 | 4.1498 | 1294.284 | 21.6406 | -144.6085 | -49.5517 | 0 | 62.3382 | 242.3382 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5898 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7655 | 23 | 0.3 | 0 | 0 | 0 | 0 | 0 | 319 | 7655 | 1380 | 314.6301 | -18.5379 | 4.1498 | 1354.284 | 22.6406 | -159.6085 | -57.1701 | 0 | 62.3382 | 242.3382 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4113 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
11 | 319 | 15 | 7656 | 24 | -0.3 | 0 | 0 | 0 | 0 | 0 | 319 | 7656 | 1440 | 314.6301 | -18.5379 | 4.1498 | 1414.284 | 23.6406 | -174.6085 | -61.414 | 0 | 62.3382 | 242.3382 | 70.8358 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0803 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7657 | 1 | -0.4 | 0 | 0 | 0 | 0 | 0 | 320 | 7657 | 60 | 315.6164 | -18.7899 | 4.1293 | 34.284 | 0.64022 | 170.3967 | -60.922 | 0 | 61.9439 | 118.0561 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6124 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7658 | 2 | -1 | 0 | 0 | 0 | 0 | 0 | 320 | 7658 | 120 | 315.6164 | -18.7899 | 4.1293 | 94.284 | 1.6402 | 155.3967 | -55.5059 | 0 | 61.9439 | 118.0561 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2739 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7659 | 3 | -1.1 | 0 | 0 | 0 | 0 | 0 | 320 | 7659 | 180 | 315.6164 | -18.7899 | 4.1293 | 154.284 | 2.6402 | 140.3967 | -47.2428 | 0 | 61.9439 | 118.0561 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1734 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7660 | 4 | -1.4 | 0 | 0 | 0 | 0 | 0 | 320 | 7660 | 240 | 315.6164 | -18.7899 | 4.1293 | 214.284 | 3.6402 | 125.3967 | -37.6075 | 0 | 61.9439 | 118.0561 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6306 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7661 | 5 | -1.7 | 0 | 0 | 0 | 0 | 0 | 320 | 7661 | 300 | 315.6164 | -18.7899 | 4.1293 | 274.284 | 4.6402 | 110.3967 | -27.4303 | 0 | 61.9439 | 118.0561 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.7182 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7662 | 6 | -2 | 0 | 0 | 0 | 0 | 0 | 320 | 7662 | 360 | 315.6164 | -18.7899 | 4.1293 | 334.284 | 5.6402 | 95.3967 | -17.199 | 0 | 61.9439 | 118.0561 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.587 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7663 | 7 | -2.2 | 0 | 0 | 0 | 0 | 0 | 320 | 7663 | 420 | 315.6164 | -18.7899 | 4.1293 | 394.284 | 6.6402 | 80.3967 | -7.2707 | 0 | 61.9439 | 118.0561 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.3296 | 141.3296 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7664 | 8 | -2.5 | 0 | 0 | 0 | 0 | 0 | 320 | 7664 | 480 | 315.6164 | -18.7899 | 4.1293 | 454.284 | 7.6402 | 65.3967 | 2.0176 | 2.0176 | 59.4618 | 120.5382 | 67.4207 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.6856 | 144.6856 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7665 | 9 | -2.4 | 8.61 | 21.81 | 30.42 | 21.81 | 10.91 | 320 | 7665 | 540 | 315.6164 | -18.7899 | 4.1293 | 514.284 | 8.6402 | 50.3967 | 10.2868 | 10.2868 | 47.8449 | 132.1551 | 53.6148 | 28.6017 | 28.6017 | 18.616 | 47.2177 | -2.7417 | 0% | 21.3518 | 0 | 0 | 126.6734 | 126.6734 | 0% | 12.28% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7666 | 10 | -1.9 | 43.81 | 45.64 | 89.45 | 45.64 | 22.82 | 320 | 7666 | 600 | 315.6164 | -18.7899 | 4.1293 | 574.284 | 9.6402 | 35.3967 | 17.0843 | 17.0843 | 35.0072 | 144.9928 | 40.4164 | 113.5374 | 113.5374 | 38.9562 | 152.4936 | -0.2857 | 0% | 68.9576 | 0 | 0 | 129.6289 | 129.6289 | 0% | 12.13% | 12.13% | 80% | 9.706% | 6.6927 | 10.9403 | 6 | 40.1562 | 14.8003 | 30.98% | 30.98%
11 | 320 | 16 | 7667 | 11 | -1.3 | 59.17 | 75.75 | 134.92 | 75.75 | 37.88 | 320 | 7667 | 660 | 315.6164 | -18.7899 | 4.1293 | 634.284 | 10.6402 | 20.3967 | 21.8987 | 21.8987 | 20.8304 | 159.1696 | 28.7259 | 139.1222 | 139.1222 | 64.6567 | 203.7788 | -0.0041238 | 0% | 92.1488 | 0 | 0 | 128.9795 | 128.9795 | 0% | 12.05% | 12.05% | 80% | 9.64% | 8.8835 | 10.7313 | 6 | 53.301 | 19.6451 | 41.33% | 41.33%
11 | 320 | 16 | 7668 | 12 | -0.8 | 59.44 | 109.53 | 168.97 | 109.53 | 54.77 | 320 | 7668 | 720 | 315.6164 | -18.7899 | 4.1293 | 694.284 | 11.6402 | 5.3967 | 24.2514 | 24.2514 | 5.6042 | 174.3958 | 21.2414 | 134.8824 | 134.8824 | 93.4897 | 228.3721 | 0.088339 | 8.834% | 103.2699 | 9.1228 | 6.3859 | 125.9998 | 125.9998 | 5.068% | 12.01% | 12.01% | 80% | 9.605% | 9.9188 | 10.559 | 6 | 59.5129 | 21.9346 | 47.23% | 47.23%
11 | 320 | 16 | 7669 | 13 | -0.7 | 83.33 | 118.06 | 201.39 | 118.06 | 59.03 | 320 | 7669 | 780 | 315.6164 | -18.7899 | 4.1293 | 754.284 | 12.6402 | -9.6033 | 23.8617 | 23.8617 | 9.9446 | 189.9446 | 22.6319 | 190.1301 | 190.1301 | 100.7705 | 290.9006 | 0.24302 | 24.3% | 131.5453 | 31.9683 | 22.3778 | 105.2111 | 105.2111 | 21.27% | 11.93% | 11.93% | 80% | 9.545% | 12.5564 | 10.5248 | 6 | 75.3382 | 27.7673 | 71.61% | 71.61%
11 | 320 | 16 | 7670 | 14 | -0.4 | 88.25 | 89.36 | 177.61 | 89.36 | 44.68 | 320 | 7670 | 840 | 315.6164 | -18.7899 | 4.1293 | 814.284 | 13.6402 | -24.6033 | 20.7784 | 20.7784 | 24.9334 | 204.9334 | 31.7504 | 211.5357 | 211.5357 | 76.2735 | 287.8092 | 0.23958 | 23.96% | 130.1473 | 31.1803 | 21.8262 | 124.8404 | 124.8404 | 17.48% | 11.93% | 11.93% | 80% | 9.541% | 12.4178 | 10.4224 | 6 | 74.5068 | 27.4609 | 59.68% | 59.68%
11 | 320 | 16 | 7671 | 15 | -0.1 | 66.03 | 80.56 | 146.59 | 80.56 | 40.28 | 320 | 7671 | 900 | 315.6164 | -18.7899 | 4.1293 | 874.284 | 14.6402 | -39.6033 | 15.3556 | 15.3556 | 38.7437 | 218.7437 | 44.0223 | 179.3003 | 179.3003 | 68.7623 | 248.0626 | 0.15213 | 15.21% | 112.1739 | 17.0651 | 11.9455 | 143.2337 | 143.2337 | 8.34% | 11.96% | 11.96% | 80% | 9.57% | 10.7347 | 10.3208 | 6 | 64.4085 | 23.7389 | 44.97% | 44.97%
11 | 320 | 16 | 7672 | 16 | 0.6 | 33.61 | 57.86 | 91.47 | 57.86 | 28.93 | 320 | 7672 | 960 | 315.6164 | -18.7899 | 4.1293 | 934.284 | 15.6402 | -54.6033 | 8.0953 | 8.0953 | 51.2135 | 231.2135 | 57.4452 | 0 | 0 | 49.3866 | 49.3866 | -2.4353 | 0% | 22.3326 | 0 | 0 | 140.5151 | 140.5151 | 0% | 12.15% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7673 | 17 | 0.7 | 8.33 | 23.69 | 32.02 | 23.69 | 11.85 | 320 | 7673 | 1020 | 315.6164 | -18.7899 | 4.1293 | 994.284 | 16.6402 | -69.6033 | -0.50193 | 0 | 61.9439 | 241.9439 | 70.5747 | 0 | 0 | 20.2207 | 20.2207 | -7.0955 | 0% | 9.1438 | 0 | 0 | 135.9698 | 135.9698 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7674 | 18 | 1 | 0 | 1.67 | 1.67 | 1.67 | 0.84 | 320 | 7674 | 1080 | 315.6164 | -18.7899 | 4.1293 | 1054.284 | 17.6402 | -84.6033 | -10.0053 | 0 | 61.9439 | 241.9439 | 70.5747 | 0 | 0 | 1.4254 | 1.4254 | -110.7376 | 0% | 0.64458 | 0 | 0 | 132.3287 | 132.3287 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7675 | 19 | 1.1 | 0 | 0 | 0 | 0 | 0 | 320 | 7675 | 1140 | 315.6164 | -18.7899 | 4.1293 | 1114.284 | 18.6402 | -99.6033 | -20.052 | 0 | 61.9439 | 241.9439 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.3679 | 130.3679 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7676 | 20 | 1.2 | 0 | 0 | 0 | 0 | 0 | 320 | 7676 | 1200 | 315.6164 | -18.7899 | 4.1293 | 1174.284 | 19.6402 | -114.6033 | -30.3072 | 0 | 61.9439 | 241.9439 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.477 | 127.477 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7677 | 21 | 1.3 | 0 | 0 | 0 | 0 | 0 | 320 | 7677 | 1260 | 315.6164 | -18.7899 | 4.1293 | 1234.284 | 20.6402 | -129.6033 | -40.3913 | 0 | 61.9439 | 241.9439 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1006 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7678 | 22 | 1.4 | 0 | 0 | 0 | 0 | 0 | 320 | 7678 | 1320 | 315.6164 | -18.7899 | 4.1293 | 1294.284 | 21.6402 | -144.6033 | -49.7479 | 0 | 61.9439 | 241.9439 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.628 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7679 | 23 | 1.6 | 0 | 0 | 0 | 0 | 0 | 320 | 7679 | 1380 | 315.6164 | -18.7899 | 4.1293 | 1354.284 | 22.6402 | -159.6033 | -57.394 | 0 | 61.9439 | 241.9439 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0703 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
11 | 320 | 16 | 7680 | 24 | 1.9 | 0 | 0 | 0 | 0 | 0 | 320 | 7680 | 1440 | 315.6164 | -18.7899 | 4.1293 | 1414.284 | 23.6402 | -174.6033 | -61.663 | 0 | 61.9439 | 241.9439 | 70.5747 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.3602 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7681 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 321 | 7681 | 60 | 316.6027 | -19.0357 | 4.0985 | 34.284 | 0.63971 | 170.4044 | -61.1627 | 0 | 61.5584 | 118.4416 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3561 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7682 | 2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 321 | 7682 | 120 | 316.6027 | -19.0357 | 4.0985 | 94.284 | 1.6397 | 155.4044 | -55.7218 | 0 | 61.5584 | 118.4416 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1207 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7683 | 3 | 2.2 | 0 | 0 | 0 | 0 | 0 | 321 | 7683 | 180 | 316.6027 | -19.0357 | 4.0985 | 154.284 | 2.6397 | 140.4044 | -47.4356 | 0 | 61.5584 | 118.4416 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8853 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7684 | 4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 321 | 7684 | 240 | 316.6027 | -19.0357 | 4.0985 | 214.284 | 3.6397 | 125.4044 | -37.7869 | 0 | 61.5584 | 118.4416 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7329 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7685 | 5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 321 | 7685 | 300 | 316.6027 | -19.0357 | 4.0985 | 274.284 | 4.6397 | 110.4044 | -27.6052 | 0 | 61.5584 | 118.4416 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.7332 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7686 | 6 | 2.4 | 0 | 0 | 0 | 0 | 0 | 321 | 7686 | 360 | 316.6027 | -19.0357 | 4.0985 | 334.284 | 5.6397 | 95.4044 | -17.3763 | 0 | 61.5584 | 118.4416 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.9679 | 0 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7687 | 7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 321 | 7687 | 420 | 316.6027 | -19.0357 | 4.0985 | 394.284 | 6.6397 | 80.4044 | -7.4557 | 0 | 61.5584 | 118.4416 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.8241 | 135.8241 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7688 | 8 | 2.8 | 0 | 0 | 0 | 0 | 0 | 321 | 7688 | 480 | 316.6027 | -19.0357 | 4.0985 | 454.284 | 7.6397 | 65.4044 | 1.8208 | 1.8208 | 59.3143 | 120.6857 | 67.4716 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.0651 | 139.0651 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7689 | 9 | 3 | 0.36 | 10.75 | 11.11 | 10.75 | 5.38 | 321 | 7689 | 540 | 316.6027 | -19.0357 | 4.0985 | 514.284 | 8.6397 | 50.4044 | 10.0754 | 10.0754 | 47.7172 | 132.2828 | 53.6937 | 1.2184 | 1.2184 | 9.1757 | 10.3941 | -14.0227 | 0% | 4.7002 | 0 | 0 | 119.8044 | 119.8044 | 0% | 12.09% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7690 | 10 | 3.4 | 0.56 | 35.08 | 35.64 | 35.08 | 17.54 | 321 | 7690 | 600 | 316.6027 | -19.0357 | 4.0985 | 574.284 | 9.6397 | 35.4044 | 16.8576 | 16.8576 | 34.9075 | 145.0925 | 40.534 | 1.4677 | 1.4677 | 29.9427 | 31.4103 | -4.0715 | 0% | 14.2037 | 0 | 0 | 122.8141 | 122.8141 | 0% | 12.05% | 12.05% | 80% | 9.643% | 1.3697 | 9.181 | 6 | 8.218 | 3.0289 | 6.691% | 6.691%
11 | 321 | 17 | 7691 | 11 | 4.4 | 3.25 | 63.53 | 66.78 | 63.53 | 31.77 | 321 | 7691 | 660 | 316.6027 | -19.0357 | 4.0985 | 634.284 | 10.6397 | 20.4044 | 21.6592 | 21.6592 | 20.7699 | 159.2301 | 28.901 | 7.7089 | 7.7089 | 54.2262 | 61.9351 | -1.6296 | 0% | 28.0071 | 0 | 0 | 125.0071 | 125.0071 | 0% | 11.99% | 11.99% | 80% | 9.588% | 2.6854 | 8.8711 | 6 | 16.1122 | 5.9385 | 12.89% | 12.89%
11 | 321 | 17 | 7692 | 12 | 5.1 | 70.92 | 106.58 | 177.5 | 106.58 | 53.29 | 321 | 7692 | 720 | 316.6027 | -19.0357 | 4.0985 | 694.284 | 11.6397 | 5.4044 | 24.0057 | 24.0057 | 5.5932 | 174.4068 | 21.4807 | 162.2161 | 162.2161 | 90.9717 | 253.1878 | 0.21535 | 21.53% | 114.4915 | 24.6554 | 17.2588 | 129.2495 | 129.2495 | 13.35% | 11.8% | 11.8% | 80% | 9.44% | 10.8081 | 8.6583 | 6 | 64.8486 | 23.9012 | 50.17% | 50.17%
11 | 321 | 17 | 7693 | 13 | 6.6 | 105 | 85.47 | 190.47 | 85.47 | 42.74 | 321 | 7693 | 780 | 316.6027 | -19.0357 | 4.0985 | 754.284 | 12.6397 | -9.5956 | 23.6187 | 23.6187 | 9.9032 | 189.9032 | 22.8505 | 241.5084 | 241.5084 | 72.9532 | 314.4616 | 0.34145 | 34.15% | 142.1995 | 48.5541 | 33.9879 | 131.892 | 131.892 | 25.77% | 11.71% | 11.71% | 85% | 9.953% | 14.1536 | 8.2139 | 6 | 84.9218 | 31.2995 | 64.39% | 64.39%
11 | 321 | 17 | 7694 | 14 | 7.7 | 98.06 | 90.28 | 188.34 | 90.28 | 45.14 | 321 | 7694 | 840 | 316.6027 | -19.0357 | 4.0985 | 814.284 | 13.6397 | -24.5956 | 20.5465 | 20.5465 | 24.8459 | 204.8459 | 31.8957 | 237.2134 | 237.2134 | 77.0588 | 314.2722 | 0.34948 | 34.95% | 142.1139 | 49.6657 | 34.766 | 133.6523 | 133.6523 | 26.01% | 11.68% | 11.68% | 85% | 9.929% | 14.1098 | 7.8981 | 6 | 84.6587 | 31.2025 | 63.34% | 63.34%
11 | 321 | 17 | 7695 | 15 | 8.1 | 130.64 | 94.81 | 225.45 | 94.81 | 47.41 | 321 | 7695 | 900 | 316.6027 | -19.0357 | 4.0985 | 874.284 | 14.6397 | -39.5956 | 15.1396 | 15.1396 | 38.6217 | 218.6217 | 44.1142 | 359.1254 | 359.1254 | 80.9254 | 440.0508 | 0.48154 | 48.15% | 198.991 | 95.8224 | 67.0757 | 114.0947 | 114.0947 | 58.79% | 11.59% | 11.59% | 85% | 9.849% | 19.5995 | 7.7853 | 6 | 117.5971 | 43.3426 | 103.1% | 103.1%
11 | 321 | 17 | 7696 | 16 | 9.5 | 73.42 | 73.25 | 146.67 | 73.25 | 36.63 | 321 | 7696 | 960 | 316.6027 | -19.0357 | 4.0985 | 934.284 | 15.6397 | -54.5956 | 7.8963 | 7.8963 | 51.0675 | 231.0675 | 57.5014 | 0 | 0 | 62.5228 | 62.5228 | -1.4129 | 0% | 28.2728 | 0 | 0 | 154.2438 | 154.2438 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7697 | 17 | 10.9 | 19.17 | 43.25 | 62.42 | 43.25 | 21.63 | 321 | 7697 | 1020 | 316.6027 | -19.0357 | 4.0985 | 994.284 | 16.6397 | -69.5956 | -0.68577 | 0 | 61.5584 | 241.5584 | 70.3199 | 0 | 0 | 36.9162 | 36.9162 | -2.8622 | 0% | 16.6935 | 0 | 0 | 150.4156 | 150.4156 | 0% | 11.73% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7698 | 18 | 10.6 | 0 | 2.22 | 2.22 | 2.22 | 1.11 | 321 | 7698 | 1080 | 316.6027 | -19.0357 | 4.0985 | 1054.284 | 17.6397 | -84.5956 | -10.1776 | 0 | 61.5584 | 241.5584 | 70.3199 | 0 | 0 | 1.8949 | 1.8949 | -70.9886 | 0% | 0.85687 | 0 | 0 | 143.7054 | 143.7054 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7699 | 19 | 9.5 | 0 | 0 | 0 | 0 | 0 | 321 | 7699 | 1140 | 316.6027 | -19.0357 | 4.0985 | 1114.284 | 18.6397 | -99.5956 | -20.2176 | 0 | 61.5584 | 241.5584 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.4066 | 139.4066 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7700 | 20 | 8.2 | 0 | 0 | 0 | 0 | 0 | 321 | 7700 | 1200 | 316.6027 | -19.0357 | 4.0985 | 1174.284 | 19.6397 | -114.5956 | -30.4721 | 0 | 61.5584 | 241.5584 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.3633 | 134.3633 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7573 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7701 | 21 | 7.7 | 0 | 0 | 0 | 0 | 0 | 321 | 7701 | 1260 | 316.6027 | -19.0357 | 4.0985 | 1234.284 | 20.6397 | -129.5956 | -40.5634 | 0 | 61.5584 | 241.5584 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.1969 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7702 | 22 | 7.1 | 0 | 0 | 0 | 0 | 0 | 321 | 7702 | 1320 | 316.6027 | -19.0357 | 4.0985 | 1294.284 | 21.6397 | -144.5956 | -49.9372 | 0 | 61.5584 | 241.5584 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8329 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7703 | 23 | 6 | 0 | 0 | 0 | 0 | 0 | 321 | 7703 | 1380 | 316.6027 | -19.0357 | 4.0985 | 1354.284 | 22.6397 | -159.5956 | -57.611 | 0 | 61.5584 | 241.5584 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4263 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
11 | 321 | 17 | 7704 | 24 | 5.4 | 0 | 0 | 0 | 0 | 0 | 321 | 7704 | 1440 | 316.6027 | -19.0357 | 4.0985 | 1414.284 | 23.6397 | -174.5956 | -61.9055 | 0 | 61.5584 | 241.5584 | 70.3199 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.2576 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7705 | 1 | 5.3 | 0 | 0 | 0 | 0 | 0 | 322 | 7705 | 60 | 317.589 | -19.2753 | 4.0577 | 34.284 | 0.63903 | 170.4146 | -61.3977 | 0 | 61.1818 | 118.8182 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1676 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7706 | 2 | 4.9 | 0 | 0 | 0 | 0 | 0 | 322 | 7706 | 120 | 317.589 | -19.2753 | 4.0577 | 94.284 | 1.639 | 155.4146 | -55.9332 | 0 | 61.1818 | 118.8182 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4922 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7707 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 322 | 7707 | 180 | 317.589 | -19.2753 | 4.0577 | 154.284 | 2.639 | 140.4146 | -47.6246 | 0 | 61.1818 | 118.8182 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0547 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6885 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7708 | 4 | 4.9 | 0 | 0 | 0 | 0 | 0 | 322 | 7708 | 240 | 317.589 | -19.2753 | 4.0577 | 214.284 | 3.639 | 125.4146 | -37.9632 | 0 | 61.1818 | 118.8182 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2071 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7709 | 5 | 4.8 | 0 | 0 | 0 | 0 | 0 | 322 | 7709 | 300 | 317.589 | -19.2753 | 4.0577 | 274.284 | 4.639 | 110.4146 | -27.7773 | 0 | 61.1818 | 118.8182 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1376 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7710 | 6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 322 | 7710 | 360 | 317.589 | -19.2753 | 4.0577 | 334.284 | 5.639 | 95.4146 | -17.5508 | 0 | 61.1818 | 118.8182 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.1199 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7711 | 7 | 3.9 | 0 | 0 | 0 | 0 | 0 | 322 | 7711 | 420 | 317.589 | -19.2753 | 4.0577 | 394.284 | 6.639 | 80.4146 | -7.6377 | 0 | 61.1818 | 118.8182 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 153.1809 | 153.1809 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7712 | 8 | 3 | 0 | 0 | 0 | 0 | 0 | 322 | 7712 | 480 | 317.589 | -19.2753 | 4.0577 | 454.284 | 7.639 | 65.4146 | 1.6273 | 1.6273 | 59.1724 | 120.8276 | 67.5241 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 157.2874 | 157.2874 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.3069 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7713 | 9 | 4.3 | 7.42 | 16.31 | 23.73 | 16.31 | 8.16 | 322 | 7713 | 540 | 317.589 | -19.2753 | 4.0577 | 514.284 | 8.639 | 50.4146 | 9.8679 | 9.8679 | 47.5951 | 132.4049 | 53.7738 | 0 | 0 | 13.9215 | 13.9215 | -10.04 | 0% | 6.2953 | 0 | 0 | 141.3995 | 141.3995 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7714 | 10 | 6 | 55.28 | 52.5 | 107.78 | 52.5 | 26.25 | 322 | 7714 | 600 | 317.589 | -19.2753 | 4.0577 | 574.284 | 9.639 | 35.4146 | 16.6355 | 16.6355 | 34.8129 | 145.1871 | 40.6518 | 146.4986 | 146.4986 | 44.8116 | 191.3102 | 0.036217 | 3.622% | 86.5105 | 3.1331 | 2.1932 | 148.911 | 148.911 | 1.473% | 11.82% | 11.82% | 80% | 9.457% | 8.1809 | 8.3898 | 6 | 49.0854 | 18.0913 | 32.96% | 32.96%
11 | 322 | 18 | 7715 | 11 | 6.8 | 81.19 | 65.08 | 146.27 | 65.08 | 32.54 | 322 | 7715 | 660 | 317.589 | -19.2753 | 4.0577 | 634.284 | 10.639 | 20.4146 | 21.4251 | 21.4251 | 20.7138 | 159.2862 | 29.0745 | 194.2568 | 194.2568 | 55.5493 | 249.806 | 0.22364 | 22.36% | 112.9623 | 25.2626 | 17.6838 | 148.0227 | 148.0227 | 11.95% | 11.75% | 11.75% | 80% | 9.401% | 10.6198 | 8.1559 | 6 | 63.7185 | 23.4846 | 43.05% | 43.05%
11 | 322 | 18 | 7716 | 12 | 6.4 | 178.33 | 77.42 | 255.75 | 77.42 | 38.71 | 322 | 7716 | 720 | 317.589 | -19.2753 | 4.0577 | 694.284 | 11.639 | 5.4146 | 23.766 | 23.766 | 5.5852 | 174.4148 | 21.7149 | 411.1028 | 411.1028 | 66.0821 | 477.1849 | 0.49818 | 49.82% | 215.783 | 107.4998 | 75.2499 | 125.246 | 125.246 | 60.08% | 11.59% | 11.59% | 85% | 9.854% | 21.2642 | 8.2723 | 6 | 127.5853 | 47.0239 | 101.9% | 101.9%
11 | 322 | 18 | 7717 | 13 | 7 | 215 | 128.42 | 343.42 | 128.42 | 64.21 | 322 | 7717 | 780 | 317.589 | -19.2753 | 4.0577 | 754.284 | 12.639 | -9.5854 | 23.3821 | 23.3821 | 9.8603 | 189.8603 | 23.0631 | 498.4516 | 498.4516 | 109.6133 | 608.0649 | 0.56636 | 56.64% | 274.967 | 155.7293 | 109.0105 | 128.4404 | 128.4404 | 84.87% | 11.49% | 11.49% | 90% | 10.34% | 28.4324 | 8.0981 | 6 | 170.5946 | 62.8758 | 132.8% | 132.8%
11 | 322 | 18 | 7718 | 14 | 7.7 | 195 | 97.42 | 292.42 | 97.42 | 48.71 | 322 | 7718 | 840 | 317.589 | -19.2753 | 4.0577 | 814.284 | 13.639 | -24.5854 | 20.3211 | 20.3211 | 24.7584 | 204.7584 | 32.0364 | 475.9939 | 475.9939 | 83.1532 | 559.147 | 0.54853 | 54.85% | 252.8463 | 138.6946 | 97.0862 | 126.7519 | 126.7519 | 76.6% | 11.51% | 11.51% | 90% | 10.36% | 26.2036 | 7.8981 | 6 | 157.2215 | 57.9469 | 124% | 124%
11 | 322 | 18 | 7719 | 15 | 6.6 | 153.97 | 67.14 | 221.11 | 67.14 | 33.57 | 322 | 7719 | 900 | 317.589 | -19.2753 | 4.0577 | 874.284 | 14.639 | -39.5854 | 14.9302 | 14.9302 | 38.5006 | 218.5006 | 44.2024 | 428.417 | 428.417 | 57.3076 | 485.7246 | 0.50454 | 50.45% | 219.6447 | 110.82 | 77.574 | 119.4403 | 119.4403 | 64.95% | 11.58% | 0% | 85% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7720 | 16 | 6.5 | 86.47 | 50.47 | 136.94 | 50.47 | 25.24 | 322 | 7720 | 960 | 317.589 | -19.2753 | 4.0577 | 934.284 | 15.639 | -54.5854 | 7.7038 | 7.7038 | 50.9232 | 230.9232 | 57.5544 | 0 | 0 | 43.0788 | 43.0788 | -2.578 | 0% | 19.4803 | 0 | 0 | 156.0685 | 156.0685 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7721 | 17 | 6.3 | 7.86 | 24.81 | 32.67 | 24.81 | 12.41 | 322 | 7721 | 1020 | 317.589 | -19.2753 | 4.0577 | 994.284 | 16.639 | -69.5854 | -0.86333 | 0 | 61.1818 | 241.1818 | 70.0715 | 0 | 0 | 21.1767 | 21.1767 | -6.0984 | 0% | 9.5761 | 0 | 0 | 146.686 | 146.686 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7722 | 18 | 5.7 | 0 | 0.92 | 0.92 | 0.92 | 0.46 | 322 | 7722 | 1080 | 317.589 | -19.2753 | 4.0577 | 1054.284 | 17.639 | -84.5854 | -10.3437 | 0 | 61.1818 | 241.1818 | 70.0715 | 0 | 0 | 0.78527 | 0.78527 | -187.1594 | 0% | 0.3551 | 0 | 0 | 140.1683 | 140.1683 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7723 | 19 | 5.3 | 0 | 0 | 0 | 0 | 0 | 322 | 7723 | 1140 | 317.589 | -19.2753 | 4.0577 | 1114.284 | 18.639 | -99.5854 | -20.377 | 0 | 61.1818 | 241.1818 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.982 | 135.982 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7724 | 20 | 4.4 | 0 | 0 | 0 | 0 | 0 | 322 | 7724 | 1200 | 317.589 | -19.2753 | 4.0577 | 1174.284 | 19.639 | -114.5854 | -30.6306 | 0 | 61.1818 | 241.1818 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.8848 | 129.8848 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.8711 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7725 | 21 | 4.7 | 0 | 0 | 0 | 0 | 0 | 322 | 7725 | 1260 | 317.589 | -19.2753 | 4.0577 | 1234.284 | 20.639 | -129.5854 | -40.7288 | 0 | 61.1818 | 241.1818 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.8433 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.7795 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7726 | 22 | 4.1 | 0 | 0 | 0 | 0 | 0 | 322 | 7726 | 1320 | 317.589 | -19.2753 | 4.0577 | 1294.284 | 21.639 | -144.5854 | -50.1197 | 0 | 61.1818 | 241.1818 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.8515 | 0 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7727 | 23 | 3.8 | 0 | 0 | 0 | 0 | 0 | 322 | 7727 | 1380 | 317.589 | -19.2753 | 4.0577 | 1354.284 | 22.639 | -159.5854 | -57.821 | 0 | 61.1818 | 241.1818 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0236 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
11 | 322 | 18 | 7728 | 24 | 3.6 | 0 | 0 | 0 | 0 | 0 | 322 | 7728 | 1440 | 317.589 | -19.2753 | 4.0577 | 1414.284 | 23.639 | -174.5854 | -62.1416 | 0 | 61.1818 | 241.1818 | 70.0715 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0434 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7729 | 1 | 3.6 | 0 | 0 | 0 | 0 | 0 | 323 | 7729 | 60 | 318.5753 | -19.5087 | 4.0068 | 34.284 | 0.63818 | 170.4273 | -61.6272 | 0 | 60.8143 | 119.1857 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.4092 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7730 | 2 | 3.8 | 0 | 0 | 0 | 0 | 0 | 323 | 7730 | 120 | 318.5753 | -19.5087 | 4.0068 | 94.284 | 1.6382 | 155.4273 | -56.14 | 0 | 60.8143 | 119.1857 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9438 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7731 | 3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 323 | 7731 | 180 | 318.5753 | -19.5087 | 4.0068 | 154.284 | 2.6382 | 140.4273 | -47.8101 | 0 | 60.8143 | 119.1857 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0879 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.1184 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7732 | 4 | 3.9 | 0 | 0 | 0 | 0 | 0 | 323 | 7732 | 240 | 318.5753 | -19.5087 | 4.0068 | 214.284 | 3.6382 | 125.4273 | -38.1363 | 0 | 60.8143 | 119.1857 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6307 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7733 | 5 | 3.9 | 0 | 0 | 0 | 0 | 0 | 323 | 7733 | 300 | 318.5753 | -19.5087 | 4.0068 | 274.284 | 4.6382 | 110.4273 | -27.9465 | 0 | 60.8143 | 119.1857 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.0161 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7734 | 6 | 3.7 | 0 | 0 | 0 | 0 | 0 | 323 | 7734 | 360 | 318.5753 | -19.5087 | 4.0068 | 334.284 | 5.6382 | 95.4273 | -17.7224 | 0 | 60.8143 | 119.1857 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.7712 | 0 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.0873 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7735 | 7 | 3.8 | 0 | 0 | 0 | 0 | 0 | 323 | 7735 | 420 | 318.5753 | -19.5087 | 4.0068 | 394.284 | 6.6382 | 80.4273 | -7.8166 | 0 | 60.8143 | 119.1857 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.8727 | 140.8727 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7736 | 8 | 3.9 | 0 | 1.11 | 1.11 | 1.11 | 0.56 | 323 | 7736 | 480 | 318.5753 | -19.5087 | 4.0068 | 454.284 | 7.6382 | 65.4273 | 1.4373 | 1.4373 | 59.0364 | 120.9636 | 67.5781 | 0 | 0 | 0.94744 | 0.94744 | -159.554 | 0% | 0.42843 | 0 | 0 | 144.103 | 144.103 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7737 | 9 | 4.1 | 3.89 | 13.97 | 17.86 | 13.97 | 6.99 | 323 | 7737 | 540 | 318.5753 | -19.5087 | 4.0068 | 514.284 | 8.6382 | 50.4273 | 9.6644 | 9.6644 | 47.4786 | 132.5214 | 53.8548 | 0 | 0 | 11.9241 | 11.9241 | -11.8969 | 0% | 5.3921 | 0 | 0 | 125.2128 | 125.2128 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7738 | 10 | 4.6 | 6.58 | 54.08 | 60.66 | 54.08 | 27.04 | 323 | 7738 | 600 | 318.5753 | -19.5087 | 4.0068 | 574.284 | 9.6382 | 35.4273 | 16.4181 | 16.4181 | 34.7236 | 145.2764 | 40.7697 | 17.631 | 17.631 | 46.1602 | 63.7911 | -1.5512 | 0% | 28.8463 | 0 | 0 | 127.6067 | 127.6067 | 0% | 11.98% | 11.98% | 80% | 9.58% | 2.7636 | 8.8099 | 6 | 16.5817 | 6.1115 | 12.99% | 12.99%
11 | 323 | 19 | 7739 | 11 | 5 | 20 | 120.19 | 140.19 | 120.19 | 60.1 | 323 | 7739 | 660 | 318.5753 | -19.5087 | 4.0068 | 634.284 | 10.6382 | 20.4273 | 21.1965 | 21.1965 | 20.662 | 159.338 | 29.246 | 48.2637 | 48.2637 | 102.5886 | 150.8523 | -0.18558 | 0% | 68.2154 | 0 | 0 | 129.9562 | 129.9562 | 0% | 11.89% | 11.89% | 80% | 9.51% | 6.4873 | 8.6885 | 6 | 38.9239 | 14.3461 | 29.95% | 29.95%
11 | 323 | 19 | 7740 | 12 | 5 | 17.86 | 171.03 | 188.89 | 171.03 | 85.52 | 323 | 7740 | 720 | 318.5753 | -19.5087 | 4.0068 | 694.284 | 11.6382 | 5.4273 | 23.5323 | 23.5323 | 5.5802 | 174.4198 | 21.9436 | 41.4913 | 41.4913 | 145.9832 | 187.4745 | 0.0077318 | 0.7732% | 84.776 | 0.65547 | 0.45883 | 128.8462 | 128.8462 | 0.3561% | 11.86% | 11.86% | 80% | 9.486% | 8.0417 | 8.6885 | 6 | 48.2504 | 17.7836 | 37.45% | 37.45%
11 | 323 | 19 | 7741 | 13 | 5.4 | 43.42 | 159.44 | 202.86 | 159.44 | 79.72 | 323 | 7741 | 780 | 318.5753 | -19.5087 | 4.0068 | 754.284 | 12.6382 | -9.5727 | 23.152 | 23.152 | 9.8158 | 189.8158 | 23.2695 | 101.452 | 101.452 | 136.0906 | 237.5426 | 0.17961 | 17.96% | 107.4167 | 19.2926 | 13.5048 | 108.4226 | 108.4226 | 12.46% | 11.8% | 11.8% | 80% | 9.443% | 10.1433 | 8.5682 | 6 | 60.8597 | 22.431 | 56.13% | 56.13%
11 | 323 | 19 | 7742 | 14 | 5.3 | 31.11 | 164.36 | 195.47 | 164.36 | 82.18 | 323 | 7742 | 840 | 318.5753 | -19.5087 | 4.0068 | 814.284 | 13.6382 | -24.5727 | 20.1024 | 20.1024 | 24.6707 | 204.6707 | 32.1723 | 76.6166 | 76.6166 | 140.29 | 216.9067 | 0.1191 | 11.91% | 98.0852 | 11.6817 | 8.1772 | 128.536 | 128.536 | 6.362% | 11.82% | 11.82% | 80% | 9.459% | 9.2776 | 8.5982 | 6 | 55.6658 | 20.5166 | 43.31% | 43.31%
11 | 323 | 19 | 7743 | 15 | 5.8 | 53.42 | 142.97 | 196.39 | 142.97 | 71.49 | 323 | 7743 | 900 | 318.5753 | -19.5087 | 4.0068 | 874.284 | 14.6382 | -39.5727 | 14.7274 | 14.7274 | 38.3806 | 218.3806 | 44.2868 | 150.4245 | 150.4245 | 122.0325 | 272.457 | 0.26313 | 26.31% | 123.2051 | 32.4195 | 22.6936 | 107.1584 | 107.1584 | 21.18% | 11.76% | 0% | 80% | 0% | 0 | 8.449 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7744 | 16 | 5.9 | 23.97 | 73.97 | 97.94 | 73.97 | 36.99 | 323 | 7744 | 960 | 318.5753 | -19.5087 | 4.0068 | 934.284 | 15.6382 | -54.5727 | 7.5177 | 7.5177 | 50.7806 | 230.7806 | 57.6041 | 0 | 0 | 63.1373 | 63.1373 | -1.5262 | 0% | 28.5507 | 0 | 0 | 143.7947 | 143.7947 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7745 | 17 | 5.9 | 1.39 | 31.31 | 32.7 | 31.31 | 15.66 | 323 | 7745 | 1020 | 318.5753 | -19.5087 | 4.0068 | 994.284 | 16.6382 | -69.5727 | -1.0346 | 0 | 60.8143 | 240.8143 | 69.8295 | 0 | 0 | 26.7248 | 26.7248 | -4.7011 | 0% | 12.0849 | 0 | 0 | 138.9601 | 138.9601 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7746 | 18 | 6 | 0 | 2.08 | 2.08 | 2.08 | 1.04 | 323 | 7746 | 1080 | 318.5753 | -19.5087 | 4.0068 | 1054.284 | 17.6382 | -84.5727 | -10.5036 | 0 | 60.8143 | 240.8143 | 69.8295 | 0 | 0 | 1.7754 | 1.7754 | -81.9297 | 0% | 0.80283 | 0 | 0 | 135.8471 | 135.8471 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3898 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7747 | 19 | 5.9 | 0 | 0 | 0 | 0 | 0 | 323 | 7747 | 1140 | 318.5753 | -19.5087 | 4.0068 | 1114.284 | 18.6382 | -99.5727 | -20.5301 | 0 | 60.8143 | 240.8143 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.655 | 133.655 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7748 | 20 | 5.9 | 0 | 0 | 0 | 0 | 0 | 323 | 7748 | 1200 | 318.5753 | -19.5087 | 4.0068 | 1174.284 | 19.6382 | -114.5727 | -30.7828 | 0 | 60.8143 | 240.8143 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.9039 | 130.9039 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.4194 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7749 | 21 | 6.1 | 0 | 0 | 0 | 0 | 0 | 323 | 7749 | 1260 | 318.5753 | -19.5087 | 4.0068 | 1234.284 | 20.6382 | -129.5727 | -40.8877 | 0 | 60.8143 | 240.8143 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4648 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7750 | 22 | 6.1 | 0 | 0 | 0 | 0 | 0 | 323 | 7750 | 1320 | 318.5753 | -19.5087 | 4.0068 | 1294.284 | 21.6382 | -144.5727 | -50.2953 | 0 | 60.8143 | 240.8143 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.0811 | 0 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7751 | 23 | 5.4 | 0 | 0 | 0 | 0 | 0 | 323 | 7751 | 1380 | 318.5753 | -19.5087 | 4.0068 | 1354.284 | 22.6382 | -159.5727 | -58.024 | 0 | 60.8143 | 240.8143 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.9873 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
11 | 323 | 19 | 7752 | 24 | 5.2 | 0 | 0 | 0 | 0 | 0 | 323 | 7752 | 1440 | 318.5753 | -19.5087 | 4.0068 | 1414.284 | 23.6382 | -174.5727 | -62.371 | 0 | 60.8143 | 240.8143 | 69.8295 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.1314 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7753 | 1 | 4.8 | 0 | 0 | 0 | 0 | 0 | 324 | 7753 | 60 | 319.5616 | -19.7357 | 3.946 | 34.284 | 0.63717 | 170.4425 | -61.851 | 0 | 60.4561 | 119.5439 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.1014 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7754 | 2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 324 | 7754 | 120 | 319.5616 | -19.7357 | 3.946 | 94.284 | 1.6372 | 155.4425 | -56.3423 | 0 | 60.4561 | 119.5439 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.5947 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7755 | 3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 324 | 7755 | 180 | 319.5616 | -19.7357 | 3.946 | 154.284 | 2.6372 | 140.4425 | -47.9917 | 0 | 60.4561 | 119.5439 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5452 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7756 | 4 | 2.6 | 0 | 0 | 0 | 0 | 0 | 324 | 7756 | 240 | 319.5616 | -19.7357 | 3.946 | 214.284 | 3.6372 | 125.4425 | -38.3063 | 0 | 60.4561 | 119.5439 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9168 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7757 | 5 | -0.7 | 0 | 0 | 0 | 0 | 0 | 324 | 7757 | 300 | 319.5616 | -19.7357 | 3.946 | 274.284 | 4.6372 | 110.4425 | -28.1128 | 0 | 60.4561 | 119.5439 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.1393 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7758 | 6 | 1.7 | 0 | 0 | 0 | 0 | 0 | 324 | 7758 | 360 | 319.5616 | -19.7357 | 3.946 | 334.284 | 5.6372 | 95.4425 | -17.8911 | 0 | 60.4561 | 119.5439 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.7196 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7759 | 7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 324 | 7759 | 420 | 319.5616 | -19.7357 | 3.946 | 394.284 | 6.6372 | 80.4425 | -7.9925 | 0 | 60.4561 | 119.5439 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.7885 | 148.7885 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4339 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7760 | 8 | 8.4 | 0 | 0 | 0 | 0 | 0 | 324 | 7760 | 480 | 319.5616 | -19.7357 | 3.946 | 454.284 | 7.6372 | 65.4425 | 1.2508 | 1.2508 | 58.9061 | 121.0939 | 67.6336 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 163.0863 | 163.0863 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.7015 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7761 | 9 | 8.1 | 6.31 | 14.81 | 21.12 | 14.81 | 7.41 | 324 | 7761 | 540 | 319.5616 | -19.7357 | 3.946 | 514.284 | 8.6372 | 50.4425 | 9.465 | 9.465 | 47.3676 | 132.6324 | 53.9367 | 0 | 0 | 12.6411 | 12.6411 | -10.4211 | 0% | 5.7163 | 0 | 0 | 144.6789 | 144.6789 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7762 | 10 | 10.8 | 35.75 | 63.06 | 98.81 | 63.06 | 31.53 | 324 | 7762 | 600 | 319.5616 | -19.7357 | 3.946 | 574.284 | 9.6372 | 35.4425 | 16.2055 | 16.2055 | 34.6393 | 145.3607 | 40.8875 | 96.8413 | 96.8413 | 53.8251 | 150.6664 | -0.095827 | 0% | 68.1314 | 0 | 0 | 153.7237 | 153.7237 | 0% | 11.68% | 11.68% | 80% | 9.344% | 6.3665 | 7.0535 | 6 | 38.199 | 14.0789 | 24.85% | 24.85%
11 | 324 | 20 | 7763 | 11 | -1.3 | 107.78 | 109.08 | 216.86 | 109.08 | 54.54 | 324 | 7763 | 660 | 319.5616 | -19.7357 | 3.946 | 634.284 | 10.6372 | 20.4425 | 20.9734 | 20.9734 | 20.6144 | 159.3856 | 29.4155 | 262.2965 | 262.2965 | 93.1056 | 355.4022 | 0.34064 | 34.06% | 160.7129 | 54.7455 | 38.3219 | 117.0049 | 117.0049 | 32.75% | 11.87% | 11.87% | 85% | 10.09% | 16.219 | 10.7313 | 6 | 97.3141 | 35.8669 | 83.17% | 83.17%
11 | 324 | 20 | 7764 | 12 | 12.9 | 235.19 | 107.5 | 342.69 | 107.5 | 53.75 | 324 | 7764 | 720 | 319.5616 | -19.7357 | 3.946 | 694.284 | 11.6372 | 5.4425 | 23.3049 | 23.3049 | 5.5783 | 174.4217 | 22.1669 | 550.5401 | 550.5401 | 91.757 | 642.297 | 0.60048 | 60.05% | 290.4467 | 174.4065 | 122.0846 | 138.5936 | 138.5936 | 88.09% | 11.41% | 11.41% | 90% | 10.27% | 29.8353 | 6.5196 | 6 | 179.012 | 65.9782 | 129.2% | 129.2%
11 | 324 | 20 | 7765 | 13 | 12.9 | 243.89 | 119.08 | 362.97 | 119.08 | 59.54 | 324 | 7765 | 780 | 319.5616 | -19.7357 | 3.946 | 754.284 | 12.6372 | -9.5575 | 22.9285 | 22.9285 | 9.7699 | 189.7699 | 23.4697 | 574.2385 | 574.2385 | 101.6411 | 675.8797 | 0.61059 | 61.06% | 305.6328 | 186.6161 | 130.6313 | 137.5558 | 137.5558 | 94.97% | 11.4% | 11.4% | 90% | 10.26% | 31.3592 | 6.5196 | 6 | 188.1553 | 69.3481 | 136.8% | 136.8%
11 | 324 | 20 | 7766 | 14 | 13 | 228.97 | 81.39 | 310.36 | 81.39 | 40.7 | 324 | 7766 | 840 | 319.5616 | -19.7357 | 3.946 | 814.284 | 13.6372 | -24.5575 | 19.8904 | 19.8904 | 24.583 | 204.583 | 32.3035 | 568.8401 | 568.8401 | 69.4707 | 638.3108 | 0.59957 | 59.96% | 288.6442 | 173.0611 | 121.1427 | 134.8275 | 134.8275 | 89.85% | 11.41% | 11.41% | 90% | 10.27% | 29.6519 | 6.4949 | 6 | 177.9115 | 65.5726 | 132% | 132%
11 | 324 | 20 | 7767 | 15 | 12.8 | 161.19 | 90.28 | 251.47 | 90.28 | 45.14 | 324 | 7767 | 900 | 319.5616 | -19.7357 | 3.946 | 874.284 | 14.6372 | -39.5575 | 14.5312 | 14.5312 | 38.2616 | 218.2616 | 44.3673 | 459.2543 | 459.2543 | 77.0588 | 536.3131 | 0.55983 | 55.98% | 242.5208 | 135.7702 | 95.0391 | 129.1894 | 129.1894 | 73.57% | 11.46% | 0% | 90% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7768 | 16 | 11.9 | 68.42 | 55 | 123.42 | 55 | 27.5 | 324 | 7768 | 960 | 319.5616 | -19.7357 | 3.946 | 934.284 | 15.6372 | -54.5575 | 7.3381 | 7.3381 | 50.6399 | 230.6399 | 57.6504 | 0 | 0 | 46.9454 | 46.9454 | -2.0296 | 0% | 21.2287 | 0 | 0 | 162.0533 | 162.0533 | 0% | 11.69% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7769 | 17 | 10.6 | 20.56 | 19.36 | 39.92 | 19.36 | 9.68 | 324 | 7769 | 1020 | 319.5616 | -19.7357 | 3.946 | 994.284 | 16.6372 | -69.5575 | -1.1995 | 0 | 60.4561 | 240.4561 | 69.5941 | 0 | 0 | 16.5248 | 16.5248 | -7.4284 | 0% | 7.4725 | 0 | 0 | 152.9796 | 152.9796 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7770 | 18 | 8.7 | 0 | 0.97 | 0.97 | 0.97 | 0.49 | 324 | 7770 | 1080 | 319.5616 | -19.7357 | 3.946 | 1054.284 | 17.6372 | -84.5575 | -10.6572 | 0 | 60.4561 | 240.4561 | 69.5941 | 0 | 0 | 0.82795 | 0.82795 | -168.874 | 0% | 0.3744 | 0 | 0 | 143.2849 | 143.2849 | 0% | 11.85% | 0% | 80% | 0% | 0 | 7.6183 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7771 | 19 | 7.3 | 0 | 0 | 0 | 0 | 0 | 324 | 7771 | 1140 | 319.5616 | -19.7357 | 3.946 | 1114.284 | 18.6372 | -99.5575 | -20.6769 | 0 | 60.4561 | 240.4561 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.6744 | 137.6744 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.012 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7772 | 20 | 6.2 | 0 | 0 | 0 | 0 | 0 | 324 | 7772 | 1200 | 319.5616 | -19.7357 | 3.946 | 1174.284 | 19.6372 | -114.5575 | -30.9287 | 0 | 60.4561 | 240.4561 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.4481 | 131.4481 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7773 | 21 | 4.8 | 0 | 0 | 0 | 0 | 0 | 324 | 7773 | 1260 | 319.5616 | -19.7357 | 3.946 | 1234.284 | 20.6372 | -129.5575 | -41.04 | 0 | 60.4561 | 240.4561 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.8387 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7491 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7774 | 22 | 4.5 | 0 | 0 | 0 | 0 | 0 | 324 | 7774 | 1320 | 319.5616 | -19.7357 | 3.946 | 1294.284 | 21.6372 | -144.5575 | -50.464 | 0 | 60.4561 | 240.4561 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.3647 | 0 | 0% | 12.03% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7775 | 23 | 3.8 | 0 | 0 | 0 | 0 | 0 | 324 | 7775 | 1380 | 319.5616 | -19.7357 | 3.946 | 1354.284 | 22.6372 | -159.5575 | -58.22 | 0 | 60.4561 | 240.4561 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.1628 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
11 | 324 | 20 | 7776 | 24 | 2.8 | 0 | 0 | 0 | 0 | 0 | 324 | 7776 | 1440 | 319.5616 | -19.7357 | 3.946 | 1414.284 | 23.6372 | -174.5575 | -62.5937 | 0 | 60.4561 | 240.4561 | 69.5941 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4181 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7777 | 1 | 2.7 | 0 | 0 | 0 | 0 | 0 | 325 | 7777 | 60 | 320.5479 | -19.9562 | 3.8755 | 34.284 | 0.63599 | 170.4601 | -62.069 | 0 | 60.1073 | 119.8927 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0927 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.4021 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7778 | 2 | 1.9 | 0 | 0 | 0 | 0 | 0 | 325 | 7778 | 120 | 320.5479 | -19.9562 | 3.8755 | 94.284 | 1.636 | 155.4601 | -56.5399 | 0 | 60.1073 | 119.8927 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.1218 | 0 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7779 | 3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 325 | 7779 | 180 | 320.5479 | -19.9562 | 3.8755 | 154.284 | 2.636 | 140.4601 | -48.1697 | 0 | 60.1073 | 119.8927 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5412 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7780 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 325 | 7780 | 240 | 320.5479 | -19.9562 | 3.8755 | 214.284 | 3.636 | 125.4601 | -38.473 | 0 | 60.1073 | 119.8927 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3032 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7781 | 5 | 0.9 | 0 | 0 | 0 | 0 | 0 | 325 | 7781 | 300 | 320.5479 | -19.9562 | 3.8755 | 274.284 | 4.636 | 110.4601 | -28.276 | 0 | 60.1073 | 119.8927 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9331 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7782 | 6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 325 | 7782 | 360 | 320.5479 | -19.9562 | 3.8755 | 334.284 | 5.636 | 95.4601 | -18.0568 | 0 | 60.1073 | 119.8927 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2069 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7783 | 7 | 1.7 | 0 | 0 | 0 | 0 | 0 | 325 | 7783 | 420 | 320.5479 | -19.9562 | 3.8755 | 394.284 | 6.636 | 80.4601 | -8.165 | 0 | 60.1073 | 119.8927 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.4388 | 142.4388 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7784 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 325 | 7784 | 480 | 320.5479 | -19.9562 | 3.8755 | 454.284 | 7.636 | 65.4601 | 1.068 | 1.068 | 58.7817 | 121.2183 | 67.6905 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.4267 | 146.4267 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7785 | 9 | 2.3 | 5 | 12.64 | 17.64 | 12.64 | 6.32 | 325 | 7785 | 540 | 320.5479 | -19.9562 | 3.8755 | 514.284 | 8.636 | 50.4601 | 9.2698 | 9.2698 | 47.2622 | 132.7378 | 54.0194 | 0 | 0 | 10.7889 | 10.7889 | -13.6381 | 0% | 4.8787 | 0 | 0 | 127.9941 | 127.9941 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7786 | 10 | 2.8 | 33.97 | 36.47 | 70.44 | 36.47 | 18.24 | 325 | 7786 | 600 | 320.5479 | -19.9562 | 3.8755 | 574.284 | 9.636 | 35.4601 | 15.9979 | 15.9979 | 34.5601 | 145.4399 | 41.005 | 93.0166 | 93.0166 | 31.1291 | 124.1457 | -0.44129 | 0% | 56.1387 | 0 | 0 | 131.4666 | 131.4666 | 0% | 11.99% | 11.99% | 80% | 9.593% | 5.3854 | 9.3703 | 6 | 32.3126 | 11.9094 | 24.58% | 24.58%
11 | 325 | 21 | 7787 | 11 | 3.2 | 68.61 | 74.08 | 142.69 | 74.08 | 37.04 | 325 | 7787 | 660 | 320.5479 | -19.9562 | 3.8755 | 634.284 | 10.636 | 20.4601 | 20.756 | 20.756 | 20.5712 | 159.4288 | 29.5827 | 168.3638 | 168.3638 | 63.2312 | 231.595 | 0.14066 | 14.07% | 104.7273 | 14.7314 | 10.312 | 132.7866 | 132.7866 | 7.766% | 11.88% | 11.88% | 80% | 9.502% | 9.9509 | 9.2438 | 6 | 59.7056 | 22.0056 | 44.96% | 44.96%
11 | 325 | 21 | 7788 | 12 | 3.9 | 103.69 | 96.31 | 200 | 96.31 | 48.16 | 325 | 7788 | 720 | 320.5479 | -19.9562 | 3.8755 | 694.284 | 11.636 | 5.4601 | 23.0837 | 23.0837 | 5.5793 | 174.4207 | 22.3846 | 244.5364 | 244.5364 | 82.2057 | 326.7421 | 0.33901 | 33.9% | 147.7528 | 50.0904 | 35.0632 | 132.0817 | 132.0817 | 26.55% | 11.77% | 11.77% | 85% | 10.01% | 14.7833 | 9.0252 | 6 | 88.6996 | 32.6919 | 67.16% | 67.16%
11 | 325 | 21 | 7789 | 13 | 4.4 | 101.11 | 94.64 | 195.75 | 94.64 | 47.32 | 325 | 7789 | 780 | 320.5479 | -19.9562 | 3.8755 | 754.284 | 12.636 | -9.5399 | 22.7117 | 22.7117 | 9.7225 | 189.7225 | 23.6635 | 239.8598 | 239.8598 | 80.7803 | 320.6401 | 0.33393 | 33.39% | 144.9934 | 48.4175 | 33.8923 | 131.6555 | 131.6555 | 25.74% | 11.76% | 11.76% | 85% | 9.999% | 14.4976 | 8.8711 | 6 | 86.9856 | 32.0602 | 66.07% | 66.07%
11 | 325 | 21 | 7790 | 14 | 4.5 | 101.75 | 81.67 | 183.42 | 81.67 | 40.84 | 325 | 7790 | 840 | 320.5479 | -19.9562 | 3.8755 | 814.284 | 13.636 | -24.5399 | 19.6852 | 19.6852 | 24.4953 | 204.4953 | 32.4299 | 254.9544 | 254.9544 | 69.7097 | 324.6641 | 0.3405 | 34.05% | 146.8131 | 49.9895 | 34.9926 | 130.9735 | 130.9735 | 26.72% | 11.76% | 11.76% | 85% | 9.994% | 14.672 | 8.8405 | 6 | 88.0318 | 32.4458 | 67.21% | 67.21%
11 | 325 | 21 | 7791 | 15 | 4.5 | 81.58 | 66.11 | 147.69 | 66.11 | 33.06 | 325 | 7791 | 900 | 320.5479 | -19.9562 | 3.8755 | 874.284 | 14.636 | -39.5399 | 14.3417 | 14.3417 | 38.1438 | 218.1438 | 44.4439 | 235.1303 | 235.1303 | 56.4284 | 291.5587 | 0.28787 | 28.79% | 131.8428 | 37.9534 | 26.5674 | 148.991 | 148.991 | 17.83% | 11.79% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7792 | 16 | 4.6 | 47.86 | 50.28 | 98.14 | 50.28 | 25.14 | 325 | 7792 | 960 | 320.5479 | -19.9562 | 3.8755 | 934.284 | 15.636 | -54.5399 | 7.165 | 7.165 | 50.5011 | 230.5011 | 57.6935 | 0 | 0 | 42.9167 | 42.9167 | -2.6968 | 0% | 19.4069 | 0 | 0 | 146.0541 | 146.0541 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.8099 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7793 | 17 | 4.5 | 21.11 | 25.28 | 46.39 | 25.28 | 12.64 | 325 | 7793 | 1020 | 320.5479 | -19.9562 | 3.8755 | 994.284 | 16.636 | -69.5399 | -1.3579 | 0 | 60.1073 | 240.1073 | 69.3654 | 0 | 0 | 21.5778 | 21.5778 | -6.1699 | 0% | 9.7575 | 0 | 0 | 142.1274 | 142.1274 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.8405 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7794 | 18 | 4.1 | 0 | 0.97 | 0.97 | 0.97 | 0.49 | 325 | 7794 | 1080 | 320.5479 | -19.9562 | 3.8755 | 1054.284 | 17.636 | -84.5399 | -10.8045 | 0 | 60.1073 | 240.1073 | 69.3654 | 0 | 0 | 0.82795 | 0.82795 | -182.115 | 0% | 0.3744 | 0 | 0 | 135.6021 | 135.6021 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9633 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7795 | 19 | 3.9 | 0 | 0 | 0 | 0 | 0 | 325 | 7795 | 1140 | 320.5479 | -19.9562 | 3.8755 | 1114.284 | 18.636 | -99.5399 | -20.8175 | 0 | 60.1073 | 240.1073 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.8792 | 132.8792 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7796 | 20 | 3.1 | 0 | 0 | 0 | 0 | 0 | 325 | 7796 | 1200 | 320.5479 | -19.9562 | 3.8755 | 1174.284 | 19.636 | -114.5399 | -31.0681 | 0 | 60.1073 | 240.1073 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.4679 | 128.4679 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7797 | 21 | 2.8 | 0 | 0 | 0 | 0 | 0 | 325 | 7797 | 1260 | 320.5479 | -19.9562 | 3.8755 | 1234.284 | 20.636 | -129.5399 | -41.1857 | 0 | 60.1073 | 240.1073 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7829 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7798 | 22 | 2.2 | 0 | 0 | 0 | 0 | 0 | 325 | 7798 | 1320 | 320.5479 | -19.9562 | 3.8755 | 1294.284 | 21.636 | -144.5399 | -50.6258 | 0 | 60.1073 | 240.1073 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4251 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5621 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7799 | 23 | 1.7 | 0 | 0 | 0 | 0 | 0 | 325 | 7799 | 1380 | 320.5479 | -19.9562 | 3.8755 | 1354.284 | 22.636 | -159.5399 | -58.4087 | 0 | 60.1073 | 240.1073 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.997 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
11 | 325 | 21 | 7800 | 24 | 1.2 | 0 | 0 | 0 | 0 | 0 | 325 | 7800 | 1440 | 320.5479 | -19.9562 | 3.8755 | 1414.284 | 23.636 | -174.5399 | -62.8097 | 0 | 60.1073 | 240.1073 | 69.3654 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5688 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7801 | 1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 326 | 7801 | 60 | 321.5342 | -20.1702 | 3.7955 | 34.284 | 0.63466 | 170.4801 | -62.2812 | 0 | 59.7681 | 120.2319 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7395 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7802 | 2 | -0.3 | 0 | 0 | 0 | 0 | 0 | 326 | 7802 | 120 | 321.5342 | -20.1702 | 3.7955 | 94.284 | 1.6347 | 155.4801 | -56.7328 | 0 | 59.7681 | 120.2319 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6776 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7803 | 3 | -0.2 | 0 | 0 | 0 | 0 | 0 | 326 | 7803 | 180 | 321.5342 | -20.1702 | 3.7955 | 154.284 | 2.6347 | 140.4801 | -48.3437 | 0 | 59.7681 | 120.2319 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3965 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7804 | 4 | 0.2 | 0 | 0 | 0 | 0 | 0 | 326 | 7804 | 240 | 321.5342 | -20.1702 | 3.7955 | 214.284 | 3.6347 | 125.4801 | -38.6364 | 0 | 59.7681 | 120.2319 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7869 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7805 | 5 | 0.4 | 0 | 0 | 0 | 0 | 0 | 326 | 7805 | 300 | 321.5342 | -20.1702 | 3.7955 | 274.284 | 4.6347 | 110.4801 | -28.4362 | 0 | 59.7681 | 120.2319 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6953 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7806 | 6 | -0.1 | 0 | 0 | 0 | 0 | 0 | 326 | 7806 | 360 | 321.5342 | -20.1702 | 3.7955 | 334.284 | 5.6347 | 95.4801 | -18.2194 | 0 | 59.7681 | 120.2319 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.5131 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7807 | 7 | -0.8 | 0 | 0 | 0 | 0 | 0 | 326 | 7807 | 420 | 321.5342 | -20.1702 | 3.7955 | 394.284 | 6.6347 | 80.4801 | -8.3343 | 0 | 59.7681 | 120.2319 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.0251 | 134.0251 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7808 | 8 | -1.1 | 0 | 0 | 0 | 0 | 0 | 326 | 7808 | 480 | 321.5342 | -20.1702 | 3.7955 | 454.284 | 7.6347 | 65.4801 | 0.8889 | 0.8889 | 58.663 | 121.337 | 67.7486 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.4067 | 136.4067 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7809 | 9 | -0.4 | 1.03 | 15.83 | 16.86 | 15.83 | 7.92 | 326 | 7809 | 540 | 321.5342 | -20.1702 | 3.7955 | 514.284 | 8.6347 | 50.4801 | 9.079 | 9.079 | 47.1623 | 132.8377 | 54.1027 | 0 | 0 | 13.5118 | 13.5118 | -11.2186 | 0% | 6.11 | 0 | 0 | 118.125 | 118.125 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7810 | 10 | -0.1 | 1.31 | 41.67 | 42.98 | 41.67 | 20.84 | 326 | 7810 | 600 | 321.5342 | -20.1702 | 3.7955 | 574.284 | 9.6347 | 35.4801 | 15.7952 | 15.7952 | 34.486 | 145.514 | 41.1221 | 3.6254 | 3.6254 | 35.5676 | 39.193 | -3.3219 | 0% | 17.7231 | 0 | 0 | 120.5443 | 120.5443 | 0% | 12.19% | 12.19% | 80% | 9.754% | 1.7288 | 10.3208 | 6 | 10.3727 | 3.8231 | 8.605% | 8.605%
11 | 326 | 22 | 7811 | 11 | 0 | 6.94 | 85.08 | 92.02 | 85.08 | 42.54 | 326 | 7811 | 660 | 321.5342 | -20.1702 | 3.7955 | 634.284 | 10.6347 | 20.4801 | 20.5443 | 20.5443 | 20.532 | 159.468 | 29.7475 | 17.1699 | 17.1699 | 72.6203 | 89.7902 | -0.99416 | 0% | 40.6031 | 0 | 0 | 121.8607 | 121.8607 | 0% | 12.13% | 12.13% | 80% | 9.707% | 3.9412 | 10.287 | 6 | 23.6471 | 8.7156 | 19.4% | 19.4%
11 | 326 | 22 | 7812 | 12 | 0.8 | 69.36 | 117.78 | 187.14 | 117.78 | 58.89 | 326 | 7812 | 720 | 321.5342 | -20.1702 | 3.7955 | 694.284 | 11.6347 | 5.4801 | 22.8689 | 22.8689 | 5.5832 | 174.4168 | 22.5965 | 164.7748 | 164.7748 | 100.5315 | 265.3063 | 0.20286 | 20.29% | 119.9715 | 24.3373 | 17.0361 | 125.1616 | 125.1616 | 13.61% | 11.92% | 11.92% | 80% | 9.533% | 11.4373 | 10.0195 | 6 | 68.6235 | 25.2925 | 54.83% | 54.83%
11 | 326 | 22 | 7813 | 13 | 1.1 | 85.36 | 112.86 | 198.22 | 112.86 | 56.43 | 326 | 7813 | 780 | 321.5342 | -20.1702 | 3.7955 | 754.284 | 12.6347 | -9.5199 | 22.5016 | 22.5016 | 9.6739 | 189.6739 | 23.8509 | 203.9937 | 203.9937 | 96.332 | 300.3257 | 0.27541 | 27.54% | 135.8073 | 37.4024 | 26.1817 | 125.2924 | 125.2924 | 20.9% | 11.87% | 11.87% | 85% | 10.09% | 13.7039 | 9.9203 | 6 | 82.2234 | 30.305 | 65.63% | 65.63%
11 | 326 | 22 | 7814 | 14 | 1.6 | 115.28 | 102.36 | 217.64 | 102.36 | 51.18 | 326 | 7814 | 840 | 321.5342 | -20.1702 | 3.7955 | 814.284 | 13.6347 | -24.5199 | 19.4869 | 19.4869 | 24.4078 | 204.4078 | 32.5512 | 291.2875 | 291.2875 | 87.3697 | 378.6572 | 0.38799 | 38.8% | 171.2288 | 66.4355 | 46.5048 | 105.5118 | 105.5118 | 44.08% | 11.78% | 11.78% | 85% | 10.01% | 17.1428 | 9.7564 | 6 | 102.8568 | 37.9098 | 97.48% | 97.48%
11 | 326 | 22 | 7815 | 15 | 2 | 45.64 | 94.25 | 139.89 | 94.25 | 47.13 | 326 | 7815 | 900 | 321.5342 | -20.1702 | 3.7955 | 874.284 | 14.6347 | -39.5199 | 14.1591 | 14.1591 | 38.0272 | 218.0272 | 44.5165 | 133.0401 | 133.0401 | 80.4474 | 213.4875 | 0.070719 | 7.072% | 96.539 | 6.8271 | 4.779 | 142.79 | 142.79 | 3.347% | 11.93% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7816 | 16 | 2.3 | 11.94 | 61.31 | 73.25 | 61.31 | 30.66 | 326 | 7816 | 960 | 321.5342 | -20.1702 | 3.7955 | 934.284 | 15.6347 | -54.5199 | 6.9986 | 6.9986 | 50.3642 | 230.3642 | 57.7331 | 0 | 0 | 52.3314 | 52.3314 | -2.1735 | 0% | 23.6642 | 0 | 0 | 138.9563 | 138.9563 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7817 | 17 | 2.1 | 2.03 | 27.03 | 29.06 | 27.03 | 13.52 | 326 | 7817 | 1020 | 321.5342 | -20.1702 | 3.7955 | 994.284 | 16.6347 | -69.5199 | -1.51 | 0 | 59.7681 | 239.7681 | 69.1435 | 0 | 0 | 23.0715 | 23.0715 | -5.9707 | 0% | 10.433 | 0 | 0 | 134.8579 | 134.8579 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7818 | 18 | 2.1 | 0 | 0 | 0 | 0 | 0 | 326 | 7818 | 1080 | 321.5342 | -20.1702 | 3.7955 | 1054.284 | 17.6347 | -84.5199 | -10.9455 | 0 | 59.7681 | 239.7681 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.6559 | 131.6559 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7819 | 19 | 2 | 0 | 0 | 0 | 0 | 0 | 326 | 7819 | 1140 | 321.5342 | -20.1702 | 3.7955 | 1114.284 | 18.6347 | -99.5199 | -20.9518 | 0 | 59.7681 | 239.7681 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.7789 | 129.7789 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.6266 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7820 | 20 | 1.8 | 0 | 0 | 0 | 0 | 0 | 326 | 7820 | 1200 | 321.5342 | -20.1702 | 3.7955 | 1174.284 | 19.6347 | -114.5199 | -31.2012 | 0 | 59.7681 | 239.7681 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.1446 | 127.1446 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7821 | 21 | 1.2 | 0 | 0 | 0 | 0 | 0 | 326 | 7821 | 1260 | 321.5342 | -20.1702 | 3.7955 | 1234.284 | 20.6347 | -129.5199 | -41.3248 | 0 | 59.7681 | 239.7681 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3595 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7822 | 22 | 0.7 | 0 | 0 | 0 | 0 | 0 | 326 | 7822 | 1320 | 321.5342 | -20.1702 | 3.7955 | 1294.284 | 21.6347 | -144.5199 | -50.7807 | 0 | 59.7681 | 239.7681 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6685 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7823 | 23 | 0.9 | 0 | 0 | 0 | 0 | 0 | 326 | 7823 | 1380 | 321.5342 | -20.1702 | 3.7955 | 1354.284 | 22.6347 | -159.5199 | -58.5903 | 0 | 59.7681 | 239.7681 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2349 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
11 | 326 | 22 | 7824 | 24 | 0.4 | 0 | 0 | 0 | 0 | 0 | 326 | 7824 | 1440 | 321.5342 | -20.1702 | 3.7955 | 1414.284 | 23.6347 | -174.5199 | -63.0188 | 0 | 59.7681 | 239.7681 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8682 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7825 | 1 | -0.6 | 0 | 0 | 0 | 0 | 0 | 327 | 7825 | 60 | 322.5205 | -20.3776 | 3.706 | 34.284 | 0.63317 | 170.5025 | -62.4874 | 0 | 59.4388 | 120.5612 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0907 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7826 | 2 | -0.7 | 0 | 0 | 0 | 0 | 0 | 327 | 7826 | 120 | 322.5205 | -20.3776 | 3.706 | 94.284 | 1.6332 | 155.5025 | -56.921 | 0 | 59.4388 | 120.5612 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0015 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7827 | 3 | -0.6 | 0 | 0 | 0 | 0 | 0 | 327 | 7827 | 180 | 322.5205 | -20.3776 | 3.706 | 154.284 | 2.6332 | 140.5025 | -48.5139 | 0 | 59.4388 | 120.5612 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6074 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7828 | 4 | -0.4 | 0 | 0 | 0 | 0 | 0 | 327 | 7828 | 240 | 322.5205 | -20.3776 | 3.706 | 214.284 | 3.6332 | 125.5025 | -38.7965 | 0 | 59.4388 | 120.5612 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3026 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7829 | 5 | -0.7 | 0 | 0 | 0 | 0 | 0 | 327 | 7829 | 300 | 322.5205 | -20.3776 | 3.706 | 274.284 | 4.6332 | 110.5025 | -28.5932 | 0 | 59.4388 | 120.5612 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8339 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7830 | 6 | -1.1 | 0 | 0 | 0 | 0 | 0 | 327 | 7830 | 360 | 322.5205 | -20.3776 | 3.706 | 334.284 | 5.6332 | 95.5025 | -18.3788 | 0 | 59.4388 | 120.5612 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.3222 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7831 | 7 | -1.6 | 0 | 0 | 0 | 0 | 0 | 327 | 7831 | 420 | 322.5205 | -20.3776 | 3.706 | 394.284 | 6.6332 | 80.5025 | -8.5001 | 0 | 59.4388 | 120.5612 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.654 | 143.654 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7832 | 8 | -1.3 | 0 | 0 | 0 | 0 | 0 | 327 | 7832 | 480 | 322.5205 | -20.3776 | 3.706 | 454.284 | 7.6332 | 65.5025 | 0.71363 | 0.71363 | 58.5502 | 121.4498 | 67.8079 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 148.5248 | 148.5248 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7833 | 9 | -1 | 0.28 | 8.06 | 8.34 | 8.06 | 4.03 | 327 | 7833 | 540 | 322.5205 | -20.3776 | 3.706 | 514.284 | 8.6332 | 50.5025 | 8.8925 | 8.8925 | 47.0679 | 132.9321 | 54.1865 | 0 | 0 | 6.8796 | 6.8796 | -23.0247 | 0% | 3.111 | 0 | 0 | 129.2557 | 129.2557 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7834 | 10 | -0.6 | 35.75 | 46.03 | 81.78 | 46.03 | 23.02 | 327 | 7834 | 600 | 322.5205 | -20.3776 | 3.706 | 574.284 | 9.6332 | 35.5025 | 15.5977 | 15.5977 | 34.4168 | 145.5832 | 41.2385 | 99.981 | 99.981 | 39.2891 | 139.2701 | -0.36597 | 0% | 62.9779 | 0 | 0 | 134.0037 | 134.0037 | 0% | 12.1% | 12.1% | 80% | 9.68% | 6.0966 | 10.4906 | 6 | 36.5794 | 13.482 | 27.3% | 27.3%
11 | 327 | 23 | 7835 | 11 | -0.3 | 53.42 | 96.94 | 150.36 | 96.94 | 48.47 | 327 | 7835 | 660 | 322.5205 | -20.3776 | 3.706 | 634.284 | 10.6332 | 20.5025 | 20.3384 | 20.3384 | 20.4971 | 159.5029 | 29.9097 | 133.2272 | 133.2272 | 82.7435 | 215.9707 | 0.052978 | 5.298% | 97.662 | 5.1739 | 3.6217 | 134.1482 | 134.1482 | 2.7% | 12% | 12% | 80% | 9.603% | 9.3787 | 10.3885 | 6 | 56.2724 | 20.7402 | 41.95% | 41.95%
11 | 327 | 23 | 7836 | 12 | -0.1 | 34.36 | 142.86 | 177.22 | 142.86 | 71.43 | 327 | 7836 | 720 | 322.5205 | -20.3776 | 3.706 | 694.284 | 11.6332 | 5.5025 | 22.6606 | 22.6606 | 5.5899 | 174.4101 | 22.8026 | 82.2138 | 82.2138 | 121.9386 | 204.1525 | 0.011923 | 1.192% | 92.3177 | 1.1007 | 0.77049 | 130.2954 | 130.2954 | 0.5913% | 12.01% | 12.01% | 80% | 9.609% | 8.8704 | 10.3208 | 6 | 53.2225 | 19.6161 | 40.85% | 40.85%
11 | 327 | 23 | 7837 | 13 | 0 | 84.92 | 159.72 | 244.64 | 159.72 | 79.86 | 327 | 7837 | 780 | 322.5205 | -20.3776 | 3.706 | 754.284 | 12.6332 | -9.4975 | 22.2984 | 22.2984 | 9.6239 | 189.6239 | 24.0318 | 204.4097 | 204.4097 | 136.3295 | 340.7392 | 0.33016 | 33.02% | 154.0823 | 50.8711 | 35.6098 | 111.5363 | 111.5363 | 31.93% | 11.86% | 11.86% | 85% | 10.08% | 15.5294 | 10.287 | 6 | 93.1761 | 34.3418 | 83.54% | 83.54%
11 | 327 | 23 | 7838 | 14 | 0.6 | 109.25 | 122.14 | 231.39 | 122.14 | 61.07 | 327 | 7838 | 840 | 322.5205 | -20.3776 | 3.706 | 814.284 | 13.6332 | -24.4975 | 19.2954 | 19.2954 | 24.3203 | 204.3203 | 32.6676 | 278.3222 | 278.3222 | 104.253 | 382.5752 | 0.38584 | 38.58% | 173.0005 | 66.7501 | 46.7251 | 111.321 | 111.321 | 41.97% | 11.8% | 11.8% | 85% | 10.03% | 17.3481 | 10.0859 | 6 | 104.0887 | 38.3638 | 93.5% | 93.5%
11 | 327 | 23 | 7839 | 15 | 1.4 | 87.5 | 112.03 | 199.53 | 112.03 | 56.02 | 327 | 7839 | 900 | 322.5205 | -20.3776 | 3.706 | 874.284 | 14.6332 | -39.4975 | 13.9832 | 13.9832 | 37.9118 | 217.9118 | 44.5851 | 257.9002 | 257.9002 | 95.6236 | 353.5238 | 0.35703 | 35.7% | 159.8635 | 57.0763 | 39.9534 | 109.4114 | 109.4114 | 36.52% | 11.81% | 0% | 85% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7840 | 16 | 1.3 | 58.61 | 59.17 | 117.78 | 59.17 | 29.59 | 327 | 7840 | 960 | 322.5205 | -20.3776 | 3.706 | 934.284 | 15.6332 | -54.4975 | 6.8388 | 6.8388 | 50.2294 | 230.2294 | 57.7694 | 0 | 0 | 50.5048 | 50.5048 | -2.3295 | 0% | 22.8382 | 0 | 0 | 146.5585 | 146.5585 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7841 | 17 | 1.6 | 21.19 | 28.89 | 50.08 | 28.89 | 14.45 | 327 | 7841 | 1020 | 322.5205 | -20.3776 | 3.706 | 994.284 | 16.6332 | -69.4975 | -1.6556 | 0 | 59.4388 | 239.4388 | 68.9284 | 0 | 0 | 24.6592 | 24.6592 | -5.5841 | 0% | 11.1509 | 0 | 0 | 141.9754 | 141.9754 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7842 | 18 | 1.5 | 0 | 0 | 0 | 0 | 0 | 327 | 7842 | 1080 | 322.5205 | -20.3776 | 3.706 | 1054.284 | 17.6332 | -84.4975 | -11.0801 | 0 | 59.4388 | 239.4388 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.1771 | 135.1771 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7843 | 19 | 1.3 | 0 | 0 | 0 | 0 | 0 | 327 | 7843 | 1140 | 322.5205 | -20.3776 | 3.706 | 1114.284 | 18.6332 | -99.4975 | -21.0798 | 0 | 59.4388 | 239.4388 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.9534 | 131.9534 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7844 | 20 | 1.1 | 0 | 0 | 0 | 0 | 0 | 327 | 7844 | 1200 | 322.5205 | -20.3776 | 3.706 | 1174.284 | 19.6332 | -114.4975 | -31.3279 | 0 | 59.4388 | 239.4388 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.6605 | 127.6605 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7845 | 21 | 0.8 | 0 | 0 | 0 | 0 | 0 | 327 | 7845 | 1260 | 322.5205 | -20.3776 | 3.706 | 1234.284 | 20.6332 | -129.4975 | -41.4572 | 0 | 59.4388 | 239.4388 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.7804 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7846 | 22 | 0.9 | 0 | 0 | 0 | 0 | 0 | 327 | 7846 | 1320 | 322.5205 | -20.3776 | 3.706 | 1294.284 | 21.6332 | -144.4975 | -50.9285 | 0 | 59.4388 | 239.4388 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.5297 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7847 | 23 | 0.5 | 0 | 0 | 0 | 0 | 0 | 327 | 7847 | 1380 | 322.5205 | -20.3776 | 3.706 | 1354.284 | 22.6332 | -159.4975 | -58.7647 | 0 | 59.4388 | 239.4388 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8977 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
11 | 327 | 23 | 7848 | 24 | 0.1 | 0 | 0 | 0 | 0 | 0 | 327 | 7848 | 1440 | 322.5205 | -20.3776 | 3.706 | 1414.284 | 23.6332 | -174.4975 | -63.221 | 0 | 59.4388 | 239.4388 | 68.9284 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2656 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7849 | 1 | -0.5 | 0 | 0 | 0 | 0 | 0 | 328 | 7849 | 60 | 323.5068 | -20.5783 | 3.6073 | 34.284 | 0.63152 | 170.5272 | -62.6876 | 0 | 59.1194 | 120.8806 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8192 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7850 | 2 | -0.3 | 0 | 0 | 0 | 0 | 0 | 328 | 7850 | 120 | 323.5068 | -20.5783 | 3.6073 | 94.284 | 1.6315 | 155.5272 | -57.1043 | 0 | 59.1194 | 120.8806 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.2239 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7851 | 3 | -0.6 | 0 | 0 | 0 | 0 | 0 | 328 | 7851 | 180 | 323.5068 | -20.5783 | 3.6073 | 154.284 | 2.6315 | 140.5272 | -48.6802 | 0 | 59.1194 | 120.8806 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3906 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7852 | 4 | -1.2 | 0 | 0 | 0 | 0 | 0 | 328 | 7852 | 240 | 323.5068 | -20.5783 | 3.6073 | 214.284 | 3.6315 | 125.5272 | -38.9531 | 0 | 59.1194 | 120.8806 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.305 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7853 | 5 | -1.1 | 0 | 0 | 0 | 0 | 0 | 328 | 7853 | 300 | 323.5068 | -20.5783 | 3.6073 | 274.284 | 4.6315 | 110.5272 | -28.7471 | 0 | 59.1194 | 120.8806 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7967 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7854 | 6 | -1.2 | 0 | 0 | 0 | 0 | 0 | 328 | 7854 | 360 | 323.5068 | -20.5783 | 3.6073 | 334.284 | 5.6315 | 95.5272 | -18.535 | 0 | 59.1194 | 120.8806 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.5661 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7855 | 7 | -1 | 0 | 0 | 0 | 0 | 0 | 328 | 7855 | 420 | 323.5068 | -20.5783 | 3.6073 | 394.284 | 6.6315 | 80.5272 | -8.6625 | 0 | 59.1194 | 120.8806 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.1863 | 146.1863 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7856 | 8 | -1.5 | 0 | 0 | 0 | 0 | 0 | 328 | 7856 | 480 | 323.5068 | -20.5783 | 3.6073 | 454.284 | 7.6315 | 65.5272 | 0.54228 | 0.54228 | 58.4431 | 121.5569 | 67.8683 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 150.1792 | 150.1792 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7857 | 9 | -1.5 | 3.06 | 13.53 | 16.59 | 13.53 | 6.77 | 328 | 7857 | 540 | 323.5068 | -20.5783 | 3.6073 | 514.284 | 8.6315 | 50.5272 | 8.7106 | 8.7106 | 46.979 | 133.021 | 54.2707 | 0 | 0 | 11.5486 | 11.5486 | -13.4987 | 0% | 5.2223 | 0 | 0 | 131.2715 | 131.2715 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7858 | 10 | -1.1 | 41.19 | 44.36 | 85.55 | 44.36 | 22.18 | 328 | 7858 | 600 | 323.5068 | -20.5783 | 3.6073 | 574.284 | 9.6315 | 35.5272 | 15.4053 | 15.4053 | 34.3527 | 145.6473 | 41.3543 | 116.391 | 116.391 | 37.8636 | 154.2546 | -0.26035 | 0% | 69.7539 | 0 | 0 | 135.8405 | 135.8405 | 0% | 12.1% | 12.1% | 80% | 9.681% | 6.753 | 10.6622 | 6 | 40.5177 | 14.9336 | 29.83% | 29.83%
11 | 328 | 24 | 7859 | 11 | -0.7 | 50.92 | 101.11 | 152.03 | 101.11 | 50.56 | 328 | 7859 | 660 | 323.5068 | -20.5783 | 3.6073 | 634.284 | 10.6315 | 20.5272 | 20.1385 | 20.1385 | 20.4662 | 159.5338 | 30.0691 | 127.9944 | 127.9944 | 86.3028 | 214.2972 | 0.042492 | 4.249% | 96.9052 | 4.1177 | 2.8824 | 135.7052 | 135.7052 | 2.124% | 12.02% | 12.02% | 80% | 9.615% | 9.3175 | 10.5248 | 6 | 55.9049 | 20.6048 | 41.2% | 41.2%
11 | 328 | 24 | 7860 | 12 | -0.2 | 71.47 | 142.78 | 214.25 | 142.78 | 71.39 | 328 | 7860 | 720 | 323.5068 | -20.5783 | 3.6073 | 694.284 | 11.6315 | 5.5272 | 22.4587 | 22.4587 | 5.5994 | 174.4006 | 23.0028 | 172.2095 | 172.2095 | 121.8704 | 294.0798 | 0.25329 | 25.33% | 132.9829 | 33.6837 | 23.5786 | 112.6209 | 112.6209 | 20.94% | 11.91% | 11.91% | 80% | 9.531% | 12.6749 | 10.3546 | 6 | 76.0497 | 28.0295 | 67.53% | 67.53%
11 | 328 | 24 | 7861 | 13 | 0 | 150.08 | 119.81 | 269.89 | 119.81 | 59.91 | 328 | 7861 | 780 | 323.5068 | -20.5783 | 3.6073 | 754.284 | 12.6315 | -9.4728 | 22.102 | 22.102 | 9.5727 | 189.5727 | 24.2061 | 363.8063 | 363.8063 | 102.2642 | 466.0706 | 0.45758 | 45.76% | 210.7571 | 96.4376 | 67.5063 | 113.5211 | 113.5211 | 59.47% | 11.72% | 11.72% | 85% | 9.961% | 20.9944 | 10.287 | 6 | 125.9665 | 46.4273 | 111% | 111%
11 | 328 | 24 | 7862 | 14 | 0.9 | 125.08 | 117.58 | 242.66 | 117.58 | 58.79 | 328 | 7862 | 840 | 323.5068 | -20.5783 | 3.6073 | 814.284 | 13.6315 | -24.4728 | 19.1109 | 19.1109 | 24.2331 | 204.2331 | 32.7788 | 321.2086 | 321.2086 | 100.3608 | 421.5694 | 0.42627 | 42.63% | 190.6337 | 81.2608 | 56.8825 | 112.7196 | 112.7196 | 50.46% | 11.75% | 11.75% | 85% | 9.987% | 19.0388 | 9.9864 | 6 | 114.2328 | 42.1026 | 101.3% | 101.3%
11 | 328 | 24 | 7863 | 15 | 1 | 60.92 | 116.86 | 177.78 | 116.86 | 58.43 | 328 | 7863 | 900 | 323.5068 | -20.5783 | 3.6073 | 874.284 | 14.6315 | -39.4728 | 13.8142 | 13.8142 | 37.7978 | 217.7978 | 44.6496 | 181.5089 | 181.5089 | 99.7462 | 281.2552 | 0.23869 | 23.87% | 127.1836 | 30.358 | 21.2506 | 107.1654 | 107.1654 | 19.83% | 11.89% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7864 | 16 | 1.6 | 24.53 | 67.03 | 91.56 | 67.03 | 33.52 | 328 | 7864 | 960 | 323.5068 | -20.5783 | 3.6073 | 934.284 | 15.6315 | -54.4728 | 6.6857 | 6.6857 | 50.0966 | 230.0966 | 57.8022 | 0 | 0 | 57.2137 | 57.2137 | -1.9493 | 0% | 25.872 | 0 | 0 | 144.214 | 144.214 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7865 | 17 | 1.9 | 2.14 | 26.86 | 29 | 26.86 | 13.43 | 328 | 7865 | 1020 | 323.5068 | -20.5783 | 3.6073 | 994.284 | 16.6315 | -69.4728 | -1.7947 | 0 | 59.1194 | 239.1194 | 68.7202 | 0 | 0 | 22.9264 | 22.9264 | -6.0349 | 0% | 10.3673 | 0 | 0 | 138.9158 | 138.9158 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7866 | 18 | 1.8 | 0 | 0 | 0 | 0 | 0 | 328 | 7866 | 1080 | 323.5068 | -20.5783 | 3.6073 | 1054.284 | 17.6315 | -84.4728 | -11.2084 | 0 | 59.1194 | 239.1194 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.5587 | 134.5587 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7867 | 19 | 1.5 | 0 | 0 | 0 | 0 | 0 | 328 | 7867 | 1140 | 323.5068 | -20.5783 | 3.6073 | 1114.284 | 18.6315 | -99.4728 | -21.2014 | 0 | 59.1194 | 239.1194 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.6498 | 131.6498 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7868 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 328 | 7868 | 1200 | 323.5068 | -20.5783 | 3.6073 | 1174.284 | 19.6315 | -114.4728 | -31.4481 | 0 | 59.1194 | 239.1194 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.2951 | 127.2951 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7869 | 21 | 0.7 | 0 | 0 | 0 | 0 | 0 | 328 | 7869 | 1260 | 323.5068 | -20.5783 | 3.6073 | 1234.284 | 20.6315 | -129.4728 | -41.5831 | 0 | 59.1194 | 239.1194 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0392 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7870 | 22 | 0.1 | 0 | 0 | 0 | 0 | 0 | 328 | 7870 | 1320 | 323.5068 | -20.5783 | 3.6073 | 1294.284 | 21.6315 | -144.4728 | -51.0695 | 0 | 59.1194 | 239.1194 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7764 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7871 | 23 | 0.2 | 0 | 0 | 0 | 0 | 0 | 328 | 7871 | 1380 | 323.5068 | -20.5783 | 3.6073 | 1354.284 | 22.6315 | -159.4728 | -58.9317 | 0 | 59.1194 | 239.1194 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3334 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
11 | 328 | 24 | 7872 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 7872 | 1440 | 323.5068 | -20.5783 | 3.6073 | 1414.284 | 23.6315 | -174.4728 | -63.4161 | 0 | 59.1194 | 239.1194 | 68.7202 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3477 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7873 | 1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 329 | 7873 | 60 | 324.4932 | -20.7723 | 3.4996 | 34.284 | 0.62973 | 170.5541 | -62.8818 | 0 | 58.8102 | 121.1898 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5307 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7874 | 2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 329 | 7874 | 120 | 324.4932 | -20.7723 | 3.4996 | 94.284 | 1.6297 | 155.5541 | -57.2827 | 0 | 58.8102 | 121.1898 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2217 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7875 | 3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 329 | 7875 | 180 | 324.4932 | -20.7723 | 3.4996 | 154.284 | 2.6297 | 140.5541 | -48.8425 | 0 | 58.8102 | 121.1898 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4555 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7876 | 4 | 0.3 | 0 | 0 | 0 | 0 | 0 | 329 | 7876 | 240 | 324.4932 | -20.7723 | 3.4996 | 214.284 | 3.6297 | 125.5541 | -39.1063 | 0 | 58.8102 | 121.1898 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9127 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7877 | 5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 329 | 7877 | 300 | 324.4932 | -20.7723 | 3.4996 | 274.284 | 4.6297 | 110.5541 | -28.8977 | 0 | 58.8102 | 121.1898 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2258 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7878 | 6 | -0.1 | 0 | 0 | 0 | 0 | 0 | 329 | 7878 | 360 | 324.4932 | -20.7723 | 3.4996 | 334.284 | 5.6297 | 95.5541 | -18.6878 | 0 | 58.8102 | 121.1898 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.4843 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7879 | 7 | -0.2 | 0 | 0 | 0 | 0 | 0 | 329 | 7879 | 420 | 324.4932 | -20.7723 | 3.4996 | 394.284 | 6.6297 | 80.5541 | -8.8213 | 0 | 58.8102 | 121.1898 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.1193 | 134.1193 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7880 | 8 | -0.2 | 0 | 0 | 0 | 0 | 0 | 329 | 7880 | 480 | 324.4932 | -20.7723 | 3.4996 | 454.284 | 7.6297 | 65.5541 | 0.37494 | 0.37494 | 58.3419 | 121.6581 | 67.9297 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.6539 | 136.6539 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7881 | 9 | -0.1 | 0.28 | 9.25 | 9.53 | 9.25 | 4.63 | 329 | 7881 | 540 | 324.4932 | -20.7723 | 3.4996 | 514.284 | 8.6297 | 50.5541 | 8.5332 | 8.5332 | 46.8957 | 133.1043 | 54.3551 | 0 | 0 | 7.8954 | 7.8954 | -19.6769 | 0% | 3.5703 | 0 | 0 | 116.7074 | 116.7074 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7882 | 10 | 1.2 | 12.5 | 62.03 | 74.53 | 62.03 | 31.02 | 329 | 7882 | 600 | 324.4932 | -20.7723 | 3.4996 | 574.284 | 9.6297 | 35.5541 | 15.2183 | 15.2183 | 34.2935 | 145.7065 | 41.4691 | 35.6819 | 35.6819 | 52.9459 | 88.6278 | -0.98443 | 0% | 40.0775 | 0 | 0 | 121.7068 | 121.7068 | 0% | 12.09% | 12.09% | 80% | 9.67% | 3.8755 | 9.8874 | 6 | 23.2531 | 8.5704 | 19.11% | 19.11%
11 | 329 | 25 | 7883 | 11 | 1.8 | 25.92 | 113.25 | 139.17 | 113.25 | 56.63 | 329 | 7883 | 660 | 324.4932 | -20.7723 | 3.4996 | 634.284 | 10.6297 | 20.5541 | 19.9446 | 19.9446 | 20.4393 | 159.5607 | 30.2255 | 65.6566 | 65.6566 | 96.6649 | 162.3215 | -0.16343 | 0% | 73.4018 | 0 | 0 | 123.6598 | 123.6598 | 0% | 11.99% | 11.99% | 80% | 9.592% | 7.0409 | 9.6914 | 6 | 42.2453 | 15.5703 | 34.16% | 34.16%
11 | 329 | 25 | 7884 | 12 | 2.9 | 33.97 | 150.92 | 184.89 | 150.92 | 75.46 | 329 | 7884 | 720 | 324.4932 | -20.7723 | 3.4996 | 694.284 | 11.6297 | 5.5541 | 22.2635 | 22.2635 | 5.6116 | 174.3884 | 23.197 | 82.4135 | 82.4135 | 128.8183 | 211.2318 | 0.073268 | 7.327% | 95.519 | 6.9985 | 4.899 | 124.3222 | 124.3222 | 3.941% | 11.91% | 11.91% | 80% | 9.525% | 9.0978 | 9.3386 | 6 | 54.5868 | 20.119 | 43.91% | 43.91%
11 | 329 | 25 | 7885 | 13 | 4.2 | 14.25 | 131.31 | 145.56 | 131.31 | 65.66 | 329 | 7885 | 780 | 324.4932 | -20.7723 | 3.4996 | 754.284 | 12.6297 | -9.4459 | 21.9125 | 21.9125 | 9.5203 | 189.5203 | 24.3739 | 34.7809 | 34.7809 | 112.0801 | 146.861 | -0.22558 | 0% | 66.4106 | 0 | 0 | 123.6805 | 123.6805 | 0% | 11.92% | 11.92% | 80% | 9.536% | 6.3327 | 8.9325 | 6 | 37.9961 | 14.0042 | 30.72% | 30.72%
11 | 329 | 25 | 7886 | 14 | 5.9 | 1.58 | 111.86 | 113.44 | 111.86 | 55.93 | 329 | 7886 | 840 | 324.4932 | -20.7723 | 3.4996 | 814.284 | 13.6297 | -24.4459 | 18.9335 | 18.9335 | 24.1462 | 204.1462 | 32.8848 | 4.0892 | 4.0892 | 95.4785 | 99.5677 | -0.67362 | 0% | 45.0245 | 0 | 0 | 124.1401 | 124.1401 | 0% | 11.9% | 11.9% | 80% | 9.516% | 4.2846 | 8.4194 | 6 | 25.7076 | 9.475 | 20.71% | 20.71%
11 | 329 | 25 | 7887 | 15 | 6.2 | 1.67 | 88.42 | 90.09 | 88.42 | 44.21 | 329 | 7887 | 900 | 324.4932 | -20.7723 | 3.4996 | 874.284 | 14.6297 | -39.4459 | 13.6521 | 13.6521 | 37.6851 | 217.6851 | 44.71 | 5.0284 | 5.0284 | 75.4712 | 80.4996 | -1.0147 | 0% | 36.4019 | 0 | 0 | 143.1319 | 143.1319 | 0% | 11.9% | 0% | 80% | 0% | 0 | 8.3309 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7888 | 16 | 6.7 | 2.22 | 67.78 | 70 | 67.78 | 33.89 | 329 | 7888 | 960 | 324.4932 | -20.7723 | 3.4996 | 934.284 | 15.6297 | -54.4459 | 6.5393 | 6.5393 | 49.9661 | 229.9661 | 57.8317 | 0 | 0 | 57.8538 | 57.8538 | -1.706 | 0% | 26.1615 | 0 | 0 | 142.0485 | 142.0485 | 0% | 11.89% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7889 | 17 | 6.5 | 0.19 | 15.83 | 16.02 | 15.83 | 7.92 | 329 | 7889 | 1020 | 324.4932 | -20.7723 | 3.4996 | 994.284 | 16.6297 | -69.4459 | -1.9273 | 0 | 58.8102 | 238.8102 | 68.519 | 0 | 0 | 13.5118 | 13.5118 | -9.9786 | 0% | 6.11 | 0 | 0 | 138.0832 | 138.0832 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7890 | 18 | 5.7 | 0 | 0 | 0 | 0 | 0 | 329 | 7890 | 1080 | 324.4932 | -20.7723 | 3.4996 | 1054.284 | 17.6297 | -84.4459 | -11.3304 | 0 | 58.8102 | 238.8102 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.8635 | 134.8635 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7891 | 19 | 4.9 | 0 | 0 | 0 | 0 | 0 | 329 | 7891 | 1140 | 324.4932 | -20.7723 | 3.4996 | 1114.284 | 18.6297 | -99.4459 | -21.3168 | 0 | 58.8102 | 238.8102 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.3057 | 132.3057 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7892 | 20 | 4.9 | 0 | 0 | 0 | 0 | 0 | 329 | 7892 | 1200 | 324.4932 | -20.7723 | 3.4996 | 1174.284 | 19.6297 | -114.4459 | -31.562 | 0 | 58.8102 | 238.8102 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.2564 | 130.2564 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7893 | 21 | 5.1 | 0 | 0 | 0 | 0 | 0 | 329 | 7893 | 1260 | 324.4932 | -20.7723 | 3.4996 | 1234.284 | 20.6297 | -129.4459 | -41.7023 | 0 | 58.8102 | 238.8102 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9273 | 0 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7894 | 22 | 4.9 | 0 | 0 | 0 | 0 | 0 | 329 | 7894 | 1320 | 324.4932 | -20.7723 | 3.4996 | 1294.284 | 21.6297 | -144.4459 | -51.2034 | 0 | 58.8102 | 238.8102 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6853 | 0 | 0% | 12.02% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7895 | 23 | 5.4 | 0 | 0 | 0 | 0 | 0 | 329 | 7895 | 1380 | 324.4932 | -20.7723 | 3.4996 | 1354.284 | 22.6297 | -159.4459 | -59.0915 | 0 | 58.8102 | 238.8102 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7667 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
11 | 329 | 25 | 7896 | 24 | 5.5 | 0 | 0 | 0 | 0 | 0 | 329 | 7896 | 1440 | 324.4932 | -20.7723 | 3.4996 | 1414.284 | 23.6297 | -174.4459 | -63.6042 | 0 | 58.8102 | 238.8102 | 68.519 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.4577 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7897 | 1 | 5.3 | 0 | 0 | 0 | 0 | 0 | 330 | 7897 | 60 | 325.4795 | -20.9594 | 3.3831 | 34.284 | 0.62778 | 170.5832 | -63.0698 | 0 | 58.5113 | 121.4887 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0181 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7898 | 2 | 5.3 | 0 | 0 | 0 | 0 | 0 | 330 | 7898 | 120 | 325.4795 | -20.9594 | 3.3831 | 94.284 | 1.6278 | 155.5832 | -57.4562 | 0 | 58.5113 | 121.4887 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9458 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7899 | 3 | 4.3 | 0 | 0 | 0 | 0 | 0 | 330 | 7899 | 180 | 325.4795 | -20.9594 | 3.3831 | 154.284 | 2.6278 | 140.5832 | -49.0007 | 0 | 58.5113 | 121.4887 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3975 | 0 | 0% | 12.04% | 0% | 80% | 0% | 0 | 8.9018 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7900 | 4 | 3.1 | 0 | 0 | 0 | 0 | 0 | 330 | 7900 | 240 | 325.4795 | -20.9594 | 3.3831 | 214.284 | 3.6278 | 125.5832 | -39.256 | 0 | 58.5113 | 121.4887 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2263 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7901 | 5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 330 | 7901 | 300 | 325.4795 | -20.9594 | 3.3831 | 274.284 | 4.6278 | 110.5832 | -29.0449 | 0 | 58.5113 | 121.4887 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2376 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7902 | 6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 330 | 7902 | 360 | 325.4795 | -20.9594 | 3.3831 | 334.284 | 5.6278 | 95.5832 | -18.8373 | 0 | 58.5113 | 121.4887 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6603 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7903 | 7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 330 | 7903 | 420 | 325.4795 | -20.9594 | 3.3831 | 394.284 | 6.6278 | 80.5832 | -8.9764 | 0 | 58.5113 | 121.4887 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.8759 | 129.8759 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7904 | 8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 330 | 7904 | 480 | 325.4795 | -20.9594 | 3.3831 | 454.284 | 7.6278 | 65.5832 | 0.21169 | 0.21169 | 58.2466 | 121.7534 | 67.992 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.3949 | 131.3949 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7905 | 9 | 1 | 0.08 | 6.67 | 6.75 | 6.67 | 3.34 | 330 | 7905 | 540 | 325.4795 | -20.9594 | 3.3831 | 514.284 | 8.6278 | 50.5832 | 8.3606 | 8.3606 | 46.8178 | 133.1822 | 54.4396 | 0 | 0 | 5.6932 | 5.6932 | -27.1232 | 0% | 2.5745 | 0 | 0 | 109.5847 | 109.5847 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7906 | 10 | 2.4 | 0.19 | 37.58 | 37.77 | 37.58 | 18.79 | 330 | 7906 | 600 | 325.4795 | -20.9594 | 3.3831 | 574.284 | 9.6278 | 35.5832 | 15.0366 | 15.0366 | 34.2392 | 145.7608 | 41.5829 | 0.5478 | 0.5478 | 32.0765 | 32.6243 | -3.9645 | 0% | 14.7527 | 0 | 0 | 113.8682 | 113.8682 | 0% | 12.09% | 12.09% | 80% | 9.676% | 1.4275 | 9.4979 | 6 | 8.5647 | 3.1567 | 7.522% | 7.522%
11 | 330 | 26 | 7907 | 11 | 3.1 | 1.58 | 84.81 | 86.39 | 84.81 | 42.41 | 330 | 7907 | 660 | 325.4795 | -20.9594 | 3.3831 | 634.284 | 10.6278 | 20.5832 | 19.7568 | 19.7568 | 20.4164 | 159.5836 | 30.3788 | 4.0324 | 4.0324 | 72.3899 | 76.4223 | -1.2094 | 0% | 34.5582 | 0 | 0 | 116.6361 | 116.6361 | 0% | 12.02% | 12.02% | 80% | 9.62% | 3.3244 | 9.2753 | 6 | 19.9462 | 7.3516 | 17.1% | 17.1%
11 | 330 | 26 | 7908 | 12 | 7.7 | 6.11 | 109.81 | 115.92 | 109.81 | 54.91 | 330 | 7908 | 720 | 325.4795 | -20.9594 | 3.3831 | 694.284 | 11.6278 | 5.5832 | 22.0749 | 22.0749 | 5.6264 | 174.3736 | 23.3851 | 14.9224 | 14.9224 | 93.7287 | 108.6511 | -0.5107 | 0% | 49.132 | 0 | 0 | 123.6705 | 123.6705 | 0% | 11.82% | 11.82% | 80% | 9.456% | 4.6458 | 7.8981 | 6 | 27.8748 | 10.2738 | 22.54% | 22.54%
11 | 330 | 26 | 7909 | 13 | 9.7 | 10.97 | 128.61 | 139.58 | 128.61 | 64.31 | 330 | 7909 | 780 | 325.4795 | -20.9594 | 3.3831 | 754.284 | 12.6278 | -9.4168 | 21.7301 | 21.7301 | 9.4669 | 189.4669 | 24.5349 | 26.9545 | 26.9545 | 109.7755 | 136.73 | -0.2063 | 0% | 61.8293 | 0 | 0 | 127.6368 | 127.6368 | 0% | 11.73% | 11.73% | 80% | 9.382% | 5.8009 | 7.3455 | 6 | 34.8057 | 12.8283 | 27.27% | 27.27%
11 | 330 | 26 | 7910 | 14 | 13.5 | 65.69 | 129.44 | 195.13 | 129.44 | 64.72 | 330 | 7910 | 840 | 325.4795 | -20.9594 | 3.3831 | 814.284 | 13.6278 | -24.4168 | 18.7631 | 18.7631 | 24.0595 | 204.0595 | 32.9857 | 171.3047 | 171.3047 | 110.484 | 281.7887 | 0.34498 | 34.5% | 127.4248 | 43.9588 | 30.7712 | 135.6442 | 135.6442 | 22.69% | 11.54% | 11.54% | 80% | 9.23% | 11.7611 | 6.3727 | 6 | 70.5664 | 26.0086 | 52.02% | 52.02%
11 | 330 | 26 | 7911 | 15 | 13.5 | 24.58 | 116.94 | 141.52 | 116.94 | 58.47 | 330 | 7911 | 900 | 325.4795 | -20.9594 | 3.3831 | 874.284 | 14.6278 | -39.4168 | 13.4969 | 13.4969 | 37.574 | 217.574 | 44.7662 | 74.7726 | 74.7726 | 99.8145 | 174.5872 | 0.063126 | 6.313% | 78.9483 | 4.9837 | 3.4886 | 152.9974 | 152.9974 | 2.28% | 11.58% | 0% | 80% | 0% | 0 | 6.3727 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7912 | 16 | 14.4 | 11.47 | 57.69 | 69.16 | 57.69 | 28.85 | 330 | 7912 | 960 | 325.4795 | -20.9594 | 3.3831 | 934.284 | 15.6278 | -54.4168 | 6.3996 | 6.3996 | 49.8379 | 229.8379 | 57.8577 | 0 | 0 | 49.2415 | 49.2415 | -1.7811 | 0% | 22.267 | 0 | 0 | 150.3383 | 150.3383 | 0% | 11.58% | 0% | 80% | 0% | 0 | 6.1571 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7913 | 17 | 13.2 | 0.28 | 25.08 | 25.36 | 25.08 | 12.54 | 330 | 7913 | 1020 | 325.4795 | -20.9594 | 3.3831 | 994.284 | 16.6278 | -69.4168 | -2.0533 | 0 | 58.5113 | 238.5113 | 68.3249 | 0 | 0 | 21.4071 | 21.4071 | -5.2703 | 0% | 9.6803 | 0 | 0 | 145.1489 | 145.1489 | 0% | 11.64% | 0% | 80% | 0% | 0 | 6.4458 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7914 | 18 | 11.9 | 0 | 0 | 0 | 0 | 0 | 330 | 7914 | 1080 | 325.4795 | -20.9594 | 3.3831 | 1054.284 | 17.6278 | -84.4168 | -11.4459 | 0 | 58.5113 | 238.5113 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.8171 | 140.8171 | 0% | 11.71% | 0% | 80% | 0% | 0 | 6.77 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7915 | 19 | 11.4 | 0 | 0 | 0 | 0 | 0 | 330 | 7915 | 1140 | 325.4795 | -20.9594 | 3.3831 | 1114.284 | 18.6278 | -99.4168 | -21.4258 | 0 | 58.5113 | 238.5113 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.7118 | 138.7118 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8978 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7916 | 20 | 14.1 | 0 | 0 | 0 | 0 | 0 | 330 | 7916 | 1200 | 325.4795 | -20.9594 | 3.3831 | 1174.284 | 19.6278 | -114.4168 | -31.6695 | 0 | 58.5113 | 238.5113 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.0439 | 141.0439 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7917 | 21 | 11.3 | 0 | 0 | 0 | 0 | 0 | 330 | 7917 | 1260 | 325.4795 | -20.9594 | 3.3831 | 1234.284 | 20.6278 | -129.4168 | -41.8149 | 0 | 58.5113 | 238.5113 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.6762 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.9236 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7918 | 22 | 10.5 | 0 | 0 | 0 | 0 | 0 | 330 | 7918 | 1320 | 325.4795 | -20.9594 | 3.3831 | 1294.284 | 21.6278 | -144.4168 | -51.3303 | 0 | 58.5113 | 238.5113 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3102 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7919 | 23 | 10.9 | 0 | 0 | 0 | 0 | 0 | 330 | 7919 | 1380 | 325.4795 | -20.9594 | 3.3831 | 1354.284 | 22.6278 | -159.4168 | -59.2439 | 0 | 58.5113 | 238.5113 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.6283 | 0 | 0% | 11.75% | 0% | 80% | 0% | 0 | 7.0274 | 6 | 0 | 0 | 0% | 0%
11 | 330 | 26 | 7920 | 24 | 10.5 | 0 | 0 | 0 | 0 | 0 | 330 | 7920 | 1440 | 325.4795 | -20.9594 | 3.3831 | 1414.284 | 23.6278 | -174.4168 | -63.7851 | 0 | 58.5113 | 238.5113 | 68.3249 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.1656 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1323 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7921 | 1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 331 | 7921 | 60 | 326.4658 | -21.1396 | 3.258 | 34.284 | 0.6257 | 170.6145 | -63.2517 | 0 | 58.2229 | 121.7771 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.8699 | 0 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.2117 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7922 | 2 | 9.8 | 0 | 0 | 0 | 0 | 0 | 331 | 7922 | 120 | 326.4658 | -21.1396 | 3.258 | 94.284 | 1.6257 | 155.6145 | -57.6247 | 0 | 58.2229 | 121.7771 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.2903 | 0 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.3186 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7923 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 331 | 7923 | 180 | 326.4658 | -21.1396 | 3.258 | 154.284 | 2.6257 | 140.6145 | -49.1549 | 0 | 58.2229 | 121.7771 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5584 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7924 | 4 | 9.3 | 0 | 0 | 0 | 0 | 0 | 331 | 7924 | 240 | 326.4658 | -21.1396 | 3.258 | 214.284 | 3.6257 | 125.6145 | -39.4021 | 0 | 58.2229 | 121.7771 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.8632 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7925 | 5 | -0.7 | 0 | 0 | 0 | 0 | 0 | 331 | 7925 | 300 | 326.4658 | -21.1396 | 3.258 | 274.284 | 4.6257 | 110.6145 | -29.1888 | 0 | 58.2229 | 121.7771 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.137 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7926 | 6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 331 | 7926 | 360 | 326.4658 | -21.1396 | 3.258 | 334.284 | 5.6257 | 95.6145 | -18.9833 | 0 | 58.2229 | 121.7771 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -3.0694 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7927 | 7 | 8.8 | 0 | 0 | 0 | 0 | 0 | 331 | 7927 | 420 | 326.4658 | -21.1396 | 3.258 | 394.284 | 6.6257 | 80.6145 | -9.1278 | 0 | 58.2229 | 121.7771 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.2796 | 149.2796 | 0% | 11.84% | 0% | 80% | 0% | 0 | 7.5907 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7928 | 8 | 9.2 | 0 | 0 | 0 | 0 | 0 | 331 | 7928 | 480 | 326.4658 | -21.1396 | 3.258 | 454.284 | 7.6257 | 65.6145 | 0.052621 | 0.052621 | 58.157 | 121.843 | 68.0551 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 154.0391 | 154.0391 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.481 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7929 | 9 | 8 | 1.67 | 20.14 | 21.81 | 20.14 | 10.07 | 331 | 7929 | 540 | 326.4658 | -21.1396 | 3.258 | 514.284 | 8.6257 | 50.6145 | 8.1927 | 8.1927 | 46.7453 | 133.2547 | 54.5242 | 0 | 0 | 17.1906 | 17.1906 | -7.4642 | 0% | 7.7736 | 0 | 0 | 133.4119 | 133.4119 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7930 | 10 | 8 | 25.08 | 55.28 | 80.36 | 55.28 | 27.64 | 331 | 7930 | 600 | 326.4658 | -21.1396 | 3.258 | 574.284 | 9.6257 | 35.6145 | 14.8605 | 14.8605 | 34.1898 | 145.8102 | 41.6955 | 73.0195 | 73.0195 | 47.1844 | 120.2039 | -0.37844 | 0% | 54.3562 | 0 | 0 | 137.3083 | 137.3083 | 0% | 11.8% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7931 | 11 | 10.6 | 43.14 | 93.14 | 136.28 | 93.14 | 46.57 | 331 | 7931 | 660 | 326.4658 | -21.1396 | 3.258 | 634.284 | 10.6257 | 20.6145 | 19.5751 | 19.5751 | 20.3974 | 159.6026 | 30.5288 | 110.9106 | 110.9106 | 79.5 | 190.4105 | 0.089549 | 8.955% | 86.1036 | 7.7105 | 5.3974 | 141.4115 | 141.4115 | 3.817% | 11.67% | 11.67% | 80% | 9.334% | 8.0367 | 7.1059 | 6 | 48.2201 | 17.7724 | 34.1% | 34.1%
11 | 331 | 27 | 7932 | 12 | 12.4 | 43.14 | 153.42 | 196.56 | 153.42 | 76.71 | 331 | 7932 | 720 | 326.4658 | -21.1396 | 3.258 | 694.284 | 11.6257 | 5.6145 | 21.8931 | 21.8931 | 5.6438 | 174.3562 | 23.5669 | 106.0456 | 106.0456 | 130.9522 | 236.9978 | 0.24757 | 24.76% | 107.1704 | 26.5324 | 18.5727 | 142.7113 | 142.7113 | 13.01% | 11.59% | 11.59% | 80% | 9.27% | 9.9346 | 6.6439 | 6 | 59.6073 | 21.9694 | 41.77% | 41.77%
11 | 331 | 27 | 7933 | 13 | 14.3 | 111.75 | 142.78 | 254.53 | 142.78 | 71.39 | 331 | 7933 | 780 | 326.4658 | -21.1396 | 3.258 | 754.284 | 12.6257 | -9.3855 | 21.5547 | 21.5547 | 9.4124 | 189.4124 | 24.6893 | 276.3674 | 276.3674 | 121.8704 | 398.2378 | 0.48379 | 48.38% | 180.0831 | 87.1219 | 60.9853 | 126.452 | 126.452 | 48.23% | 11.48% | 11.48% | 85% | 9.756% | 17.5694 | 6.1808 | 6 | 105.4163 | 38.8531 | 83.36% | 83.36%
11 | 331 | 27 | 7934 | 14 | 14.1 | 133.89 | 129.92 | 263.81 | 129.92 | 64.96 | 331 | 7934 | 840 | 326.4658 | -21.1396 | 3.258 | 814.284 | 13.6257 | -24.3855 | 18.5999 | 18.5999 | 23.9733 | 203.9733 | 33.0812 | 351.7282 | 351.7282 | 110.8937 | 462.6219 | 0.52737 | 52.74% | 209.1976 | 110.3238 | 77.2267 | 126.2771 | 126.2771 | 61.16% | 11.46% | 11.46% | 85% | 9.742% | 20.3806 | 6.2283 | 6 | 122.2834 | 45.0698 | 96.84% | 96.84%
11 | 331 | 27 | 7935 | 15 | 14.7 | 84.36 | 104.25 | 188.61 | 104.25 | 52.13 | 331 | 7935 | 900 | 326.4658 | -21.1396 | 3.258 | 874.284 | 14.6257 | -39.3855 | 13.3488 | 13.3488 | 37.4643 | 217.4643 | 44.8183 | 259.1858 | 259.1858 | 88.9829 | 348.1687 | 0.44035 | 44.04% | 157.4419 | 69.3298 | 48.5308 | 121.8924 | 121.8924 | 39.81% | 11.48% | 0% | 85% | 0% | 0 | 6.0865 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7936 | 16 | 13.7 | 61.67 | 64.58 | 126.25 | 64.58 | 32.29 | 331 | 7936 | 960 | 326.4658 | -21.1396 | 3.258 | 934.284 | 15.6257 | -54.3855 | 6.2667 | 6.2667 | 49.712 | 229.712 | 57.8803 | 0 | 0 | 55.1225 | 55.1225 | -1.5342 | 0% | 24.9264 | 0 | 0 | 158.7927 | 158.7927 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7937 | 17 | 12.3 | 7.22 | 20.56 | 27.78 | 20.56 | 10.28 | 331 | 7937 | 1020 | 326.4658 | -21.1396 | 3.258 | 994.284 | 16.6257 | -69.3855 | -2.1728 | 0 | 58.2229 | 238.2229 | 68.1379 | 0 | 0 | 17.5491 | 17.5491 | -6.7236 | 0% | 7.9357 | 0 | 0 | 149.0087 | 149.0087 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.669 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7938 | 18 | 12.6 | 0 | 0 | 0 | 0 | 0 | 331 | 7938 | 1080 | 326.4658 | -21.1396 | 3.258 | 1054.284 | 17.6257 | -84.3855 | -11.5551 | 0 | 58.2229 | 238.2229 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.8573 | 144.8573 | 0% | 11.68% | 0% | 80% | 0% | 0 | 6.5939 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7939 | 19 | 13.3 | 0 | 0 | 0 | 0 | 0 | 331 | 7939 | 1140 | 326.4658 | -21.1396 | 3.258 | 1114.284 | 18.6257 | -99.3855 | -21.5285 | 0 | 58.2229 | 238.2229 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.9868 | 142.9868 | 0% | 11.65% | 0% | 80% | 0% | 0 | 6.4214 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7940 | 20 | 14.1 | 0 | 0 | 0 | 0 | 0 | 331 | 7940 | 1200 | 326.4658 | -21.1396 | 3.258 | 1174.284 | 19.6257 | -114.3855 | -31.7707 | 0 | 58.2229 | 238.2229 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.3622 | 140.3622 | 0% | 11.61% | 0% | 80% | 0% | 0 | 6.2283 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7941 | 21 | 13.7 | 0 | 0 | 0 | 0 | 0 | 331 | 7941 | 1260 | 326.4658 | -21.1396 | 3.258 | 1234.284 | 20.6257 | -129.3855 | -41.921 | 0 | 58.2229 | 238.2229 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.2169 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7942 | 22 | 13.7 | 0 | 0 | 0 | 0 | 0 | 331 | 7942 | 1320 | 326.4658 | -21.1396 | 3.258 | 1294.284 | 21.6257 | -144.3855 | -51.4503 | 0 | 58.2229 | 238.2229 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.1033 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7943 | 23 | 13.7 | 0 | 0 | 0 | 0 | 0 | 331 | 7943 | 1380 | 326.4658 | -21.1396 | 3.258 | 1354.284 | 22.6257 | -159.3855 | -59.389 | 0 | 58.2229 | 238.2229 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.9142 | 0 | 0% | 11.63% | 0% | 80% | 0% | 0 | 6.3243 | 6 | 0 | 0 | 0% | 0%
11 | 331 | 27 | 7944 | 24 | 11.5 | 0 | 0 | 0 | 0 | 0 | 331 | 7944 | 1440 | 326.4658 | -21.1396 | 3.258 | 1414.284 | 23.6257 | -174.3855 | -63.9588 | 0 | 58.2229 | 238.2229 | 68.1379 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0778 | 0 | 0% | 11.73% | 0% | 80% | 0% | 0 | 6.8721 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7945 | 1 | 10.6 | 0 | 0 | 0 | 0 | 0 | 332 | 7945 | 60 | 327.4521 | -21.3128 | 3.1245 | 34.284 | 0.62348 | 170.6479 | -63.4272 | 0 | 57.9451 | 122.0549 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.0288 | 0 | 0% | 11.77% | 0% | 80% | 0% | 0 | 7.1059 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7946 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 332 | 7946 | 120 | 327.4521 | -21.3128 | 3.1245 | 94.284 | 1.6235 | 155.6479 | -57.7882 | 0 | 57.9451 | 122.0549 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.5858 | 0 | 0% | 11.79% | 0% | 80% | 0% | 0 | 7.265 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7947 | 3 | 9.3 | 0 | 0 | 0 | 0 | 0 | 332 | 7947 | 180 | 327.4521 | -21.3128 | 3.1245 | 154.284 | 2.6235 | 140.6479 | -49.305 | 0 | 57.9451 | 122.0549 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.2953 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7948 | 4 | 7.7 | 0 | 0 | 0 | 0 | 0 | 332 | 7948 | 240 | 327.4521 | -21.3128 | 3.1245 | 214.284 | 3.6235 | 125.6479 | -39.5445 | 0 | 57.9451 | 122.0549 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.7337 | 0 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.8981 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7949 | 5 | 7.2 | 0 | 0 | 0 | 0 | 0 | 332 | 7949 | 300 | 327.4521 | -21.3128 | 3.1245 | 274.284 | 4.6235 | 110.6479 | -29.3291 | 0 | 57.9451 | 122.0549 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -5.4207 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7950 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 7950 | 360 | 327.4521 | -21.3128 | 3.1245 | 334.284 | 5.6235 | 95.6479 | -19.1257 | 0 | 57.9451 | 122.0549 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 3.0267 | 3.0267 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.8134 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7951 | 7 | 6.7 | 0 | 0 | 0 | 0 | 0 | 332 | 7951 | 420 | 327.4521 | -21.3128 | 3.1245 | 394.284 | 6.6235 | 80.6479 | -9.2754 | 0 | 57.9451 | 122.0549 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 160.3071 | 160.3071 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7952 | 8 | 7.1 | 0 | 0 | 0 | 0 | 0 | 332 | 7952 | 480 | 327.4521 | -21.3128 | 3.1245 | 454.284 | 7.6235 | 65.6479 | -0.10218 | 0 | 57.9451 | 122.0549 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 167.2221 | 167.2221 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7953 | 9 | 4 | 1.67 | 8.89 | 10.56 | 8.89 | 4.45 | 332 | 7953 | 540 | 327.4521 | -21.3128 | 3.1245 | 514.284 | 8.6235 | 50.6479 | 8.0297 | 8.0297 | 46.6783 | 133.3217 | 54.6086 | 0 | 0 | 7.5881 | 7.5881 | -19.1864 | 0% | 3.4313 | 0 | 0 | 143.4353 | 143.4353 | 0% | 12.05% | 0% | 80% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7954 | 10 | 9.3 | 60.19 | 37.58 | 97.77 | 37.58 | 18.79 | 332 | 7954 | 600 | 327.4521 | -21.3128 | 3.1245 | 574.284 | 9.6235 | 35.6479 | 14.6898 | 14.6898 | 34.1451 | 145.8549 | 41.8067 | 176.9242 | 176.9242 | 32.0765 | 209.0007 | 0.13857 | 13.86% | 94.5101 | 13.0963 | 9.1674 | 156.9736 | 156.9736 | 5.84% | 11.7% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7955 | 11 | 10.6 | 130.28 | 61.67 | 191.95 | 61.67 | 30.84 | 332 | 7955 | 660 | 327.4521 | -21.3128 | 3.1245 | 634.284 | 10.6235 | 20.6479 | 19.3997 | 19.3997 | 20.3822 | 159.6178 | 30.6754 | 337.3424 | 337.3424 | 52.6386 | 389.981 | 0.45517 | 45.52% | 176.3494 | 80.2681 | 56.1877 | 158.3111 | 158.3111 | 35.49% | 11.56% | 11.56% | 85% | 9.829% | 17.3341 | 7.1059 | 6 | 104.0044 | 38.3327 | 65.7% | 65.7%
11 | 332 | 28 | 7956 | 12 | 13.9 | 177.86 | 85.83 | 263.69 | 85.83 | 42.92 | 332 | 7956 | 720 | 327.4521 | -21.3128 | 3.1245 | 694.284 | 11.6235 | 5.6479 | 21.7181 | 21.7181 | 5.6637 | 174.3363 | 23.7425 | 439.971 | 439.971 | 73.2605 | 513.2314 | 0.55376 | 55.38% | 232.0833 | 128.5176 | 89.9623 | 137.2995 | 137.2995 | 65.52% | 11.45% | 11.45% | 90% | 10.3% | 23.9124 | 6.2762 | 6 | 143.4747 | 52.8802 | 104.5% | 104.5%
11 | 332 | 28 | 7957 | 13 | 15.9 | 189.53 | 125.47 | 315 | 125.47 | 62.74 | 332 | 7957 | 780 | 327.4521 | -21.3128 | 3.1245 | 754.284 | 12.6235 | -9.3521 | 21.3865 | 21.3865 | 9.3569 | 189.3569 | 24.8368 | 471.6764 | 471.6764 | 107.0953 | 578.7717 | 0.58994 | 58.99% | 261.7206 | 154.3984 | 108.0789 | 140.7499 | 140.7499 | 76.79% | 11.4% | 11.4% | 90% | 10.26% | 26.857 | 5.8104 | 5.8104 | 156.0486 | 59.3918 | 110.9% | 110.9%
11 | 332 | 28 | 7958 | 14 | 16.9 | 154.64 | 108.81 | 263.45 | 108.81 | 54.41 | 332 | 7958 | 840 | 327.4521 | -21.3128 | 3.1245 | 814.284 | 13.6235 | -24.3521 | 18.4438 | 18.4438 | 23.8876 | 203.8876 | 33.1714 | 409.1349 | 409.1349 | 92.8751 | 502.0101 | 0.56168 | 56.17% | 227.009 | 127.5073 | 89.2551 | 139.3104 | 139.3104 | 64.07% | 11.4% | 11.4% | 90% | 10.26% | 23.2969 | 5.588 | 5.588 | 130.1818 | 51.5189 | 93.45% | 93.45%
11 | 332 | 28 | 7959 | 15 | 15.8 | 122.31 | 86.86 | 209.17 | 86.86 | 43.43 | 332 | 7959 | 900 | 327.4521 | -21.3128 | 3.1245 | 874.284 | 14.6235 | -39.3521 | 13.2076 | 13.2076 | 37.3563 | 217.3563 | 44.8662 | 379.4104 | 379.4104 | 74.1396 | 453.55 | 0.53034 | 53.03% | 205.0953 | 108.7696 | 76.1387 | 132.5502 | 132.5502 | 57.44% | 11.43% | 0% | 85% | 0% | 0 | 5.833 | 5.833 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7960 | 16 | 15 | 102.64 | 47.36 | 150 | 47.36 | 23.68 | 332 | 7960 | 960 | 327.4521 | -21.3128 | 3.1245 | 934.284 | 15.6235 | -54.3521 | 6.1406 | 6.1406 | 49.5885 | 229.5885 | 57.8995 | 0 | 0 | 40.4243 | 40.4243 | -2.3112 | 0% | 18.2799 | 0 | 0 | 169.7547 | 169.7547 | 0% | 11.56% | 0% | 80% | 0% | 0 | 6.0165 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7961 | 17 | 14.9 | 33.19 | 19.31 | 52.5 | 19.31 | 9.66 | 332 | 7961 | 1020 | 327.4521 | -21.3128 | 3.1245 | 994.284 | 16.6235 | -69.3521 | -2.2858 | 0 | 57.9451 | 237.9451 | 67.9581 | 0 | 0 | 16.4821 | 16.4821 | -6.8502 | 0% | 7.4532 | 0 | 0 | 162.1325 | 162.1325 | 0% | 11.57% | 0% | 80% | 0% | 0 | 6.0398 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7962 | 18 | 12.8 | 0 | 0 | 0 | 0 | 0 | 332 | 7962 | 1080 | 327.4521 | -21.3128 | 3.1245 | 1054.284 | 17.6235 | -84.3521 | -11.6579 | 0 | 57.9451 | 237.9451 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.5809 | 149.5809 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5443 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7963 | 19 | 12.7 | 0 | 0 | 0 | 0 | 0 | 332 | 7963 | 1140 | 327.4521 | -21.3128 | 3.1245 | 1114.284 | 18.6235 | -99.3521 | -21.625 | 0 | 57.9451 | 237.9451 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.3043 | 145.3043 | 0% | 11.67% | 0% | 80% | 0% | 0 | 6.5691 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7964 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 332 | 7964 | 1200 | 327.4521 | -21.3128 | 3.1245 | 1174.284 | 19.6235 | -114.3521 | -31.8655 | 0 | 57.9451 | 237.9451 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.6802 | 138.6802 | 0% | 11.7% | 0% | 80% | 0% | 0 | 6.7446 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7965 | 21 | 10.8 | 0 | 0 | 0 | 0 | 0 | 332 | 7965 | 1260 | 327.4521 | -21.3128 | 3.1245 | 1234.284 | 20.6235 | -129.3521 | -42.0204 | 0 | 57.9451 | 237.9451 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -10.5271 | 0 | 0% | 11.76% | 0% | 80% | 0% | 0 | 7.0535 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7966 | 22 | 9.7 | 0 | 0 | 0 | 0 | 0 | 332 | 7966 | 1320 | 327.4521 | -21.3128 | 3.1245 | 1294.284 | 21.6235 | -144.3521 | -51.5634 | 0 | 57.9451 | 237.9451 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4723 | 0 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7967 | 23 | 9.4 | 0 | 0 | 0 | 0 | 0 | 332 | 7967 | 1380 | 327.4521 | -21.3128 | 3.1245 | 1354.284 | 22.6235 | -159.3521 | -59.5267 | 0 | 57.9451 | 237.9451 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.5722 | 0 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.4266 | 6 | 0 | 0 | 0% | 0%
11 | 332 | 28 | 7968 | 24 | 9.1 | 0 | 0 | 0 | 0 | 0 | 332 | 7968 | 1440 | 327.4521 | -21.3128 | 3.1245 | 1414.284 | 23.6235 | -174.3521 | -64.1252 | 0 | 57.9451 | 237.9451 | 67.9581 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.6721 | 0 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.5083 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7969 | 1 | 8.1 | 0 | 0 | 0 | 0 | 0 | 333 | 7969 | 60 | 328.4384 | -21.479 | 2.983 | 34.284 | 0.62112 | 170.6833 | -63.5964 | 0 | 57.6781 | 122.3219 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.7593 | 0 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.7853 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7970 | 2 | 7.4 | 0 | 0 | 0 | 0 | 0 | 333 | 7970 | 120 | 328.4384 | -21.479 | 2.983 | 94.284 | 1.6211 | 155.6833 | -57.9466 | 0 | 57.6781 | 122.3219 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.4512 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7971 | 3 | 7.2 | 0 | 0 | 0 | 0 | 0 | 333 | 7971 | 180 | 328.4384 | -21.479 | 2.983 | 154.284 | 2.6211 | 140.6833 | -49.4508 | 0 | 57.6781 | 122.3219 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3811 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7972 | 4 | 7.2 | 0 | 0 | 0 | 0 | 0 | 333 | 7972 | 240 | 328.4384 | -21.479 | 2.983 | 214.284 | 3.6211 | 125.6833 | -39.6833 | 0 | 57.6781 | 122.3219 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.3811 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7973 | 5 | 6.6 | 0 | 0 | 0 | 0 | 0 | 333 | 7973 | 300 | 328.4384 | -21.479 | 2.983 | 274.284 | 4.6211 | 110.6833 | -29.466 | 0 | 57.6781 | 122.3219 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.7589 | 0 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7974 | 6 | 6.3 | 0 | 0 | 0 | 0 | 0 | 333 | 7974 | 360 | 328.4384 | -21.479 | 2.983 | 334.284 | 5.6211 | 95.6833 | -19.2646 | 0 | 57.6781 | 122.3219 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 1.4608 | 1.4608 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7975 | 7 | 6.1 | 0 | 0 | 0 | 0 | 0 | 333 | 7975 | 420 | 328.4384 | -21.479 | 2.983 | 394.284 | 6.6211 | 80.6833 | -9.4191 | 0 | 57.6781 | 122.3219 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 159.9071 | 159.9071 | 0% | 11.96% | 0% | 80% | 0% | 0 | 8.3603 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7976 | 8 | 6.6 | 0 | 0 | 0 | 0 | 0 | 333 | 7976 | 480 | 328.4384 | -21.479 | 2.983 | 454.284 | 7.6211 | 65.6833 | -0.25262 | 0 | 57.6781 | 122.3219 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 166.1952 | 166.1952 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.2139 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7977 | 9 | 6.8 | 2.36 | 10.42 | 12.78 | 10.42 | 5.21 | 333 | 7977 | 540 | 328.4384 | -21.479 | 2.983 | 514.284 | 8.6211 | 50.6833 | 7.8716 | 7.8716 | 46.6166 | 133.3834 | 54.6929 | 0 | 0 | 8.894 | 8.894 | -15.4966 | 0% | 4.0219 | 0 | 0 | 147.246 | 147.246 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7978 | 10 | 7.1 | 60.97 | 22.36 | 83.33 | 22.36 | 11.18 | 333 | 7978 | 600 | 328.4384 | -21.479 | 2.983 | 574.284 | 9.6211 | 35.6833 | 14.5248 | 14.5248 | 34.1053 | 145.8947 | 41.9165 | 180.8975 | 180.8975 | 19.0855 | 199.9829 | 0.082612 | 8.261% | 90.4323 | 7.4708 | 5.2295 | 151.3911 | 151.3911 | 3.454% | 11.78% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7979 | 11 | 7.3 | 102.22 | 34.44 | 136.66 | 34.44 | 17.22 | 333 | 7979 | 660 | 328.4384 | -21.479 | 2.983 | 634.284 | 10.6211 | 20.6833 | 19.2305 | 19.2305 | 20.3709 | 159.6291 | 30.8184 | 266.5271 | 266.5271 | 29.3964 | 295.9234 | 0.31809 | 31.81% | 133.8166 | 42.5663 | 29.7964 | 148.4495 | 148.4495 | 20.07% | 11.7% | 11.7% | 80% | 9.363% | 12.5296 | 8.012 | 6 | 75.1777 | 27.7081 | 50.64% | 50.64%
11 | 333 | 29 | 7980 | 12 | 8 | 93.53 | 66.31 | 159.84 | 66.31 | 33.16 | 333 | 7980 | 720 | 328.4384 | -21.479 | 2.983 | 694.284 | 11.6211 | 5.6833 | 21.5499 | 21.5499 | 5.686 | 174.314 | 23.9117 | 232.7792 | 232.7792 | 56.5991 | 289.3783 | 0.31283 | 31.28% | 130.8569 | 40.9358 | 28.6551 | 142.2113 | 142.2113 | 20.15% | 11.69% | 11.69% | 80% | 9.351% | 12.2367 | 7.8134 | 6 | 73.4202 | 27.0604 | 51.63% | 51.63%
11 | 333 | 29 | 7981 | 13 | 8.9 | 105 | 75.56 | 180.56 | 75.56 | 37.78 | 333 | 7981 | 780 | 328.4384 | -21.479 | 2.983 | 754.284 | 12.6211 | -9.3167 | 21.2254 | 21.2254 | 9.3005 | 189.3005 | 24.9775 | 262.9004 | 262.9004 | 64.4945 | 327.3949 | 0.37634 | 37.63% | 148.048 | 55.7162 | 39.0013 | 142.5346 | 142.5346 | 27.36% | 11.64% | 11.64% | 85% | 9.894% | 14.6485 | 7.5632 | 6 | 87.8912 | 32.3939 | 61.66% | 61.66%
11 | 333 | 29 | 7982 | 14 | 9.5 | 100.36 | 74.44 | 174.8 | 74.44 | 37.22 | 333 | 7982 | 840 | 328.4384 | -21.479 | 2.983 | 814.284 | 13.6211 | -24.3167 | 18.2949 | 18.2949 | 23.8024 | 203.8024 | 33.2562 | 267.352 | 267.352 | 63.5385 | 330.8905 | 0.38511 | 38.51% | 149.6287 | 57.6235 | 40.3365 | 142.1887 | 142.1887 | 28.37% | 11.62% | 11.62% | 85% | 9.879% | 14.7825 | 7.3995 | 6 | 88.6952 | 32.6902 | 62.38% | 62.38%
11 | 333 | 29 | 7983 | 15 | 9.7 | 115.56 | 89.92 | 205.48 | 89.92 | 44.96 | 333 | 7983 | 900 | 328.4384 | -21.479 | 2.983 | 874.284 | 14.6211 | -39.3167 | 13.0735 | 13.0735 | 37.2499 | 217.2499 | 44.9098 | 361.809 | 361.809 | 76.7515 | 438.5605 | 0.48902 | 48.9% | 198.3171 | 96.9806 | 67.8864 | 120.9076 | 120.9076 | 56.15% | 11.56% | 0% | 85% | 0% | 0 | 7.3455 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7984 | 16 | 9.5 | 70.47 | 60.83 | 131.3 | 60.83 | 30.42 | 333 | 7984 | 960 | 328.4384 | -21.479 | 2.983 | 934.284 | 15.6211 | -54.3167 | 6.0212 | 6.0212 | 49.4675 | 229.4675 | 57.9153 | 0 | 0 | 51.9217 | 51.9217 | -1.8655 | 0% | 23.479 | 0 | 0 | 157.8175 | 157.8175 | 0% | 11.78% | 0% | 80% | 0% | 0 | 7.3995 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7985 | 17 | 9.3 | 18.69 | 23.33 | 42.02 | 23.33 | 11.67 | 333 | 7985 | 1020 | 328.4384 | -21.479 | 2.983 | 994.284 | 16.6211 | -69.3167 | -2.3922 | 0 | 57.6781 | 237.6781 | 67.7856 | 0 | 0 | 19.9134 | 19.9134 | -6.18 | 0% | 9.0048 | 0 | 0 | 150.6093 | 150.6093 | 0% | 11.81% | 0% | 80% | 0% | 0 | 7.4538 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7986 | 18 | 8.5 | 0 | 0 | 0 | 0 | 0 | 333 | 7986 | 1080 | 328.4384 | -21.479 | 2.983 | 1054.284 | 17.6211 | -84.3167 | -11.7543 | 0 | 57.6781 | 237.6781 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.4491 | 142.4491 | 0% | 11.86% | 0% | 80% | 0% | 0 | 7.6737 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7987 | 19 | 8.3 | 0 | 0 | 0 | 0 | 0 | 333 | 7987 | 1140 | 328.4384 | -21.479 | 2.983 | 1114.284 | 18.6211 | -99.3167 | -21.7151 | 0 | 57.6781 | 237.6781 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.0204 | 139.0204 | 0% | 11.87% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7988 | 20 | 7.5 | 0 | 0 | 0 | 0 | 0 | 333 | 7988 | 1200 | 328.4384 | -21.479 | 2.983 | 1174.284 | 19.6211 | -114.3167 | -31.9539 | 0 | 57.6781 | 237.6781 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.2981 | 133.2981 | 0% | 11.9% | 0% | 80% | 0% | 0 | 7.9549 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7989 | 21 | 7.4 | 0 | 0 | 0 | 0 | 0 | 333 | 7989 | 1260 | 328.4384 | -21.479 | 2.983 | 1234.284 | 20.6211 | -129.3167 | -42.1134 | 0 | 57.6781 | 237.6781 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9408 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7990 | 22 | 6.9 | 0 | 0 | 0 | 0 | 0 | 333 | 7990 | 1320 | 328.4384 | -21.479 | 2.983 | 1294.284 | 21.6211 | -144.3167 | -51.6695 | 0 | 57.6781 | 237.6781 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.7127 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7991 | 23 | 7.2 | 0 | 0 | 0 | 0 | 0 | 333 | 7991 | 1380 | 328.4384 | -21.479 | 2.983 | 1354.284 | 22.6211 | -159.3167 | -59.657 | 0 | 57.6781 | 237.6781 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8806 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0406 | 6 | 0 | 0 | 0% | 0%
11 | 333 | 29 | 7992 | 24 | 7.1 | 0 | 0 | 0 | 0 | 0 | 333 | 7992 | 1440 | 328.4384 | -21.479 | 2.983 | 1414.284 | 23.6211 | -174.3167 | -64.2842 | 0 | 57.6781 | 237.6781 | 67.7856 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6581 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 7993 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 334 | 7993 | 60 | 329.4247 | -21.6382 | 2.8336 | 34.284 | 0.61863 | 170.7206 | -63.7591 | 0 | 57.422 | 122.578 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.87 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 7994 | 2 | 7.4 | 0 | 0 | 0 | 0 | 0 | 334 | 7994 | 120 | 329.4247 | -21.6382 | 2.8336 | 94.284 | 1.6186 | 155.7206 | -58.0998 | 0 | 57.422 | 122.578 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.9862 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 7995 | 3 | 7.4 | 0 | 0 | 0 | 0 | 0 | 334 | 7995 | 180 | 329.4247 | -21.6382 | 2.8336 | 154.284 | 2.6186 | 140.7206 | -49.5924 | 0 | 57.422 | 122.578 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -13.712 | 0 | 0% | 11.91% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 7996 | 4 | 7.1 | 0 | 0 | 0 | 0 | 0 | 334 | 7996 | 240 | 329.4247 | -21.6382 | 2.8336 | 214.284 | 3.6186 | 125.7206 | -39.8183 | 0 | 57.422 | 122.578 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1692 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 7997 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 334 | 7997 | 300 | 329.4247 | -21.6382 | 2.8336 | 274.284 | 4.6186 | 110.7206 | -29.5992 | 0 | 57.422 | 122.578 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -7.5965 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 7998 | 6 | 7.1 | 0 | 0 | 0 | 0 | 0 | 334 | 7998 | 360 | 329.4247 | -21.6382 | 2.8336 | 334.284 | 5.6186 | 95.7206 | -19.3998 | 0 | 57.422 | 122.578 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -2.5051 | 0 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0693 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 7999 | 7 | 6.7 | 0 | 0 | 0 | 0 | 0 | 334 | 7999 | 420 | 329.4247 | -21.6382 | 2.8336 | 394.284 | 6.6186 | 80.7206 | -9.5588 | 0 | 57.422 | 122.578 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 151.7146 | 151.7146 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8000 | 8 | 6.7 | 0 | 0 | 0 | 0 | 0 | 334 | 8000 | 480 | 329.4247 | -21.6382 | 2.8336 | 454.284 | 7.6186 | 65.7206 | -0.39863 | 0 | 57.422 | 122.578 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 156.5299 | 156.5299 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.1849 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8001 | 9 | 6.9 | 2.14 | 7.5 | 9.64 | 7.5 | 3.75 | 334 | 8001 | 540 | 329.4247 | -21.6382 | 2.8336 | 514.284 | 8.6186 | 50.7206 | 7.7186 | 7.7186 | 46.5603 | 133.4397 | 54.7767 | 0 | 0 | 6.4017 | 6.4017 | -21.8059 | 0% | 2.8948 | 0 | 0 | 137.7649 | 137.7649 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8002 | 10 | 6.9 | 36.75 | 30.28 | 67.03 | 30.28 | 15.14 | 334 | 8002 | 600 | 329.4247 | -21.6382 | 2.8336 | 574.284 | 9.6186 | 35.7206 | 14.3655 | 14.3655 | 34.0701 | 145.9299 | 42.0246 | 110.0331 | 110.0331 | 25.8456 | 135.8787 | -0.26122 | 0% | 61.4444 | 0 | 0 | 142.5765 | 142.5765 | 0% | 11.83% | 0% | 80% | 0% | 0 | 8.127 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8003 | 11 | 7.6 | 70.83 | 75 | 145.83 | 75 | 37.5 | 334 | 8003 | 660 | 329.4247 | -21.6382 | 2.8336 | 634.284 | 10.6186 | 20.7206 | 19.0678 | 19.0678 | 20.3632 | 159.6368 | 30.9578 | 185.9272 | 185.9272 | 64.0165 | 249.9437 | 0.23155 | 23.16% | 113.0245 | 26.1709 | 18.3196 | 144.5675 | 144.5675 | 12.67% | 11.73% | 11.73% | 80% | 9.382% | 10.6036 | 7.9264 | 6 | 63.6218 | 23.449 | 44.01% | 44.01%
11 | 334 | 30 | 8004 | 12 | 8.2 | 99.58 | 81.39 | 180.97 | 81.39 | 40.7 | 334 | 8004 | 720 | 329.4247 | -21.6382 | 2.8336 | 694.284 | 11.6186 | 5.7206 | 21.3886 | 21.3886 | 5.7108 | 174.2892 | 24.0745 | 249.3009 | 249.3009 | 69.4707 | 318.7716 | 0.3596 | 35.96% | 144.1485 | 51.8358 | 36.285 | 142.0374 | 142.0374 | 25.55% | 11.66% | 11.66% | 85% | 9.915% | 14.2919 | 7.7573 | 6 | 85.7511 | 31.6052 | 60.37% | 60.37%
11 | 334 | 30 | 8005 | 13 | 8.8 | 224.72 | 90.28 | 315 | 90.28 | 45.14 | 334 | 8005 | 780 | 329.4247 | -21.6382 | 2.8336 | 754.284 | 12.6186 | -9.2794 | 21.0715 | 21.0715 | 9.2433 | 189.2433 | 25.1114 | 565.9591 | 565.9591 | 77.0588 | 643.0179 | 0.58589 | 58.59% | 290.7727 | 170.3606 | 119.2524 | 125.7572 | 125.7572 | 94.83% | 11.45% | 11.45% | 90% | 10.3% | 29.9607 | 7.5907 | 6 | 179.7644 | 66.2555 | 142.9% | 142.9%
11 | 334 | 30 | 8006 | 14 | 8.5 | 46.94 | 90.97 | 137.91 | 90.97 | 45.49 | 334 | 8006 | 840 | 329.4247 | -21.6382 | 2.8336 | 814.284 | 13.6186 | -24.2794 | 18.1532 | 18.1532 | 23.7177 | 203.7177 | 33.3356 | 125.8729 | 125.8729 | 77.6478 | 203.5206 | 0.11142 | 11.14% | 92.032 | 10.2539 | 7.1777 | 136.9035 | 136.9035 | 5.243% | 11.73% | 11.73% | 80% | 9.383% | 8.6358 | 7.6737 | 6 | 51.8145 | 19.0972 | 37.85% | 37.85%
11 | 334 | 30 | 8007 | 15 | 7.8 | 10.56 | 82.92 | 93.48 | 82.92 | 41.46 | 334 | 8007 | 900 | 329.4247 | -21.6382 | 2.8336 | 874.284 | 14.6186 | -39.2794 | 12.9465 | 12.9465 | 37.1453 | 217.1453 | 44.9493 | 33.3584 | 33.3584 | 70.7766 | 104.1351 | -0.56544 | 0% | 47.0899 | 0 | 0 | 150.6619 | 150.6619 | 0% | 11.82% | 0% | 80% | 0% | 0 | 7.8698 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8008 | 16 | 7.4 | 14.72 | 39.64 | 54.36 | 39.64 | 19.82 | 334 | 8008 | 960 | 329.4247 | -21.6382 | 2.8336 | 934.284 | 15.6186 | -54.2794 | 5.9087 | 5.9087 | 49.3491 | 229.3491 | 57.9277 | 0 | 0 | 33.8349 | 33.8349 | -3.4388 | 0% | 15.3001 | 0 | 0 | 146.2663 | 146.2663 | 0% | 11.88% | 0% | 80% | 0% | 0 | 7.9834 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8009 | 17 | 7.09 | 4.31 | 14.86 | 19.17 | 14.86 | 7.43 | 334 | 8009 | 1020 | 329.4247 | -21.6382 | 2.8336 | 994.284 | 16.6186 | -69.2794 | -2.4921 | 0 | 57.422 | 237.422 | 67.6205 | 0 | 0 | 12.6838 | 12.6838 | -10.5719 | 0% | 5.7356 | 0 | 0 | 141.2579 | 141.2579 | 0% | 11.91% | 0% | 80% | 0% | 0 | 8.0722 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8010 | 18 | 6.96 | 0 | 0 | 0 | 0 | 0 | 334 | 8010 | 1080 | 329.4247 | -21.6382 | 2.8336 | 1054.284 | 17.6186 | -84.2794 | -11.8444 | 0 | 57.422 | 237.422 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.073 | 137.073 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1096 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8011 | 19 | 6.91 | 0 | 0 | 0 | 0 | 0 | 334 | 8011 | 1140 | 329.4247 | -21.6382 | 2.8336 | 1114.284 | 18.6186 | -99.2794 | -21.799 | 0 | 57.422 | 237.422 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.8492 | 134.8492 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1241 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8012 | 20 | 6.86 | 0 | 0 | 0 | 0 | 0 | 334 | 8012 | 1200 | 329.4247 | -21.6382 | 2.8336 | 1174.284 | 19.6186 | -114.2794 | -32.0361 | 0 | 57.422 | 237.422 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.6357 | 131.6357 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1385 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8013 | 21 | 6.8 | 0 | 0 | 0 | 0 | 0 | 334 | 8013 | 1260 | 329.4247 | -21.6382 | 2.8336 | 1234.284 | 20.6186 | -129.2794 | -42.1998 | 0 | 57.422 | 237.422 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2426 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8014 | 22 | 6.8 | 0 | 0 | 0 | 0 | 0 | 334 | 8014 | 1320 | 329.4247 | -21.6382 | 2.8336 | 1294.284 | 21.6186 | -144.2794 | -51.7686 | 0 | 57.422 | 237.422 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.9974 | 0 | 0% | 11.93% | 0% | 80% | 0% | 0 | 8.1559 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8015 | 23 | 6.5 | 0 | 0 | 0 | 0 | 0 | 334 | 8015 | 1380 | 329.4247 | -21.6382 | 2.8336 | 1354.284 | 22.6186 | -159.2794 | -59.7799 | 0 | 57.422 | 237.422 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1804 | 0 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.2431 | 6 | 0 | 0 | 0% | 0%
11 | 334 | 30 | 8016 | 24 | 6.01 | 0 | 0 | 0 | 0 | 0 | 334 | 8016 | 1440 | 329.4247 | -21.6382 | 2.8336 | 1414.284 | 23.6186 | -174.2794 | -64.4359 | 0 | 57.422 | 237.422 | 67.6205 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.6529 | 0 | 0% | 11.97% | 0% | 80% | 0% | 0 | 8.3868 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8017 | 1 | 5.62 | 0 | 0 | 0 | 0 | 0 | 335 | 8017 | 60 | 330.411 | -21.7902 | 2.6767 | 34.284 | 0.61601 | 170.7598 | -63.9154 | 0 | 57.1769 | 122.8231 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.341 | 0 | 0% | 11.98% | 0% | 80% | 0% | 0 | 8.5025 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8018 | 2 | 5.51 | 0 | 0 | 0 | 0 | 0 | 335 | 8018 | 120 | 330.411 | -21.7902 | 2.6767 | 94.284 | 1.616 | 155.7598 | -58.2478 | 0 | 57.1769 | 122.8231 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.2357 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5353 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8019 | 3 | 5.46 | 0 | 0 | 0 | 0 | 0 | 335 | 8019 | 180 | 330.411 | -21.7902 | 2.6767 | 154.284 | 2.616 | 140.7598 | -49.7297 | 0 | 57.1769 | 122.8231 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.039 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5502 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8020 | 4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 335 | 8020 | 240 | 330.411 | -21.7902 | 2.6767 | 214.284 | 3.616 | 125.7598 | -39.9495 | 0 | 57.1769 | 122.8231 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1305 | 0 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.5682 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8021 | 5 | 5.37 | 0 | 0 | 0 | 0 | 0 | 335 | 8021 | 300 | 330.411 | -21.7902 | 2.6767 | 274.284 | 4.616 | 110.7598 | -29.7288 | 0 | 57.1769 | 122.8231 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.1723 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5772 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8022 | 6 | 5.33 | 0 | 0 | 0 | 0 | 0 | 335 | 8022 | 360 | 330.411 | -21.7902 | 2.6767 | 334.284 | 5.616 | 95.7598 | -19.5312 | 0 | 57.1769 | 122.8231 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -4.088 | 0 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5892 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8023 | 7 | 5.3 | 0 | 0 | 0 | 0 | 0 | 335 | 8023 | 420 | 330.411 | -21.7902 | 2.6767 | 394.284 | 6.616 | 80.7598 | -9.6944 | 0 | 57.1769 | 122.8231 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 150.9326 | 150.9326 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8024 | 8 | 5.3 | 0 | 0 | 0 | 0 | 0 | 335 | 8024 | 480 | 330.411 | -21.7902 | 2.6767 | 454.284 | 7.616 | 65.7598 | -0.54012 | 0 | 57.1769 | 122.8231 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 155.6934 | 155.6934 | 0% | 12% | 0% | 80% | 0% | 0 | 8.5982 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8025 | 9 | 5.2 | 1.11 | 8.89 | 10 | 8.89 | 4.45 | 335 | 8025 | 540 | 330.411 | -21.7902 | 2.6767 | 514.284 | 8.616 | 50.7598 | 7.5706 | 7.5706 | 46.5094 | 133.4906 | 54.8601 | 0 | 0 | 7.5881 | 7.5881 | -18.8057 | 0% | 3.4313 | 0 | 0 | 136.226 | 136.226 | 0% | 12% | 0% | 80% | 0% | 0 | 8.6282 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8026 | 10 | 5.7 | 31.39 | 39.03 | 70.42 | 39.03 | 19.52 | 335 | 8026 | 600 | 330.411 | -21.7902 | 2.6767 | 574.284 | 9.616 | 35.7598 | 14.212 | 14.212 | 34.0396 | 145.9604 | 42.131 | 94.8195 | 94.8195 | 33.3142 | 128.1337 | -0.34794 | 0% | 57.9421 | 0 | 0 | 141.3169 | 141.3169 | 0% | 11.88% | 0% | 80% | 0% | 0 | 8.4787 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8027 | 11 | 6.4 | 82.08 | 73.19 | 155.27 | 73.19 | 36.6 | 335 | 8027 | 660 | 330.411 | -21.7902 | 2.6767 | 634.284 | 10.616 | 20.7598 | 18.9116 | 18.9116 | 20.3593 | 159.6407 | 31.0933 | 216.8638 | 216.8638 | 62.4716 | 279.3354 | 0.28158 | 28.16% | 126.3155 | 35.5679 | 24.8976 | 143.4333 | 143.4333 | 17.36% | 11.74% | 11.74% | 80% | 9.393% | 11.865 | 8.2723 | 6 | 71.1901 | 26.2384 | 49.63% | 49.63%
12 | 335 | 1 | 8028 | 12 | 8.3 | 124.58 | 95.42 | 220 | 95.42 | 47.71 | 335 | 8028 | 720 | 330.411 | -21.7902 | 2.6767 | 694.284 | 11.616 | 5.7598 | 21.2344 | 21.2344 | 5.7378 | 174.2622 | 24.2308 | 313.6652 | 313.6652 | 81.4461 | 395.1113 | 0.44606 | 44.61% | 178.6693 | 79.6971 | 55.788 | 122.827 | 122.827 | 45.42% | 11.61% | 11.61% | 85% | 9.871% | 17.6358 | 7.7294 | 6 | 105.8151 | 39.0001 | 86.15% | 86.15%
12 | 335 | 1 | 8029 | 13 | 9.4 | 177.5 | 119.58 | 297.08 | 119.58 | 59.79 | 335 | 8029 | 780 | 330.411 | -21.7902 | 2.6767 | 754.284 | 12.616 | -9.2402 | 20.9248 | 20.9248 | 9.1853 | 189.1853 | 25.2383 | 449.5575 | 449.5575 | 102.0679 | 551.6254 | 0.55231 | 55.23% | 249.445 | 137.7699 | 96.439 | 126.0122 | 126.0122 | 76.53% | 11.5% | 11.5% | 90% | 10.35% | 25.8104 | 7.4266 | 6 | 154.8623 | 57.0774 | 122.9% | 122.9%
12 | 335 | 1 | 8030 | 14 | 9.5 | 167.22 | 91.94 | 259.16 | 91.94 | 45.97 | 335 | 8030 | 840 | 330.411 | -21.7902 | 2.6767 | 814.284 | 13.616 | -24.2402 | 18.0188 | 18.0188 | 23.6338 | 203.6338 | 33.4095 | 451.2609 | 451.2609 | 78.4757 | 529.7366 | 0.54235 | 54.23% | 239.5469 | 129.9178 | 90.9424 | 123.4308 | 123.4308 | 73.68% | 11.51% | 11.51% | 90% | 10.36% | 24.8105 | 7.3995 | 6 | 148.8631 | 54.8662 | 120.6% | 120.6%
12 | 335 | 1 | 8031 | 15 | 8.9 | 37.69 | 92.5 | 130.19 | 92.5 | 46.25 | 335 | 8031 | 900 | 330.411 | -21.7902 | 2.6767 | 874.284 | 14.616 | -39.2402 | 12.8266 | 12.8266 | 37.0425 | 217.0425 | 44.9844 | 120.0813 | 120.0813 | 78.9537 | 199.035 | 0.10054 | 10.05% | 90.0036 | 9.0485 | 6.334 | 155.2763 | 155.2763 | 4.079% | 11.72% | 0% | 80% | 0% | 0 | 7.5632 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8032 | 16 | 8.3 | 16.47 | 71.03 | 87.5 | 71.03 | 35.52 | 335 | 8032 | 960 | 330.411 | -21.7902 | 2.6767 | 934.284 | 15.616 | -54.2402 | 5.803 | 5.803 | 49.2333 | 229.2333 | 57.9367 | 0 | 0 | 60.6279 | 60.6279 | -1.5287 | 0% | 27.4159 | 0 | 0 | 150.4685 | 150.4685 | 0% | 11.83% | 0% | 80% | 0% | 0 | 7.7294 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8033 | 17 | 7.6 | 5.92 | 21.39 | 27.31 | 21.39 | 10.7 | 335 | 8033 | 1020 | 330.411 | -21.7902 | 2.6767 | 994.284 | 16.616 | -69.2402 | -2.5853 | 0 | 57.1769 | 237.1769 | 67.4627 | 0 | 0 | 18.2575 | 18.2575 | -7.0328 | 0% | 8.256 | 0 | 0 | 144.0414 | 144.0414 | 0% | 11.89% | 0% | 80% | 0% | 0 | 7.9264 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8034 | 18 | 7 | 0 | 0 | 0 | 0 | 0 | 335 | 8034 | 1080 | 330.411 | -21.7902 | 2.6767 | 1054.284 | 17.616 | -84.2402 | -11.9281 | 0 | 57.1769 | 237.1769 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.57 | 138.57 | 0% | 11.92% | 0% | 80% | 0% | 0 | 8.0981 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8035 | 19 | 6.3 | 0 | 0 | 0 | 0 | 0 | 335 | 8035 | 1140 | 330.411 | -21.7902 | 2.6767 | 1114.284 | 18.616 | -99.2402 | -21.8766 | 0 | 57.1769 | 237.1769 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.0598 | 135.0598 | 0% | 11.95% | 0% | 80% | 0% | 0 | 8.3016 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8036 | 20 | 5.1 | 0 | 0 | 0 | 0 | 0 | 335 | 8036 | 1200 | 330.411 | -21.7902 | 2.6767 | 1174.284 | 19.616 | -114.2402 | -32.112 | 0 | 57.1769 | 237.1769 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.7335 | 129.7335 | 0% | 12.01% | 0% | 80% | 0% | 0 | 8.6583 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8037 | 21 | 3.9 | 0 | 0 | 0 | 0 | 0 | 335 | 8037 | 1260 | 330.411 | -21.7902 | 2.6767 | 1234.284 | 20.616 | -129.2402 | -42.2798 | 0 | 57.1769 | 237.1769 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9633 | 0 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8038 | 22 | 3.5 | 0 | 0 | 0 | 0 | 0 | 335 | 8038 | 1320 | 330.411 | -21.7902 | 2.6767 | 1294.284 | 21.616 | -144.2402 | -51.861 | 0 | 57.1769 | 237.1769 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.3906 | 0 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8039 | 23 | 2.8 | 0 | 0 | 0 | 0 | 0 | 335 | 8039 | 1380 | 330.411 | -21.7902 | 2.6767 | 1354.284 | 22.616 | -159.2402 | -59.8954 | 0 | 57.1769 | 237.1769 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1845 | 0 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
12 | 335 | 1 | 8040 | 24 | 2.1 | 0 | 0 | 0 | 0 | 0 | 335 | 8040 | 1440 | 330.411 | -21.7902 | 2.6767 | 1414.284 | 23.616 | -174.2402 | -64.5802 | 0 | 57.1769 | 237.1769 | 67.4627 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9783 | 0 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5943 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8041 | 1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 336 | 8041 | 60 | 331.3973 | -21.935 | 2.5125 | 34.284 | 0.61327 | 170.8009 | -64.0652 | 0 | 56.943 | 123.057 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0223 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8042 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 336 | 8042 | 120 | 331.3973 | -21.935 | 2.5125 | 94.284 | 1.6133 | 155.8009 | -58.3906 | 0 | 56.943 | 123.057 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.7403 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8043 | 3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 336 | 8043 | 180 | 331.3973 | -21.935 | 2.5125 | 154.284 | 2.6133 | 140.8009 | -49.8627 | 0 | 56.943 | 123.057 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.1536 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8044 | 4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 336 | 8044 | 240 | 331.3973 | -21.935 | 2.5125 | 214.284 | 3.6133 | 125.8009 | -40.0768 | 0 | 56.943 | 123.057 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.3059 | 0 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8045 | 5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 336 | 8045 | 300 | 331.3973 | -21.935 | 2.5125 | 274.284 | 4.6133 | 110.8009 | -29.8547 | 0 | 56.943 | 123.057 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.9088 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8046 | 6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 336 | 8046 | 360 | 331.3973 | -21.935 | 2.5125 | 334.284 | 5.6133 | 95.8009 | -19.6587 | 0 | 56.943 | 123.057 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -6.889 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8047 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 336 | 8047 | 420 | 331.3973 | -21.935 | 2.5125 | 394.284 | 6.6133 | 80.8009 | -9.826 | 0 | 56.943 | 123.057 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 149.5787 | 149.5787 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8048 | 8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 336 | 8048 | 480 | 331.3973 | -21.935 | 2.5125 | 454.284 | 7.6133 | 65.8009 | -0.67702 | 0 | 56.943 | 123.057 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 154.562 | 154.562 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8049 | 9 | 0.3 | 0.08 | 8.14 | 8.22 | 8.14 | 4.07 | 336 | 8049 | 540 | 331.3973 | -21.935 | 2.5125 | 514.284 | 8.6133 | 50.8009 | 7.4279 | 7.4279 | 46.4636 | 133.5364 | 54.9429 | 0 | 0 | 6.9479 | 6.9479 | -22.3277 | 0% | 3.1419 | 0 | 0 | 134.1867 | 134.1867 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8050 | 10 | 0.9 | 38.89 | 54.17 | 93.06 | 54.17 | 27.09 | 336 | 8050 | 600 | 331.3973 | -21.935 | 2.5125 | 574.284 | 9.6133 | 35.8009 | 14.0644 | 14.0644 | 34.0138 | 145.9862 | 42.2355 | 118.4866 | 118.4866 | 46.237 | 164.7236 | -0.16272 | 0% | 74.488 | 0 | 0 | 140.8546 | 140.8546 | 0% | 12.02% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8051 | 11 | 1.7 | 90.83 | 88.61 | 179.44 | 88.61 | 44.31 | 336 | 8051 | 660 | 331.3973 | -21.935 | 2.5125 | 634.284 | 10.6133 | 20.8009 | 18.7618 | 18.7618 | 20.3589 | 159.6411 | 31.2249 | 241.4924 | 241.4924 | 75.6334 | 317.1258 | 0.30805 | 30.8% | 143.4043 | 44.1752 | 30.9226 | 142.6949 | 142.6949 | 21.67% | 11.84% | 11.84% | 85% | 10.06% | 14.4298 | 9.7239 | 6 | 86.5787 | 31.9102 | 60.67% | 60.67%
12 | 336 | 2 | 8052 | 12 | 1.8 | 80.28 | 117.86 | 198.14 | 117.86 | 58.93 | 336 | 8052 | 720 | 331.3973 | -21.935 | 2.5125 | 694.284 | 11.6133 | 5.8009 | 21.0871 | 21.0871 | 5.767 | 174.233 | 24.3806 | 203.2339 | 203.2339 | 100.5998 | 303.8337 | 0.28715 | 28.72% | 137.3936 | 39.4532 | 27.6173 | 137.5173 | 137.5173 | 20.08% | 11.85% | 11.85% | 85% | 10.07% | 13.8374 | 9.6914 | 6 | 83.0244 | 30.6002 | 60.37% | 60.37%
12 | 336 | 2 | 8053 | 13 | 2.3 | 159.44 | 120.64 | 280.08 | 120.64 | 60.32 | 336 | 8053 | 780 | 331.3973 | -21.935 | 2.5125 | 754.284 | 12.6133 | -9.1991 | 20.7855 | 20.7855 | 9.1266 | 189.1266 | 25.3583 | 406.0008 | 406.0008 | 102.9727 | 508.9735 | 0.49787 | 49.79% | 230.1578 | 114.5877 | 80.2114 | 119.3527 | 119.3527 | 67.21% | 11.64% | 11.64% | 90% | 10.47% | 24.1016 | 9.53 | 6 | 144.6097 | 53.2986 | 121.2% | 121.2%
12 | 336 | 2 | 8054 | 14 | 2.7 | 176.19 | 109.53 | 285.72 | 109.53 | 54.77 | 336 | 8054 | 840 | 331.3973 | -21.935 | 2.5125 | 814.284 | 13.6133 | -24.1991 | 17.8917 | 17.8917 | 23.5506 | 203.5506 | 33.4779 | 478.3563 | 478.3563 | 93.4897 | 571.846 | 0.53323 | 53.32% | 258.5888 | 137.8867 | 96.5207 | 119.4089 | 119.4089 | 80.83% | 11.57% | 11.57% | 90% | 10.41% | 26.9247 | 9.4021 | 6 | 161.5484 | 59.5416 | 135.3% | 135.3%
12 | 336 | 2 | 8055 | 15 | 3.4 | 120.36 | 87.69 | 208.05 | 87.69 | 43.85 | 336 | 8055 | 900 | 331.3973 | -21.935 | 2.5125 | 874.284 | 14.6133 | -39.1991 | 12.7137 | 12.7137 | 36.9415 | 216.9415 | 45.0153 | 386.6085 | 386.6085 | 74.8481 | 461.4566 | 0.47214 | 47.21% | 208.6707 | 98.5212 | 68.9648 | 114.381 | 114.381 | 60.29% | 11.66% | 0% | 85% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8056 | 16 | 3.5 | 42.5 | 46.11 | 88.61 | 46.11 | 23.06 | 336 | 8056 | 960 | 331.3973 | -21.935 | 2.5125 | 934.284 | 15.6133 | -54.1991 | 5.7042 | 5.7042 | 49.1203 | 229.1203 | 57.9424 | 0 | 0 | 39.3573 | 39.3573 | -3.0809 | 0% | 17.7974 | 0 | 0 | 149.0077 | 149.0077 | 0% | 12.04% | 0% | 80% | 0% | 0 | 9.1497 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8057 | 17 | 3.2 | 6.75 | 24.44 | 31.19 | 24.44 | 12.22 | 336 | 8057 | 1020 | 331.3973 | -21.935 | 2.5125 | 994.284 | 16.6133 | -69.1991 | -2.6721 | 0 | 56.943 | 236.943 | 67.3123 | 0 | 0 | 20.8608 | 20.8608 | -6.5603 | 0% | 9.4333 | 0 | 0 | 142.6304 | 142.6304 | 0% | 12.07% | 0% | 80% | 0% | 0 | 9.2438 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8058 | 18 | 2.8 | 0 | 0 | 0 | 0 | 0 | 336 | 8058 | 1080 | 331.3973 | -21.935 | 2.5125 | 1054.284 | 17.6133 | -84.1991 | -12.0055 | 0 | 56.943 | 236.943 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.7502 | 136.7502 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8059 | 19 | 1.9 | 0 | 0 | 0 | 0 | 0 | 336 | 8059 | 1140 | 331.3973 | -21.935 | 2.5125 | 1114.284 | 18.6133 | -99.1991 | -21.9481 | 0 | 56.943 | 236.943 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.352 | 132.352 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8060 | 20 | 1.1 | 0 | 0 | 0 | 0 | 0 | 336 | 8060 | 1200 | 331.3973 | -21.935 | 2.5125 | 1174.284 | 19.6133 | -114.1991 | -32.1817 | 0 | 56.943 | 236.943 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.9792 | 126.9792 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8061 | 21 | 0.5 | 0 | 0 | 0 | 0 | 0 | 336 | 8061 | 1260 | 331.3973 | -21.935 | 2.5125 | 1234.284 | 20.6133 | -129.1991 | -42.3534 | 0 | 56.943 | 236.943 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9713 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8062 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 8062 | 1320 | 331.3973 | -21.935 | 2.5125 | 1294.284 | 21.6133 | -144.1991 | -51.9464 | 0 | 56.943 | 236.943 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.697 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8063 | 23 | -0.5 | 0 | 0 | 0 | 0 | 0 | 336 | 8063 | 1380 | 331.3973 | -21.935 | 2.5125 | 1354.284 | 22.6133 | -159.1991 | -60.0036 | 0 | 56.943 | 236.943 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.177 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 336 | 2 | 8064 | 24 | -1.1 | 0 | 0 | 0 | 0 | 0 | 336 | 8064 | 1440 | 331.3973 | -21.935 | 2.5125 | 1414.284 | 23.6133 | -174.1991 | -64.717 | 0 | 56.943 | 236.943 | 67.3123 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8094 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8065 | 1 | -1.7 | 0 | 0 | 0 | 0 | 0 | 337 | 8065 | 60 | 332.3836 | -22.0726 | 2.3413 | 34.284 | 0.61042 | 170.8437 | -64.2083 | 0 | 56.7205 | 123.2795 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3777 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8066 | 2 | -2.1 | 0 | 0 | 0 | 0 | 0 | 337 | 8066 | 120 | 332.3836 | -22.0726 | 2.3413 | 94.284 | 1.6104 | 155.8437 | -58.528 | 0 | 56.7205 | 123.2795 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8579 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8067 | 3 | -2.2 | 0 | 0 | 0 | 0 | 0 | 337 | 8067 | 180 | 332.3836 | -22.0726 | 2.3413 | 154.284 | 2.6104 | 140.8437 | -49.9912 | 0 | 56.7205 | 123.2795 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.881 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8068 | 4 | -2.5 | 0 | 0 | 0 | 0 | 0 | 337 | 8068 | 240 | 332.3836 | -22.0726 | 2.3413 | 214.284 | 3.6104 | 125.8437 | -40.2002 | 0 | 56.7205 | 123.2795 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.3382 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8069 | 5 | -3 | 0 | 0 | 0 | 0 | 0 | 337 | 8069 | 300 | 332.3836 | -22.0726 | 2.3413 | 274.284 | 4.6104 | 110.8437 | -29.9768 | 0 | 56.7205 | 123.2795 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6937 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8070 | 6 | -2.5 | 0 | 0 | 0 | 0 | 0 | 337 | 8070 | 360 | 332.3836 | -22.0726 | 2.3413 | 334.284 | 5.6104 | 95.8437 | -19.7824 | 0 | 56.7205 | 123.2795 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.3186 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8071 | 7 | -2.7 | 0 | 0 | 0 | 0 | 0 | 337 | 8071 | 420 | 332.3836 | -22.0726 | 2.3413 | 394.284 | 6.6104 | 80.8437 | -9.9533 | 0 | 56.7205 | 123.2795 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.5483 | 131.5483 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8072 | 8 | -2 | 0 | 0 | 0 | 0 | 0 | 337 | 8072 | 480 | 332.3836 | -22.0726 | 2.3413 | 454.284 | 7.6104 | 65.8437 | -0.80924 | 0 | 56.7205 | 123.2795 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.0572 | 135.0572 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8073 | 9 | -2.5 | 0 | 6.67 | 6.67 | 6.67 | 3.34 | 337 | 8073 | 540 | 332.3836 | -22.0726 | 2.3413 | 514.284 | 8.6104 | 50.8437 | 7.2905 | 7.2905 | 46.4232 | 133.5768 | 55.025 | 0 | 0 | 5.6932 | 5.6932 | -28.6472 | 0% | 2.5745 | 0 | 0 | 114.1875 | 114.1875 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8074 | 10 | -2.3 | 0.56 | 21.94 | 22.5 | 21.94 | 10.97 | 337 | 8074 | 600 | 332.3836 | -22.0726 | 2.3413 | 574.284 | 9.6104 | 35.8437 | 13.9227 | 13.9227 | 33.9924 | 146.0076 | 42.3379 | 1.7204 | 1.7204 | 18.727 | 20.4473 | -7.3717 | 0% | 9.2463 | 0 | 0 | 115.7226 | 115.7226 | 0% | 12.31% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8075 | 11 | -1.9 | 1.94 | 57.31 | 59.25 | 57.31 | 28.66 | 337 | 8075 | 660 | 332.3836 | -22.0726 | 2.3413 | 634.284 | 10.6104 | 20.8437 | 18.6186 | 18.6186 | 20.362 | 159.638 | 31.3524 | 5.1892 | 5.1892 | 48.9171 | 54.1063 | -2.2672 | 0% | 24.4669 | 0 | 0 | 116.8405 | 116.8405 | 0% | 12.25% | 12.25% | 80% | 9.8% | 2.3978 | 10.9403 | 6 | 14.387 | 5.3026 | 12.31% | 12.31%
12 | 337 | 3 | 8076 | 12 | -1.7 | 58.25 | 70.28 | 128.53 | 70.28 | 35.14 | 337 | 8076 | 720 | 332.3836 | -22.0726 | 2.3413 | 694.284 | 11.6104 | 5.8437 | 20.947 | 20.947 | 5.7984 | 174.2016 | 24.5237 | 148.237 | 148.237 | 59.9877 | 208.2248 | 0.0083494 | 0.8349% | 94.1592 | 0.78617 | 0.55032 | 118.2015 | 118.2015 | 0.4656% | 12.06% | 12.06% | 80% | 9.647% | 9.0832 | 10.8704 | 6 | 54.4991 | 20.0867 | 46.11% | 46.11%
12 | 337 | 3 | 8077 | 13 | -0.9 | 82.31 | 82.69 | 165 | 82.69 | 41.35 | 337 | 8077 | 780 | 332.3836 | -22.0726 | 2.3413 | 754.284 | 12.6104 | -9.1563 | 20.6535 | 20.6535 | 9.0673 | 189.0673 | 25.4713 | 210.6788 | 210.6788 | 70.5803 | 281.2591 | 0.22203 | 22.2% | 127.1854 | 28.2387 | 19.7671 | 120.1422 | 120.1422 | 16.45% | 11.95% | 11.95% | 80% | 9.559% | 12.1572 | 10.5933 | 6 | 72.9431 | 26.8845 | 60.71% | 60.71%
12 | 337 | 3 | 8078 | 14 | -0.2 | 26.19 | 103.61 | 129.8 | 103.61 | 51.81 | 337 | 8078 | 840 | 332.3836 | -22.0726 | 2.3413 | 814.284 | 13.6104 | -24.1563 | 17.7719 | 17.7719 | 23.4681 | 203.4681 | 33.5408 | 71.5176 | 71.5176 | 88.4367 | 159.9543 | -0.20849 | 0% | 72.3313 | 0 | 0 | 119.0661 | 119.0661 | 0% | 12.06% | 12.06% | 80% | 9.65% | 6.9803 | 10.3546 | 6 | 41.8819 | 15.4363 | 35.18% | 35.18%
12 | 337 | 3 | 8079 | 15 | 0.1 | 13.14 | 95.83 | 108.97 | 95.83 | 47.92 | 337 | 8079 | 900 | 332.3836 | -22.0726 | 2.3413 | 874.284 | 14.6104 | -39.1563 | 12.608 | 12.608 | 36.8426 | 216.8426 | 45.042 | 42.5354 | 42.5354 | 81.796 | 124.3314 | -0.49262 | 0% | 56.2227 | 0 | 0 | 137.8395 | 137.8395 | 0% | 12.09% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8080 | 16 | 0.8 | 3.53 | 58.53 | 62.06 | 58.53 | 29.27 | 337 | 8080 | 960 | 332.3836 | -22.0726 | 2.3413 | 934.284 | 15.6104 | -54.1563 | 5.6121 | 5.6121 | 49.01 | 229.01 | 57.9447 | 0 | 0 | 49.9585 | 49.9585 | -2.3884 | 0% | 22.5912 | 0 | 0 | 135.6757 | 135.6757 | 0% | 12.14% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8081 | 17 | 0.2 | 1.39 | 20.56 | 21.95 | 20.56 | 10.28 | 337 | 8081 | 1020 | 332.3836 | -22.0726 | 2.3413 | 994.284 | 16.6104 | -69.1563 | -2.7523 | 0 | 56.7205 | 236.7205 | 67.1695 | 0 | 0 | 17.5491 | 17.5491 | -8.3682 | 0% | 7.9357 | 0 | 0 | 131.5875 | 131.5875 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8082 | 18 | -0.9 | 0 | 0 | 0 | 0 | 0 | 337 | 8082 | 1080 | 332.3836 | -22.0726 | 2.3413 | 1054.284 | 17.6104 | -84.1563 | -12.0766 | 0 | 56.7205 | 236.7205 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.4349 | 127.4349 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8083 | 19 | -0.5 | 0 | 0 | 0 | 0 | 0 | 337 | 8083 | 1140 | 332.3836 | -22.0726 | 2.3413 | 1114.284 | 18.6104 | -99.1563 | -22.0133 | 0 | 56.7205 | 236.7205 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.7748 | 126.7748 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8084 | 20 | -0.8 | 0 | 0 | 0 | 0 | 0 | 337 | 8084 | 1200 | 332.3836 | -22.0726 | 2.3413 | 1174.284 | 19.6104 | -114.1563 | -32.2452 | 0 | 56.7205 | 236.7205 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.4868 | 124.4868 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8085 | 21 | -1.3 | 0 | 0 | 0 | 0 | 0 | 337 | 8085 | 1260 | 332.3836 | -22.0726 | 2.3413 | 1234.284 | 20.6104 | -129.1563 | -42.4205 | 0 | 56.7205 | 236.7205 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.7298 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8086 | 22 | -2 | 0 | 0 | 0 | 0 | 0 | 337 | 8086 | 1320 | 332.3836 | -22.0726 | 2.3413 | 1294.284 | 21.6104 | -144.1563 | -52.0251 | 0 | 56.7205 | 236.7205 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.223 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8087 | 23 | -2.5 | 0 | 0 | 0 | 0 | 0 | 337 | 8087 | 1380 | 332.3836 | -22.0726 | 2.3413 | 1354.284 | 22.6104 | -159.1563 | -60.1044 | 0 | 56.7205 | 236.7205 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8556 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 337 | 3 | 8088 | 24 | -3 | 0 | 0 | 0 | 0 | 0 | 337 | 8088 | 1440 | 332.3836 | -22.0726 | 2.3413 | 1414.284 | 23.6104 | -174.1563 | -64.8463 | 0 | 56.7205 | 236.7205 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.4883 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8089 | 1 | -3.2 | 0 | 0 | 0 | 0 | 0 | 338 | 8089 | 60 | 333.3699 | -22.2029 | 2.1635 | 34.284 | 0.60746 | 170.8881 | -64.3448 | 0 | 56.5094 | 123.4906 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.9106 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8090 | 2 | -3.5 | 0 | 0 | 0 | 0 | 0 | 338 | 8090 | 120 | 333.3699 | -22.2029 | 2.1635 | 94.284 | 1.6075 | 155.8881 | -58.66 | 0 | 56.5094 | 123.4906 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.2713 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8091 | 3 | -4.1 | 0 | 0 | 0 | 0 | 0 | 338 | 8091 | 180 | 333.3699 | -22.2029 | 2.1635 | 154.284 | 2.6075 | 140.8881 | -50.1153 | 0 | 56.5094 | 123.4906 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.0891 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8092 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 338 | 8092 | 240 | 333.3699 | -22.2029 | 2.1635 | 214.284 | 3.6075 | 125.8881 | -40.3196 | 0 | 56.5094 | 123.4906 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.9367 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8093 | 5 | -4.1 | 0 | 0 | 0 | 0 | 0 | 338 | 8093 | 300 | 333.3699 | -22.2029 | 2.1635 | 274.284 | 4.6075 | 110.8881 | -30.095 | 0 | 56.5094 | 123.4906 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.572 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8094 | 6 | -3.9 | 0 | 0 | 0 | 0 | 0 | 338 | 8094 | 360 | 333.3699 | -22.2029 | 2.1635 | 334.284 | 5.6075 | 95.8881 | -19.9021 | 0 | 56.5094 | 123.4906 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.317 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8095 | 7 | -4.3 | 0 | 0 | 0 | 0 | 0 | 338 | 8095 | 420 | 333.3699 | -22.2029 | 2.1635 | 394.284 | 6.6075 | 80.8881 | -10.0763 | 0 | 56.5094 | 123.4906 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.002 | 126.002 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8096 | 8 | -4.2 | 0 | 0 | 0 | 0 | 0 | 338 | 8096 | 480 | 333.3699 | -22.2029 | 2.1635 | 454.284 | 7.6075 | 65.8881 | -0.93672 | 0 | 56.5094 | 123.4906 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.77 | 127.77 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8097 | 9 | -3.8 | 0.08 | 3.33 | 3.41 | 3.33 | 1.67 | 338 | 8097 | 540 | 333.3699 | -22.2029 | 2.1635 | 514.284 | 8.6075 | 50.8881 | 7.1583 | 7.1583 | 46.3879 | 133.6121 | 55.1064 | 0 | 0 | 2.8423 | 2.8423 | -59.3355 | 0% | 1.2853 | 0 | 0 | 107.8159 | 107.8159 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8098 | 10 | -3.2 | 1.11 | 27.03 | 28.14 | 27.03 | 13.52 | 338 | 8098 | 600 | 333.3699 | -22.2029 | 2.1635 | 574.284 | 9.6075 | 35.8881 | 13.787 | 13.787 | 33.9756 | 146.0244 | 42.4383 | 3.4374 | 3.4374 | 23.0715 | 26.509 | -5.5873 | 0% | 11.9874 | 0 | 0 | 109.711 | 109.711 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8099 | 11 | -1.1 | 12.03 | 68.89 | 80.92 | 68.89 | 34.45 | 338 | 8099 | 660 | 333.3699 | -22.2029 | 2.1635 | 634.284 | 10.6075 | 20.8881 | 18.4821 | 18.4821 | 20.3687 | 159.6313 | 31.4757 | 32.3649 | 32.3649 | 58.8013 | 91.1661 | -0.9969 | 0% | 41.2253 | 0 | 0 | 114.3034 | 114.3034 | 0% | 12.17% | 12.17% | 80% | 9.74% | 4.0152 | 10.6622 | 6 | 24.0913 | 8.8793 | 21.08% | 21.08%
12 | 338 | 4 | 8100 | 12 | 0 | 15.75 | 108.53 | 124.28 | 108.53 | 54.27 | 338 | 8100 | 720 | 333.3699 | -22.2029 | 2.1635 | 694.284 | 11.6075 | 5.8881 | 20.8139 | 20.8139 | 5.832 | 174.168 | 24.6602 | 40.2821 | 40.2821 | 92.6361 | 132.9182 | -0.41071 | 0% | 60.1056 | 0 | 0 | 116.0706 | 116.0706 | 0% | 12.09% | 12.09% | 80% | 9.669% | 5.8114 | 10.287 | 6 | 34.8683 | 12.8514 | 30.04% | 30.04%
12 | 338 | 4 | 8101 | 13 | 0.8 | 7.58 | 88.97 | 96.55 | 88.97 | 44.49 | 338 | 8101 | 780 | 333.3699 | -22.2029 | 2.1635 | 754.284 | 12.6075 | -9.1119 | 20.5288 | 20.5288 | 9.0074 | 189.0074 | 25.5774 | 19.497 | 19.497 | 75.9406 | 95.4377 | -0.86711 | 0% | 43.1569 | 0 | 0 | 115.5253 | 115.5253 | 0% | 12.1% | 12.1% | 80% | 9.677% | 4.1762 | 10.0195 | 6 | 25.0573 | 9.2353 | 21.69% | 21.69%
12 | 338 | 4 | 8102 | 14 | 2.2 | 3.89 | 81.53 | 85.42 | 81.53 | 40.77 | 338 | 8102 | 840 | 333.3699 | -22.2029 | 2.1635 | 814.284 | 13.6075 | -24.1119 | 17.6594 | 17.6594 | 23.3866 | 203.3866 | 33.5982 | 10.6809 | 10.6809 | 69.5902 | 80.2711 | -1.1401 | 0% | 36.2986 | 0 | 0 | 116.7621 | 116.7621 | 0% | 12.06% | 12.06% | 80% | 9.645% | 3.5011 | 9.5621 | 6 | 21.0066 | 7.7424 | 17.99% | 17.99%
12 | 338 | 4 | 8103 | 15 | 3.3 | 0.83 | 67.78 | 68.61 | 67.78 | 33.89 | 338 | 8103 | 900 | 333.3699 | -22.2029 | 2.1635 | 874.284 | 14.6075 | -39.1119 | 12.5093 | 12.5093 | 36.7456 | 216.7456 | 45.0644 | 2.7066 | 2.7066 | 57.8538 | 60.5604 | -1.7287 | 0% | 27.3854 | 0 | 0 | 137.8187 | 137.8187 | 0% | 12.03% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8104 | 16 | 2.8 | 0.28 | 36.75 | 37.03 | 36.75 | 18.38 | 338 | 8104 | 960 | 333.3699 | -22.2029 | 2.1635 | 934.284 | 15.6075 | -54.1119 | 5.5269 | 5.5269 | 48.9027 | 228.9027 | 57.9437 | 0 | 0 | 31.3681 | 31.3681 | -4.1245 | 0% | 14.1846 | 0 | 0 | 134.9916 | 134.9916 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8105 | 17 | 1.9 | 0 | 11.39 | 11.39 | 11.39 | 5.7 | 338 | 8105 | 1020 | 333.3699 | -22.2029 | 2.1635 | 994.284 | 16.6075 | -69.1119 | -2.826 | 0 | 56.5094 | 236.5094 | 67.0342 | 0 | 0 | 9.722 | 9.722 | -15.3234 | 0% | 4.3963 | 0 | 0 | 131.7367 | 131.7367 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8106 | 18 | 1 | 0 | 1.11 | 1.11 | 1.11 | 0.56 | 338 | 8106 | 1080 | 333.3699 | -22.2029 | 2.1635 | 1054.284 | 17.6075 | -84.1119 | -12.1414 | 0 | 56.5094 | 236.5094 | 67.0342 | 0 | 0 | 0.94744 | 0.94744 | -167.0108 | 0% | 0.42843 | 0 | 0 | 129.0988 | 129.0988 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8107 | 19 | 0.2 | 0 | 0 | 0 | 0 | 0 | 338 | 8107 | 1140 | 333.3699 | -22.2029 | 2.1635 | 1114.284 | 18.6075 | -99.1119 | -22.0724 | 0 | 56.5094 | 236.5094 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.9501 | 126.9501 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8108 | 20 | -0.8 | 0 | 0 | 0 | 0 | 0 | 338 | 8108 | 1200 | 333.3699 | -22.2029 | 2.1635 | 1174.284 | 19.6075 | -114.1119 | -32.3026 | 0 | 56.5094 | 236.5094 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.0765 | 124.0765 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8109 | 21 | -1 | 0 | 0 | 0 | 0 | 0 | 338 | 8109 | 1260 | 333.3699 | -22.2029 | 2.1635 | 1234.284 | 20.6075 | -129.1119 | -42.4813 | 0 | 56.5094 | 236.5094 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5503 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8110 | 22 | -1.8 | 0 | 0 | 0 | 0 | 0 | 338 | 8110 | 1320 | 333.3699 | -22.2029 | 2.1635 | 1294.284 | 21.6075 | -144.1119 | -52.0969 | 0 | 56.5094 | 236.5094 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0668 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8111 | 23 | -1.9 | 0 | 0 | 0 | 0 | 0 | 338 | 8111 | 1380 | 333.3699 | -22.2029 | 2.1635 | 1354.284 | 22.6075 | -159.1119 | -60.1978 | 0 | 56.5094 | 236.5094 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.1226 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
12 | 338 | 4 | 8112 | 24 | -2.5 | 0 | 0 | 0 | 0 | 0 | 338 | 8112 | 1440 | 333.3699 | -22.2029 | 2.1635 | 1414.284 | 23.6075 | -174.1119 | -64.968 | 0 | 56.5094 | 236.5094 | 67.0342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9404 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8113 | 1 | -2.4 | 0 | 0 | 0 | 0 | 0 | 339 | 8113 | 60 | 334.3562 | -22.3259 | 1.9793 | 34.284 | 0.60439 | 170.9342 | -64.4746 | 0 | 56.3098 | 123.6902 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6302 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8114 | 2 | -3.3 | 0 | 0 | 0 | 0 | 0 | 339 | 8114 | 120 | 334.3562 | -22.3259 | 1.9793 | 94.284 | 1.6044 | 155.9342 | -58.7866 | 0 | 56.3098 | 123.6902 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8747 | 0 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8115 | 3 | -3.6 | 0 | 0 | 0 | 0 | 0 | 339 | 8115 | 180 | 334.3562 | -22.3259 | 1.9793 | 154.284 | 2.6044 | 140.9342 | -50.2349 | 0 | 56.3098 | 123.6902 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2048 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8116 | 4 | -3.9 | 0 | 0 | 0 | 0 | 0 | 339 | 8116 | 240 | 334.3562 | -22.3259 | 1.9793 | 214.284 | 3.6044 | 125.9342 | -40.435 | 0 | 56.3098 | 123.6902 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.662 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8117 | 5 | -4.5 | 0 | 0 | 0 | 0 | 0 | 339 | 8117 | 300 | 334.3562 | -22.3259 | 1.9793 | 274.284 | 4.6044 | 110.9342 | -30.2093 | 0 | 56.3098 | 123.6902 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6912 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8118 | 6 | -4.5 | 0 | 0 | 0 | 0 | 0 | 339 | 8118 | 360 | 334.3562 | -22.3259 | 1.9793 | 334.284 | 5.6044 | 95.9342 | -20.0177 | 0 | 56.3098 | 123.6902 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.6932 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8119 | 7 | -5 | 0 | 0 | 0 | 0 | 0 | 339 | 8119 | 420 | 334.3562 | -22.3259 | 1.9793 | 394.284 | 6.6044 | 80.9342 | -10.195 | 0 | 56.3098 | 123.6902 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.2227 | 130.2227 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8120 | 8 | -5.7 | 0 | 0 | 0 | 0 | 0 | 339 | 8120 | 480 | 334.3562 | -22.3259 | 1.9793 | 454.284 | 7.6044 | 65.9342 | -1.0594 | 0 | 56.3098 | 123.6902 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.8533 | 131.8533 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8121 | 9 | -5.2 | 0.28 | 8.06 | 8.34 | 8.06 | 4.03 | 339 | 8121 | 540 | 334.3562 | -22.3259 | 1.9793 | 514.284 | 8.6044 | 50.9342 | 7.0316 | 7.0316 | 46.3577 | 133.6423 | 55.1867 | 0 | 0 | 6.8796 | 6.8796 | -24.5574 | 0% | 3.111 | 0 | 0 | 112.6072 | 112.6072 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8122 | 10 | -4.8 | 0.75 | 43.81 | 44.56 | 43.81 | 21.91 | 339 | 8122 | 600 | 334.3562 | -22.3259 | 1.9793 | 574.284 | 9.6044 | 35.9342 | 13.6574 | 13.6574 | 33.9632 | 146.0368 | 42.5364 | 2.3405 | 2.3405 | 37.3942 | 39.7347 | -3.5615 | 0% | 17.968 | 0 | 0 | 115.2576 | 115.2576 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8123 | 11 | -1.8 | 2.42 | 85.47 | 87.89 | 85.47 | 42.74 | 339 | 8123 | 660 | 334.3562 | -22.3259 | 1.9793 | 634.284 | 10.6044 | 20.9342 | 18.3522 | 18.3522 | 20.3786 | 159.6214 | 31.5947 | 6.5467 | 6.5467 | 72.9532 | 79.5 | -1.2831 | 0% | 35.9499 | 0 | 0 | 120.4027 | 120.4027 | 0% | 12.22% | 12.22% | 80% | 9.773% | 3.5133 | 10.9053 | 6 | 21.0797 | 7.7693 | 17.51% | 17.51%
12 | 339 | 5 | 8124 | 12 | -2.1 | 57.22 | 123.42 | 180.64 | 123.42 | 61.71 | 339 | 8124 | 720 | 334.3562 | -22.3259 | 1.9793 | 694.284 | 11.6044 | 5.9342 | 20.688 | 20.688 | 5.8675 | 174.1325 | 24.7899 | 147.0431 | 147.0431 | 105.3456 | 252.3886 | 0.14362 | 14.36% | 114.1301 | 16.3916 | 11.4741 | 121.7931 | 121.7931 | 9.421% | 12.02% | 12.02% | 80% | 9.614% | 10.9726 | 11.0106 | 6 | 65.8355 | 24.2649 | 54.06% | 54.06%
12 | 339 | 5 | 8125 | 13 | -1.3 | 68.89 | 128.69 | 197.58 | 128.69 | 64.35 | 339 | 8125 | 780 | 334.3562 | -22.3259 | 1.9793 | 754.284 | 12.6044 | -9.0658 | 20.4115 | 20.4115 | 8.9471 | 188.9471 | 25.6763 | 178.0235 | 178.0235 | 109.8438 | 287.8673 | 0.23194 | 23.19% | 130.1736 | 30.1919 | 21.1344 | 123.1485 | 123.1485 | 17.16% | 11.95% | 11.95% | 80% | 9.562% | 12.4466 | 10.7313 | 6 | 74.6798 | 27.5246 | 60.64% | 60.64%
12 | 339 | 5 | 8126 | 14 | -2.5 | 9.64 | 130.64 | 140.28 | 130.64 | 65.32 | 339 | 8126 | 840 | 334.3562 | -22.3259 | 1.9793 | 814.284 | 13.6044 | -24.0658 | 17.5543 | 17.5543 | 23.306 | 203.306 | 33.65 | 26.6063 | 26.6063 | 111.5082 | 138.1145 | -0.41001 | 0% | 62.4554 | 0 | 0 | 118.384 | 118.384 | 0% | 12.17% | 12.17% | 80% | 9.737% | 6.0812 | 11.1519 | 6 | 36.4872 | 13.448 | 30.82% | 30.82%
12 | 339 | 5 | 8127 | 15 | -2.8 | 58.14 | 97.69 | 155.83 | 97.69 | 48.85 | 339 | 8127 | 900 | 334.3562 | -22.3259 | 1.9793 | 874.284 | 14.6044 | -39.0658 | 12.4179 | 12.4179 | 36.6508 | 216.6508 | 45.0825 | 190.9042 | 190.9042 | 83.3836 | 274.2878 | 0.18996 | 19% | 124.033 | 23.5615 | 16.4931 | 96.5707 | 96.5707 | 17.08% | 12.01% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8128 | 16 | -2.6 | 28.25 | 70.83 | 99.08 | 70.83 | 35.42 | 339 | 8128 | 960 | 334.3562 | -22.3259 | 1.9793 | 934.284 | 15.6044 | -54.0658 | 5.4485 | 5.4485 | 48.7983 | 228.7983 | 57.9394 | 0 | 0 | 60.4572 | 60.4572 | -1.9735 | 0% | 27.3387 | 0 | 0 | 135.5098 | 135.5098 | 0% | 12.27% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8129 | 17 | -0.8 | 1.03 | 23.33 | 24.36 | 23.33 | 11.67 | 339 | 8129 | 1020 | 334.3562 | -22.3259 | 1.9793 | 994.284 | 16.6044 | -69.0658 | -2.8932 | 0 | 56.3098 | 236.3098 | 66.9065 | 0 | 0 | 19.9134 | 19.9134 | -7.4034 | 0% | 9.0048 | 0 | 0 | 132.7926 | 132.7926 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8130 | 18 | -1.5 | 0 | 2.22 | 2.22 | 2.22 | 1.11 | 339 | 8130 | 1080 | 334.3562 | -22.3259 | 1.9793 | 1054.284 | 17.6044 | -84.0658 | -12.1999 | 0 | 56.3098 | 236.3098 | 66.9065 | 0 | 0 | 1.8949 | 1.8949 | -86.3653 | 0% | 0.85687 | 0 | 0 | 128.9232 | 128.9232 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8131 | 19 | -2.2 | 0 | 0 | 0 | 0 | 0 | 339 | 8131 | 1140 | 334.3562 | -22.3259 | 1.9793 | 1114.284 | 18.6044 | -99.0658 | -22.1254 | 0 | 56.3098 | 236.3098 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.9398 | 125.9398 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8132 | 20 | -2.1 | 0 | 0 | 0 | 0 | 0 | 339 | 8132 | 1200 | 334.3562 | -22.3259 | 1.9793 | 1174.284 | 19.6044 | -114.0658 | -32.3538 | 0 | 56.3098 | 236.3098 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.6252 | 123.6252 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8133 | 21 | -2.1 | 0 | 0 | 0 | 0 | 0 | 339 | 8133 | 1260 | 334.3562 | -22.3259 | 1.9793 | 1234.284 | 20.6044 | -129.0658 | -42.5358 | 0 | 56.3098 | 236.3098 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9907 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8134 | 22 | -1.8 | 0 | 0 | 0 | 0 | 0 | 339 | 8134 | 1320 | 334.3562 | -22.3259 | 1.9793 | 1294.284 | 21.6044 | -144.0658 | -52.1621 | 0 | 56.3098 | 236.3098 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.097 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8135 | 23 | -1.8 | 0 | 0 | 0 | 0 | 0 | 339 | 8135 | 1380 | 334.3562 | -22.3259 | 1.9793 | 1354.284 | 22.6044 | -159.0658 | -60.2839 | 0 | 56.3098 | 236.3098 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9699 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 339 | 5 | 8136 | 24 | -1.7 | 0 | 0 | 0 | 0 | 0 | 339 | 8136 | 1440 | 334.3562 | -22.3259 | 1.9793 | 1414.284 | 23.6044 | -174.0658 | -65.0822 | 0 | 56.3098 | 236.3098 | 66.9065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6905 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8137 | 1 | -1.6 | 0 | 0 | 0 | 0 | 0 | 340 | 8137 | 60 | 335.3425 | -22.4416 | 1.7891 | 34.284 | 0.60122 | 170.9817 | -64.5976 | 0 | 56.1219 | 123.8781 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1404 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8138 | 2 | -1.5 | 0 | 0 | 0 | 0 | 0 | 340 | 8138 | 120 | 335.3425 | -22.4416 | 1.7891 | 94.284 | 1.6012 | 155.9817 | -58.9078 | 0 | 56.1219 | 123.8781 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.778 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8139 | 3 | -1.4 | 0 | 0 | 0 | 0 | 0 | 340 | 8139 | 180 | 335.3425 | -22.4416 | 1.7891 | 154.284 | 2.6012 | 140.9817 | -50.3499 | 0 | 56.1219 | 123.8781 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4156 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8140 | 4 | -1.3 | 0 | 0 | 0 | 0 | 0 | 340 | 8140 | 240 | 335.3425 | -22.4416 | 1.7891 | 214.284 | 3.6012 | 125.9817 | -40.5462 | 0 | 56.1219 | 123.8781 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.2632 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8141 | 5 | -1.3 | 0 | 0 | 0 | 0 | 0 | 340 | 8141 | 300 | 335.3425 | -22.4416 | 1.7891 | 274.284 | 4.6012 | 110.9817 | -30.3196 | 0 | 56.1219 | 123.8781 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -16.1991 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8142 | 6 | -1.2 | 0 | 0 | 0 | 0 | 0 | 340 | 8142 | 360 | 335.3425 | -22.4416 | 1.7891 | 334.284 | 5.6012 | 95.9817 | -20.1293 | 0 | 56.1219 | 123.8781 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.6286 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8143 | 7 | -1.3 | 0 | 0 | 0 | 0 | 0 | 340 | 8143 | 420 | 335.3425 | -22.4416 | 1.7891 | 394.284 | 6.6012 | 80.9817 | -10.3092 | 0 | 56.1219 | 123.8781 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.2178 | 142.2178 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8144 | 8 | -1.4 | 0 | 0 | 0 | 0 | 0 | 340 | 8144 | 480 | 335.3425 | -22.4416 | 1.7891 | 454.284 | 7.6012 | 65.9817 | -1.1771 | 0 | 56.1219 | 123.8781 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.2394 | 146.2394 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8145 | 9 | -1.5 | 0.08 | 5 | 5.08 | 5 | 2.5 | 340 | 8145 | 540 | 335.3425 | -22.4416 | 1.7891 | 514.284 | 8.6012 | 50.9817 | 6.9104 | 6.9104 | 46.3327 | 133.6673 | 55.2661 | 0 | 0 | 4.2678 | 4.2678 | -37.8992 | 0% | 1.9299 | 0 | 0 | 126.3481 | 126.3481 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8146 | 10 | -1.4 | 21.75 | 26.39 | 48.14 | 26.39 | 13.2 | 340 | 8146 | 600 | 335.3425 | -22.4416 | 1.7891 | 574.284 | 9.6012 | 35.9817 | 13.5339 | 13.5339 | 33.9551 | 146.0449 | 42.6321 | 68.3782 | 68.3782 | 22.5253 | 90.9034 | -1.0103 | 0% | 41.1065 | 0 | 0 | 130.1336 | 130.1336 | 0% | 12.19% | 0% | 80% | 0% | 0 | 10.7659 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8147 | 11 | -1.5 | 74.17 | 63.89 | 138.06 | 63.89 | 31.95 | 340 | 8147 | 660 | 335.3425 | -22.4416 | 1.7891 | 634.284 | 10.6012 | 20.9817 | 18.2291 | 18.2291 | 20.392 | 159.608 | 31.7094 | 201.7092 | 201.7092 | 54.5335 | 256.2428 | 0.15939 | 15.94% | 115.873 | 18.4693 | 12.9285 | 132.0251 | 132.0251 | 9.792% | 11.99% | 11.99% | 80% | 9.596% | 11.1192 | 10.8007 | 6 | 66.715 | 24.589 | 50.53% | 50.53%
12 | 340 | 6 | 8148 | 12 | -0.8 | 140 | 57.14 | 197.14 | 57.14 | 28.57 | 340 | 8148 | 720 | 335.3425 | -22.4416 | 1.7891 | 694.284 | 11.6012 | 5.9817 | 20.5693 | 20.5693 | 5.9049 | 174.0951 | 24.9128 | 361.3956 | 361.3956 | 48.772 | 410.1677 | 0.40554 | 40.55% | 185.4778 | 75.218 | 52.6526 | 131.2188 | 131.2188 | 40.13% | 11.8% | 11.8% | 85% | 10.03% | 18.6002 | 10.559 | 6 | 111.6013 | 41.1327 | 85.05% | 85.05%
12 | 340 | 6 | 8149 | 13 | -0.4 | 166.31 | 53.06 | 219.37 | 53.06 | 26.53 | 340 | 8149 | 780 | 335.3425 | -22.4416 | 1.7891 | 754.284 | 12.6012 | -9.0183 | 20.3016 | 20.3016 | 8.8863 | 188.8863 | 25.7682 | 431.6665 | 431.6665 | 45.2895 | 476.956 | 0.46341 | 46.34% | 215.6795 | 99.9482 | 69.9637 | 110.3538 | 110.3538 | 63.4% | 11.71% | 11.71% | 85% | 9.957% | 21.4758 | 10.4224 | 6 | 128.855 | 47.4919 | 116.8% | 116.8%
12 | 340 | 6 | 8150 | 14 | -0.4 | 106.31 | 68.53 | 174.84 | 68.53 | 34.27 | 340 | 8150 | 840 | 335.3425 | -22.4416 | 1.7891 | 814.284 | 13.6012 | -24.0183 | 17.4565 | 17.4565 | 23.2264 | 203.2264 | 33.6962 | 294.8474 | 294.8474 | 58.494 | 353.3414 | 0.34426 | 34.43% | 159.781 | 55.0057 | 38.504 | 128.7933 | 128.7933 | 29.9% | 11.85% | 11.85% | 85% | 10.08% | 16.0982 | 10.4224 | 6 | 96.5893 | 35.5998 | 75% | 75%
12 | 340 | 6 | 8151 | 15 | 0.3 | 120.08 | 53.25 | 173.33 | 53.25 | 26.63 | 340 | 8151 | 900 | 335.3425 | -22.4416 | 1.7891 | 874.284 | 14.6012 | -39.0183 | 12.3335 | 12.3335 | 36.5581 | 216.5581 | 45.0964 | 396.8442 | 396.8442 | 45.4517 | 442.2959 | 0.44063 | 44.06% | 200.0062 | 88.1286 | 61.69 | 106.8663 | 106.8663 | 57.73% | 11.74% | 0% | 85% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8152 | 16 | -0.1 | 59.08 | 41.19 | 100.27 | 41.19 | 20.6 | 340 | 8152 | 960 | 335.3425 | -22.4416 | 1.7891 | 934.284 | 15.6012 | -54.0183 | 5.3769 | 5.3769 | 48.6969 | 228.6969 | 57.9319 | 0 | 0 | 35.1579 | 35.1579 | -3.7954 | 0% | 15.8984 | 0 | 0 | 143.7046 | 143.7046 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8153 | 17 | 1.3 | 7.78 | 16.31 | 24.09 | 16.31 | 8.16 | 340 | 8153 | 1020 | 335.3425 | -22.4416 | 1.7891 | 994.284 | 16.6012 | -69.0183 | -2.9539 | 0 | 56.1219 | 236.1219 | 66.7863 | 0 | 0 | 13.9215 | 13.9215 | -10.564 | 0% | 6.2953 | 0 | 0 | 139.1158 | 139.1158 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8154 | 18 | 3.4 | 0 | 0 | 0 | 0 | 0 | 340 | 8154 | 1080 | 335.3425 | -22.4416 | 1.7891 | 1054.284 | 17.6012 | -84.0183 | -12.2522 | 0 | 56.1219 | 236.1219 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.6626 | 137.6626 | 0% | 12.08% | 0% | 80% | 0% | 0 | 9.181 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8155 | 19 | -0.2 | 0 | 0 | 0 | 0 | 0 | 340 | 8155 | 1140 | 335.3425 | -22.4416 | 1.7891 | 1114.284 | 18.6012 | -99.0183 | -22.1724 | 0 | 56.1219 | 236.1219 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.5367 | 129.5367 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8156 | 20 | -0.6 | 0 | 0 | 0 | 0 | 0 | 340 | 8156 | 1200 | 335.3425 | -22.4416 | 1.7891 | 1174.284 | 19.6012 | -114.0183 | -32.399 | 0 | 56.1219 | 236.1219 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.452 | 125.452 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8157 | 21 | -1.3 | 0 | 0 | 0 | 0 | 0 | 340 | 8157 | 1260 | 335.3425 | -22.4416 | 1.7891 | 1234.284 | 20.6012 | -129.0183 | -42.5841 | 0 | 56.1219 | 236.1219 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4961 | 0 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8158 | 22 | -1.5 | 0 | 0 | 0 | 0 | 0 | 340 | 8158 | 1320 | 335.3425 | -22.4416 | 1.7891 | 1294.284 | 21.6012 | -144.0183 | -52.2206 | 0 | 56.1219 | 236.1219 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.618 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8159 | 23 | -1.9 | 0 | 0 | 0 | 0 | 0 | 340 | 8159 | 1380 | 335.3425 | -22.4416 | 1.7891 | 1354.284 | 22.6012 | -159.0183 | -60.3627 | 0 | 56.1219 | 236.1219 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0176 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
12 | 340 | 6 | 8160 | 24 | -2 | 0 | 0 | 0 | 0 | 0 | 340 | 8160 | 1440 | 335.3425 | -22.4416 | 1.7891 | 1414.284 | 23.6012 | -174.0183 | -65.1888 | 0 | 56.1219 | 236.1219 | 66.7863 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.96 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8161 | 1 | -1.7 | 0 | 0 | 0 | 0 | 0 | 341 | 8161 | 60 | 336.3288 | -22.5499 | 1.5932 | 34.284 | 0.59795 | 171.0307 | -64.7138 | 0 | 55.9457 | 124.0543 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3741 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8162 | 2 | -1.8 | 0 | 0 | 0 | 0 | 0 | 341 | 8162 | 120 | 336.3288 | -22.5499 | 1.5932 | 94.284 | 1.598 | 156.0307 | -59.0233 | 0 | 55.9457 | 124.0543 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4863 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8163 | 3 | -1.8 | 0 | 0 | 0 | 0 | 0 | 341 | 8163 | 180 | 336.3288 | -22.5499 | 1.5932 | 154.284 | 2.598 | 141.0307 | -50.4603 | 0 | 55.9457 | 124.0543 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.446 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8164 | 4 | -1.6 | 0 | 0 | 0 | 0 | 0 | 341 | 8164 | 240 | 336.3288 | -22.5499 | 1.5932 | 214.284 | 3.598 | 126.0307 | -40.6533 | 0 | 55.9457 | 124.0543 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1412 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8165 | 5 | -1.8 | 0 | 0 | 0 | 0 | 0 | 341 | 8165 | 300 | 336.3288 | -22.5499 | 1.5932 | 274.284 | 4.598 | 111.0307 | -30.4259 | 0 | 55.9457 | 124.0543 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9664 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8166 | 6 | -2.7 | 0 | 0 | 0 | 0 | 0 | 341 | 8166 | 360 | 336.3288 | -22.5499 | 1.5932 | 334.284 | 5.598 | 96.0307 | -20.2366 | 0 | 55.9457 | 124.0543 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3374 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8167 | 7 | -3.9 | 0 | 0 | 0 | 0 | 0 | 341 | 8167 | 420 | 336.3288 | -22.5499 | 1.5932 | 394.284 | 6.598 | 81.0307 | -10.419 | 0 | 55.9457 | 124.0543 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.8293 | 130.8293 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8168 | 8 | -4.3 | 0 | 0 | 0 | 0 | 0 | 341 | 8168 | 480 | 336.3288 | -22.5499 | 1.5932 | 454.284 | 7.598 | 66.0307 | -1.2899 | 0 | 55.9457 | 124.0543 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.8247 | 133.8247 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8169 | 9 | -4.5 | 0.08 | 5.64 | 5.72 | 5.64 | 2.82 | 341 | 8169 | 540 | 336.3288 | -22.5499 | 1.5932 | 514.284 | 8.598 | 51.0307 | 6.7947 | 6.7947 | 46.3127 | 133.6873 | 55.3443 | 0 | 0 | 4.814 | 4.814 | -35.071 | 0% | 2.1769 | 0 | 0 | 114.2019 | 114.2019 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8170 | 10 | -3.8 | 0.28 | 40.19 | 40.47 | 40.19 | 20.1 | 341 | 8170 | 600 | 336.3288 | -22.5499 | 1.5932 | 574.284 | 9.598 | 36.0307 | 13.4166 | 13.4166 | 33.9513 | 146.0487 | 42.7253 | 0.88649 | 0.88649 | 34.3043 | 35.1908 | -4.0534 | 0% | 15.9133 | 0 | 0 | 120.0215 | 120.0215 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8171 | 11 | -2.7 | 1.03 | 64.36 | 65.39 | 64.36 | 32.18 | 341 | 8171 | 660 | 336.3288 | -22.5499 | 1.5932 | 634.284 | 10.598 | 21.0307 | 18.1128 | 18.1128 | 20.4085 | 159.5915 | 31.8195 | 2.8152 | 2.8152 | 54.9347 | 57.7499 | -2.1081 | 0% | 26.1145 | 0 | 0 | 123.2496 | 123.2496 | 0% | 12.28% | 12.28% | 80% | 9.823% | 2.5652 | 11.223 | 6 | 15.3913 | 5.6727 | 12.49% | 12.49%
12 | 341 | 7 | 8172 | 12 | -2.1 | 16.94 | 77.69 | 94.63 | 77.69 | 38.85 | 341 | 8172 | 720 | 336.3288 | -22.5499 | 1.5932 | 694.284 | 11.598 | 6.0307 | 20.4579 | 20.4579 | 5.9443 | 174.0557 | 25.029 | 43.9153 | 43.9153 | 66.3126 | 110.2279 | -0.70807 | 0% | 49.8451 | 0 | 0 | 124.5839 | 124.5839 | 0% | 12.19% | 12.19% | 80% | 9.752% | 4.8611 | 11.0106 | 6 | 29.1663 | 10.7498 | 23.41% | 23.41%
12 | 341 | 7 | 8173 | 13 | -2.2 | 103.47 | 132.5 | 235.97 | 132.5 | 66.25 | 341 | 8173 | 780 | 336.3288 | -22.5499 | 1.5932 | 754.284 | 12.598 | -8.9693 | 20.1992 | 20.1992 | 8.8252 | 188.8252 | 25.8531 | 269.6733 | 269.6733 | 113.0958 | 382.7691 | 0.36791 | 36.79% | 173.0882 | 63.6809 | 44.5766 | 110.3152 | 110.3152 | 40.41% | 11.86% | 11.86% | 85% | 10.08% | 17.4511 | 11.0458 | 6 | 104.7068 | 38.5916 | 94.92% | 94.92%
12 | 341 | 7 | 8174 | 14 | -1.7 | 212.92 | 84.44 | 297.36 | 84.44 | 42.22 | 341 | 8174 | 840 | 336.3288 | -22.5499 | 1.5932 | 814.284 | 13.598 | -23.9693 | 17.3662 | 17.3662 | 23.1479 | 203.1479 | 33.7368 | 593.224 | 593.224 | 72.074 | 665.298 | 0.55498 | 55.5% | 300.8478 | 166.9637 | 116.8746 | 113.8811 | 113.8811 | 102.6% | 11.51% | 11.51% | 90% | 10.36% | 31.1723 | 10.8704 | 6 | 187.0339 | 68.9348 | 164.2% | 164.2%
12 | 341 | 7 | 8175 | 15 | -2 | 162.78 | 74.17 | 236.95 | 74.17 | 37.09 | 341 | 8175 | 900 | 336.3288 | -22.5499 | 1.5932 | 874.284 | 14.598 | -38.9693 | 12.2562 | 12.2562 | 36.4676 | 216.4676 | 45.106 | 541.2072 | 541.2072 | 63.3081 | 604.5153 | 0.5287 | 52.87% | 273.3618 | 144.5267 | 101.1687 | 109.0024 | 109.0024 | 92.81% | 11.59% | 0% | 90% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8176 | 16 | -2.2 | 78.47 | 58.61 | 137.08 | 58.61 | 29.31 | 341 | 8176 | 960 | 336.3288 | -22.5499 | 1.5932 | 934.284 | 15.598 | -53.9693 | 5.3121 | 5.3121 | 48.5986 | 228.5986 | 57.9211 | 0 | 0 | 50.0268 | 50.0268 | -2.5326 | 0% | 22.6221 | 0 | 0 | 145.4237 | 145.4237 | 0% | 12.27% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8177 | 17 | -3 | 5.92 | 17.78 | 23.7 | 17.78 | 8.89 | 341 | 8177 | 1020 | 336.3288 | -22.5499 | 1.5932 | 994.284 | 16.598 | -68.9693 | -3.0081 | 0 | 55.9457 | 235.9457 | 66.6739 | 0 | 0 | 15.1762 | 15.1762 | -10.3269 | 0% | 6.8627 | 0 | 0 | 134.947 | 134.947 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8178 | 18 | -3.5 | 0 | 0 | 0 | 0 | 0 | 341 | 8178 | 1080 | 336.3288 | -22.5499 | 1.5932 | 1054.284 | 17.598 | -83.9693 | -12.2983 | 0 | 55.9457 | 235.9457 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.6541 | 129.6541 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8179 | 19 | -4.4 | 0 | 0 | 0 | 0 | 0 | 341 | 8179 | 1140 | 336.3288 | -22.5499 | 1.5932 | 1114.284 | 18.598 | -98.9693 | -22.2133 | 0 | 55.9457 | 235.9457 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.0248 | 125.0248 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8180 | 20 | -4.2 | 0 | 0 | 0 | 0 | 0 | 341 | 8180 | 1200 | 336.3288 | -22.5499 | 1.5932 | 1174.284 | 19.598 | -113.9693 | -32.4381 | 0 | 55.9457 | 235.9457 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.6126 | 121.6126 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8181 | 21 | -4.5 | 0 | 0 | 0 | 0 | 0 | 341 | 8181 | 1260 | 336.3288 | -22.5499 | 1.5932 | 1234.284 | 20.598 | -128.9693 | -42.6262 | 0 | 55.9457 | 235.9457 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.8505 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8753 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8182 | 22 | -5.1 | 0 | 0 | 0 | 0 | 0 | 341 | 8182 | 1320 | 336.3288 | -22.5499 | 1.5932 | 1294.284 | 21.598 | -143.9693 | -52.2724 | 0 | 55.9457 | 235.9457 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.6763 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8183 | 23 | -6 | 0 | 0 | 0 | 0 | 0 | 341 | 8183 | 1380 | 336.3288 | -22.5499 | 1.5932 | 1354.284 | 22.598 | -158.9693 | -60.4341 | 0 | 55.9457 | 235.9457 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.0076 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
12 | 341 | 7 | 8184 | 24 | -6.7 | 0 | 0 | 0 | 0 | 0 | 341 | 8184 | 1440 | 336.3288 | -22.5499 | 1.5932 | 1414.284 | 23.598 | -173.9693 | -65.2877 | 0 | 55.9457 | 235.9457 | 66.6739 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.0342 | 0 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7034 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8185 | 1 | -7.7 | 0 | 0 | 0 | 0 | 0 | 342 | 8185 | 60 | 337.3151 | -22.6508 | 1.3919 | 34.284 | 0.5946 | 171.081 | -64.8231 | 0 | 55.7814 | 124.2186 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.5741 | 0 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.091 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8186 | 2 | -7.1 | 0 | 0 | 0 | 0 | 0 | 342 | 8186 | 120 | 337.3151 | -22.6508 | 1.3919 | 94.284 | 1.5946 | 156.081 | -59.1333 | 0 | 55.7814 | 124.2186 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.5985 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8187 | 3 | -7.5 | 0 | 0 | 0 | 0 | 0 | 342 | 8187 | 180 | 337.3151 | -22.6508 | 1.3919 | 154.284 | 2.5946 | 141.081 | -50.566 | 0 | 55.7814 | 124.2186 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.1468 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8188 | 4 | -8.3 | 0 | 0 | 0 | 0 | 0 | 342 | 8188 | 240 | 337.3151 | -22.6508 | 1.3919 | 214.284 | 3.5946 | 126.081 | -40.7561 | 0 | 55.7814 | 124.2186 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.366 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8189 | 5 | -8.4 | 0 | 0 | 0 | 0 | 0 | 342 | 8189 | 300 | 337.3151 | -22.6508 | 1.3919 | 274.284 | 4.5946 | 111.081 | -30.528 | 0 | 55.7814 | 124.2186 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.734 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8190 | 6 | -8.6 | 0 | 0 | 0 | 0 | 0 | 342 | 8190 | 360 | 337.3151 | -22.6508 | 1.3919 | 334.284 | 5.5946 | 96.081 | -20.3397 | 0 | 55.7814 | 124.2186 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.5849 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4458 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8191 | 7 | -9.2 | 0 | 0 | 0 | 0 | 0 | 342 | 8191 | 420 | 337.3151 | -22.6508 | 1.3919 | 394.284 | 6.5946 | 81.081 | -10.5242 | 0 | 55.7814 | 124.2186 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 118.4193 | 118.4193 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.6855 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8192 | 8 | -9.7 | 0 | 0 | 0 | 0 | 0 | 342 | 8192 | 480 | 337.3151 | -22.6508 | 1.3919 | 454.284 | 7.5946 | 66.081 | -1.3977 | 0 | 55.7814 | 124.2186 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 118.8704 | 118.8704 | 0% | 12.66% | 0% | 80% | 0% | 0 | 13.8872 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8193 | 9 | -9.1 | 0 | 7.22 | 7.22 | 7.22 | 3.61 | 342 | 8193 | 540 | 337.3151 | -22.6508 | 1.3919 | 514.284 | 8.5946 | 51.081 | 6.6846 | 6.6846 | 46.2977 | 133.7023 | 55.4213 | 0 | 0 | 6.1627 | 6.1627 | -29.1312 | 0% | 2.7868 | 0 | 0 | 99.3413 | 99.3413 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.6454 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8194 | 10 | -7 | 0.08 | 27.03 | 27.11 | 27.03 | 13.52 | 342 | 8194 | 600 | 337.3151 | -22.6508 | 1.3919 | 574.284 | 9.5946 | 36.081 | 13.3055 | 13.3055 | 33.9518 | 146.0482 | 42.8159 | 0.25499 | 0.25499 | 23.0715 | 23.3265 | -6.8726 | 0% | 10.5483 | 0 | 0 | 103.3987 | 103.3987 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.8189 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8195 | 11 | -4.8 | 0.36 | 61.03 | 61.39 | 61.03 | 30.52 | 342 | 8195 | 660 | 337.3151 | -22.6508 | 1.3919 | 634.284 | 10.5946 | 21.081 | 18.0033 | 18.0033 | 20.4282 | 159.5718 | 31.9251 | 0.98859 | 0.98859 | 52.0924 | 53.081 | -2.4639 | 0% | 24.0032 | 0 | 0 | 107.6058 | 107.6058 | 0% | 12.37% | 12.37% | 80% | 9.897% | 2.3755 | 11.9862 | 6 | 14.2531 | 5.2532 | 13.25% | 13.25%
12 | 342 | 8 | 8196 | 12 | -2.7 | 0.56 | 85.08 | 85.64 | 85.08 | 42.54 | 342 | 8196 | 720 | 337.3151 | -22.6508 | 1.3919 | 694.284 | 11.5946 | 6.081 | 20.3537 | 20.3537 | 5.9854 | 174.0146 | 25.1382 | 1.4576 | 1.4576 | 72.6203 | 74.0779 | -1.4662 | 0% | 33.498 | 0 | 0 | 110.7172 | 110.7172 | 0% | 12.26% | 12.26% | 80% | 9.807% | 3.285 | 11.223 | 6 | 19.7102 | 7.2646 | 17.8% | 17.8%
12 | 342 | 8 | 8197 | 13 | -0.7 | 1.67 | 106.19 | 107.86 | 106.19 | 53.1 | 342 | 8197 | 780 | 337.3151 | -22.6508 | 1.3919 | 754.284 | 12.5946 | -8.919 | 20.1042 | 20.1042 | 8.7639 | 188.7639 | 25.9309 | 4.3693 | 4.3693 | 90.6388 | 95.0082 | -0.91363 | 0% | 42.9627 | 0 | 0 | 114.6204 | 114.6204 | 0% | 12.15% | 12.15% | 80% | 9.724% | 4.1776 | 10.5248 | 6 | 25.0654 | 9.2383 | 21.87% | 21.87%
12 | 342 | 8 | 8198 | 14 | 0.7 | 6.67 | 98.42 | 105.09 | 98.42 | 49.21 | 342 | 8198 | 840 | 337.3151 | -22.6508 | 1.3919 | 814.284 | 13.5946 | -23.919 | 17.2831 | 17.2831 | 23.0706 | 203.0706 | 33.7719 | 18.6624 | 18.6624 | 84.0067 | 102.6691 | -0.7518 | 0% | 46.427 | 0 | 0 | 116.418 | 116.418 | 0% | 12.09% | 12.09% | 80% | 9.674% | 4.4912 | 10.0527 | 6 | 26.9474 | 9.932 | 23.15% | 23.15%
12 | 342 | 8 | 8199 | 15 | 0.3 | 1.39 | 79.72 | 81.11 | 79.72 | 39.86 | 342 | 8199 | 900 | 337.3151 | -22.6508 | 1.3919 | 874.284 | 14.5946 | -38.919 | 12.1861 | 12.1861 | 36.3795 | 216.3795 | 45.1115 | 4.6472 | 4.6472 | 68.0453 | 72.6925 | -1.4069 | 0% | 32.8715 | 0 | 0 | 135.1395 | 135.1395 | 0% | 12.14% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8200 | 16 | -0.8 | 0.28 | 41.39 | 41.67 | 41.39 | 20.7 | 342 | 8200 | 960 | 337.3151 | -22.6508 | 1.3919 | 934.284 | 15.5946 | -53.919 | 5.254 | 5.254 | 48.5035 | 228.5035 | 57.9071 | 0 | 0 | 35.3286 | 35.3286 | -3.8222 | 0% | 15.9756 | 0 | 0 | 131.2146 | 131.2146 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8201 | 17 | -1.7 | 0 | 12.97 | 12.97 | 12.97 | 6.49 | 342 | 8201 | 1020 | 337.3151 | -22.6508 | 1.3919 | 994.284 | 16.5946 | -68.919 | -3.0559 | 0 | 55.7814 | 235.7814 | 66.5691 | 0 | 0 | 11.0706 | 11.0706 | -14.1613 | 0% | 5.0061 | 0 | 0 | 128.0061 | 128.0061 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8202 | 18 | -2.7 | 0 | 0 | 0 | 0 | 0 | 342 | 8202 | 1080 | 337.3151 | -22.6508 | 1.3919 | 1054.284 | 17.5946 | -83.919 | -12.3383 | 0 | 55.7814 | 235.7814 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.2931 | 125.2931 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8203 | 19 | -3.8 | 0 | 0 | 0 | 0 | 0 | 342 | 8203 | 1140 | 337.3151 | -22.6508 | 1.3919 | 1114.284 | 18.5946 | -98.919 | -22.2482 | 0 | 55.7814 | 235.7814 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 122.8385 | 122.8385 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8204 | 20 | -4.8 | 0 | 0 | 0 | 0 | 0 | 342 | 8204 | 1200 | 337.3151 | -22.6508 | 1.3919 | 1174.284 | 19.5946 | -113.919 | -32.4714 | 0 | 55.7814 | 235.7814 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.1836 | 120.1836 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8205 | 21 | -5.2 | 0 | 0 | 0 | 0 | 0 | 342 | 8205 | 1260 | 337.3151 | -22.6508 | 1.3919 | 1234.284 | 20.5946 | -128.919 | -42.6621 | 0 | 55.7814 | 235.7814 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.6992 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8206 | 22 | -5.9 | 0 | 0 | 0 | 0 | 0 | 342 | 8206 | 1320 | 337.3151 | -22.6508 | 1.3919 | 1294.284 | 21.5946 | -143.919 | -52.3177 | 0 | 55.7814 | 235.7814 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.0147 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8207 | 23 | -6.2 | 0 | 0 | 0 | 0 | 0 | 342 | 8207 | 1380 | 337.3151 | -22.6508 | 1.3919 | 1354.284 | 22.5946 | -158.919 | -60.4984 | 0 | 55.7814 | 235.7814 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.4106 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
12 | 342 | 8 | 8208 | 24 | -6.1 | 0 | 0 | 0 | 0 | 0 | 342 | 8208 | 1440 | 337.3151 | -22.6508 | 1.3919 | 1414.284 | 23.5946 | -173.919 | -65.3791 | 0 | 55.7814 | 235.7814 | 66.5691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.197 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8209 | 1 | -6.4 | 0 | 0 | 0 | 0 | 0 | 343 | 8209 | 60 | 338.3014 | -22.7443 | 1.1857 | 34.284 | 0.59116 | 171.1326 | -64.9255 | 0 | 55.629 | 124.371 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.9402 | 0 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8210 | 2 | -6.5 | 0 | 0 | 0 | 0 | 0 | 343 | 8210 | 120 | 338.3014 | -22.7443 | 1.1857 | 94.284 | 1.5912 | 156.1326 | -59.2377 | 0 | 55.629 | 124.371 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.9165 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8211 | 3 | -7.1 | 0 | 0 | 0 | 0 | 0 | 343 | 8211 | 180 | 338.3014 | -22.7443 | 1.1857 | 154.284 | 2.5912 | 141.1326 | -50.667 | 0 | 55.629 | 124.371 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.6549 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8212 | 4 | -7.5 | 0 | 0 | 0 | 0 | 0 | 343 | 8212 | 240 | 338.3014 | -22.7443 | 1.1857 | 214.284 | 3.5912 | 126.1326 | -40.8547 | 0 | 55.629 | 124.371 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.2645 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8213 | 5 | -7.2 | 0 | 0 | 0 | 0 | 0 | 343 | 8213 | 300 | 338.3014 | -22.7443 | 1.1857 | 274.284 | 4.5912 | 111.1326 | -30.6259 | 0 | 55.629 | 124.371 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.9869 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8214 | 6 | -7.3 | 0 | 0 | 0 | 0 | 0 | 343 | 8214 | 360 | 338.3014 | -22.7443 | 1.1857 | 334.284 | 5.5912 | 96.1326 | -20.4385 | 0 | 55.629 | 124.371 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.7694 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8215 | 7 | -6.6 | 0 | 0 | 0 | 0 | 0 | 343 | 8215 | 420 | 338.3014 | -22.7443 | 1.1857 | 394.284 | 6.5912 | 81.1326 | -10.6247 | 0 | 55.629 | 124.371 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.6568 | 135.6568 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.665 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8216 | 8 | -7.1 | 0 | 0 | 0 | 0 | 0 | 343 | 8216 | 480 | 338.3014 | -22.7443 | 1.1857 | 454.284 | 7.5912 | 66.1326 | -1.5003 | 0 | 55.629 | 124.371 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 138.9444 | 138.9444 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8217 | 9 | -7.2 | 0 | 4.08 | 4.08 | 4.08 | 2.04 | 343 | 8217 | 540 | 338.3014 | -22.7443 | 1.1857 | 514.284 | 8.5912 | 51.1326 | 6.5802 | 6.5802 | 46.2876 | 133.7124 | 55.497 | 0 | 0 | 3.4825 | 3.4825 | -50.7629 | 0% | 1.5748 | 0 | 0 | 118.9647 | 118.9647 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8218 | 10 | -5.5 | 0.47 | 30.36 | 30.83 | 30.36 | 15.18 | 343 | 8218 | 600 | 338.3014 | -22.7443 | 1.1857 | 574.284 | 9.5912 | 36.1326 | 13.2007 | 13.2007 | 33.9565 | 146.0435 | 42.9039 | 1.5076 | 1.5076 | 25.9139 | 27.4215 | -5.5866 | 0% | 12.4 | 0 | 0 | 123.5787 | 123.5787 | 0% | 12.44% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8219 | 11 | -2.8 | 1.53 | 68.06 | 69.59 | 68.06 | 34.03 | 343 | 8219 | 660 | 338.3014 | -22.7443 | 1.1857 | 634.284 | 10.5912 | 21.1326 | 17.9007 | 17.9007 | 20.4511 | 159.5489 | 32.026 | 4.2202 | 4.2202 | 58.0928 | 62.313 | -1.8989 | 0% | 28.1779 | 0 | 0 | 127.4424 | 127.4424 | 0% | 12.28% | 12.28% | 80% | 9.822% | 2.7675 | 11.2586 | 6 | 16.6052 | 6.1202 | 13.03% | 13.03%
12 | 343 | 9 | 8220 | 12 | -2.2 | 119.44 | 123.33 | 242.77 | 123.33 | 61.67 | 343 | 8220 | 720 | 338.3014 | -22.7443 | 1.1857 | 694.284 | 11.5912 | 6.1326 | 20.2568 | 20.2568 | 6.0282 | 173.9718 | 25.2406 | 312.0377 | 312.0377 | 105.2687 | 417.3065 | 0.404 | 40.4% | 188.706 | 76.2376 | 53.3663 | 111.9377 | 111.9377 | 47.68% | 11.82% | 11.82% | 85% | 10.05% | 18.9581 | 11.0458 | 6 | 113.7487 | 41.9242 | 101.6% | 101.6%
12 | 343 | 9 | 8221 | 13 | -1.8 | 114.86 | 87.92 | 202.78 | 87.92 | 43.96 | 343 | 8221 | 780 | 338.3014 | -22.7443 | 1.1857 | 754.284 | 12.5912 | -8.8674 | 20.0167 | 20.0167 | 8.7024 | 188.7024 | 26.0015 | 301.5947 | 301.5947 | 75.0444 | 376.6391 | 0.36346 | 36.35% | 170.3162 | 61.9037 | 43.3326 | 109.7895 | 109.7895 | 39.47% | 11.86% | 11.86% | 85% | 10.08% | 17.169 | 10.9053 | 6 | 103.0141 | 37.9677 | 93.83% | 93.83%
12 | 343 | 9 | 8222 | 14 | -1.7 | 129.72 | 102.36 | 232.08 | 102.36 | 51.18 | 343 | 8222 | 840 | 338.3014 | -22.7443 | 1.1857 | 814.284 | 13.5912 | -23.8674 | 17.2075 | 17.2075 | 22.9945 | 202.9945 | 33.8013 | 364.3728 | 364.3728 | 87.3697 | 451.7425 | 0.43726 | 43.73% | 204.278 | 89.3216 | 62.5251 | 111.0876 | 111.0876 | 56.28% | 11.77% | 11.77% | 85% | 10% | 20.4329 | 10.8704 | 6 | 122.5974 | 45.1855 | 110.4% | 110.4%
12 | 343 | 9 | 8223 | 15 | -1.5 | 102.08 | 87.5 | 189.58 | 87.5 | 43.75 | 343 | 8223 | 900 | 338.3014 | -22.7443 | 1.1857 | 874.284 | 14.5912 | -38.8674 | 12.1231 | 12.1231 | 36.2937 | 216.2937 | 45.1127 | 343.024 | 343.024 | 74.6859 | 417.7099 | 0.40857 | 40.86% | 188.8884 | 77.1737 | 54.0216 | 107.9023 | 107.9023 | 50.07% | 11.8% | 0% | 85% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8224 | 16 | -1.9 | 71.58 | 44.17 | 115.75 | 44.17 | 22.09 | 343 | 8224 | 960 | 338.3014 | -22.7443 | 1.1857 | 934.284 | 15.5912 | -53.8674 | 5.2027 | 5.2027 | 48.4116 | 228.4116 | 57.89 | 0 | 0 | 37.7015 | 37.7015 | -3.6036 | 0% | 17.0486 | 0 | 0 | 145.4212 | 145.4212 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8225 | 17 | -2.5 | 9.03 | 17.5 | 26.53 | 17.5 | 8.75 | 343 | 8225 | 1020 | 338.3014 | -22.7443 | 1.1857 | 994.284 | 16.5912 | -68.8674 | -3.0973 | 0 | 55.629 | 235.629 | 66.472 | 0 | 0 | 14.9372 | 14.9372 | -10.4211 | 0% | 6.7546 | 0 | 0 | 137.1894 | 137.1894 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8226 | 18 | -2.8 | 0 | 0 | 0 | 0 | 0 | 343 | 8226 | 1080 | 338.3014 | -22.7443 | 1.1857 | 1054.284 | 17.5912 | -83.8674 | -12.3722 | 0 | 55.629 | 235.629 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.8081 | 131.8081 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8227 | 19 | -3.2 | 0 | 0 | 0 | 0 | 0 | 343 | 8227 | 1140 | 338.3014 | -22.7443 | 1.1857 | 1114.284 | 18.5912 | -98.8674 | -22.2772 | 0 | 55.629 | 235.629 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.165 | 128.165 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8228 | 20 | -4 | 0 | 0 | 0 | 0 | 0 | 343 | 8228 | 1200 | 338.3014 | -22.7443 | 1.1857 | 1174.284 | 19.5912 | -113.8674 | -32.4987 | 0 | 55.629 | 235.629 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.0711 | 123.0711 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8229 | 21 | -4.7 | 0 | 0 | 0 | 0 | 0 | 343 | 8229 | 1260 | 338.3014 | -22.7443 | 1.1857 | 1234.284 | 20.5912 | -128.8674 | -42.692 | 0 | 55.629 | 235.629 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.9801 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8230 | 22 | -5.9 | 0 | 0 | 0 | 0 | 0 | 343 | 8230 | 1320 | 338.3014 | -22.7443 | 1.1857 | 1294.284 | 21.5912 | -143.8674 | -52.3564 | 0 | 55.629 | 235.629 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.7063 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8231 | 23 | -6.4 | 0 | 0 | 0 | 0 | 0 | 343 | 8231 | 1380 | 338.3014 | -22.7443 | 1.1857 | 1354.284 | 22.5912 | -158.8674 | -60.5554 | 0 | 55.629 | 235.629 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.2922 | 0 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
12 | 343 | 9 | 8232 | 24 | -6.1 | 0 | 0 | 0 | 0 | 0 | 343 | 8232 | 1440 | 338.3014 | -22.7443 | 1.1857 | 1414.284 | 23.5912 | -173.8674 | -65.4628 | 0 | 55.629 | 235.629 | 66.472 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.659 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8233 | 1 | -7.2 | 0 | 0 | 0 | 0 | 0 | 344 | 8233 | 60 | 339.2877 | -22.8303 | 0.97485 | 34.284 | 0.58765 | 171.1853 | -65.0209 | 0 | 55.4885 | 124.5115 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.8046 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8234 | 2 | -7.9 | 0 | 0 | 0 | 0 | 0 | 344 | 8234 | 120 | 339.2877 | -22.8303 | 0.97485 | 94.284 | 1.5876 | 156.1853 | -59.3363 | 0 | 55.4885 | 124.5115 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.7618 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1693 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8235 | 3 | -7.9 | 0 | 0 | 0 | 0 | 0 | 344 | 8235 | 180 | 339.2877 | -22.8303 | 0.97485 | 154.284 | 2.5876 | 141.1853 | -50.7632 | 0 | 55.4885 | 124.5115 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.6522 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1693 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8236 | 4 | -8.1 | 0 | 0 | 0 | 0 | 0 | 344 | 8236 | 240 | 339.2877 | -22.8303 | 0.97485 | 214.284 | 3.5876 | 126.1853 | -40.9489 | 0 | 55.4885 | 124.5115 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.957 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.248 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8237 | 5 | -8.4 | 0 | 0 | 0 | 0 | 0 | 344 | 8237 | 300 | 339.2877 | -22.8303 | 0.97485 | 274.284 | 4.5876 | 111.1853 | -30.7197 | 0 | 55.4885 | 124.5115 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.0971 | 0 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3664 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8238 | 6 | -7.2 | 0 | 0 | 0 | 0 | 0 | 344 | 8238 | 360 | 339.2877 | -22.8303 | 0.97485 | 334.284 | 5.5876 | 96.1853 | -20.5329 | 0 | 55.4885 | 124.5115 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.851 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8239 | 7 | -7.8 | 0 | 0 | 0 | 0 | 0 | 344 | 8239 | 420 | 339.2877 | -22.8303 | 0.97485 | 394.284 | 6.5876 | 81.1853 | -10.7205 | 0 | 55.4885 | 124.5115 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.598 | 127.598 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8240 | 8 | -8.8 | 0 | 0 | 0 | 0 | 0 | 344 | 8240 | 480 | 339.2877 | -22.8303 | 0.97485 | 454.284 | 7.5876 | 66.1853 | -1.5978 | 0 | 55.4885 | 124.5115 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.7931 | 129.7931 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5254 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8241 | 9 | -7.8 | 0.56 | 3.61 | 4.17 | 3.61 | 1.81 | 344 | 8241 | 540 | 339.2877 | -22.8303 | 0.97485 | 514.284 | 8.5876 | 51.1853 | 6.4816 | 6.4816 | 46.2824 | 133.7176 | 55.5712 | 0 | 0 | 3.0813 | 3.0813 | -57.9769 | 0% | 1.3934 | 0 | 0 | 111.7443 | 111.7443 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.1301 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8242 | 10 | -4.6 | 3.69 | 24.92 | 28.61 | 24.92 | 12.46 | 344 | 8242 | 600 | 339.2877 | -22.8303 | 0.97485 | 574.284 | 9.5876 | 36.1853 | 13.1023 | 13.1023 | 33.9652 | 146.0348 | 42.989 | 11.9069 | 11.9069 | 21.2706 | 33.1775 | -4.4091 | 0% | 15.0029 | 0 | 0 | 120.148 | 120.148 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8243 | 11 | -2.9 | 31.75 | 67.22 | 98.97 | 67.22 | 33.61 | 344 | 8243 | 660 | 339.2877 | -22.8303 | 0.97485 | 634.284 | 10.5876 | 21.1853 | 17.805 | 17.805 | 20.4769 | 159.5231 | 32.1221 | 87.938 | 87.938 | 57.3759 | 145.3139 | -0.35676 | 0% | 65.7109 | 0 | 0 | 125.6978 | 125.6978 | 0% | 12.18% | 12.18% | 80% | 9.741% | 6.4011 | 11.2943 | 6 | 38.4064 | 14.1554 | 30.55% | 30.55%
12 | 344 | 10 | 8244 | 12 | 0.1 | 72.69 | 100.47 | 173.16 | 100.47 | 50.24 | 344 | 8244 | 720 | 339.2877 | -22.8303 | 0.97485 | 694.284 | 11.5876 | 6.1853 | 20.1673 | 20.1673 | 6.0726 | 173.9274 | 25.3361 | 190.561 | 190.561 | 85.7565 | 276.3175 | 0.22057 | 22.06% | 124.9508 | 27.561 | 19.2927 | 131.4483 | 131.4483 | 14.68% | 11.93% | 11.93% | 80% | 9.54% | 11.9205 | 10.2533 | 6 | 71.5228 | 26.3611 | 54.41% | 54.41%
12 | 344 | 10 | 8245 | 13 | 2 | 158.81 | 100.19 | 259 | 100.19 | 50.1 | 344 | 8245 | 780 | 339.2877 | -22.8303 | 0.97485 | 754.284 | 12.5876 | -8.8147 | 19.9367 | 19.9367 | 8.6407 | 188.6407 | 26.0651 | 418.3755 | 418.3755 | 85.5175 | 503.893 | 0.49333 | 49.33% | 227.8604 | 112.4096 | 78.6867 | 116.6746 | 116.6746 | 67.44% | 11.65% | 11.65% | 90% | 10.48% | 23.8812 | 9.6266 | 6 | 143.2873 | 52.8112 | 122.8% | 122.8%
12 | 344 | 10 | 8246 | 14 | 2.6 | 191.03 | 95.19 | 286.22 | 95.19 | 47.6 | 344 | 8246 | 840 | 339.2877 | -22.8303 | 0.97485 | 814.284 | 13.5876 | -23.8147 | 17.1393 | 17.1393 | 22.9198 | 202.9198 | 33.8252 | 538.5095 | 538.5095 | 81.2497 | 619.7592 | 0.55377 | 55.38% | 280.2551 | 155.1964 | 108.6375 | 118.5724 | 118.5724 | 91.62% | 11.52% | 11.52% | 90% | 10.37% | 29.0682 | 9.4339 | 6 | 174.4091 | 64.2817 | 147.1% | 147.1%
12 | 344 | 10 | 8247 | 15 | 4 | 131.47 | 101.11 | 232.58 | 101.11 | 50.56 | 344 | 8247 | 900 | 339.2877 | -22.8303 | 0.97485 | 874.284 | 14.5876 | -38.8147 | 12.0672 | 12.0672 | 36.2104 | 216.2104 | 45.1098 | 443.8243 | 443.8243 | 86.3028 | 530.1271 | 0.51786 | 51.79% | 239.7235 | 124.144 | 86.9008 | 116.2906 | 116.2906 | 74.73% | 11.59% | 0% | 90% | 0% | 0 | 8.9942 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8248 | 16 | 3.3 | 57.14 | 69.53 | 126.67 | 69.53 | 34.77 | 344 | 8248 | 960 | 339.2877 | -22.8303 | 0.97485 | 934.284 | 15.5876 | -53.8147 | 5.1582 | 5.1582 | 48.3231 | 228.3231 | 57.8698 | 0 | 0 | 59.3476 | 59.3476 | -1.7805 | 0% | 26.837 | 0 | 0 | 151.2089 | 151.2089 | 0% | 12.03% | 0% | 80% | 0% | 0 | 9.2124 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8249 | 17 | 2.5 | 5 | 23.14 | 28.14 | 23.14 | 11.57 | 344 | 8249 | 1020 | 339.2877 | -22.8303 | 0.97485 | 994.284 | 16.5876 | -68.8147 | -3.1323 | 0 | 55.4885 | 235.4885 | 66.3827 | 0 | 0 | 19.7512 | 19.7512 | -7.0602 | 0% | 8.9315 | 0 | 0 | 141.9521 | 141.9521 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8250 | 18 | 1.2 | 0 | 0 | 0 | 0 | 0 | 344 | 8250 | 1080 | 339.2877 | -22.8303 | 0.97485 | 1054.284 | 17.5876 | -83.8147 | -12.4 | 0 | 55.4885 | 235.4885 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.4908 | 135.4908 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8251 | 19 | 0.5 | 0 | 0 | 0 | 0 | 0 | 344 | 8251 | 1140 | 339.2877 | -22.8303 | 0.97485 | 1114.284 | 18.5876 | -98.8147 | -22.3003 | 0 | 55.4885 | 235.4885 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.6575 | 131.6575 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8252 | 20 | -1 | 0 | 0 | 0 | 0 | 0 | 344 | 8252 | 1200 | 339.2877 | -22.8303 | 0.97485 | 1174.284 | 19.5876 | -113.8147 | -32.5202 | 0 | 55.4885 | 235.4885 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.0173 | 126.0173 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8253 | 21 | -2.3 | 0 | 0 | 0 | 0 | 0 | 344 | 8253 | 1260 | 339.2877 | -22.8303 | 0.97485 | 1234.284 | 20.5876 | -128.8147 | -42.7159 | 0 | 55.4885 | 235.4885 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.8511 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8254 | 22 | -2.3 | 0 | 0 | 0 | 0 | 0 | 344 | 8254 | 1320 | 339.2877 | -22.8303 | 0.97485 | 1294.284 | 21.5876 | -143.8147 | -52.3888 | 0 | 55.4885 | 235.4885 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.6659 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8255 | 23 | -3.3 | 0 | 0 | 0 | 0 | 0 | 344 | 8255 | 1380 | 339.2877 | -22.8303 | 0.97485 | 1354.284 | 22.5876 | -158.8147 | -60.6053 | 0 | 55.4885 | 235.4885 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.0803 | 0 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
12 | 344 | 10 | 8256 | 24 | -4 | 0 | 0 | 0 | 0 | 0 | 344 | 8256 | 1440 | 339.2877 | -22.8303 | 0.97485 | 1414.284 | 23.5876 | -173.8147 | -65.5388 | 0 | 55.4885 | 235.4885 | 66.3827 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.0375 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8257 | 1 | -4.6 | 0 | 0 | 0 | 0 | 0 | 345 | 8257 | 60 | 340.274 | -22.9089 | 0.75974 | 34.284 | 0.58406 | 171.2391 | -65.1092 | 0 | 55.3602 | 124.6398 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.3623 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8258 | 2 | -5 | 0 | 0 | 0 | 0 | 0 | 345 | 8258 | 120 | 340.274 | -22.9089 | 0.75974 | 94.284 | 1.5841 | 156.2391 | -59.4292 | 0 | 55.3602 | 124.6398 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.848 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8259 | 3 | -5.1 | 0 | 0 | 0 | 0 | 0 | 345 | 8259 | 180 | 340.274 | -22.9089 | 0.75974 | 154.284 | 2.5841 | 141.2391 | -50.8545 | 0 | 55.3602 | 124.6398 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.8766 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8260 | 4 | -4.7 | 0 | 0 | 0 | 0 | 0 | 345 | 8260 | 240 | 340.274 | -22.9089 | 0.75974 | 214.284 | 3.5841 | 126.2391 | -41.0387 | 0 | 55.3602 | 124.6398 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.267 | 0 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9492 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8261 | 5 | -5.4 | 0 | 0 | 0 | 0 | 0 | 345 | 8261 | 300 | 340.274 | -22.9089 | 0.75974 | 274.284 | 4.5841 | 111.2391 | -30.809 | 0 | 55.3602 | 124.6398 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.922 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8262 | 6 | -5.2 | 0 | 0 | 0 | 0 | 0 | 345 | 8262 | 360 | 340.274 | -22.9089 | 0.75974 | 334.284 | 5.5841 | 96.2391 | -20.6229 | 0 | 55.3602 | 124.6398 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0312 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8263 | 7 | -5.3 | 0 | 0 | 0 | 0 | 0 | 345 | 8263 | 420 | 340.274 | -22.9089 | 0.75974 | 394.284 | 6.5841 | 81.2391 | -10.8116 | 0 | 55.3602 | 124.6398 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.0179 | 128.0179 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.1725 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8264 | 8 | -5.2 | 0 | 0 | 0 | 0 | 0 | 345 | 8264 | 480 | 340.274 | -22.9089 | 0.75974 | 454.284 | 7.5841 | 66.2391 | -1.6901 | 0 | 55.3602 | 124.6398 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.4885 | 130.4885 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8265 | 9 | -5 | 0.08 | 3.61 | 3.69 | 3.61 | 1.81 | 345 | 8265 | 540 | 340.274 | -22.9089 | 0.75974 | 514.284 | 8.5841 | 51.2391 | 6.3887 | 6.3887 | 46.282 | 133.718 | 55.6438 | 0 | 0 | 3.0813 | 3.0813 | -55.6554 | 0% | 1.3934 | 0 | 0 | 110.4289 | 110.4289 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8266 | 10 | -4.4 | 4.44 | 32.5 | 36.94 | 32.5 | 16.25 | 345 | 8266 | 600 | 340.274 | -22.9089 | 0.75974 | 574.284 | 9.5841 | 36.2391 | 13.0102 | 13.0102 | 33.978 | 146.022 | 43.0713 | 14.4073 | 14.4073 | 27.7405 | 42.1478 | -3.2876 | 0% | 19.0592 | 0 | 0 | 113.3113 | 113.3113 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8267 | 11 | -1.7 | 13.14 | 73.61 | 86.75 | 73.61 | 36.81 | 345 | 8267 | 660 | 340.274 | -22.9089 | 0.75974 | 634.284 | 10.5841 | 21.2391 | 17.7163 | 17.7163 | 20.5057 | 159.4943 | 32.2134 | 36.5336 | 36.5336 | 62.8301 | 99.3637 | -0.86335 | 0% | 44.9323 | 0 | 0 | 118.3846 | 118.3846 | 0% | 12.19% | 12.19% | 80% | 9.751% | 4.3812 | 10.8704 | 6 | 26.2869 | 9.6885 | 22.2% | 22.2%
12 | 345 | 11 | 8268 | 12 | 0.1 | 56.67 | 88.25 | 144.92 | 88.25 | 44.13 | 345 | 8268 | 720 | 340.274 | -22.9089 | 0.75974 | 694.284 | 11.5841 | 6.2391 | 20.085 | 20.085 | 6.1186 | 173.8814 | 25.4246 | 149.0372 | 149.0372 | 75.3261 | 224.3633 | 0.085475 | 8.547% | 101.4571 | 8.672 | 6.0704 | 121.4778 | 121.4778 | 4.997% | 11.98% | 11.98% | 80% | 9.586% | 9.7253 | 10.2533 | 6 | 58.3518 | 21.5066 | 48.03% | 48.03%
12 | 345 | 11 | 8269 | 13 | 2.3 | 32.58 | 98.97 | 131.55 | 98.97 | 49.49 | 345 | 8269 | 780 | 340.274 | -22.9089 | 0.75974 | 754.284 | 12.5841 | -8.7609 | 19.8641 | 19.8641 | 8.5791 | 188.5791 | 26.1216 | 86.0893 | 86.0893 | 84.4762 | 170.5654 | -0.10952 | 0% | 77.1297 | 0 | 0 | 123.4969 | 123.4969 | 0% | 11.96% | 11.96% | 80% | 9.572% | 7.3827 | 9.53 | 6 | 44.2962 | 16.3262 | 35.87% | 35.87%
12 | 345 | 11 | 8270 | 14 | 2.3 | 10.08 | 85.92 | 96 | 85.92 | 42.96 | 345 | 8270 | 840 | 340.274 | -22.9089 | 0.75974 | 814.284 | 13.5841 | -23.7609 | 17.0784 | 17.0784 | 22.8464 | 202.8464 | 33.8435 | 28.5075 | 28.5075 | 73.3373 | 101.8448 | -0.72592 | 0% | 46.0542 | 0 | 0 | 121.3367 | 121.3367 | 0% | 12.03% | 12.03% | 80% | 9.625% | 4.4329 | 9.53 | 6 | 26.5972 | 9.8029 | 21.92% | 21.92%
12 | 345 | 11 | 8271 | 15 | 2.8 | 13.33 | 74.81 | 88.14 | 74.81 | 37.41 | 345 | 8271 | 900 | 340.274 | -22.9089 | 0.75974 | 874.284 | 14.5841 | -38.7609 | 12.0183 | 12.0183 | 36.1297 | 216.1297 | 45.1027 | 45.186 | 45.186 | 63.8543 | 109.0403 | -0.61379 | 0% | 49.308 | 0 | 0 | 141.3718 | 141.3718 | 0% | 12.01% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8272 | 16 | 2.9 | 15.56 | 50.14 | 65.7 | 50.14 | 25.07 | 345 | 8272 | 960 | 340.274 | -22.9089 | 0.75974 | 934.284 | 15.5841 | -53.7609 | 5.1203 | 5.1203 | 48.2379 | 228.2379 | 57.8466 | 0 | 0 | 42.7972 | 42.7972 | -2.8026 | 0% | 19.3529 | 0 | 0 | 139.8746 | 139.8746 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.3386 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8273 | 17 | 1.4 | 0.69 | 18.89 | 19.58 | 18.89 | 9.45 | 345 | 8273 | 1020 | 340.274 | -22.9089 | 0.75974 | 994.284 | 16.5841 | -68.7609 | -3.1611 | 0 | 55.3602 | 235.3602 | 66.3011 | 0 | 0 | 16.1236 | 16.1236 | -8.9962 | 0% | 7.2911 | 0 | 0 | 133.9225 | 133.9225 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8274 | 18 | 0.7 | 0 | 0 | 0 | 0 | 0 | 345 | 8274 | 1080 | 340.274 | -22.9089 | 0.75974 | 1054.284 | 17.5841 | -83.7609 | -12.4217 | 0 | 55.3602 | 235.3602 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.5391 | 130.5391 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8275 | 19 | -0.1 | 0 | 0 | 0 | 0 | 0 | 345 | 8275 | 1140 | 340.274 | -22.9089 | 0.75974 | 1114.284 | 18.5841 | -98.7609 | -22.3176 | 0 | 55.3602 | 235.3602 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.9551 | 127.9551 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8276 | 20 | -1.8 | 0 | 0 | 0 | 0 | 0 | 345 | 8276 | 1200 | 340.274 | -22.9089 | 0.75974 | 1174.284 | 19.5841 | -113.7609 | -32.5359 | 0 | 55.3602 | 235.3602 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.4464 | 123.4464 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8277 | 21 | -2.3 | 0 | 0 | 0 | 0 | 0 | 345 | 8277 | 1260 | 340.274 | -22.9089 | 0.75974 | 1234.284 | 20.5841 | -128.7609 | -42.7339 | 0 | 55.3602 | 235.3602 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.7896 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8278 | 22 | -3 | 0 | 0 | 0 | 0 | 0 | 345 | 8278 | 1320 | 340.274 | -22.9089 | 0.75974 | 1294.284 | 21.5841 | -143.7609 | -52.4147 | 0 | 55.3602 | 235.3602 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2954 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8279 | 23 | -3.5 | 0 | 0 | 0 | 0 | 0 | 345 | 8279 | 1380 | 340.274 | -22.9089 | 0.75974 | 1354.284 | 22.5841 | -158.7609 | -60.6481 | 0 | 55.3602 | 235.3602 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.9335 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
12 | 345 | 11 | 8280 | 24 | -3.6 | 0 | 0 | 0 | 0 | 0 | 345 | 8280 | 1440 | 340.274 | -22.9089 | 0.75974 | 1414.284 | 23.5841 | -173.7609 | -65.6072 | 0 | 55.3602 | 235.3602 | 66.3011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.9621 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8281 | 1 | -3.8 | 0 | 0 | 0 | 0 | 0 | 346 | 8281 | 60 | 341.2603 | -22.9799 | 0.54076 | 34.284 | 0.58041 | 171.2938 | -65.1906 | 0 | 55.244 | 124.756 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.8824 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8282 | 2 | -4.1 | 0 | 0 | 0 | 0 | 0 | 346 | 8282 | 120 | 341.2603 | -22.9799 | 0.54076 | 94.284 | 1.5804 | 156.2938 | -59.5162 | 0 | 55.244 | 124.756 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.2633 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8283 | 3 | -4 | 0 | 0 | 0 | 0 | 0 | 346 | 8283 | 180 | 341.2603 | -22.9799 | 0.54076 | 154.284 | 2.5804 | 141.2938 | -50.9409 | 0 | 55.244 | 124.756 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.0346 | 0 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.6918 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8284 | 4 | -3.4 | 0 | 0 | 0 | 0 | 0 | 346 | 8284 | 240 | 341.2603 | -22.9799 | 0.54076 | 214.284 | 3.5804 | 126.2938 | -41.124 | 0 | 55.244 | 124.756 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.1202 | 0 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4739 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8285 | 5 | -3.5 | 0 | 0 | 0 | 0 | 0 | 346 | 8285 | 300 | 341.2603 | -22.9799 | 0.54076 | 274.284 | 4.5804 | 111.2938 | -30.8941 | 0 | 55.244 | 124.756 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0948 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8286 | 6 | -3.7 | 0 | 0 | 0 | 0 | 0 | 346 | 8286 | 360 | 341.2603 | -22.9799 | 0.54076 | 334.284 | 5.5804 | 96.2938 | -20.7083 | 0 | 55.244 | 124.756 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6358 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8287 | 7 | -3.9 | 0 | 0 | 0 | 0 | 0 | 346 | 8287 | 420 | 341.2603 | -22.9799 | 0.54076 | 394.284 | 6.5804 | 81.2938 | -10.8979 | 0 | 55.244 | 124.756 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.4044 | 125.4044 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8288 | 8 | -3.7 | 0 | 0 | 0 | 0 | 0 | 346 | 8288 | 480 | 341.2603 | -22.9799 | 0.54076 | 454.284 | 7.5804 | 66.2938 | -1.7771 | 0 | 55.244 | 124.756 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.1417 | 127.1417 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8289 | 9 | -3.1 | 0 | 3.19 | 3.19 | 3.19 | 1.6 | 346 | 8289 | 540 | 341.2603 | -22.9799 | 0.54076 | 514.284 | 8.5804 | 51.2938 | 6.3017 | 6.3017 | 46.2863 | 133.7137 | 55.7149 | 0 | 0 | 2.7228 | 2.7228 | -61.3282 | 0% | 1.2313 | 0 | 0 | 107.4044 | 107.4044 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8290 | 10 | -2.1 | 0.28 | 27.5 | 27.78 | 27.5 | 13.75 | 346 | 8290 | 600 | 341.2603 | -22.9799 | 0.54076 | 574.284 | 9.5804 | 36.2938 | 12.9246 | 12.9246 | 33.9948 | 146.0052 | 43.1505 | 0.9133 | 0.9133 | 23.4727 | 24.386 | -6.0307 | 0% | 11.0274 | 0 | 0 | 109.9128 | 109.9128 | 0% | 12.29% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8291 | 11 | -1.3 | 0.47 | 58.61 | 59.08 | 58.61 | 29.31 | 346 | 8291 | 660 | 341.2603 | -22.9799 | 0.54076 | 634.284 | 10.5804 | 21.2938 | 17.6346 | 17.6346 | 20.5373 | 159.4627 | 32.2998 | 1.3114 | 1.3114 | 50.0268 | 51.3381 | -2.4037 | 0% | 23.2151 | 0 | 0 | 111.6056 | 111.6056 | 0% | 12.23% | 12.23% | 80% | 9.783% | 2.2712 | 10.7313 | 6 | 13.6271 | 5.0225 | 12.21% | 12.21%
12 | 346 | 12 | 8292 | 12 | -0.3 | 0.64 | 82.86 | 83.5 | 82.86 | 41.43 | 346 | 8292 | 720 | 341.2603 | -22.9799 | 0.54076 | 694.284 | 11.5804 | 6.2938 | 20.0102 | 20.0102 | 6.1661 | 173.8339 | 25.5062 | 1.688 | 1.688 | 70.7254 | 72.4135 | -1.4359 | 0% | 32.7454 | 0 | 0 | 112.7273 | 112.7273 | 0% | 12.16% | 12.16% | 80% | 9.731% | 3.1866 | 10.3885 | 6 | 19.1197 | 7.0469 | 16.96% | 16.96%
12 | 346 | 12 | 8293 | 13 | 0.1 | 0.97 | 129.58 | 130.55 | 129.58 | 64.79 | 346 | 8293 | 780 | 341.2603 | -22.9799 | 0.54076 | 754.284 | 12.5804 | -8.7062 | 19.7991 | 19.7991 | 8.5175 | 188.5175 | 26.1709 | 2.5701 | 2.5701 | 110.6034 | 113.1736 | -0.62046 | 0% | 51.1771 | 0 | 0 | 115.3122 | 115.3122 | 0% | 12.1% | 12.1% | 80% | 9.683% | 4.9555 | 10.2533 | 6 | 29.7328 | 10.9586 | 25.78% | 25.78%
12 | 346 | 12 | 8294 | 14 | 0 | 1.39 | 101.11 | 102.5 | 101.11 | 50.56 | 346 | 8294 | 840 | 341.2603 | -22.9799 | 0.54076 | 814.284 | 13.5804 | -23.7062 | 17.0249 | 17.0249 | 22.7745 | 202.7745 | 33.8562 | 3.9425 | 3.9425 | 86.3028 | 90.2453 | -0.9851 | 0% | 40.8089 | 0 | 0 | 113.6059 | 113.6059 | 0% | 12.13% | 12.13% | 80% | 9.706% | 3.961 | 10.287 | 6 | 23.7659 | 8.7594 | 20.92% | 20.92%
12 | 346 | 12 | 8295 | 15 | -0.1 | 1.11 | 62.69 | 63.8 | 62.69 | 31.35 | 346 | 8295 | 900 | 341.2603 | -22.9799 | 0.54076 | 874.284 | 14.5804 | -38.7062 | 11.9765 | 11.9765 | 36.0515 | 216.0515 | 45.0916 | 3.7764 | 3.7764 | 53.5093 | 57.2856 | -2.0188 | 0% | 25.9046 | 0 | 0 | 132.05 | 132.05 | 0% | 12.17% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8296 | 16 | -0.2 | 0.28 | 39.72 | 40 | 39.72 | 19.86 | 346 | 8296 | 960 | 341.2603 | -22.9799 | 0.54076 | 934.284 | 15.5804 | -53.7062 | 5.0891 | 5.0891 | 48.1562 | 228.1562 | 57.8203 | 0 | 0 | 33.9031 | 33.9031 | -3.9729 | 0% | 15.331 | 0 | 0 | 130.3295 | 130.3295 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8297 | 17 | -0.1 | 0.19 | 17.97 | 18.16 | 17.97 | 8.99 | 346 | 8297 | 1020 | 341.2603 | -22.9799 | 0.54076 | 994.284 | 16.5804 | -68.7062 | -3.1835 | 0 | 55.244 | 235.244 | 66.2273 | 0 | 0 | 15.3384 | 15.3384 | -9.7385 | 0% | 6.936 | 0 | 0 | 128.9382 | 128.9382 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8298 | 18 | -0.1 | 0 | 0 | 0 | 0 | 0 | 346 | 8298 | 1080 | 341.2603 | -22.9799 | 0.54076 | 1054.284 | 17.5804 | -83.7062 | -12.4375 | 0 | 55.244 | 235.244 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.4018 | 127.4018 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8299 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 8299 | 1140 | 341.2603 | -22.9799 | 0.54076 | 1114.284 | 18.5804 | -98.7062 | -22.3292 | 0 | 55.244 | 235.244 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.6417 | 126.6417 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8300 | 20 | 0.3 | 0 | 0 | 0 | 0 | 0 | 346 | 8300 | 1200 | 341.2603 | -22.9799 | 0.54076 | 1174.284 | 19.5804 | -113.7062 | -32.5459 | 0 | 55.244 | 235.244 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.7525 | 125.7525 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8301 | 21 | 0.2 | 0 | 0 | 0 | 0 | 0 | 346 | 8301 | 1260 | 341.2603 | -22.9799 | 0.54076 | 1234.284 | 20.5804 | -128.7062 | -42.746 | 0 | 55.244 | 235.244 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7223 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8302 | 22 | 0.1 | 0 | 0 | 0 | 0 | 0 | 346 | 8302 | 1320 | 341.2603 | -22.9799 | 0.54076 | 1294.284 | 21.5804 | -143.7062 | -52.4343 | 0 | 55.244 | 235.244 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1677 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8303 | 23 | 0.2 | 0 | 0 | 0 | 0 | 0 | 346 | 8303 | 1380 | 341.2603 | -22.9799 | 0.54076 | 1354.284 | 22.5804 | -158.7062 | -60.6838 | 0 | 55.244 | 235.244 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.939 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
12 | 346 | 12 | 8304 | 24 | 0.4 | 0 | 0 | 0 | 0 | 0 | 346 | 8304 | 1440 | 341.2603 | -22.9799 | 0.54076 | 1414.284 | 23.5804 | -173.7062 | -65.668 | 0 | 55.244 | 235.244 | 66.2273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.558 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8305 | 1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 347 | 8305 | 60 | 342.2466 | -23.0435 | 0.31827 | 34.284 | 0.5767 | 171.3494 | -65.2648 | 0 | 55.1399 | 124.8601 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4996 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8306 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 347 | 8306 | 120 | 342.2466 | -23.0435 | 0.31827 | 94.284 | 1.5767 | 156.3494 | -59.5974 | 0 | 55.1399 | 124.8601 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3944 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8307 | 3 | 0.5 | 0 | 0 | 0 | 0 | 0 | 347 | 8307 | 180 | 342.2466 | -23.0435 | 0.31827 | 154.284 | 2.5767 | 141.3494 | -51.0223 | 0 | 55.1399 | 124.8601 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4416 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8308 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 347 | 8308 | 240 | 342.2466 | -23.0435 | 0.31827 | 214.284 | 3.5767 | 126.3494 | -41.2048 | 0 | 55.1399 | 124.8601 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4416 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8309 | 5 | 0.6 | 0 | 0 | 0 | 0 | 0 | 347 | 8309 | 300 | 342.2466 | -23.0435 | 0.31827 | 274.284 | 4.5767 | 111.3494 | -30.9746 | 0 | 55.1399 | 124.8601 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.5905 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8310 | 6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 347 | 8310 | 360 | 342.2466 | -23.0435 | 0.31827 | 334.284 | 5.5767 | 96.3494 | -20.7892 | 0 | 55.1399 | 124.8601 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.6881 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8311 | 7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 347 | 8311 | 420 | 342.2466 | -23.0435 | 0.31827 | 394.284 | 6.5767 | 81.3494 | -10.9792 | 0 | 55.1399 | 124.8601 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.1057 | 136.1057 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8312 | 8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 347 | 8312 | 480 | 342.2466 | -23.0435 | 0.31827 | 454.284 | 7.5767 | 66.3494 | -1.8587 | 0 | 55.1399 | 124.8601 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.1262 | 139.1262 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8313 | 9 | 0.8 | 0 | 1.94 | 1.94 | 1.94 | 0.97 | 347 | 8313 | 540 | 342.2466 | -23.0435 | 0.31827 | 514.284 | 8.5767 | 51.3494 | 6.2205 | 6.2205 | 46.2953 | 133.7047 | 55.7842 | 0 | 0 | 1.6559 | 1.6559 | -95.5105 | 0% | 0.7488 | 0 | 0 | 118.8517 | 118.8517 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8314 | 10 | 1.1 | 0.28 | 22.42 | 22.7 | 22.42 | 11.21 | 347 | 8314 | 600 | 342.2466 | -23.0435 | 0.31827 | 574.284 | 9.5767 | 36.3494 | 12.8455 | 12.8455 | 34.0154 | 145.9846 | 43.2267 | 0.91768 | 0.91768 | 19.1367 | 20.0543 | -7.112 | 0% | 9.0686 | 0 | 0 | 121.3758 | 121.3758 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8315 | 11 | 1.9 | 1.39 | 66.53 | 67.92 | 66.53 | 33.27 | 347 | 8315 | 660 | 342.2466 | -23.0435 | 0.31827 | 634.284 | 10.5767 | 21.3494 | 17.5598 | 17.5598 | 20.5717 | 159.4283 | 32.3812 | 3.8908 | 3.8908 | 56.7869 | 60.6777 | -1.78 | 0% | 27.4385 | 0 | 0 | 123.7701 | 123.7701 | 0% | 12.09% | 12.09% | 80% | 9.67% | 2.6534 | 9.659 | 6 | 15.9204 | 5.8678 | 12.86% | 12.86%
12 | 347 | 13 | 8316 | 12 | 1.7 | 51.58 | 86.58 | 138.16 | 86.58 | 43.29 | 347 | 8316 | 720 | 342.2466 | -23.0435 | 0.31827 | 694.284 | 11.5767 | 6.3494 | 19.9427 | 19.9427 | 6.215 | 173.785 | 25.5807 | 136.4019 | 136.4019 | 73.9007 | 210.3026 | 0.056127 | 5.613% | 95.0988 | 5.3376 | 3.7363 | 124.7506 | 124.7506 | 2.995% | 11.95% | 11.95% | 80% | 9.556% | 9.088 | 9.7239 | 6 | 54.5283 | 20.0974 | 43.71% | 43.71%
12 | 347 | 13 | 8317 | 13 | 1.7 | 108.47 | 101.81 | 210.28 | 101.81 | 50.91 | 347 | 8317 | 780 | 342.2466 | -23.0435 | 0.31827 | 754.284 | 12.5767 | -8.6506 | 19.7415 | 19.7415 | 8.456 | 188.456 | 26.2132 | 288.103 | 288.103 | 86.9003 | 375.0032 | 0.38459 | 38.46% | 169.5765 | 65.2177 | 45.6524 | 106.5597 | 106.5597 | 42.84% | 11.78% | 11.78% | 85% | 10.01% | 16.9793 | 9.7239 | 6 | 101.8761 | 37.5483 | 95.6% | 95.6%
12 | 347 | 13 | 8318 | 14 | 1.8 | 82.78 | 112.08 | 194.86 | 112.08 | 56.04 | 347 | 8318 | 840 | 342.2466 | -23.0435 | 0.31827 | 814.284 | 13.5767 | -23.6506 | 16.9787 | 16.9787 | 22.7041 | 202.7041 | 33.8634 | 235.3904 | 235.3904 | 95.6663 | 331.0567 | 0.32966 | 32.97% | 149.7038 | 49.3507 | 34.5455 | 126.7859 | 126.7859 | 27.25% | 11.82% | 11.82% | 85% | 10.05% | 15.0425 | 9.6914 | 6 | 90.2552 | 33.2652 | 71.19% | 71.19%
12 | 347 | 13 | 8319 | 15 | 1.8 | 89.08 | 86.47 | 175.55 | 86.47 | 43.24 | 347 | 8319 | 900 | 342.2466 | -23.0435 | 0.31827 | 874.284 | 14.5767 | -38.6506 | 11.9417 | 11.9417 | 35.976 | 215.976 | 45.0764 | 304.0113 | 304.0113 | 73.8068 | 377.8181 | 0.38836 | 38.84% | 170.8493 | 66.3516 | 46.4461 | 103.6664 | 103.6664 | 44.8% | 11.77% | 0% | 85% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8320 | 16 | 1.6 | 16.58 | 52.31 | 68.89 | 52.31 | 26.16 | 347 | 8320 | 960 | 342.2466 | -23.0435 | 0.31827 | 934.284 | 15.5767 | -53.6506 | 5.0645 | 5.0645 | 48.0781 | 228.0781 | 57.7911 | 0 | 0 | 44.6494 | 44.6494 | -2.724 | 0% | 20.1904 | 0 | 0 | 139.0463 | 139.0463 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8321 | 17 | 1.5 | 4.36 | 16.94 | 21.3 | 16.94 | 8.47 | 347 | 8321 | 1020 | 342.2466 | -23.0435 | 0.31827 | 994.284 | 16.5767 | -68.6506 | -3.1997 | 0 | 55.1399 | 235.1399 | 66.1612 | 0 | 0 | 14.4592 | 14.4592 | -10.1073 | 0% | 6.5384 | 0 | 0 | 134.9753 | 134.9753 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8322 | 18 | 1.2 | 0 | 0 | 0 | 0 | 0 | 347 | 8322 | 1080 | 342.2466 | -23.0435 | 0.31827 | 1054.284 | 17.5767 | -83.6506 | -12.4474 | 0 | 55.1399 | 235.1399 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.1708 | 131.1708 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8323 | 19 | 1.1 | 0 | 0 | 0 | 0 | 0 | 347 | 8323 | 1140 | 342.2466 | -23.0435 | 0.31827 | 1114.284 | 18.5767 | -98.6506 | -22.335 | 0 | 55.1399 | 235.1399 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.9179 | 128.9179 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8324 | 20 | 1.2 | 0 | 0 | 0 | 0 | 0 | 347 | 8324 | 1200 | 342.2466 | -23.0435 | 0.31827 | 1174.284 | 19.5767 | -113.6506 | -32.5503 | 0 | 55.1399 | 235.1399 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.4107 | 126.4107 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8325 | 21 | 1.1 | 0 | 0 | 0 | 0 | 0 | 347 | 8325 | 1260 | 342.2466 | -23.0435 | 0.31827 | 1234.284 | 20.5767 | -128.6506 | -42.7523 | 0 | 55.1399 | 235.1399 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.4266 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8326 | 22 | 0.7 | 0 | 0 | 0 | 0 | 0 | 347 | 8326 | 1320 | 342.2466 | -23.0435 | 0.31827 | 1294.284 | 21.5767 | -143.6506 | -52.4477 | 0 | 55.1399 | 235.1399 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6627 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8327 | 23 | 0.3 | 0 | 0 | 0 | 0 | 0 | 347 | 8327 | 1380 | 342.2466 | -23.0435 | 0.31827 | 1354.284 | 22.5767 | -158.6506 | -60.7124 | 0 | 55.1399 | 235.1399 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.1671 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 347 | 13 | 8328 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 8328 | 1440 | 342.2466 | -23.0435 | 0.31827 | 1414.284 | 23.5767 | -173.6506 | -65.7211 | 0 | 55.1399 | 235.1399 | 66.1612 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5191 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8329 | 1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 348 | 8329 | 60 | 343.2329 | -23.0996 | 0.092669 | 34.284 | 0.57294 | 171.4058 | -65.3319 | 0 | 55.048 | 124.952 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.0137 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8330 | 2 | 0.3 | 0 | 0 | 0 | 0 | 0 | 348 | 8330 | 120 | 343.2329 | -23.0996 | 0.092669 | 94.284 | 1.5729 | 156.4058 | -59.6726 | 0 | 55.048 | 124.952 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7709 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8331 | 3 | -0.3 | 0 | 0 | 0 | 0 | 0 | 348 | 8331 | 180 | 343.2329 | -23.0996 | 0.092669 | 154.284 | 2.5729 | 141.4058 | -51.0987 | 0 | 55.048 | 124.952 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4425 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8332 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 8332 | 240 | 343.2329 | -23.0996 | 0.092669 | 214.284 | 3.5729 | 126.4058 | -41.2809 | 0 | 55.048 | 124.952 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9853 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8333 | 5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 348 | 8333 | 300 | 343.2329 | -23.0996 | 0.092669 | 274.284 | 4.5729 | 111.4058 | -31.0507 | 0 | 55.048 | 124.952 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.1114 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8334 | 6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 348 | 8334 | 360 | 343.2329 | -23.0996 | 0.092669 | 334.284 | 5.5729 | 96.4058 | -20.8654 | 0 | 55.048 | 124.952 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -8.554 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8335 | 7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 348 | 8335 | 420 | 343.2329 | -23.0996 | 0.092669 | 394.284 | 6.5729 | 81.4058 | -11.0556 | 0 | 55.048 | 124.952 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.3421 | 146.3421 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8336 | 8 | 0.4 | 0 | 0 | 0 | 0 | 0 | 348 | 8336 | 480 | 343.2329 | -23.0996 | 0.092669 | 454.284 | 7.5729 | 66.4058 | -1.9349 | 0 | 55.048 | 124.952 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 150.7128 | 150.7128 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8337 | 9 | 0.2 | 0.28 | 3.89 | 4.17 | 3.89 | 1.95 | 348 | 8337 | 540 | 343.2329 | -23.0996 | 0.092669 | 514.284 | 8.5729 | 51.4058 | 6.1454 | 6.1454 | 46.309 | 133.691 | 55.8517 | 0 | 0 | 3.3203 | 3.3203 | -47.6744 | 0% | 1.5014 | 0 | 0 | 130.7018 | 130.7018 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8338 | 10 | 0.4 | 15 | 40.92 | 55.92 | 40.92 | 20.46 | 348 | 8338 | 600 | 343.2329 | -23.0996 | 0.092669 | 574.284 | 9.5729 | 36.4058 | 12.7729 | 12.7729 | 34.0398 | 145.9602 | 43.2997 | 49.3769 | 49.3769 | 34.9274 | 84.3043 | -1.0995 | 0% | 38.1224 | 0 | 0 | 135.0728 | 135.0728 | 0% | 12.12% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8339 | 11 | 0.5 | 69.25 | 85.83 | 155.08 | 85.83 | 42.92 | 348 | 8339 | 660 | 343.2329 | -23.0996 | 0.092669 | 634.284 | 10.5729 | 21.4058 | 17.4921 | 17.4921 | 20.6089 | 159.3911 | 32.4576 | 194.4021 | 194.4021 | 73.2605 | 267.6626 | 0.20539 | 20.54% | 121.037 | 24.8602 | 17.4021 | 137.6692 | 137.6692 | 12.64% | 11.92% | 11.92% | 80% | 9.538% | 11.5449 | 10.1193 | 6 | 69.2696 | 25.5306 | 50.32% | 50.32%
12 | 348 | 14 | 8340 | 12 | 0.7 | 114.81 | 101.75 | 216.56 | 101.75 | 50.88 | 348 | 8340 | 720 | 343.2329 | -23.0996 | 0.092669 | 694.284 | 11.5729 | 6.4058 | 19.8826 | 19.8826 | 6.2652 | 173.7348 | 25.6482 | 304.3201 | 304.3201 | 86.8491 | 391.1692 | 0.39565 | 39.57% | 176.8867 | 69.9859 | 48.9901 | 114.7521 | 114.7521 | 42.69% | 11.79% | 11.79% | 85% | 10.02% | 17.7206 | 10.0527 | 6 | 106.3239 | 39.1876 | 92.66% | 92.66%
12 | 348 | 14 | 8341 | 13 | 0.8 | 165.92 | 96.75 | 262.67 | 96.75 | 48.38 | 348 | 8341 | 780 | 343.2329 | -23.0996 | 0.092669 | 754.284 | 12.5729 | -8.5942 | 19.6914 | 19.6914 | 8.3947 | 188.3947 | 26.2483 | 441.6361 | 441.6361 | 82.5813 | 524.2174 | 0.49976 | 49.98% | 237.0511 | 118.4693 | 82.9285 | 115.336 | 115.336 | 71.9% | 11.64% | 11.64% | 90% | 10.48% | 24.8404 | 10.0195 | 6 | 149.0422 | 54.9322 | 129.2% | 129.2%
12 | 348 | 14 | 8342 | 14 | 0.7 | 172.42 | 79.92 | 252.34 | 79.92 | 39.96 | 348 | 8342 | 840 | 343.2329 | -23.0996 | 0.092669 | 814.284 | 13.5729 | -23.5942 | 16.9399 | 16.9399 | 22.6353 | 202.6353 | 33.8651 | 491.3687 | 491.3687 | 68.216 | 559.5846 | 0.51855 | 51.86% | 253.0442 | 131.2165 | 91.8515 | 113.806 | 113.806 | 80.71% | 11.61% | 11.61% | 90% | 10.45% | 26.4342 | 10.0527 | 6 | 158.6053 | 58.4569 | 139.4% | 139.4%
12 | 348 | 14 | 8343 | 15 | 1.6 | 76.75 | 80.56 | 157.31 | 80.56 | 40.28 | 348 | 8343 | 900 | 343.2329 | -23.0996 | 0.092669 | 874.284 | 14.5729 | -38.5942 | 11.914 | 11.914 | 35.9033 | 215.9033 | 45.0571 | 262.6215 | 262.6215 | 68.7623 | 331.3837 | 0.32865 | 32.86% | 149.8517 | 49.2483 | 34.4738 | 107.9974 | 107.9974 | 31.92% | 11.83% | 0% | 85% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8344 | 16 | 1.6 | 48.53 | 45.08 | 93.61 | 45.08 | 22.54 | 348 | 8344 | 960 | 343.2329 | -23.0996 | 0.092669 | 934.284 | 15.5729 | -53.5942 | 5.0466 | 5.0466 | 48.0036 | 228.0036 | 57.759 | 0 | 0 | 38.4782 | 38.4782 | -3.2899 | 0% | 17.3998 | 0 | 0 | 145.7185 | 145.7185 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.7564 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8345 | 17 | 1.2 | 8.42 | 18.33 | 26.75 | 18.33 | 9.17 | 348 | 8345 | 1020 | 343.2329 | -23.0996 | 0.092669 | 994.284 | 16.5729 | -68.5942 | -3.2097 | 0 | 55.048 | 235.048 | 66.103 | 0 | 0 | 15.6456 | 15.6456 | -9.3269 | 0% | 7.075 | 0 | 0 | 138.8793 | 138.8793 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.8874 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8346 | 18 | 0.7 | 0 | 0 | 0 | 0 | 0 | 348 | 8346 | 1080 | 343.2329 | -23.0996 | 0.092669 | 1054.284 | 17.5729 | -83.5942 | -12.4515 | 0 | 55.048 | 235.048 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.1123 | 133.1123 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8347 | 19 | 0.7 | 0 | 0 | 0 | 0 | 0 | 348 | 8347 | 1140 | 343.2329 | -23.0996 | 0.092669 | 1114.284 | 18.5729 | -98.5942 | -22.3352 | 0 | 55.048 | 235.048 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.377 | 130.377 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8348 | 20 | 0.8 | 0 | 0 | 0 | 0 | 0 | 348 | 8348 | 1200 | 343.2329 | -23.0996 | 0.092669 | 1174.284 | 19.5729 | -113.5942 | -32.5491 | 0 | 55.048 | 235.048 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.8252 | 126.8252 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8349 | 21 | 0.4 | 0 | 0 | 0 | 0 | 0 | 348 | 8349 | 1260 | 343.2329 | -23.0996 | 0.092669 | 1234.284 | 20.5729 | -128.5942 | -42.7529 | 0 | 55.048 | 235.048 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7184 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8350 | 22 | 0.2 | 0 | 0 | 0 | 0 | 0 | 348 | 8350 | 1320 | 343.2329 | -23.0996 | 0.092669 | 1294.284 | 21.5729 | -143.5942 | -52.4549 | 0 | 55.048 | 235.048 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8944 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8351 | 23 | 0.1 | 0 | 0 | 0 | 0 | 0 | 348 | 8351 | 1380 | 343.2329 | -23.0996 | 0.092669 | 1354.284 | 22.5729 | -158.5942 | -60.7342 | 0 | 55.048 | 235.048 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.804 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
12 | 348 | 14 | 8352 | 24 | -0.1 | 0 | 0 | 0 | 0 | 0 | 348 | 8352 | 1440 | 343.2329 | -23.0996 | 0.092669 | 1414.284 | 23.5729 | -173.5942 | -65.7666 | 0 | 55.048 | 235.048 | 66.103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8661 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8353 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 8353 | 60 | 344.2192 | -23.1481 | -0.13565 | 34.284 | 0.56914 | 171.4629 | -65.3918 | 0 | 54.9684 | 125.0316 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5854 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8354 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 8354 | 120 | 344.2192 | -23.1481 | -0.13565 | 94.284 | 1.5691 | 156.4629 | -59.7419 | 0 | 54.9684 | 125.0316 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.387 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8355 | 3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 349 | 8355 | 180 | 344.2192 | -23.1481 | -0.13565 | 154.284 | 2.5691 | 141.4629 | -51.17 | 0 | 54.9684 | 125.0316 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7314 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8356 | 4 | 1.7 | 0 | 0 | 0 | 0 | 0 | 349 | 8356 | 240 | 344.2192 | -23.1481 | -0.13565 | 214.284 | 3.5691 | 126.4629 | -41.3524 | 0 | 54.9684 | 125.0316 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5978 | 0 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8357 | 5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 349 | 8357 | 300 | 344.2192 | -23.1481 | -0.13565 | 274.284 | 4.5691 | 111.4629 | -31.1222 | 0 | 54.9684 | 125.0316 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -12.0913 | 0 | 0% | 12.1% | 0% | 80% | 0% | 0 | 9.2753 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8358 | 6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 349 | 8358 | 360 | 344.2192 | -23.1481 | -0.13565 | 334.284 | 5.5691 | 96.4629 | -20.9369 | 0 | 54.9684 | 125.0316 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -9.0693 | 0 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.4659 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8359 | 7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 349 | 8359 | 420 | 344.2192 | -23.1481 | -0.13565 | 394.284 | 6.5691 | 81.4629 | -11.1269 | 0 | 54.9684 | 125.0316 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 143.6676 | 143.6676 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8360 | 8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 349 | 8360 | 480 | 344.2192 | -23.1481 | -0.13565 | 454.284 | 7.5691 | 66.4629 | -2.0056 | 0 | 54.9684 | 125.0316 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.3621 | 146.3621 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.659 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8361 | 9 | 2.3 | 0.08 | 3.69 | 3.77 | 3.69 | 1.85 | 349 | 8361 | 540 | 344.2192 | -23.1481 | -0.13565 | 514.284 | 8.5691 | 51.4629 | 6.0762 | 6.0762 | 46.3272 | 133.6728 | 55.9172 | 0 | 0 | 3.1496 | 3.1496 | -48.6669 | 0% | 1.4243 | 0 | 0 | 126.8026 | 126.8026 | 0% | 12.13% | 0% | 80% | 0% | 0 | 9.53 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8362 | 10 | 2.8 | 13.69 | 32.69 | 46.38 | 32.69 | 16.35 | 349 | 8362 | 600 | 344.2192 | -23.1481 | -0.13565 | 574.284 | 9.5691 | 36.4629 | 12.7069 | 12.7069 | 34.068 | 145.932 | 43.3695 | 45.2429 | 45.2429 | 27.9027 | 73.1456 | -1.3095 | 0% | 33.0764 | 0 | 0 | 130.2177 | 130.2177 | 0% | 12.04% | 0% | 80% | 0% | 0 | 9.3703 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8363 | 11 | 4.9 | 51.19 | 52.22 | 103.41 | 52.22 | 26.11 | 349 | 8363 | 660 | 344.2192 | -23.1481 | -0.13565 | 634.284 | 10.5691 | 21.4629 | 17.4315 | 17.4315 | 20.6486 | 159.3514 | 32.5289 | 144.0732 | 144.0732 | 44.5726 | 188.6457 | 0.011402 | 1.14% | 85.3056 | 0.97264 | 0.68085 | 133.8047 | 133.8047 | 0.5088% | 11.86% | 11.86% | 80% | 9.488% | 8.0936 | 8.7188 | 6 | 48.5617 | 17.8983 | 36.29% | 36.29%
12 | 349 | 15 | 8364 | 12 | 5 | 76.47 | 70.28 | 146.75 | 70.28 | 35.14 | 349 | 8364 | 720 | 344.2192 | -23.1481 | -0.13565 | 694.284 | 11.5691 | 6.4629 | 19.83 | 19.83 | 6.3166 | 173.6834 | 25.7087 | 203.1081 | 203.1081 | 59.9877 | 263.0959 | 0.2366 | 23.66% | 118.972 | 28.149 | 19.7043 | 131.6458 | 131.6458 | 14.97% | 11.79% | 11.79% | 80% | 9.436% | 11.2261 | 8.6885 | 6 | 67.3569 | 24.8256 | 51.17% | 51.17%
12 | 349 | 15 | 8365 | 13 | 5.3 | 89.44 | 79.81 | 169.25 | 79.81 | 39.91 | 349 | 8365 | 780 | 344.2192 | -23.1481 | -0.13565 | 754.284 | 12.5691 | -8.5371 | 19.6488 | 19.6488 | 8.3337 | 188.3337 | 26.2764 | 238.504 | 238.504 | 68.1221 | 306.6261 | 0.3195 | 31.95% | 138.6563 | 44.3009 | 31.0106 | 131.9504 | 131.9504 | 23.5% | 11.75% | 11.75% | 85% | 9.988% | 13.8494 | 8.5982 | 6 | 83.0961 | 30.6266 | 62.98% | 62.98%
12 | 349 | 15 | 8366 | 14 | 5 | 85.75 | 103.97 | 189.72 | 103.97 | 51.99 | 349 | 8366 | 840 | 344.2192 | -23.1481 | -0.13565 | 814.284 | 13.5691 | -23.5371 | 16.9084 | 16.9084 | 22.5682 | 202.5682 | 33.8613 | 244.8263 | 244.8263 | 88.7439 | 333.5702 | 0.35648 | 35.65% | 150.8405 | 53.7713 | 37.6399 | 131.8411 | 131.8411 | 28.55% | 11.74% | 11.74% | 85% | 9.976% | 15.0483 | 8.6885 | 6 | 90.2896 | 33.2779 | 68.48% | 68.48%
12 | 349 | 15 | 8367 | 15 | 4.2 | 67.5 | 83.97 | 151.47 | 83.97 | 41.99 | 349 | 8367 | 900 | 344.2192 | -23.1481 | -0.13565 | 874.284 | 14.5691 | -38.5371 | 11.8932 | 11.8932 | 35.8334 | 215.8334 | 45.0339 | 231.4618 | 231.4618 | 71.6729 | 303.1347 | 0.30519 | 30.52% | 137.0775 | 41.835 | 29.2845 | 106.3152 | 106.3152 | 27.54% | 11.78% | 0% | 85% | 0% | 0 | 8.9325 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8368 | 16 | 3.8 | 35.08 | 43.42 | 78.5 | 43.42 | 21.71 | 349 | 8368 | 960 | 344.2192 | -23.1481 | -0.13565 | 934.284 | 15.5691 | -53.5371 | 5.0351 | 5.0351 | 47.9327 | 227.9327 | 57.7242 | 0 | 0 | 37.0613 | 37.0613 | -3.302 | 0% | 16.7591 | 0 | 0 | 143.3095 | 143.3095 | 0% | 12.03% | 0% | 80% | 0% | 0 | 9.0562 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8369 | 17 | 3.9 | 3.42 | 18.69 | 22.11 | 18.69 | 9.35 | 349 | 8369 | 1020 | 344.2192 | -23.1481 | -0.13565 | 994.284 | 16.5691 | -68.5371 | -3.2135 | 0 | 54.9684 | 234.9684 | 66.0525 | 0 | 0 | 15.9529 | 15.9529 | -8.7197 | 0% | 7.2139 | 0 | 0 | 138.5179 | 138.5179 | 0% | 12.05% | 0% | 80% | 0% | 0 | 9.0252 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8370 | 18 | 1.7 | 0 | 0 | 0 | 0 | 0 | 349 | 8370 | 1080 | 344.2192 | -23.1481 | -0.13565 | 1054.284 | 17.5691 | -83.5371 | -12.4497 | 0 | 54.9684 | 234.9684 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.7048 | 131.7048 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8371 | 19 | 1.7 | 0 | 0 | 0 | 0 | 0 | 349 | 8371 | 1140 | 344.2192 | -23.1481 | -0.13565 | 1114.284 | 18.5691 | -98.5371 | -22.3299 | 0 | 54.9684 | 234.9684 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.6478 | 129.6478 | 0% | 12.16% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8372 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 8372 | 1200 | 344.2192 | -23.1481 | -0.13565 | 1174.284 | 19.5691 | -113.5371 | -32.5424 | 0 | 54.9684 | 234.9684 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.1831 | 124.1831 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8373 | 21 | -0.8 | 0 | 0 | 0 | 0 | 0 | 349 | 8373 | 1260 | 344.2192 | -23.1481 | -0.13565 | 1234.284 | 20.5691 | -128.5371 | -42.7478 | 0 | 54.9684 | 234.9684 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.7441 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8374 | 22 | -1.1 | 0 | 0 | 0 | 0 | 0 | 349 | 8374 | 1320 | 344.2192 | -23.1481 | -0.13565 | 1294.284 | 21.5691 | -143.5371 | -52.4561 | 0 | 54.9684 | 234.9684 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8571 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8375 | 23 | -1.2 | 0 | 0 | 0 | 0 | 0 | 349 | 8375 | 1380 | 344.2192 | -23.1481 | -0.13565 | 1354.284 | 22.5691 | -158.5371 | -60.749 | 0 | 54.9684 | 234.9684 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.8111 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
12 | 349 | 15 | 8376 | 24 | -2.2 | 0 | 0 | 0 | 0 | 0 | 349 | 8376 | 1440 | 344.2192 | -23.1481 | -0.13565 | 1414.284 | 23.5691 | -173.5371 | -65.8045 | 0 | 54.9684 | 234.9684 | 66.0525 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.1367 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8377 | 1 | -2.4 | 0 | 0 | 0 | 0 | 0 | 350 | 8377 | 60 | 345.2055 | -23.1892 | -0.36629 | 34.284 | 0.5653 | 171.5206 | -65.4446 | 0 | 54.9011 | 125.0989 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.102 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8378 | 2 | -2.9 | 0 | 0 | 0 | 0 | 0 | 350 | 8378 | 120 | 345.2055 | -23.1892 | -0.36629 | 94.284 | 1.5653 | 156.5206 | -59.8052 | 0 | 54.9011 | 125.0989 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.7053 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2943 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8379 | 3 | -2.7 | 0 | 0 | 0 | 0 | 0 | 350 | 8379 | 180 | 345.2055 | -23.1892 | -0.36629 | 154.284 | 2.5653 | 141.5206 | -51.2362 | 0 | 54.9011 | 125.0989 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2417 | 0 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8380 | 4 | -3.2 | 0 | 0 | 0 | 0 | 0 | 350 | 8380 | 240 | 345.2055 | -23.1892 | -0.36629 | 214.284 | 3.5653 | 126.5206 | -41.4192 | 0 | 54.9011 | 125.0989 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0037 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.4019 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8381 | 5 | -2.2 | 0 | 0 | 0 | 0 | 0 | 350 | 8381 | 300 | 345.2055 | -23.1892 | -0.36629 | 274.284 | 4.5653 | 111.5206 | -31.1891 | 0 | 54.9011 | 125.0989 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.2199 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8382 | 6 | -2.1 | 0 | 0 | 0 | 0 | 0 | 350 | 8382 | 360 | 345.2055 | -23.1892 | -0.36629 | 334.284 | 5.5653 | 96.5206 | -21.0036 | 0 | 54.9011 | 125.0989 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.8067 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8383 | 7 | -1.9 | 0 | 0 | 0 | 0 | 0 | 350 | 8383 | 420 | 345.2055 | -23.1892 | -0.36629 | 394.284 | 6.5653 | 81.5206 | -11.1932 | 0 | 54.9011 | 125.0989 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 136.6716 | 136.6716 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8384 | 8 | -2.2 | 0 | 0 | 0 | 0 | 0 | 350 | 8384 | 480 | 345.2055 | -23.1892 | -0.36629 | 454.284 | 7.5653 | 66.5206 | -2.0709 | 0 | 54.9011 | 125.0989 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.1456 | 139.1456 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8385 | 9 | -2.7 | 0 | 3.97 | 3.97 | 3.97 | 1.99 | 350 | 8385 | 540 | 345.2055 | -23.1892 | -0.36629 | 514.284 | 8.5653 | 51.5206 | 6.013 | 6.013 | 46.3498 | 133.6502 | 55.9808 | 0 | 0 | 3.3886 | 3.3886 | -48.8248 | 0% | 1.5323 | 0 | 0 | 118.1633 | 118.1633 | 0% | 12.35% | 0% | 80% | 0% | 0 | 11.223 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8386 | 10 | -2.6 | 1.75 | 34.08 | 35.83 | 34.08 | 17.04 | 350 | 8386 | 600 | 345.2055 | -23.1892 | -0.36629 | 574.284 | 9.5653 | 36.5206 | 12.6475 | 12.6475 | 34.0998 | 145.9002 | 43.4359 | 5.8038 | 5.8038 | 29.0891 | 34.8929 | -4.0085 | 0% | 15.7786 | 0 | 0 | 120.2006 | 120.2006 | 0% | 12.3% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8387 | 11 | -1.8 | 22.58 | 78.61 | 101.19 | 78.61 | 39.31 | 350 | 8387 | 660 | 345.2055 | -23.1892 | -0.36629 | 634.284 | 10.5653 | 21.5206 | 17.378 | 17.378 | 20.6909 | 159.3091 | 32.5951 | 63.6937 | 63.6937 | 67.0978 | 130.7915 | -0.46461 | 0% | 59.1439 | 0 | 0 | 123.0249 | 123.0249 | 0% | 12.15% | 12.15% | 80% | 9.724% | 5.7509 | 10.9053 | 6 | 34.5052 | 12.7175 | 28.05% | 28.05%
12 | 350 | 16 | 8388 | 12 | -1.7 | 59.72 | 133.53 | 193.25 | 133.53 | 66.77 | 350 | 8388 | 720 | 345.2055 | -23.1892 | -0.36629 | 694.284 | 11.5653 | 6.5206 | 19.7847 | 19.7847 | 6.3691 | 173.6309 | 25.7621 | 158.8962 | 158.8962 | 113.975 | 272.8712 | 0.19685 | 19.68% | 123.3924 | 24.2896 | 17.0027 | 124.4535 | 124.4535 | 13.66% | 11.98% | 11.98% | 80% | 9.585% | 11.827 | 10.8704 | 6 | 70.9622 | 26.1544 | 57.02% | 57.02%
12 | 350 | 16 | 8389 | 13 | -1.8 | 73.81 | 138.42 | 212.23 | 138.42 | 69.21 | 350 | 8389 | 780 | 345.2055 | -23.1892 | -0.36629 | 754.284 | 12.5653 | -8.4794 | 19.6137 | 19.6137 | 8.273 | 188.273 | 26.2974 | 197.1272 | 197.1272 | 118.1489 | 315.2761 | 0.27772 | 27.77% | 142.5678 | 39.594 | 27.7158 | 103.1454 | 103.1454 | 26.87% | 11.93% | 11.93% | 85% | 10.14% | 14.4609 | 10.9053 | 6 | 86.7657 | 31.9791 | 84.12% | 84.12%
12 | 350 | 16 | 8390 | 14 | -1.4 | 17.58 | 136.86 | 154.44 | 136.86 | 68.43 | 350 | 8390 | 840 | 345.2055 | -23.1892 | -0.36629 | 814.284 | 13.5653 | -23.4794 | 16.8842 | 16.8842 | 22.5028 | 202.5028 | 33.852 | 50.2683 | 50.2683 | 116.8173 | 167.0856 | -0.18308 | 0% | 75.5561 | 0 | 0 | 121.4216 | 121.4216 | 0% | 12.1% | 12.1% | 80% | 9.678% | 7.312 | 10.7659 | 6 | 43.8719 | 16.1698 | 36.13% | 36.13%
12 | 350 | 16 | 8391 | 15 | -1.3 | 25.28 | 106.86 | 132.14 | 106.86 | 53.43 | 350 | 8391 | 900 | 345.2055 | -23.1892 | -0.36629 | 874.284 | 14.5653 | -38.4794 | 11.8793 | 11.8793 | 35.7663 | 215.7663 | 45.0068 | 86.8274 | 86.8274 | 91.2107 | 178.0382 | -0.12096 | 0% | 80.5089 | 0 | 0 | 139.8039 | 139.8039 | 0% | 12.08% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8392 | 16 | -2.4 | 7.14 | 66.39 | 73.53 | 66.39 | 33.2 | 350 | 8392 | 960 | 345.2055 | -23.1892 | -0.36629 | 934.284 | 15.5653 | -53.4794 | 5.0302 | 5.0302 | 47.8656 | 227.8656 | 57.6865 | 0 | 0 | 56.6674 | 56.6674 | -2.1505 | 0% | 25.625 | 0 | 0 | 134.2122 | 134.2122 | 0% | 12.27% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8393 | 17 | -3.4 | 0.56 | 19.92 | 20.48 | 19.92 | 9.96 | 350 | 8393 | 1020 | 345.2055 | -23.1892 | -0.36629 | 994.284 | 16.5653 | -68.4794 | -3.2113 | 0 | 54.9011 | 234.9011 | 66.0099 | 0 | 0 | 17.0028 | 17.0028 | -9.1902 | 0% | 7.6887 | 0 | 0 | 128.5854 | 128.5854 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.4739 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8394 | 18 | -4.6 | 0 | 0 | 0 | 0 | 0 | 350 | 8394 | 1080 | 345.2055 | -23.1892 | -0.36629 | 1054.284 | 17.5653 | -83.4794 | -12.4422 | 0 | 54.9011 | 234.9011 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.1482 | 124.1482 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8395 | 19 | -6 | 0 | 0 | 0 | 0 | 0 | 350 | 8395 | 1140 | 345.2055 | -23.1892 | -0.36629 | 1114.284 | 18.5653 | -98.4794 | -22.319 | 0 | 54.9011 | 234.9011 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.3873 | 120.3873 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8396 | 20 | -6.9 | 0 | 0 | 0 | 0 | 0 | 350 | 8396 | 1200 | 345.2055 | -23.1892 | -0.36629 | 1174.284 | 19.5653 | -113.4794 | -32.5303 | 0 | 54.9011 | 234.9011 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 116.6753 | 116.6753 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.7803 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8397 | 21 | -7.5 | 0 | 0 | 0 | 0 | 0 | 350 | 8397 | 1260 | 345.2055 | -23.1892 | -0.36629 | 1234.284 | 20.5653 | -128.4794 | -42.7372 | 0 | 54.9011 | 234.9011 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.815 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8398 | 22 | -7.1 | 0 | 0 | 0 | 0 | 0 | 350 | 8398 | 1320 | 345.2055 | -23.1892 | -0.36629 | 1294.284 | 21.5653 | -143.4794 | -52.4512 | 0 | 54.9011 | 234.9011 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.741 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8399 | 23 | -7.6 | 0 | 0 | 0 | 0 | 0 | 350 | 8399 | 1380 | 345.2055 | -23.1892 | -0.36629 | 1354.284 | 22.5653 | -158.4794 | -60.757 | 0 | 54.9011 | 234.9011 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.3443 | 0 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.0519 | 6 | 0 | 0 | 0% | 0%
12 | 350 | 16 | 8400 | 24 | -8 | 0 | 0 | 0 | 0 | 0 | 350 | 8400 | 1440 | 345.2055 | -23.1892 | -0.36629 | 1414.284 | 23.5653 | -173.4794 | -65.8348 | 0 | 54.9011 | 234.9011 | 66.0099 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.7951 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.2086 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8401 | 1 | -8.7 | 0 | 0 | 0 | 0 | 0 | 351 | 8401 | 60 | 346.1918 | -23.2227 | -0.59884 | 34.284 | 0.56142 | 171.5787 | -65.49 | 0 | 54.8461 | 125.1539 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.3782 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8402 | 2 | -8.5 | 0 | 0 | 0 | 0 | 0 | 351 | 8402 | 120 | 346.1918 | -23.2227 | -0.59884 | 94.284 | 1.5614 | 156.5787 | -59.8623 | 0 | 54.8461 | 125.1539 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.8967 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4061 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8403 | 3 | -7.5 | 0 | 0 | 0 | 0 | 0 | 351 | 8403 | 180 | 346.1918 | -23.2227 | -0.59884 | 154.284 | 2.5614 | 141.5787 | -51.2971 | 0 | 54.8461 | 125.1539 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.196 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8404 | 4 | -7.4 | 0 | 0 | 0 | 0 | 0 | 351 | 8404 | 240 | 346.1918 | -23.2227 | -0.59884 | 214.284 | 3.5614 | 126.5787 | -41.4812 | 0 | 54.8461 | 125.1539 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.0436 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 12.9739 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8405 | 5 | -6.5 | 0 | 0 | 0 | 0 | 0 | 351 | 8405 | 300 | 346.1918 | -23.2227 | -0.59884 | 274.284 | 4.5614 | 111.5787 | -31.2512 | 0 | 54.8461 | 125.1539 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.113 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8406 | 6 | -6.2 | 0 | 0 | 0 | 0 | 0 | 351 | 8406 | 360 | 346.1918 | -23.2227 | -0.59884 | 334.284 | 5.5614 | 96.5787 | -21.0655 | 0 | 54.8461 | 125.1539 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.2921 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8407 | 7 | -4.4 | 0 | 0 | 0 | 0 | 0 | 351 | 8407 | 420 | 346.1918 | -23.2227 | -0.59884 | 394.284 | 6.5614 | 81.5787 | -11.2544 | 0 | 54.8461 | 125.1539 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 134.164 | 134.164 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8408 | 8 | -2.5 | 0 | 0 | 0 | 0 | 0 | 351 | 8408 | 480 | 346.1918 | -23.2227 | -0.59884 | 454.284 | 7.5614 | 66.5787 | -2.1306 | 0 | 54.8461 | 125.1539 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.8768 | 139.8768 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8409 | 9 | -2.3 | 0.08 | 3.25 | 3.33 | 3.25 | 1.63 | 351 | 8409 | 540 | 346.1918 | -23.2227 | -0.59884 | 514.284 | 8.5614 | 51.5787 | 5.956 | 5.956 | 46.3769 | 133.6231 | 56.0423 | 0 | 0 | 2.774 | 2.774 | -59.4587 | 0% | 1.2544 | 0 | 0 | 119.7794 | 119.7794 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8410 | 10 | -2 | 13.89 | 40.28 | 54.17 | 40.28 | 20.14 | 351 | 8410 | 600 | 346.1918 | -23.2227 | -0.59884 | 574.284 | 9.5614 | 36.5787 | 12.5947 | 12.5947 | 34.1352 | 145.8648 | 43.499 | 46.2072 | 46.2072 | 34.3811 | 80.5884 | -1.2611 | 0% | 36.4421 | 0 | 0 | 122.9227 | 122.9227 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8411 | 11 | -1.8 | 36.47 | 69.17 | 105.64 | 69.17 | 34.59 | 351 | 8411 | 660 | 346.1918 | -23.2227 | -0.59884 | 634.284 | 10.5614 | 21.5787 | 17.3315 | 17.3315 | 20.7356 | 159.2644 | 32.656 | 103.0715 | 103.0715 | 59.0403 | 162.1118 | -0.21951 | 0% | 73.307 | 0 | 0 | 123.3051 | 123.3051 | 0% | 12.12% | 12.12% | 80% | 9.693% | 7.106 | 10.9053 | 6 | 42.6359 | 15.7142 | 34.58% | 34.58%
12 | 351 | 17 | 8412 | 12 | -2 | 19.17 | 105.19 | 124.36 | 105.19 | 52.6 | 351 | 8412 | 720 | 346.1918 | -23.2227 | -0.59884 | 694.284 | 11.5614 | 6.5787 | 19.7468 | 19.7468 | 6.4228 | 173.5772 | 25.8085 | 51.0793 | 51.0793 | 89.7853 | 140.8645 | -0.37744 | 0% | 63.6989 | 0 | 0 | 120.003 | 120.003 | 0% | 12.15% | 12.15% | 80% | 9.72% | 6.1913 | 10.9754 | 6 | 37.1479 | 13.6915 | 30.96% | 30.96%
12 | 351 | 17 | 8413 | 13 | -1.2 | 17.69 | 106.19 | 123.88 | 106.19 | 53.1 | 351 | 8413 | 780 | 346.1918 | -23.2227 | -0.59884 | 754.284 | 12.5614 | -8.4213 | 19.5861 | 19.5861 | 8.2128 | 188.2128 | 26.3113 | 47.3037 | 47.3037 | 90.6388 | 137.9426 | -0.38802 | 0% | 62.3776 | 0 | 0 | 120.3638 | 120.3638 | 0% | 12.12% | 12.12% | 80% | 9.699% | 6.0501 | 10.6967 | 6 | 36.3007 | 13.3793 | 30.16% | 30.16%
12 | 351 | 17 | 8414 | 14 | -0.5 | 22.97 | 104.53 | 127.5 | 104.53 | 52.27 | 351 | 8414 | 840 | 346.1918 | -23.2227 | -0.59884 | 814.284 | 13.5614 | -23.4213 | 16.8673 | 16.8673 | 22.4393 | 202.4393 | 33.8374 | 65.7558 | 65.7558 | 89.2219 | 154.9777 | -0.24579 | 0% | 70.0809 | 0 | 0 | 120.9223 | 120.9223 | 0% | 12.08% | 12.08% | 80% | 9.663% | 6.7722 | 10.4565 | 6 | 40.6332 | 14.9761 | 33.6% | 33.6%
12 | 351 | 17 | 8415 | 15 | -0.6 | 24.44 | 116.94 | 141.38 | 116.94 | 58.47 | 351 | 8415 | 900 | 346.1918 | -23.2227 | -0.59884 | 874.284 | 14.5614 | -38.4213 | 11.8724 | 11.8724 | 35.7022 | 215.7022 | 44.9758 | 84.0362 | 84.0362 | 99.8145 | 183.8507 | -0.08227 | 0% | 83.1373 | 0 | 0 | 141.0897 | 141.0897 | 0% | 12.05% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8416 | 16 | -1.5 | 17.36 | 67.08 | 84.44 | 67.08 | 33.54 | 351 | 8416 | 960 | 346.1918 | -23.2227 | -0.59884 | 934.284 | 15.5614 | -53.4213 | 5.0318 | 5.0318 | 47.8023 | 227.8023 | 57.6462 | 0 | 0 | 57.2564 | 57.2564 | -2.0809 | 0% | 25.8913 | 0 | 0 | 136.2278 | 136.2278 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8417 | 17 | -2 | 0.19 | 13.42 | 13.61 | 13.42 | 6.71 | 351 | 8417 | 1020 | 346.1918 | -23.2227 | -0.59884 | 994.284 | 16.5614 | -68.4213 | -3.203 | 0 | 54.8461 | 234.8461 | 65.9751 | 0 | 0 | 11.4547 | 11.4547 | -13.7248 | 0% | 5.1798 | 0 | 0 | 130.4449 | 130.4449 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8418 | 18 | -2.1 | 0 | 0 | 0 | 0 | 0 | 351 | 8418 | 1080 | 346.1918 | -23.2227 | -0.59884 | 1054.284 | 17.5614 | -83.4213 | -12.4291 | 0 | 54.8461 | 234.8461 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.0876 | 128.0876 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8419 | 19 | -2.3 | 0 | 0 | 0 | 0 | 0 | 351 | 8419 | 1140 | 346.1918 | -23.2227 | -0.59884 | 1114.284 | 18.5614 | -98.4213 | -22.3027 | 0 | 54.8461 | 234.8461 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.2201 | 126.2201 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8420 | 20 | -2.5 | 0 | 0 | 0 | 0 | 0 | 351 | 8420 | 1200 | 346.1918 | -23.2227 | -0.59884 | 1174.284 | 19.5614 | -113.4213 | -32.5129 | 0 | 54.8461 | 234.8461 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.61 | 123.61 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8421 | 21 | -3.1 | 0 | 0 | 0 | 0 | 0 | 351 | 8421 | 1260 | 346.1918 | -23.2227 | -0.59884 | 1234.284 | 20.5614 | -128.4213 | -42.7211 | 0 | 54.8461 | 234.8461 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8594 | 0 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.366 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8422 | 22 | -4.4 | 0 | 0 | 0 | 0 | 0 | 351 | 8422 | 1320 | 346.1918 | -23.2227 | -0.59884 | 1294.284 | 21.5614 | -143.4213 | -52.4403 | 0 | 54.8461 | 234.8461 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.3552 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.8384 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8423 | 23 | -5.6 | 0 | 0 | 0 | 0 | 0 | 351 | 8423 | 1380 | 346.1918 | -23.2227 | -0.59884 | 1354.284 | 22.5614 | -158.4213 | -60.7582 | 0 | 54.8461 | 234.8461 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.0073 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
12 | 351 | 17 | 8424 | 24 | -5.6 | 0 | 0 | 0 | 0 | 0 | 351 | 8424 | 1440 | 346.1918 | -23.2227 | -0.59884 | 1414.284 | 23.5614 | -173.4213 | -65.8575 | 0 | 54.8461 | 234.8461 | 65.9751 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.8306 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8425 | 1 | -5.5 | 0 | 0 | 0 | 0 | 0 | 352 | 8425 | 60 | 347.1781 | -23.2487 | -0.83292 | 34.284 | 0.55752 | 171.6372 | -65.5283 | 0 | 54.8034 | 125.1966 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.2038 | 0 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8426 | 2 | -6.4 | 0 | 0 | 0 | 0 | 0 | 352 | 8426 | 120 | 347.1781 | -23.2487 | -0.83292 | 94.284 | 1.5575 | 156.6372 | -59.9133 | 0 | 54.8034 | 125.1966 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.4462 | 0 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5884 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8427 | 3 | -5.9 | 0 | 0 | 0 | 0 | 0 | 352 | 8427 | 180 | 347.1781 | -23.2487 | -0.83292 | 154.284 | 2.5575 | 141.6372 | -51.3528 | 0 | 54.8034 | 125.1966 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.555 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8428 | 4 | -4.9 | 0 | 0 | 0 | 0 | 0 | 352 | 8428 | 240 | 347.1781 | -23.2487 | -0.83292 | 214.284 | 3.5575 | 126.6372 | -41.5384 | 0 | 54.8034 | 125.1966 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.031 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8429 | 5 | -4.9 | 0 | 0 | 0 | 0 | 0 | 352 | 8429 | 300 | 347.1781 | -23.2487 | -0.83292 | 274.284 | 4.5575 | 111.6372 | -31.3087 | 0 | 54.8034 | 125.1966 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5735 | 0 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0233 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8430 | 6 | -3.8 | 0 | 0 | 0 | 0 | 0 | 352 | 8430 | 360 | 347.1781 | -23.2487 | -0.83292 | 334.284 | 5.5575 | 96.6372 | -21.1226 | 0 | 54.8034 | 125.1966 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.2986 | 0 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6189 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8431 | 7 | -3.9 | 0 | 0 | 0 | 0 | 0 | 352 | 8431 | 420 | 347.1781 | -23.2487 | -0.83292 | 394.284 | 6.5575 | 81.6372 | -11.3104 | 0 | 54.8034 | 125.1966 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.8006 | 130.8006 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.6553 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8432 | 8 | -3.4 | 0 | 0 | 0 | 0 | 0 | 352 | 8432 | 480 | 347.1781 | -23.2487 | -0.83292 | 454.284 | 7.5575 | 66.6372 | -2.1846 | 0 | 54.8034 | 125.1966 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.7885 | 133.7885 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4739 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8433 | 9 | -3.6 | 0 | 2.5 | 2.5 | 2.5 | 1.25 | 352 | 8433 | 540 | 347.1781 | -23.2487 | -0.83292 | 514.284 | 8.5575 | 51.6372 | 5.905 | 5.905 | 46.4083 | 133.5917 | 56.1017 | 0 | 0 | 2.1339 | 2.1339 | -79.0657 | 0% | 0.96494 | 0 | 0 | 112.9898 | 112.9898 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5463 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8434 | 10 | -3.3 | 8.97 | 23.61 | 32.58 | 23.61 | 11.81 | 352 | 8434 | 600 | 347.1781 | -23.2487 | -0.83292 | 574.284 | 9.5575 | 36.6372 | 12.5485 | 12.5485 | 34.174 | 145.826 | 43.5586 | 29.9185 | 29.9185 | 20.1524 | 50.0709 | -2.5848 | 0% | 22.6421 | 0 | 0 | 115.1875 | 115.1875 | 0% | 12.31% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8435 | 11 | -2.4 | 3.53 | 60.92 | 64.45 | 60.92 | 30.46 | 352 | 8435 | 660 | 347.1781 | -23.2487 | -0.83292 | 634.284 | 10.5575 | 21.6372 | 17.2922 | 17.2922 | 20.7828 | 159.2172 | 32.7117 | 9.9922 | 9.9922 | 51.9985 | 61.9907 | -1.8968 | 0% | 28.0322 | 0 | 0 | 116.1393 | 116.1393 | 0% | 12.26% | 12.26% | 80% | 9.809% | 2.7497 | 11.1164 | 6 | 16.498 | 6.0807 | 14.21% | 14.21%
12 | 352 | 18 | 8436 | 12 | -1.8 | 8.69 | 88.14 | 96.83 | 88.14 | 44.07 | 352 | 8436 | 720 | 347.1781 | -23.2487 | -0.83292 | 694.284 | 11.5575 | 6.6372 | 19.7164 | 19.7164 | 6.4774 | 173.5226 | 25.8478 | 23.1815 | 23.1815 | 75.2322 | 98.4137 | -0.88198 | 0% | 44.5027 | 0 | 0 | 116.0337 | 116.0337 | 0% | 12.19% | 12.19% | 80% | 9.755% | 4.341 | 10.9053 | 6 | 26.0462 | 9.5998 | 22.45% | 22.45%
12 | 352 | 18 | 8437 | 13 | -1.7 | 8.14 | 103.14 | 111.28 | 103.14 | 51.57 | 352 | 8437 | 780 | 347.1781 | -23.2487 | -0.83292 | 754.284 | 12.5575 | -8.3628 | 19.5659 | 19.5659 | 8.1532 | 188.1532 | 26.3182 | 21.7869 | 21.7869 | 88.0355 | 109.8224 | -0.70456 | 0% | 49.6617 | 0 | 0 | 116.3215 | 116.3215 | 0% | 12.18% | 12.18% | 80% | 9.741% | 4.8373 | 10.8704 | 6 | 29.024 | 10.6973 | 24.95% | 24.95%
12 | 352 | 18 | 8438 | 14 | -1 | 41.39 | 98.14 | 139.53 | 98.14 | 49.07 | 352 | 8438 | 840 | 347.1781 | -23.2487 | -0.83292 | 814.284 | 13.5575 | -23.3628 | 16.8576 | 16.8576 | 22.3777 | 202.3777 | 33.8173 | 118.5802 | 118.5802 | 83.7677 | 202.348 | -0.0061549 | 0% | 91.5017 | 0 | 0 | 118.1771 | 118.1771 | 0% | 12.04% | 12.04% | 80% | 9.634% | 8.8151 | 10.6277 | 6 | 52.8907 | 19.4939 | 44.76% | 44.76%
12 | 352 | 18 | 8439 | 15 | -0.8 | 30.64 | 98.97 | 129.61 | 98.97 | 49.49 | 352 | 8439 | 900 | 347.1781 | -23.2487 | -0.83292 | 874.284 | 14.5575 | -38.3628 | 11.8723 | 11.8723 | 35.6412 | 215.6412 | 44.941 | 105.4193 | 105.4193 | 84.4762 | 189.8954 | -0.056668 | 0% | 85.8707 | 0 | 0 | 138.025 | 138.025 | 0% | 12.05% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8440 | 16 | -1.3 | 5.56 | 54.64 | 60.2 | 54.64 | 27.32 | 352 | 8440 | 960 | 347.1781 | -23.2487 | -0.83292 | 934.284 | 15.5575 | -53.3628 | 5.0397 | 5.0397 | 47.7428 | 227.7428 | 57.6032 | 0 | 0 | 46.6382 | 46.6382 | -2.727 | 0% | 21.0898 | 0 | 0 | 133.0829 | 133.0829 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8441 | 17 | -2.4 | 0.28 | 13.69 | 13.97 | 13.69 | 6.85 | 352 | 8441 | 1020 | 347.1781 | -23.2487 | -0.83292 | 994.284 | 16.5575 | -68.3628 | -3.1888 | 0 | 54.8034 | 234.8034 | 65.948 | 0 | 0 | 11.6851 | 11.6851 | -13.5237 | 0% | 5.284 | 0 | 0 | 128.0777 | 128.0777 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8442 | 18 | -2.4 | 0 | 0 | 0 | 0 | 0 | 352 | 8442 | 1080 | 347.1781 | -23.2487 | -0.83292 | 1054.284 | 17.5575 | -83.3628 | -12.4103 | 0 | 54.8034 | 234.8034 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.1619 | 126.1619 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8443 | 19 | -2.4 | 0 | 0 | 0 | 0 | 0 | 352 | 8443 | 1140 | 347.1781 | -23.2487 | -0.83292 | 1114.284 | 18.5575 | -98.3628 | -22.2811 | 0 | 54.8034 | 234.8034 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.87 | 124.87 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8444 | 20 | -2.3 | 0 | 0 | 0 | 0 | 0 | 352 | 8444 | 1200 | 347.1781 | -23.2487 | -0.83292 | 1174.284 | 19.5575 | -113.3628 | -32.4902 | 0 | 54.8034 | 234.8034 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.158 | 123.158 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8445 | 21 | -2.2 | 0 | 0 | 0 | 0 | 0 | 352 | 8445 | 1260 | 347.1781 | -23.2487 | -0.83292 | 1234.284 | 20.5575 | -128.3628 | -42.6996 | 0 | 54.8034 | 234.8034 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.143 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8446 | 22 | -2.1 | 0 | 0 | 0 | 0 | 0 | 352 | 8446 | 1320 | 347.1781 | -23.2487 | -0.83292 | 1294.284 | 21.5575 | -143.3628 | -52.4237 | 0 | 54.8034 | 234.8034 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4098 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8447 | 23 | -2.2 | 0 | 0 | 0 | 0 | 0 | 352 | 8447 | 1380 | 347.1781 | -23.2487 | -0.83292 | 1354.284 | 22.5575 | -158.3628 | -60.7528 | 0 | 54.8034 | 234.8034 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.433 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 352 | 18 | 8448 | 24 | -2.3 | 0 | 0 | 0 | 0 | 0 | 352 | 8448 | 1440 | 347.1781 | -23.2487 | -0.83292 | 1414.284 | 23.5575 | -173.3628 | -65.8727 | 0 | 54.8034 | 234.8034 | 65.948 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4562 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8449 | 1 | -2.2 | 0 | 0 | 0 | 0 | 0 | 353 | 8449 | 60 | 348.1644 | -23.2673 | -1.0681 | 34.284 | 0.5536 | 171.696 | -65.5592 | 0 | 54.7729 | 125.2271 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.0493 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8450 | 2 | -2.2 | 0 | 0 | 0 | 0 | 0 | 353 | 8450 | 120 | 348.1644 | -23.2673 | -1.0681 | 94.284 | 1.5536 | 156.696 | -59.9582 | 0 | 54.7729 | 125.2271 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8782 | 0 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.0458 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8451 | 3 | -2.1 | 0 | 0 | 0 | 0 | 0 | 353 | 8451 | 180 | 348.1644 | -23.2673 | -1.0681 | 154.284 | 2.5536 | 141.696 | -51.4031 | 0 | 54.7729 | 125.2271 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5547 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8452 | 4 | -1.9 | 0 | 0 | 0 | 0 | 0 | 353 | 8452 | 240 | 348.1644 | -23.2673 | -1.0681 | 214.284 | 3.5536 | 126.696 | -41.5906 | 0 | 54.7729 | 125.2271 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2499 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9403 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8453 | 5 | -2 | 0 | 0 | 0 | 0 | 0 | 353 | 8453 | 300 | 348.1644 | -23.2673 | -1.0681 | 274.284 | 4.5536 | 111.696 | -31.3613 | 0 | 54.7729 | 125.2271 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.6111 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8454 | 6 | -2.1 | 0 | 0 | 0 | 0 | 0 | 353 | 8454 | 360 | 348.1644 | -23.2673 | -1.0681 | 334.284 | 5.5536 | 96.696 | -21.1746 | 0 | 54.7729 | 125.2271 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.2568 | 0 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.0106 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8455 | 7 | -1.8 | 0 | 0 | 0 | 0 | 0 | 353 | 8455 | 420 | 348.1644 | -23.2673 | -1.0681 | 394.284 | 6.5536 | 81.696 | -11.3611 | 0 | 54.7729 | 125.2271 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 137.4336 | 137.4336 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8456 | 8 | -2 | 0 | 0 | 0 | 0 | 0 | 353 | 8456 | 480 | 348.1644 | -23.2673 | -1.0681 | 454.284 | 7.5536 | 66.696 | -2.233 | 0 | 54.7729 | 125.2271 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 140.3546 | 140.3546 | 0% | 12.32% | 0% | 80% | 0% | 0 | 10.9754 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8457 | 9 | -1.7 | 0 | 0 | 0 | 0 | 0 | 353 | 8457 | 540 | 348.1644 | -23.2673 | -1.0681 | 514.284 | 8.5536 | 51.696 | 5.8603 | 5.8603 | 46.4439 | 133.5561 | 56.1588 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.5489 | 120.5489 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8458 | 10 | -1.3 | 13.61 | 43.89 | 57.5 | 43.89 | 21.95 | 353 | 8458 | 600 | 348.1644 | -23.2673 | -1.0681 | 574.284 | 9.5536 | 36.696 | 12.5091 | 12.5091 | 34.2163 | 145.7837 | 43.6146 | 45.4932 | 45.4932 | 37.4625 | 82.9557 | -1.1811 | 0% | 37.5126 | 0 | 0 | 124.9321 | 124.9321 | 0% | 12.19% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8459 | 11 | -0.4 | 47.5 | 48.19 | 95.69 | 48.19 | 24.1 | 353 | 8459 | 660 | 348.1644 | -23.2673 | -1.0681 | 634.284 | 10.5536 | 21.696 | 17.26 | 17.26 | 20.8322 | 159.1678 | 32.7621 | 134.6233 | 134.6233 | 41.1327 | 175.756 | -0.12027 | 0% | 79.4769 | 0 | 0 | 126.2213 | 126.2213 | 0% | 12.05% | 12.05% | 80% | 9.642% | 7.6631 | 10.4224 | 6 | 45.9786 | 16.9463 | 36.43% | 36.43%
12 | 353 | 19 | 8460 | 12 | 0.2 | 99.17 | 48.61 | 147.78 | 48.61 | 24.31 | 353 | 8460 | 720 | 348.1644 | -23.2673 | -1.0681 | 694.284 | 11.5536 | 6.696 | 19.6934 | 19.6934 | 6.5329 | 173.4671 | 25.88 | 264.7713 | 264.7713 | 41.4912 | 306.2625 | 0.27842 | 27.84% | 138.4919 | 38.5596 | 26.9917 | 125.9207 | 125.9207 | 21.44% | 11.89% | 11.89% | 85% | 10.11% | 13.9963 | 10.2197 | 6 | 83.9779 | 30.9516 | 66.69% | 66.69%
12 | 353 | 19 | 8461 | 13 | 0.1 | 45.19 | 72.78 | 117.97 | 72.78 | 36.39 | 353 | 8461 | 780 | 348.1644 | -23.2673 | -1.0681 | 754.284 | 12.5536 | -8.304 | 19.5532 | 19.5532 | 8.0941 | 188.0941 | 26.3181 | 121.0282 | 121.0282 | 62.1216 | 183.1498 | -0.076212 | 0% | 82.8203 | 0 | 0 | 123.3371 | 123.3371 | 0% | 12.03% | 12.03% | 80% | 9.622% | 7.9687 | 10.2533 | 6 | 47.8124 | 17.6221 | 38.77% | 38.77%
12 | 353 | 19 | 8462 | 14 | -0.3 | 34.53 | 60.75 | 95.28 | 60.75 | 30.38 | 353 | 8462 | 840 | 348.1644 | -23.2673 | -1.0681 | 814.284 | 13.5536 | -23.304 | 16.8551 | 16.8551 | 22.3181 | 202.3181 | 33.7919 | 98.9701 | 98.9701 | 51.8534 | 150.8235 | -0.27142 | 0% | 68.2024 | 0 | 0 | 120.9527 | 120.9527 | 0% | 12.08% | 12.08% | 80% | 9.661% | 6.5893 | 10.3885 | 6 | 39.536 | 14.5717 | 32.69% | 32.69%
12 | 353 | 19 | 8463 | 15 | -0.4 | 87.08 | 59.72 | 146.8 | 59.72 | 29.86 | 353 | 8463 | 900 | 348.1644 | -23.2673 | -1.0681 | 874.284 | 14.5536 | -38.304 | 11.8791 | 11.8791 | 35.5833 | 215.5833 | 44.9025 | 299.6386 | 299.6386 | 50.9742 | 350.6128 | 0.34068 | 34.07% | 158.5471 | 54.0137 | 37.8096 | 142.7643 | 142.7643 | 26.48% | 11.86% | 0% | 85% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8464 | 16 | -0.6 | 39.44 | 31.94 | 71.38 | 31.94 | 15.97 | 353 | 8464 | 960 | 348.1644 | -23.2673 | -1.0681 | 934.284 | 15.5536 | -53.304 | 5.0541 | 5.0541 | 47.6873 | 227.6873 | 57.5577 | 0 | 0 | 27.2625 | 27.2625 | -5.1728 | 0% | 12.3281 | 0 | 0 | 137.9556 | 137.9556 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8465 | 17 | -0.6 | 4.92 | 10.56 | 15.48 | 10.56 | 5.28 | 353 | 8465 | 1020 | 348.1644 | -23.2673 | -1.0681 | 994.284 | 16.5536 | -68.304 | -3.1686 | 0 | 54.7729 | 234.7729 | 65.9288 | 0 | 0 | 9.0135 | 9.0135 | -17.2734 | 0% | 4.0759 | 0 | 0 | 133.0398 | 133.0398 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8466 | 18 | -0.7 | 0 | 0 | 0 | 0 | 0 | 353 | 8466 | 1080 | 348.1644 | -23.2673 | -1.0681 | 1054.284 | 17.5536 | -83.304 | -12.386 | 0 | 54.7729 | 234.7729 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.6453 | 129.6453 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8467 | 19 | -0.6 | 0 | 0 | 0 | 0 | 0 | 353 | 8467 | 1140 | 348.1644 | -23.2673 | -1.0681 | 1114.284 | 18.5536 | -98.304 | -22.2542 | 0 | 54.7729 | 234.7729 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.8264 | 127.8264 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8468 | 20 | -0.5 | 0 | 0 | 0 | 0 | 0 | 353 | 8468 | 1200 | 348.1644 | -23.2673 | -1.0681 | 1174.284 | 19.5536 | -113.304 | -32.4623 | 0 | 54.7729 | 234.7729 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.3154 | 125.3154 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8469 | 21 | -0.5 | 0 | 0 | 0 | 0 | 0 | 353 | 8469 | 1260 | 348.1644 | -23.2673 | -1.0681 | 1234.284 | 20.5536 | -128.304 | -42.6728 | 0 | 54.7729 | 234.7729 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.3524 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8470 | 22 | -0.4 | 0 | 0 | 0 | 0 | 0 | 353 | 8470 | 1320 | 348.1644 | -23.2673 | -1.0681 | 1294.284 | 21.5536 | -143.304 | -52.4012 | 0 | 54.7729 | 234.7729 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8195 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8471 | 23 | -0.5 | 0 | 0 | 0 | 0 | 0 | 353 | 8471 | 1380 | 348.1644 | -23.2673 | -1.0681 | 1354.284 | 22.5536 | -158.304 | -60.7407 | 0 | 54.7729 | 234.7729 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8008 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 353 | 19 | 8472 | 24 | -0.6 | 0 | 0 | 0 | 0 | 0 | 353 | 8472 | 1440 | 348.1644 | -23.2673 | -1.0681 | 1414.284 | 23.5536 | -173.304 | -65.8803 | 0 | 54.7729 | 234.7729 | 65.9288 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7821 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8473 | 1 | -0.7 | 0 | 0 | 0 | 0 | 0 | 354 | 8473 | 60 | 349.1507 | -23.2783 | -1.304 | 34.284 | 0.54967 | 171.755 | -65.5829 | 0 | 54.7548 | 125.2452 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2895 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8474 | 2 | -0.8 | 0 | 0 | 0 | 0 | 0 | 354 | 8474 | 120 | 349.1507 | -23.2783 | -1.304 | 94.284 | 1.5497 | 156.755 | -59.9968 | 0 | 54.7548 | 125.2452 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.4134 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8475 | 3 | -0.7 | 0 | 0 | 0 | 0 | 0 | 354 | 8475 | 180 | 349.1507 | -23.2783 | -1.304 | 154.284 | 2.5497 | 141.755 | -51.4481 | 0 | 54.7548 | 125.2452 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.2325 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8476 | 4 | -0.8 | 0 | 0 | 0 | 0 | 0 | 354 | 8476 | 240 | 349.1507 | -23.2783 | -1.304 | 214.284 | 3.5497 | 126.755 | -41.6379 | 0 | 54.7548 | 125.2452 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3849 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8477 | 5 | -0.8 | 0 | 0 | 0 | 0 | 0 | 354 | 8477 | 300 | 349.1507 | -23.2783 | -1.304 | 274.284 | 4.5497 | 111.755 | -31.409 | 0 | 54.7548 | 125.2452 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5664 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8478 | 6 | -0.8 | 0 | 0 | 0 | 0 | 0 | 354 | 8478 | 360 | 349.1507 | -23.2783 | -1.304 | 334.284 | 5.5497 | 96.755 | -21.2217 | 0 | 54.7548 | 125.2452 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9018 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8479 | 7 | -0.8 | 0 | 0 | 0 | 0 | 0 | 354 | 8479 | 420 | 349.1507 | -23.2783 | -1.304 | 394.284 | 6.5497 | 81.755 | -11.4065 | 0 | 54.7548 | 125.2452 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.9756 | 124.9756 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8480 | 8 | -0.8 | 0 | 0 | 0 | 0 | 0 | 354 | 8480 | 480 | 349.1507 | -23.2783 | -1.304 | 454.284 | 7.5497 | 66.755 | -2.2757 | 0 | 54.7548 | 125.2452 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.515 | 125.515 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8481 | 9 | -0.7 | 0 | 1.25 | 1.25 | 1.25 | 0.63 | 354 | 8481 | 540 | 349.1507 | -23.2783 | -1.304 | 514.284 | 8.5497 | 51.755 | 5.8217 | 5.8217 | 46.4837 | 133.5163 | 56.2136 | 0 | 0 | 1.0669 | 1.0669 | -152.1463 | 0% | 0.48247 | 0 | 0 | 104.8004 | 104.8004 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8482 | 10 | -0.5 | 0 | 9.53 | 9.53 | 9.53 | 4.77 | 354 | 8482 | 600 | 349.1507 | -23.2783 | -1.304 | 574.284 | 9.5497 | 36.755 | 12.4763 | 12.4763 | 34.2619 | 145.7381 | 43.667 | 0 | 0 | 8.1344 | 8.1344 | -19.1968 | 0% | 3.6784 | 0 | 0 | 105.4263 | 105.4263 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8483 | 11 | 0.4 | 0 | 18.06 | 18.06 | 18.06 | 9.03 | 354 | 8483 | 660 | 349.1507 | -23.2783 | -1.304 | 634.284 | 10.5497 | 21.755 | 17.235 | 17.235 | 20.8838 | 159.1162 | 32.8072 | 0 | 0 | 15.4152 | 15.4152 | -9.6059 | 0% | 6.9707 | 0 | 0 | 106.8264 | 106.8264 | 0% | 12.2% | 12.2% | 80% | 9.758% | 0.68022 | 10.1527 | 6 | 4.0813 | 1.5042 | 3.821% | 3.821%
12 | 354 | 20 | 8484 | 12 | 0.6 | 0.19 | 43.25 | 43.44 | 43.25 | 21.63 | 354 | 8484 | 720 | 349.1507 | -23.2783 | -1.304 | 694.284 | 11.5497 | 6.755 | 19.6777 | 19.6777 | 6.5892 | 173.4108 | 25.9052 | 0.50755 | 0.50755 | 36.9162 | 37.4237 | -3.4708 | 0% | 16.923 | 0 | 0 | 107.7476 | 107.7476 | 0% | 12.17% | 12.17% | 80% | 9.733% | 1.647 | 10.0859 | 6 | 9.8822 | 3.6423 | 9.172% | 9.172%
12 | 354 | 20 | 8485 | 13 | 2.3 | 0.28 | 49.44 | 49.72 | 49.44 | 24.72 | 354 | 8485 | 780 | 349.1507 | -23.2783 | -1.304 | 754.284 | 12.5497 | -8.245 | 19.5479 | 19.5479 | 8.0357 | 188.0357 | 26.3109 | 0.75014 | 0.75014 | 42.1997 | 42.9498 | -2.8238 | 0% | 19.4219 | 0 | 0 | 110.5459 | 110.5459 | 0% | 12.09% | 12.09% | 80% | 9.671% | 1.8783 | 9.53 | 6 | 11.27 | 4.1538 | 10.19% | 10.19%
12 | 354 | 20 | 8486 | 14 | 2.4 | 0.19 | 47.03 | 47.22 | 47.03 | 23.52 | 354 | 8486 | 840 | 349.1507 | -23.2783 | -1.304 | 814.284 | 13.5497 | -23.245 | 16.8598 | 16.8598 | 22.2606 | 202.2606 | 33.7612 | 0.54463 | 0.54463 | 40.1426 | 40.6872 | -3.0196 | 0% | 18.3988 | 0 | 0 | 110.4956 | 110.4956 | 0% | 12.09% | 12.09% | 80% | 9.67% | 1.7791 | 9.4979 | 6 | 10.6745 | 3.9343 | 9.661% | 9.661%
12 | 354 | 20 | 8487 | 15 | 1.8 | 0.28 | 32.97 | 33.25 | 32.97 | 16.49 | 354 | 8487 | 900 | 349.1507 | -23.2783 | -1.304 | 874.284 | 14.5497 | -38.245 | 11.8926 | 11.8926 | 35.5285 | 215.5285 | 44.8602 | 0.96309 | 0.96309 | 28.1417 | 29.1047 | -4.5915 | 0% | 13.1612 | 0 | 0 | 129.7059 | 129.7059 | 0% | 12.12% | 0% | 80% | 0% | 0 | 9.6914 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8488 | 16 | 1.3 | 0.14 | 27.22 | 27.36 | 27.22 | 13.61 | 354 | 8488 | 960 | 349.1507 | -23.2783 | -1.304 | 934.284 | 15.5497 | -53.245 | 5.0747 | 5.0747 | 47.6358 | 227.6358 | 57.5097 | 0 | 0 | 23.2337 | 23.2337 | -6.0076 | 0% | 10.5063 | 0 | 0 | 128.5016 | 128.5016 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8489 | 17 | 0.6 | 0.08 | 10.47 | 10.55 | 10.47 | 5.24 | 354 | 8489 | 1020 | 349.1507 | -23.2783 | -1.304 | 994.284 | 16.5497 | -68.245 | -3.1426 | 0 | 54.7548 | 234.7548 | 65.9173 | 0 | 0 | 8.9367 | 8.9367 | -17.0973 | 0% | 4.0412 | 0 | 0 | 126.4494 | 126.4494 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8490 | 18 | -0.1 | 0 | 0 | 0 | 0 | 0 | 354 | 8490 | 1080 | 349.1507 | -23.2783 | -1.304 | 1054.284 | 17.5497 | -83.245 | -12.3562 | 0 | 54.7548 | 234.7548 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.6289 | 124.6289 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8491 | 19 | -0.5 | 0 | 0 | 0 | 0 | 0 | 354 | 8491 | 1140 | 349.1507 | -23.2783 | -1.304 | 1114.284 | 18.5497 | -98.245 | -22.222 | 0 | 54.7548 | 234.7548 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.673 | 123.673 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8492 | 20 | -0.3 | 0 | 0 | 0 | 0 | 0 | 354 | 8492 | 1200 | 349.1507 | -23.2783 | -1.304 | 1174.284 | 19.5497 | -113.245 | -32.4293 | 0 | 54.7548 | 234.7548 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.4677 | 123.4677 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8493 | 21 | -0.3 | 0 | 0 | 0 | 0 | 0 | 354 | 8493 | 1260 | 349.1507 | -23.2783 | -1.304 | 1234.284 | 20.5497 | -128.245 | -42.6407 | 0 | 54.7548 | 234.7548 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6545 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8494 | 22 | -0.5 | 0 | 0 | 0 | 0 | 0 | 354 | 8494 | 1320 | 349.1507 | -23.2783 | -1.304 | 1294.284 | 21.5497 | -143.245 | -52.373 | 0 | 54.7548 | 234.7548 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.0703 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8495 | 23 | -0.6 | 0 | 0 | 0 | 0 | 0 | 354 | 8495 | 1380 | 349.1507 | -23.2783 | -1.304 | 1354.284 | 22.5497 | -158.245 | -60.722 | 0 | 54.7548 | 234.7548 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1942 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 354 | 20 | 8496 | 24 | -0.6 | 0 | 0 | 0 | 0 | 0 | 354 | 8496 | 1440 | 349.1507 | -23.2783 | -1.304 | 1414.284 | 23.5497 | -173.245 | -65.8805 | 0 | 54.7548 | 234.7548 | 65.9173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1656 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8497 | 1 | -0.7 | 0 | 0 | 0 | 0 | 0 | 355 | 8497 | 60 | 350.137 | -23.2819 | -1.5401 | 34.284 | 0.54573 | 171.814 | -65.5992 | 0 | 54.7489 | 125.2511 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4126 | 0 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.5248 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8498 | 2 | -0.8 | 0 | 0 | 0 | 0 | 0 | 355 | 8498 | 120 | 350.137 | -23.2819 | -1.5401 | 94.284 | 1.5457 | 156.814 | -60.0291 | 0 | 54.7489 | 125.2511 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5071 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8499 | 3 | -0.8 | 0 | 0 | 0 | 0 | 0 | 355 | 8499 | 180 | 350.137 | -23.2819 | -1.5401 | 154.284 | 2.5457 | 141.814 | -51.4876 | 0 | 54.7489 | 125.2511 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4492 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8500 | 4 | -0.8 | 0 | 0 | 0 | 0 | 0 | 355 | 8500 | 240 | 350.137 | -23.2819 | -1.5401 | 214.284 | 3.5457 | 126.814 | -41.6801 | 0 | 54.7489 | 125.2511 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.4492 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8501 | 5 | -0.8 | 0 | 0 | 0 | 0 | 0 | 355 | 8501 | 300 | 350.137 | -23.2819 | -1.5401 | 274.284 | 4.5457 | 111.814 | -31.4518 | 0 | 54.7489 | 125.2511 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.7493 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8502 | 6 | -1 | 0 | 0 | 0 | 0 | 0 | 355 | 8502 | 360 | 350.137 | -23.2819 | -1.5401 | 334.284 | 5.5457 | 96.814 | -21.2637 | 0 | 54.7489 | 125.2511 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.671 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8503 | 7 | -1.3 | 0 | 0 | 0 | 0 | 0 | 355 | 8503 | 420 | 350.137 | -23.2819 | -1.5401 | 394.284 | 6.5457 | 81.814 | -11.4466 | 0 | 54.7489 | 125.2511 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.7063 | 127.7063 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8504 | 8 | -1.8 | 0 | 0 | 0 | 0 | 0 | 355 | 8504 | 480 | 350.137 | -23.2819 | -1.5401 | 454.284 | 7.5457 | 66.814 | -2.3126 | 0 | 54.7489 | 125.2511 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.1015 | 128.1015 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8505 | 9 | -1.7 | 0 | 0 | 0 | 0 | 0 | 355 | 8505 | 540 | 350.137 | -23.2819 | -1.5401 | 514.284 | 8.5457 | 51.814 | 5.7894 | 5.7894 | 46.5276 | 133.4724 | 56.266 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 107.4624 | 107.4624 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8506 | 10 | -1.6 | 0.14 | 9.17 | 9.31 | 9.17 | 4.59 | 355 | 8506 | 600 | 350.137 | -23.2819 | -1.5401 | 574.284 | 9.5457 | 36.814 | 12.4503 | 12.4503 | 34.3108 | 145.6892 | 43.7158 | 0.46935 | 0.46935 | 7.8271 | 8.2964 | -19.1353 | 0% | 3.7516 | 0 | 0 | 107.9898 | 107.9898 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8507 | 11 | -1.5 | 0.28 | 36.94 | 37.22 | 36.94 | 18.47 | 355 | 8507 | 660 | 350.137 | -23.2819 | -1.5401 | 634.284 | 10.5457 | 21.814 | 17.2171 | 17.2171 | 20.9375 | 159.0625 | 32.8469 | 0.79473 | 0.79473 | 31.5303 | 32.325 | -4.3059 | 0% | 14.6174 | 0 | 0 | 108.7329 | 108.7329 | 0% | 12.26% | 12.26% | 80% | 9.808% | 1.4336 | 10.8007 | 6 | 8.6019 | 3.1704 | 7.911% | 7.911%
12 | 355 | 21 | 8508 | 12 | -1.6 | 1.31 | 65.56 | 66.87 | 65.56 | 32.78 | 355 | 8508 | 720 | 350.137 | -23.2819 | -1.5401 | 694.284 | 11.5457 | 6.814 | 19.6695 | 19.6695 | 6.6463 | 173.3537 | 25.9233 | 3.5003 | 3.5003 | 55.959 | 59.4593 | -1.9782 | 0% | 26.8875 | 0 | 0 | 108.811 | 108.811 | 0% | 12.23% | 12.23% | 80% | 9.785% | 2.6311 | 10.8355 | 6 | 15.7863 | 5.8183 | 14.51% | 14.51%
12 | 355 | 21 | 8509 | 13 | -1.5 | 1.39 | 88.61 | 90 | 88.61 | 44.31 | 355 | 8509 | 780 | 350.137 | -23.2819 | -1.5401 | 754.284 | 12.5457 | -8.186 | 19.5499 | 19.5499 | 7.978 | 187.978 | 26.2968 | 3.724 | 3.724 | 75.6334 | 79.3573 | -1.2774 | 0% | 35.8854 | 0 | 0 | 109.877 | 109.877 | 0% | 12.2% | 12.2% | 80% | 9.763% | 3.5036 | 10.8007 | 6 | 21.0217 | 7.7479 | 19.13% | 19.13%
12 | 355 | 21 | 8510 | 14 | -1.4 | 6.86 | 99.72 | 106.58 | 99.72 | 49.86 | 355 | 8510 | 840 | 350.137 | -23.2819 | -1.5401 | 814.284 | 13.5457 | -23.186 | 16.8717 | 16.8717 | 22.2051 | 202.2051 | 33.7252 | 19.6587 | 19.6587 | 85.1163 | 104.775 | -0.77011 | 0% | 47.3793 | 0 | 0 | 110.6158 | 110.6158 | 0% | 12.17% | 12.17% | 80% | 9.736% | 4.613 | 10.7659 | 6 | 27.6777 | 10.2011 | 25.02% | 25.02%
12 | 355 | 21 | 8511 | 15 | -1.3 | 4.17 | 87.5 | 91.67 | 87.5 | 43.75 | 355 | 8511 | 900 | 350.137 | -23.2819 | -1.5401 | 874.284 | 14.5457 | -38.186 | 11.9128 | 11.9128 | 35.4769 | 215.4769 | 44.8144 | 14.3306 | 14.3306 | 74.6859 | 89.0165 | -1.046 | 0% | 40.2533 | 0 | 0 | 130.5751 | 130.5751 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.7313 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8512 | 16 | -1.6 | 1.58 | 52.86 | 54.44 | 52.86 | 26.43 | 355 | 8512 | 960 | 350.137 | -23.2819 | -1.5401 | 934.284 | 15.5457 | -53.186 | 5.1016 | 5.1016 | 47.5884 | 227.5884 | 57.4594 | 0 | 0 | 45.1188 | 45.1188 | -2.8624 | 0% | 20.4027 | 0 | 0 | 128.003 | 128.003 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.8355 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8513 | 17 | -1.7 | 0.08 | 16.67 | 16.75 | 16.67 | 8.34 | 355 | 8513 | 1020 | 350.137 | -23.2819 | -1.5401 | 994.284 | 16.5457 | -68.186 | -3.1109 | 0 | 54.7489 | 234.7489 | 65.9136 | 0 | 0 | 14.2287 | 14.2287 | -10.8396 | 0% | 6.4342 | 0 | 0 | 125.5839 | 125.5839 | 0% | 12.29% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8514 | 18 | -1.8 | 0 | 0 | 0 | 0 | 0 | 355 | 8514 | 1080 | 350.137 | -23.2819 | -1.5401 | 1054.284 | 17.5457 | -83.186 | -12.321 | 0 | 54.7489 | 234.7489 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.0745 | 124.0745 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8515 | 19 | -1.7 | 0 | 0 | 0 | 0 | 0 | 355 | 8515 | 1140 | 350.137 | -23.2819 | -1.5401 | 1114.284 | 18.5457 | -98.186 | -22.1848 | 0 | 54.7489 | 234.7489 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.4759 | 123.4759 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8516 | 20 | -1.7 | 0 | 0 | 0 | 0 | 0 | 355 | 8516 | 1200 | 350.137 | -23.2819 | -1.5401 | 1174.284 | 19.5457 | -113.186 | -32.3912 | 0 | 54.7489 | 234.7489 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 122.3913 | 122.3913 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8517 | 21 | -1.5 | 0 | 0 | 0 | 0 | 0 | 355 | 8517 | 1260 | 350.137 | -23.2819 | -1.5401 | 1234.284 | 20.5457 | -128.186 | -42.6035 | 0 | 54.7489 | 234.7489 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5665 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8518 | 22 | -0.9 | 0 | 0 | 0 | 0 | 0 | 355 | 8518 | 1320 | 350.137 | -23.2819 | -1.5401 | 1294.284 | 21.5457 | -143.186 | -52.3393 | 0 | 54.7489 | 234.7489 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.891 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8519 | 23 | -0.4 | 0 | 0 | 0 | 0 | 0 | 355 | 8519 | 1380 | 350.137 | -23.2819 | -1.5401 | 1354.284 | 22.5457 | -158.186 | -60.6969 | 0 | 54.7489 | 234.7489 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.0711 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
12 | 355 | 21 | 8520 | 24 | -0.8 | 0 | 0 | 0 | 0 | 0 | 355 | 8520 | 1440 | 350.137 | -23.2819 | -1.5401 | 1414.284 | 23.5457 | -173.186 | -65.8733 | 0 | 54.7489 | 234.7489 | 65.9136 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.6228 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8521 | 1 | -0.2 | 0 | 0 | 0 | 0 | 0 | 356 | 8521 | 60 | 351.1233 | -23.278 | -1.7761 | 34.284 | 0.5418 | 171.873 | -65.6081 | 0 | 54.7553 | 125.2447 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.7893 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8522 | 2 | -0.4 | 0 | 0 | 0 | 0 | 0 | 356 | 8522 | 120 | 351.1233 | -23.278 | -1.7761 | 94.284 | 1.5418 | 156.873 | -60.055 | 0 | 54.7553 | 125.2447 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.8688 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8523 | 3 | -1 | 0 | 0 | 0 | 0 | 0 | 356 | 8523 | 180 | 351.1233 | -23.278 | -1.7761 | 154.284 | 2.5418 | 141.873 | -51.5216 | 0 | 54.7553 | 125.2447 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5579 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8524 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 356 | 8524 | 240 | 351.1233 | -23.278 | -1.7761 | 214.284 | 3.5418 | 126.873 | -41.7173 | 0 | 54.7553 | 125.2447 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5579 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6277 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8525 | 5 | -0.2 | 0 | 0 | 0 | 0 | 0 | 356 | 8525 | 300 | 351.1233 | -23.278 | -1.7761 | 274.284 | 4.5418 | 111.873 | -31.4896 | 0 | 54.7553 | 125.2447 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.8405 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8526 | 6 | -0.2 | 0 | 0 | 0 | 0 | 0 | 356 | 8526 | 360 | 351.1233 | -23.278 | -1.7761 | 334.284 | 5.5418 | 96.873 | -21.3006 | 0 | 54.7553 | 125.2447 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.8085 | 0 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8527 | 7 | -0.2 | 0 | 0 | 0 | 0 | 0 | 356 | 8527 | 420 | 351.1233 | -23.278 | -1.7761 | 394.284 | 6.5418 | 81.873 | -11.4813 | 0 | 54.7553 | 125.2447 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.1298 | 141.1298 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3546 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8528 | 8 | -0.1 | 0 | 0 | 0 | 0 | 0 | 356 | 8528 | 480 | 351.1233 | -23.278 | -1.7761 | 454.284 | 7.5418 | 66.873 | -2.3438 | 0 | 54.7553 | 125.2447 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 144.6585 | 144.6585 | 0% | 12.24% | 0% | 80% | 0% | 0 | 10.3208 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8529 | 9 | 0.1 | 0 | 1.67 | 1.67 | 1.67 | 0.84 | 356 | 8529 | 540 | 351.1233 | -23.278 | -1.7761 | 514.284 | 8.5418 | 51.873 | 5.7633 | 5.7633 | 46.5755 | 133.4245 | 56.3159 | 0 | 0 | 1.4254 | 1.4254 | -112.2918 | 0% | 0.64458 | 0 | 0 | 124.5786 | 124.5786 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8530 | 10 | 0.4 | 12.31 | 21.47 | 33.78 | 21.47 | 10.74 | 356 | 8530 | 600 | 351.1233 | -23.278 | -1.7761 | 574.284 | 9.5418 | 36.873 | 12.4311 | 12.4311 | 34.3628 | 145.6372 | 43.7609 | 41.3012 | 41.3012 | 18.3258 | 59.627 | -1.8872 | 0% | 26.9633 | 0 | 0 | 126.6847 | 126.6847 | 0% | 12.15% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8531 | 11 | 0.5 | 44.92 | 55.28 | 100.2 | 55.28 | 27.64 | 356 | 8531 | 660 | 351.1233 | -23.278 | -1.7761 | 634.284 | 10.5418 | 21.873 | 17.2064 | 17.2064 | 20.9933 | 159.0067 | 32.8812 | 127.5247 | 127.5247 | 47.1844 | 174.7091 | -0.11309 | 0% | 79.0035 | 0 | 0 | 127.2835 | 127.2835 | 0% | 12.02% | 12.02% | 80% | 9.618% | 7.5986 | 10.1193 | 6 | 45.5918 | 16.8037 | 35.82% | 35.82%
12 | 356 | 22 | 8532 | 12 | 1.2 | 35 | 88.14 | 123.14 | 88.14 | 44.07 | 356 | 8532 | 720 | 351.1233 | -23.278 | -1.7761 | 694.284 | 11.5418 | 6.873 | 19.6687 | 19.6687 | 6.704 | 173.296 | 25.9343 | 93.5151 | 93.5151 | 75.2322 | 168.7473 | -0.1353 | 0% | 76.3075 | 0 | 0 | 124.687 | 124.687 | 0% | 12% | 12% | 80% | 9.604% | 7.3284 | 9.8874 | 6 | 43.9704 | 16.2061 | 35.26% | 35.26%
12 | 356 | 22 | 8533 | 13 | 1.4 | 16.94 | 118.06 | 135 | 118.06 | 59.03 | 356 | 8533 | 780 | 351.1233 | -23.278 | -1.7761 | 754.284 | 12.5418 | -8.127 | 19.5594 | 19.5594 | 7.9213 | 187.9213 | 26.2758 | 45.3715 | 45.3715 | 100.7705 | 146.142 | -0.27724 | 0% | 66.0854 | 0 | 0 | 124.3144 | 124.3144 | 0% | 12.02% | 12.02% | 80% | 9.617% | 6.3552 | 9.8218 | 6 | 38.1315 | 14.0541 | 30.67% | 30.67%
12 | 356 | 22 | 8534 | 14 | 1.6 | 7.03 | 133.97 | 141 | 133.97 | 66.99 | 356 | 8534 | 840 | 351.1233 | -23.278 | -1.7761 | 814.284 | 13.5418 | -23.127 | 16.8907 | 16.8907 | 22.1519 | 202.1519 | 33.6841 | 20.1335 | 20.1335 | 114.3505 | 134.4841 | -0.36732 | 0% | 60.8137 | 0 | 0 | 123.9005 | 123.9005 | 0% | 12.03% | 12.03% | 80% | 9.62% | 5.8505 | 9.7564 | 6 | 35.1031 | 12.9379 | 28.33% | 28.33%
12 | 356 | 22 | 8535 | 15 | 1.7 | 3.61 | 104.25 | 107.86 | 104.25 | 52.13 | 356 | 8535 | 900 | 351.1233 | -23.278 | -1.7761 | 874.284 | 14.5418 | -38.127 | 11.9398 | 11.9398 | 35.4287 | 215.4287 | 44.765 | 12.3891 | 12.3891 | 88.9829 | 101.372 | -0.74751 | 0% | 45.8404 | 0 | 0 | 141.5207 | 141.5207 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8536 | 16 | 1.4 | 9.81 | 67.78 | 77.59 | 67.78 | 33.89 | 356 | 8536 | 960 | 351.1233 | -23.278 | -1.7761 | 934.284 | 15.5418 | -53.127 | 5.1347 | 5.1347 | 47.5451 | 227.5451 | 57.4067 | 0 | 0 | 57.8538 | 57.8538 | -1.9273 | 0% | 26.1615 | 0 | 0 | 138.5116 | 138.5116 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8537 | 17 | 1.5 | 0.64 | 21.67 | 22.31 | 21.67 | 10.84 | 356 | 8537 | 1020 | 351.1233 | -23.278 | -1.7761 | 994.284 | 16.5418 | -68.127 | -3.0734 | 0 | 54.7553 | 234.7553 | 65.9176 | 0 | 0 | 18.4965 | 18.4965 | -7.7257 | 0% | 8.3641 | 0 | 0 | 134.3401 | 134.3401 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.7891 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8538 | 18 | 1.3 | 0 | 0 | 0 | 0 | 0 | 356 | 8538 | 1080 | 351.1233 | -23.278 | -1.7761 | 1054.284 | 17.5418 | -83.127 | -12.2805 | 0 | 54.7553 | 234.7553 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.1873 | 131.1873 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8546 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8539 | 19 | 1.1 | 0 | 0 | 0 | 0 | 0 | 356 | 8539 | 1140 | 351.1233 | -23.278 | -1.7761 | 1114.284 | 18.5418 | -98.127 | -22.1425 | 0 | 54.7553 | 234.7553 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.2378 | 129.2378 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8540 | 20 | 0.9 | 0 | 0 | 0 | 0 | 0 | 356 | 8540 | 1200 | 351.1233 | -23.278 | -1.7761 | 1174.284 | 19.5418 | -113.127 | -32.3482 | 0 | 54.7553 | 234.7553 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.3859 | 126.3859 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9864 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8541 | 21 | 0.6 | 0 | 0 | 0 | 0 | 0 | 356 | 8541 | 1260 | 351.1233 | -23.278 | -1.7761 | 1234.284 | 20.5418 | -128.127 | -42.5612 | 0 | 54.7553 | 234.7553 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.6775 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.0859 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8542 | 22 | 0.1 | 0 | 0 | 0 | 0 | 0 | 356 | 8542 | 1320 | 351.1233 | -23.278 | -1.7761 | 1294.284 | 21.5418 | -143.127 | -52.3 | 0 | 54.7553 | 234.7553 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.008 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8543 | 23 | 0.3 | 0 | 0 | 0 | 0 | 0 | 356 | 8543 | 1380 | 351.1233 | -23.278 | -1.7761 | 1354.284 | 22.5418 | -158.127 | -60.6654 | 0 | 54.7553 | 234.7553 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.4779 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 356 | 22 | 8544 | 24 | 0.4 | 0 | 0 | 0 | 0 | 0 | 356 | 8544 | 1440 | 351.1233 | -23.278 | -1.7761 | 1414.284 | 23.5418 | -173.127 | -65.8587 | 0 | 54.7553 | 234.7553 | 65.9176 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1002 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8545 | 1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 357 | 8545 | 60 | 352.1096 | -23.2667 | -2.0116 | 34.284 | 0.53787 | 171.9319 | -65.6098 | 0 | 54.7739 | 125.2261 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9929 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8546 | 2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 357 | 8546 | 120 | 352.1096 | -23.2667 | -2.0116 | 94.284 | 1.5379 | 156.9319 | -60.0746 | 0 | 54.7739 | 125.2261 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.353 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8547 | 3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 357 | 8547 | 180 | 352.1096 | -23.2667 | -2.0116 | 154.284 | 2.5379 | 141.9319 | -51.55 | 0 | 54.7739 | 125.2261 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1036 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8548 | 4 | 0.2 | 0 | 0 | 0 | 0 | 0 | 357 | 8548 | 240 | 352.1096 | -23.2667 | -2.0116 | 214.284 | 3.5379 | 126.9319 | -41.7493 | 0 | 54.7739 | 125.2261 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.1036 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.2197 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8549 | 5 | -0.3 | 0 | 0 | 0 | 0 | 0 | 357 | 8549 | 300 | 352.1096 | -23.2667 | -2.0116 | 274.284 | 4.5379 | 111.9319 | -31.5224 | 0 | 54.7739 | 125.2261 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.214 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.3885 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8550 | 6 | -0.4 | 0 | 0 | 0 | 0 | 0 | 357 | 8550 | 360 | 352.1096 | -23.2667 | -2.0116 | 334.284 | 5.5379 | 96.9319 | -21.3323 | 0 | 54.7739 | 125.2261 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.3194 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4224 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8551 | 7 | -0.5 | 0 | 0 | 0 | 0 | 0 | 357 | 8551 | 420 | 352.1096 | -23.2667 | -2.0116 | 394.284 | 6.5379 | 81.9319 | -11.5105 | 0 | 54.7739 | 125.2261 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 131.6727 | 131.6727 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8552 | 8 | -0.6 | 0 | 0 | 0 | 0 | 0 | 357 | 8552 | 480 | 352.1096 | -23.2667 | -2.0116 | 454.284 | 7.5379 | 66.9319 | -2.3691 | 0 | 54.7739 | 125.2261 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.2899 | 133.2899 | 0% | 12.26% | 0% | 80% | 0% | 0 | 10.4906 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8553 | 9 | -0.5 | 0 | 0 | 0 | 0 | 0 | 357 | 8553 | 540 | 352.1096 | -23.2667 | -2.0116 | 514.284 | 8.5379 | 51.9319 | 5.7435 | 5.7435 | 46.6274 | 133.3726 | 56.3633 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 112.7847 | 112.7847 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8554 | 10 | -0.5 | 0 | 24.58 | 24.58 | 24.58 | 12.29 | 357 | 8554 | 600 | 352.1096 | -23.2667 | -2.0116 | 574.284 | 9.5379 | 36.9319 | 12.4185 | 12.4185 | 34.418 | 145.582 | 43.8021 | 0 | 0 | 20.9803 | 20.9803 | -6.9506 | 0% | 9.4873 | 0 | 0 | 113.9303 | 113.9303 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8555 | 11 | -0.4 | 9.17 | 96.94 | 106.11 | 96.94 | 48.47 | 357 | 8555 | 660 | 352.1096 | -23.2667 | -2.0116 | 634.284 | 10.5379 | 21.9319 | 17.2029 | 17.2029 | 21.051 | 158.949 | 32.9101 | 26.0297 | 26.0297 | 82.7435 | 108.7732 | -0.68944 | 0% | 49.1872 | 0 | 0 | 116.9222 | 116.9222 | 0% | 12.13% | 12.13% | 80% | 9.702% | 4.7722 | 10.4224 | 6 | 28.633 | 10.5532 | 24.49% | 24.49%
12 | 357 | 23 | 8556 | 12 | -0.4 | 28.42 | 101.19 | 129.61 | 101.19 | 50.6 | 357 | 8556 | 720 | 352.1096 | -23.2667 | -2.0116 | 694.284 | 11.5379 | 6.9319 | 19.6752 | 19.6752 | 6.7622 | 173.2378 | 25.9383 | 75.9074 | 75.9074 | 86.3711 | 162.2785 | -0.19703 | 0% | 73.3823 | 0 | 0 | 116.1217 | 116.1217 | 0% | 12.07% | 12.07% | 80% | 9.654% | 7.0843 | 10.4224 | 6 | 42.5061 | 15.6664 | 36.6% | 36.6%
12 | 357 | 23 | 8557 | 13 | -0.8 | 26.81 | 91.25 | 118.06 | 91.25 | 45.63 | 357 | 8557 | 780 | 352.1096 | -23.2667 | -2.0116 | 754.284 | 12.5379 | -8.0681 | 19.5762 | 19.5762 | 7.8654 | 187.8654 | 26.2479 | 71.7651 | 71.7651 | 77.8867 | 149.6518 | -0.28812 | 0% | 67.6725 | 0 | 0 | 114.4352 | 114.4352 | 0% | 12.1% | 12.1% | 80% | 9.677% | 6.5485 | 10.559 | 6 | 39.2912 | 14.4815 | 34.33% | 34.33%
12 | 357 | 23 | 8558 | 14 | -0.6 | 6.11 | 83.06 | 89.17 | 83.06 | 41.53 | 357 | 8558 | 840 | 352.1096 | -23.2667 | -2.0116 | 814.284 | 13.5379 | -23.0681 | 16.9167 | 16.9167 | 22.101 | 202.101 | 33.6378 | 17.4819 | 17.4819 | 70.8961 | 88.3781 | -1.0397 | 0% | 39.9646 | 0 | 0 | 113.0233 | 113.0233 | 0% | 12.16% | 12.16% | 80% | 9.727% | 3.8872 | 10.4906 | 6 | 23.3232 | 8.5962 | 20.64% | 20.64%
12 | 357 | 23 | 8559 | 15 | -0.5 | 0.56 | 72.92 | 73.48 | 72.92 | 36.46 | 357 | 8559 | 900 | 352.1096 | -23.2667 | -2.0116 | 874.284 | 14.5379 | -38.0681 | 11.9734 | 11.9734 | 35.3838 | 215.3838 | 44.7122 | 1.9183 | 1.9183 | 62.2411 | 64.1594 | -1.7318 | 0% | 29.0129 | 0 | 0 | 132.4403 | 132.4403 | 0% | 12.18% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8560 | 16 | -0.5 | 7.36 | 60.97 | 68.33 | 60.97 | 30.49 | 357 | 8560 | 960 | 352.1096 | -23.2667 | -2.0116 | 934.284 | 15.5379 | -53.0681 | 5.1738 | 5.1738 | 47.506 | 227.506 | 57.3518 | 0 | 0 | 52.0412 | 52.0412 | -2.3223 | 0% | 23.533 | 0 | 0 | 131.7285 | 131.7285 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.4565 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8561 | 17 | -0.8 | 0.36 | 15.28 | 15.64 | 15.28 | 7.64 | 357 | 8561 | 1020 | 352.1096 | -23.2667 | -2.0116 | 994.284 | 16.5379 | -68.0681 | -3.0302 | 0 | 54.7739 | 234.7739 | 65.9294 | 0 | 0 | 13.0423 | 13.0423 | -11.7273 | 0% | 5.8977 | 0 | 0 | 127.8319 | 127.8319 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.559 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8562 | 18 | -0.9 | 0 | 0 | 0 | 0 | 0 | 357 | 8562 | 1080 | 352.1096 | -23.2667 | -2.0116 | 1054.284 | 17.5379 | -83.0681 | -12.2347 | 0 | 54.7739 | 234.7739 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.9749 | 125.9749 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8563 | 19 | -1.1 | 0 | 0 | 0 | 0 | 0 | 357 | 8563 | 1140 | 352.1096 | -23.2667 | -2.0116 | 1114.284 | 18.5379 | -98.0681 | -22.0952 | 0 | 54.7739 | 234.7739 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.6323 | 124.6323 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8564 | 20 | -1.2 | 0 | 0 | 0 | 0 | 0 | 357 | 8564 | 1200 | 352.1096 | -23.2667 | -2.0116 | 1174.284 | 19.5379 | -113.0681 | -32.3004 | 0 | 54.7739 | 234.7739 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 122.98 | 122.98 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6967 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8565 | 21 | -1.5 | 0 | 0 | 0 | 0 | 0 | 357 | 8565 | 1260 | 352.1096 | -23.2667 | -2.0116 | 1234.284 | 20.5379 | -128.0681 | -42.514 | 0 | 54.7739 | 234.7739 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.8426 | 0 | 0% | 12.3% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8566 | 22 | -1.1 | 0 | 0 | 0 | 0 | 0 | 357 | 8566 | 1320 | 352.1096 | -23.2667 | -2.0116 | 1294.284 | 21.5379 | -143.0681 | -52.2552 | 0 | 54.7739 | 234.7739 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.5701 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8567 | 23 | -1.8 | 0 | 0 | 0 | 0 | 0 | 357 | 8567 | 1380 | 352.1096 | -23.2667 | -2.0116 | 1354.284 | 22.5379 | -158.0681 | -60.6276 | 0 | 54.7739 | 234.7739 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.5398 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 357 | 23 | 8568 | 24 | -1.1 | 0 | 0 | 0 | 0 | 0 | 357 | 8568 | 1440 | 352.1096 | -23.2667 | -2.0116 | 1414.284 | 23.5379 | -173.0681 | -65.8367 | 0 | 54.7739 | 234.7739 | 65.9294 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.376 | 0 | 0% | 12.28% | 0% | 80% | 0% | 0 | 10.6622 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8569 | 1 | -1.7 | 0 | 0 | 0 | 0 | 0 | 358 | 8569 | 60 | 353.0959 | -23.2479 | -2.2461 | 34.284 | 0.53396 | 171.9905 | -65.604 | 0 | 54.8046 | 125.1954 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.837 | 0 | 0% | 12.31% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8570 | 2 | -2.4 | 0 | 0 | 0 | 0 | 0 | 358 | 8570 | 120 | 353.0959 | -23.2479 | -2.2461 | 94.284 | 1.534 | 156.9905 | -60.0877 | 0 | 54.8046 | 125.1954 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6447 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8571 | 3 | -2.5 | 0 | 0 | 0 | 0 | 0 | 358 | 8571 | 180 | 353.0959 | -23.2479 | -2.2461 | 154.284 | 2.534 | 141.9905 | -51.5728 | 0 | 54.8046 | 125.1954 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.5379 | 0 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.1519 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8572 | 4 | -2.8 | 0 | 0 | 0 | 0 | 0 | 358 | 8572 | 240 | 353.0959 | -23.2479 | -2.2461 | 214.284 | 3.534 | 126.9905 | -41.776 | 0 | 54.8046 | 125.1954 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9951 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8573 | 5 | -3 | 0 | 0 | 0 | 0 | 0 | 358 | 8573 | 300 | 353.0959 | -23.2479 | -2.2461 | 274.284 | 4.534 | 111.9905 | -31.55 | 0 | 54.8046 | 125.1954 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -15.3876 | 0 | 0% | 12.36% | 0% | 80% | 0% | 0 | 11.3301 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8574 | 6 | -3.7 | 0 | 0 | 0 | 0 | 0 | 358 | 8574 | 360 | 353.0959 | -23.2479 | -2.2461 | 334.284 | 5.534 | 96.9905 | -21.3588 | 0 | 54.8046 | 125.1954 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -11.3458 | 0 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8575 | 7 | -4.1 | 0 | 0 | 0 | 0 | 0 | 358 | 8575 | 420 | 353.0959 | -23.2479 | -2.2461 | 394.284 | 6.534 | 81.9905 | -11.5343 | 0 | 54.8046 | 125.1954 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 142.6922 | 142.6922 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8576 | 8 | -4.2 | 0 | 0 | 0 | 0 | 0 | 358 | 8576 | 480 | 353.0959 | -23.2479 | -2.2461 | 454.284 | 7.534 | 66.9905 | -2.3885 | 0 | 54.8046 | 125.1954 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.8169 | 146.8169 | 0% | 12.42% | 0% | 80% | 0% | 0 | 11.765 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8577 | 9 | -5.6 | 0 | 1.58 | 1.58 | 1.58 | 0.79 | 358 | 8577 | 540 | 353.0959 | -23.2479 | -2.2461 | 514.284 | 8.534 | 51.9905 | 5.7301 | 5.7301 | 46.6831 | 133.3169 | 56.4081 | 0 | 0 | 1.3486 | 1.3486 | -129.3251 | 0% | 0.60984 | 0 | 0 | 124.4692 | 124.4692 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8578 | 10 | -6 | 8.61 | 40.28 | 48.89 | 40.28 | 20.14 | 358 | 8578 | 600 | 353.0959 | -23.2479 | -2.2461 | 574.284 | 9.534 | 36.9905 | 12.4128 | 12.4128 | 34.4761 | 145.5239 | 43.8396 | 28.891 | 28.891 | 34.3811 | 63.2721 | -1.9857 | 0% | 28.6117 | 0 | 0 | 126.0002 | 126.0002 | 0% | 12.41% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8579 | 11 | -5 | 52.78 | 42.36 | 95.14 | 42.36 | 21.18 | 358 | 8579 | 660 | 353.0959 | -23.2479 | -2.2461 | 634.284 | 10.534 | 21.9905 | 17.2065 | 17.2065 | 21.1106 | 158.8894 | 32.9336 | 149.7497 | 149.7497 | 36.1565 | 185.9062 | -0.13179 | 0% | 84.0668 | 0 | 0 | 126.7089 | 126.7089 | 0% | 12.2% | 12.2% | 80% | 9.757% | 8.2025 | 12.0605 | 6 | 49.2149 | 18.1391 | 38.84% | 38.84%
12 | 358 | 24 | 8580 | 12 | -4.3 | 14.72 | 63.19 | 77.91 | 63.19 | 31.6 | 358 | 8580 | 720 | 353.0959 | -23.2479 | -2.2461 | 694.284 | 11.534 | 6.9905 | 19.6892 | 19.6892 | 6.821 | 173.179 | 25.9352 | 39.2902 | 39.2902 | 53.936 | 93.2262 | -1.0431 | 0% | 42.1569 | 0 | 0 | 121.0612 | 121.0612 | 0% | 12.3% | 12.3% | 80% | 9.837% | 4.1471 | 11.8017 | 6 | 24.8826 | 9.1709 | 20.55% | 20.55%
12 | 358 | 24 | 8581 | 13 | -2.9 | 41.25 | 98.47 | 139.72 | 98.47 | 49.24 | 358 | 8581 | 780 | 353.0959 | -23.2479 | -2.2461 | 754.284 | 12.534 | -8.0095 | 19.6003 | 19.6003 | 7.8105 | 187.8105 | 26.2131 | 110.3206 | 110.3206 | 84.0494 | 194.37 | -0.063798 | 0% | 87.8941 | 0 | 0 | 124.9939 | 124.9939 | 0% | 12.11% | 12.11% | 80% | 9.692% | 8.5185 | 11.2943 | 6 | 51.1113 | 18.838 | 40.89% | 40.89%
12 | 358 | 24 | 8582 | 14 | -2.1 | 33.33 | 178.33 | 211.66 | 178.33 | 89.17 | 358 | 8582 | 840 | 353.0959 | -23.2479 | -2.2461 | 814.284 | 13.534 | -23.0095 | 16.9498 | 16.9498 | 22.0524 | 202.0524 | 33.5865 | 95.2398 | 95.2398 | 152.2142 | 247.454 | 0.13045 | 13.05% | 111.8987 | 14.5975 | 10.2182 | 107.7282 | 107.7282 | 9.485% | 12.02% | 12.02% | 80% | 9.619% | 10.7634 | 11.0106 | 6 | 64.5805 | 23.8023 | 59.95% | 59.95%
12 | 358 | 24 | 8583 | 15 | -2.4 | 3.06 | 77.78 | 80.84 | 77.78 | 38.89 | 358 | 8583 | 900 | 353.0959 | -23.2479 | -2.2461 | 874.284 | 14.534 | -38.0095 | 12.0135 | 12.0135 | 35.3424 | 215.3424 | 44.656 | 10.4578 | 10.4578 | 66.3894 | 76.8471 | -1.3746 | 0% | 34.7503 | 0 | 0 | 140.94 | 140.94 | 0% | 12.24% | 0% | 80% | 0% | 0 | 11.1164 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8584 | 16 | -2.8 | 8.75 | 60.14 | 68.89 | 60.14 | 30.07 | 358 | 8584 | 960 | 353.0959 | -23.2479 | -2.2461 | 934.284 | 15.534 | -53.0095 | 5.2191 | 5.2191 | 47.4712 | 227.4712 | 57.2948 | 0 | 0 | 51.3327 | 51.3327 | -2.477 | 0% | 23.2126 | 0 | 0 | 138.446 | 138.446 | 0% | 12.29% | 0% | 80% | 0% | 0 | 11.2586 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8585 | 17 | -3.3 | 11.94 | 38.06 | 50 | 38.06 | 19.03 | 358 | 8585 | 1020 | 353.0959 | -23.2479 | -2.2461 | 994.284 | 16.534 | -68.0095 | -2.9815 | 0 | 54.8046 | 234.8046 | 65.9488 | 0 | 0 | 32.4862 | 32.4862 | -4.4191 | 0% | 14.6903 | 0 | 0 | 135.6416 | 135.6416 | 0% | 12.34% | 0% | 80% | 0% | 0 | 11.4379 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8586 | 18 | -3.4 | 0 | 0 | 0 | 0 | 0 | 358 | 8586 | 1080 | 353.0959 | -23.2479 | -2.2461 | 1054.284 | 17.534 | -83.0095 | -12.1838 | 0 | 54.8046 | 234.8046 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.6974 | 129.6974 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.4739 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8587 | 19 | -4.1 | 0 | 0 | 0 | 0 | 0 | 358 | 8587 | 1140 | 353.0959 | -23.2479 | -2.2461 | 1114.284 | 18.534 | -98.0095 | -22.043 | 0 | 54.8046 | 234.8046 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.0889 | 126.0889 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8588 | 20 | -5.1 | 0 | 0 | 0 | 0 | 0 | 358 | 8588 | 1200 | 353.0959 | -23.2479 | -2.2461 | 1174.284 | 19.534 | -113.0095 | -32.2477 | 0 | 54.8046 | 234.8046 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.9066 | 120.9066 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.0978 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8589 | 21 | -4.6 | 0 | 0 | 0 | 0 | 0 | 358 | 8589 | 1260 | 353.0959 | -23.2479 | -2.2461 | 1234.284 | 20.534 | -128.0095 | -42.4618 | 0 | 54.8046 | 234.8046 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.2172 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8590 | 22 | -4.6 | 0 | 0 | 0 | 0 | 0 | 358 | 8590 | 1320 | 353.0959 | -23.2479 | -2.2461 | 1294.284 | 21.534 | -143.0095 | -52.2052 | 0 | 54.8046 | 234.8046 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.034 | 0 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8591 | 23 | -5.2 | 0 | 0 | 0 | 0 | 0 | 358 | 8591 | 1380 | 353.0959 | -23.2479 | -2.2461 | 1354.284 | 22.534 | -158.0095 | -60.5835 | 0 | 54.8046 | 234.8046 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.6893 | 0 | 0% | 12.46% | 0% | 80% | 0% | 0 | 12.1351 | 6 | 0 | 0 | 0% | 0%
12 | 358 | 24 | 8592 | 24 | -5.6 | 0 | 0 | 0 | 0 | 0 | 358 | 8592 | 1440 | 353.0959 | -23.2479 | -2.2461 | 1414.284 | 23.534 | -173.0095 | -65.8074 | 0 | 54.8046 | 234.8046 | 65.9488 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.0397 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8593 | 1 | -6 | 0 | 0 | 0 | 0 | 0 | 359 | 8593 | 60 | 354.0822 | -23.2218 | -2.4793 | 34.284 | 0.53008 | 172.0488 | -65.5909 | 0 | 54.8475 | 125.1525 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.332 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8594 | 2 | -6.1 | 0 | 0 | 0 | 0 | 0 | 359 | 8594 | 120 | 354.0822 | -23.2218 | -2.4793 | 94.284 | 1.5301 | 157.0488 | -60.0944 | 0 | 54.8475 | 125.1525 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.3536 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8595 | 3 | -6.2 | 0 | 0 | 0 | 0 | 0 | 359 | 8595 | 180 | 354.0822 | -23.2218 | -2.4793 | 154.284 | 2.5301 | 142.0488 | -51.5899 | 0 | 54.8475 | 125.1525 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.3752 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8596 | 4 | -5.9 | 0 | 0 | 0 | 0 | 0 | 359 | 8596 | 240 | 354.0822 | -23.2218 | -2.4793 | 214.284 | 3.5301 | 127.0488 | -41.7976 | 0 | 54.8475 | 125.1525 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.918 | 0 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.3983 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8597 | 5 | -6.3 | 0 | 0 | 0 | 0 | 0 | 359 | 8597 | 300 | 354.0822 | -23.2218 | -2.4793 | 274.284 | 4.5301 | 112.0488 | -31.5725 | 0 | 54.8475 | 125.1525 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.3126 | 0 | 0% | 12.51% | 0% | 80% | 0% | 0 | 12.5503 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8598 | 6 | -6.8 | 0 | 0 | 0 | 0 | 0 | 359 | 8598 | 360 | 354.0822 | -23.2218 | -2.4793 | 334.284 | 5.5301 | 97.0488 | -21.3801 | 0 | 54.8475 | 125.1525 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8194 | 0 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7418 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8599 | 7 | -7.1 | 0 | 0 | 0 | 0 | 0 | 359 | 8599 | 420 | 354.0822 | -23.2218 | -2.4793 | 394.284 | 6.5301 | 82.0488 | -11.5525 | 0 | 54.8475 | 125.1525 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.9656 | 129.9656 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8600 | 8 | -7.3 | 0 | 0 | 0 | 0 | 0 | 359 | 8600 | 480 | 354.0822 | -23.2218 | -2.4793 | 454.284 | 7.5301 | 67.0488 | -2.4021 | 0 | 54.8475 | 125.1525 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.9088 | 132.9088 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8601 | 9 | -8.3 | 0 | 2.03 | 2.03 | 2.03 | 1.02 | 359 | 8601 | 540 | 354.0822 | -23.2218 | -2.4793 | 514.284 | 8.5301 | 52.0488 | 5.723 | 5.723 | 46.7426 | 133.2574 | 56.4503 | 0 | 0 | 1.7327 | 1.7327 | -104.4712 | 0% | 0.78353 | 0 | 0 | 111.3758 | 111.3758 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8602 | 10 | -6.5 | 6.58 | 30.56 | 37.14 | 30.56 | 15.28 | 359 | 8602 | 600 | 354.0822 | -23.2218 | -2.4793 | 574.284 | 9.5301 | 37.0488 | 12.4139 | 12.4139 | 34.5371 | 145.4629 | 43.8732 | 22.065 | 22.065 | 26.0846 | 48.1496 | -2.8884 | 0% | 21.7732 | 0 | 0 | 117.351 | 117.351 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8603 | 11 | -4.6 | 29.08 | 62.14 | 91.22 | 62.14 | 31.07 | 359 | 8603 | 660 | 354.0822 | -23.2218 | -2.4793 | 634.284 | 10.5301 | 22.0488 | 17.2172 | 17.2172 | 21.1719 | 158.8281 | 32.9515 | 82.4402 | 82.4402 | 53.0398 | 135.48 | -0.47262 | 0% | 61.2641 | 0 | 0 | 121.7491 | 121.7491 | 0% | 12.25% | 12.25% | 80% | 9.801% | 6.0044 | 11.9122 | 6 | 36.0265 | 13.2782 | 29.59% | 29.59%
12 | 359 | 25 | 8604 | 12 | -3.3 | 59.92 | 76.94 | 136.86 | 76.94 | 38.47 | 359 | 8604 | 720 | 354.0822 | -23.2218 | -2.4793 | 694.284 | 11.5301 | 7.0488 | 19.7104 | 19.7104 | 6.8801 | 173.1199 | 25.9251 | 159.7848 | 159.7848 | 65.6724 | 225.4572 | 0.051404 | 5.14% | 101.9518 | 5.2407 | 3.6685 | 123.1778 | 123.1778 | 2.978% | 12.09% | 12.09% | 80% | 9.671% | 9.8594 | 11.4379 | 6 | 59.1562 | 21.8031 | 48.03% | 48.03%
12 | 359 | 25 | 8605 | 13 | -1.3 | 130.42 | 83.47 | 213.89 | 83.47 | 41.74 | 359 | 8605 | 780 | 354.0822 | -23.2218 | -2.4793 | 754.284 | 12.5301 | -7.9512 | 19.6317 | 19.6317 | 7.7568 | 187.7568 | 26.1714 | 348.3889 | 348.3889 | 71.2461 | 419.635 | 0.41157 | 41.16% | 189.7589 | 78.0986 | 54.669 | 108.005 | 108.005 | 50.62% | 11.8% | 11.8% | 85% | 10.03% | 19.0289 | 10.7313 | 6 | 114.1737 | 42.0808 | 105.7% | 105.7%
12 | 359 | 25 | 8606 | 14 | -0.3 | 10.56 | 105 | 115.56 | 105 | 52.5 | 359 | 8606 | 840 | 354.0822 | -23.2218 | -2.4793 | 814.284 | 13.5301 | -22.9512 | 16.9899 | 16.9899 | 22.0063 | 202.0063 | 33.5302 | 30.1256 | 30.1256 | 89.6231 | 119.7487 | -0.55049 | 0% | 54.1503 | 0 | 0 | 125.4743 | 125.4743 | 0% | 12.11% | 12.11% | 80% | 9.689% | 5.2467 | 10.3885 | 6 | 31.4804 | 11.6027 | 25.09% | 25.09%
12 | 359 | 25 | 8607 | 15 | -1.5 | 59.44 | 68.53 | 127.97 | 68.53 | 34.27 | 359 | 8607 | 900 | 354.0822 | -23.2218 | -2.4793 | 874.284 | 14.5301 | -37.9512 | 12.0601 | 12.0601 | 35.3045 | 215.3045 | 44.5965 | 202.5736 | 202.5736 | 58.494 | 261.0676 | 0.17131 | 17.13% | 118.0548 | 20.2234 | 14.1564 | 143.2564 | 143.2564 | 9.882% | 11.99% | 0% | 80% | 0% | 0 | 10.8007 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8608 | 16 | -0.9 | 41.67 | 39.44 | 81.11 | 39.44 | 19.72 | 359 | 8608 | 960 | 354.0822 | -23.2218 | -2.4793 | 934.284 | 15.5301 | -52.9512 | 5.2703 | 5.2703 | 47.4406 | 227.4406 | 57.2357 | 0 | 0 | 33.6641 | 33.6641 | -4.0583 | 0% | 15.2229 | 0 | 0 | 141.2656 | 141.2656 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.5933 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8609 | 17 | -2.3 | 1.47 | 19.72 | 21.19 | 19.72 | 9.86 | 359 | 8609 | 1020 | 354.0822 | -23.2218 | -2.4793 | 994.284 | 16.5301 | -67.9512 | -2.9273 | 0 | 54.8475 | 234.8475 | 65.976 | 0 | 0 | 16.8321 | 16.8321 | -9.1277 | 0% | 7.6115 | 0 | 0 | 133.5361 | 133.5361 | 0% | 12.31% | 0% | 80% | 0% | 0 | 11.0811 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8610 | 18 | -3.5 | 0 | 0.97 | 0.97 | 0.97 | 0.49 | 359 | 8610 | 1080 | 354.0822 | -23.2218 | -2.4793 | 1054.284 | 17.5301 | -82.9512 | -12.1278 | 0 | 54.8475 | 234.8475 | 65.976 | 0 | 0 | 0.82795 | 0.82795 | -204.7419 | 0% | 0.3744 | 0 | 0 | 128.4861 | 128.4861 | 0% | 12.38% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8611 | 19 | -4.6 | 0 | 0 | 0 | 0 | 0 | 359 | 8611 | 1140 | 354.0822 | -23.2218 | -2.4793 | 1114.284 | 18.5301 | -97.9512 | -21.986 | 0 | 54.8475 | 234.8475 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 124.5956 | 124.5956 | 0% | 12.43% | 0% | 80% | 0% | 0 | 11.9122 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8612 | 20 | -5.5 | 0 | 0 | 0 | 0 | 0 | 359 | 8612 | 1200 | 354.0822 | -23.2218 | -2.4793 | 1174.284 | 19.5301 | -112.9512 | -32.1904 | 0 | 54.8475 | 234.8475 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.4235 | 120.4235 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8613 | 21 | -7.3 | 0 | 0 | 0 | 0 | 0 | 359 | 8613 | 1260 | 354.0822 | -23.2218 | -2.4793 | 1234.284 | 20.5301 | -127.9512 | -42.4048 | 0 | 54.8475 | 234.8475 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.0406 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.9351 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8614 | 22 | -7.7 | 0 | 0 | 0 | 0 | 0 | 359 | 8614 | 1320 | 354.0822 | -23.2218 | -2.4793 | 1294.284 | 21.5301 | -142.9512 | -52.1498 | 0 | 54.8475 | 234.8475 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.3153 | 0 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.091 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8615 | 23 | -8.2 | 0 | 0 | 0 | 0 | 0 | 359 | 8615 | 1380 | 354.0822 | -23.2218 | -2.4793 | 1354.284 | 22.5301 | -157.9512 | -60.5332 | 0 | 54.8475 | 234.8475 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.9465 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.2874 | 6 | 0 | 0 | 0% | 0%
12 | 359 | 25 | 8616 | 24 | -9.3 | 0 | 0 | 0 | 0 | 0 | 359 | 8616 | 1440 | 354.0822 | -23.2218 | -2.4793 | 1414.284 | 23.5301 | -172.9512 | -65.7709 | 0 | 54.8475 | 234.8475 | 65.976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.492 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.7257 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8617 | 1 | -9.3 | 0 | 0 | 0 | 0 | 0 | 360 | 8617 | 60 | 355.0685 | -23.1883 | -2.7106 | 34.284 | 0.52622 | 172.1067 | -65.5705 | 0 | 54.9025 | 125.0975 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.0773 | 0 | 0% | 12.64% | 0% | 80% | 0% | 0 | 13.7257 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8618 | 2 | -10.3 | 0 | 0 | 0 | 0 | 0 | 360 | 8618 | 120 | 355.0685 | -23.1883 | -2.7106 | 94.284 | 1.5262 | 157.1067 | -60.0945 | 0 | 54.9025 | 125.0975 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.3354 | 0 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.1315 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8619 | 3 | -10.1 | 0 | 0 | 0 | 0 | 0 | 360 | 8619 | 180 | 355.0685 | -23.1883 | -2.7106 | 154.284 | 2.5262 | 142.1067 | -51.6013 | 0 | 54.9025 | 125.0975 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.7647 | 0 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.0498 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8620 | 4 | -10.1 | 0 | 0 | 0 | 0 | 0 | 360 | 8620 | 240 | 355.0685 | -23.1883 | -2.7106 | 214.284 | 3.5262 | 127.1067 | -41.8137 | 0 | 54.9025 | 125.0975 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.7647 | 0 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.0498 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8621 | 5 | -11.5 | 0 | 0 | 0 | 0 | 0 | 360 | 8621 | 300 | 355.0685 | -23.1883 | -2.7106 | 274.284 | 4.5262 | 112.1067 | -31.5898 | 0 | 54.9025 | 125.0975 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.3494 | 0 | 0% | 12.74% | 0% | 80% | 0% | 0 | 14.6277 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8622 | 6 | -12.3 | 0 | 0 | 0 | 0 | 0 | 360 | 8622 | 360 | 355.0685 | -23.1883 | -2.7106 | 334.284 | 5.5262 | 97.1067 | -21.396 | 0 | 54.9025 | 125.0975 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.0503 | 0 | 0% | 12.77% | 0% | 80% | 0% | 0 | 14.9641 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8623 | 7 | -12.5 | 0 | 0 | 0 | 0 | 0 | 360 | 8623 | 420 | 355.0685 | -23.1883 | -2.7106 | 394.284 | 6.5262 | 82.1067 | -11.5651 | 0 | 54.9025 | 125.0975 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 135.4391 | 135.4391 | 0% | 12.78% | 0% | 80% | 0% | 0 | 15.0489 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8624 | 8 | -13 | 0 | 0 | 0 | 0 | 0 | 360 | 8624 | 480 | 355.0685 | -23.1883 | -2.7106 | 454.284 | 7.5262 | 67.1067 | -2.4096 | 0 | 54.9025 | 125.0975 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 139.667 | 139.667 | 0% | 12.8% | 0% | 80% | 0% | 0 | 15.2621 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8625 | 9 | -13 | 0 | 2.58 | 2.58 | 2.58 | 1.29 | 360 | 8625 | 540 | 355.0685 | -23.1883 | -2.7106 | 514.284 | 8.5262 | 52.1067 | 5.7222 | 5.7222 | 46.8057 | 133.1943 | 56.4897 | 0 | 0 | 2.2022 | 2.2022 | -87.6029 | 0% | 0.99582 | 0 | 0 | 119.8584 | 119.8584 | 0% | 12.8% | 0% | 80% | 0% | 0 | 15.2621 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8626 | 10 | -13.3 | 23.25 | 32.78 | 56.03 | 32.78 | 16.39 | 360 | 8626 | 600 | 355.0685 | -23.1883 | -2.7106 | 574.284 | 9.5262 | 37.1067 | 12.4218 | 12.4218 | 34.6009 | 145.3991 | 43.9028 | 77.8778 | 77.8778 | 27.9795 | 105.8573 | -1.0426 | 0% | 47.8687 | 0 | 0 | 123.5797 | 123.5797 | 0% | 12.62% | 0% | 80% | 0% | 0 | 15.3909 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8627 | 11 | -10.9 | 70.64 | 95.36 | 166 | 95.36 | 47.68 | 360 | 8627 | 660 | 355.0685 | -23.1883 | -2.7106 | 634.284 | 10.5262 | 22.1067 | 17.2352 | 17.2352 | 21.235 | 158.765 | 32.964 | 200.0303 | 200.0303 | 81.3949 | 281.4252 | 0.13183 | 13.18% | 127.2605 | 16.7767 | 11.7437 | 129.1587 | 129.1587 | 9.092% | 12.23% | 12.23% | 80% | 9.787% | 12.4545 | 14.3783 | 6 | 74.7272 | 27.5421 | 57.86% | 57.86%
12 | 360 | 26 | 8628 | 12 | -7.3 | 123.42 | 119.92 | 243.34 | 119.92 | 59.96 | 360 | 8628 | 720 | 355.0685 | -23.1883 | -2.7106 | 694.284 | 11.5262 | 7.1067 | 19.739 | 19.739 | 6.9395 | 173.0605 | 25.9079 | 328.7063 | 328.7063 | 102.3581 | 431.0644 | 0.3868 | 38.68% | 194.9273 | 75.3987 | 52.7791 | 111.3823 | 111.3823 | 47.39% | 11.91% | 11.91% | 85% | 10.12% | 19.7268 | 12.9351 | 6 | 118.3606 | 43.624 | 106.3% | 106.3%
12 | 360 | 26 | 8629 | 13 | -6.1 | 152.03 | 111.86 | 263.89 | 111.86 | 55.93 | 360 | 8629 | 780 | 355.0685 | -23.1883 | -2.7106 | 754.284 | 12.5262 | -7.8933 | 19.6703 | 19.6703 | 7.7042 | 187.7042 | 26.123 | 405.5171 | 405.5171 | 95.4785 | 500.9956 | 0.45117 | 45.12% | 226.5502 | 102.212 | 71.5484 | 112.5153 | 112.5153 | 63.59% | 11.78% | 11.78% | 90% | 10.6% | 24.0213 | 12.4742 | 6 | 144.1281 | 53.1211 | 128.1% | 128.1%
12 | 360 | 26 | 8630 | 14 | -5.7 | 148.33 | 91.03 | 239.36 | 91.03 | 45.52 | 360 | 8630 | 840 | 355.0685 | -23.1883 | -2.7106 | 814.284 | 13.5262 | -22.8933 | 17.0368 | 17.0368 | 21.9627 | 201.9627 | 33.469 | 422.3218 | 422.3218 | 77.699 | 500.0207 | 0.45252 | 45.25% | 226.1094 | 102.3185 | 71.6229 | 111.0615 | 111.0615 | 64.49% | 11.78% | 11.78% | 90% | 10.6% | 23.964 | 12.3228 | 6 | 143.7841 | 52.9943 | 129.5% | 129.5%
12 | 360 | 26 | 8631 | 15 | -5.6 | 135.75 | 79.08 | 214.83 | 79.08 | 39.54 | 360 | 8631 | 900 | 355.0685 | -23.1883 | -2.7106 | 874.284 | 14.5262 | -37.8933 | 12.1133 | 12.1133 | 35.2702 | 215.2702 | 44.5337 | 461.1394 | 461.1394 | 67.499 | 528.6384 | 0.47203 | 47.2% | 239.0503 | 112.838 | 78.9866 | 108.0608 | 108.0608 | 73.09% | 11.73% | 0% | 90% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8632 | 16 | -5.5 | 70.47 | 51.86 | 122.33 | 51.86 | 25.93 | 360 | 8632 | 960 | 355.0685 | -23.1883 | -2.7106 | 934.284 | 15.5262 | -52.8933 | 5.3275 | 5.3275 | 47.4144 | 227.4144 | 57.1747 | 0 | 0 | 44.2653 | 44.2653 | -3.1549 | 0% | 20.0168 | 0 | 0 | 144.6538 | 144.6538 | 0% | 12.41% | 0% | 80% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8633 | 17 | -6.5 | 11.11 | 21.39 | 32.5 | 21.39 | 10.7 | 360 | 8633 | 1020 | 355.0685 | -23.1883 | -2.7106 | 994.284 | 16.5262 | -67.8933 | -2.8677 | 0 | 54.9025 | 234.9025 | 66.0108 | 0 | 0 | 18.2575 | 18.2575 | -8.9339 | 0% | 8.256 | 0 | 0 | 135.5256 | 135.5256 | 0% | 12.49% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8634 | 18 | -7.7 | 0 | 0 | 0 | 0 | 0 | 360 | 8634 | 1080 | 355.0685 | -23.1883 | -2.7106 | 1054.284 | 17.5262 | -82.8933 | -12.0668 | 0 | 54.9025 | 234.9025 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.0377 | 128.0377 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.091 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8635 | 19 | -8.7 | 0 | 0 | 0 | 0 | 0 | 360 | 8635 | 1140 | 355.0685 | -23.1883 | -2.7106 | 1114.284 | 18.5262 | -97.8933 | -21.9243 | 0 | 54.9025 | 234.9025 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 123.3487 | 123.3487 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8636 | 20 | -9.1 | 0 | 0 | 0 | 0 | 0 | 360 | 8636 | 1200 | 355.0685 | -23.1883 | -2.7106 | 1174.284 | 19.5262 | -112.8933 | -32.1284 | 0 | 54.9025 | 234.9025 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 118.4789 | 118.4789 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6454 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8637 | 21 | -9.6 | 0 | 0 | 0 | 0 | 0 | 360 | 8637 | 1260 | 355.0685 | -23.1883 | -2.7106 | 1234.284 | 20.5262 | -127.8933 | -42.3431 | 0 | 54.9025 | 234.9025 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.3482 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8638 | 22 | -10.5 | 0 | 0 | 0 | 0 | 0 | 360 | 8638 | 1320 | 355.0685 | -23.1883 | -2.7106 | 1294.284 | 21.5262 | -142.8933 | -52.0893 | 0 | 54.9025 | 234.9025 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.7036 | 0 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.2135 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8639 | 23 | -11.3 | 0 | 0 | 0 | 0 | 0 | 360 | 8639 | 1380 | 355.0685 | -23.1883 | -2.7106 | 1354.284 | 22.5262 | -157.8933 | -60.4769 | 0 | 54.9025 | 234.9025 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.657 | 0 | 0% | 12.73% | 0% | 80% | 0% | 0 | 14.5443 | 6 | 0 | 0 | 0% | 0%
12 | 360 | 26 | 8640 | 24 | -11 | 0 | 0 | 0 | 0 | 0 | 360 | 8640 | 1440 | 355.0685 | -23.1883 | -2.7106 | 1414.284 | 23.5262 | -172.8933 | -65.7272 | 0 | 54.9025 | 234.9025 | 66.0108 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.9339 | 0 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4197 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8641 | 1 | -11.4 | 0 | 0 | 0 | 0 | 0 | 361 | 8641 | 60 | 356.0548 | -23.1475 | -2.9398 | 34.284 | 0.5224 | 172.1639 | -65.5426 | 0 | 54.9694 | 125.0306 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.6637 | 0 | 0% | 12.73% | 0% | 80% | 0% | 0 | 14.5859 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8642 | 2 | -12.2 | 0 | 0 | 0 | 0 | 0 | 361 | 8642 | 120 | 356.0548 | -23.1475 | -2.9398 | 94.284 | 1.5224 | 157.1639 | -60.0881 | 0 | 54.9694 | 125.0306 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.5243 | 0 | 0% | 12.77% | 0% | 80% | 0% | 0 | 14.9218 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8643 | 3 | -12.5 | 0 | 0 | 0 | 0 | 0 | 361 | 8643 | 180 | 356.0548 | -23.1475 | -2.9398 | 154.284 | 2.5224 | 142.1639 | -51.6069 | 0 | 54.9694 | 125.0306 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.623 | 0 | 0% | 12.78% | 0% | 80% | 0% | 0 | 15.0489 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8644 | 4 | -12.3 | 0 | 0 | 0 | 0 | 0 | 361 | 8644 | 240 | 356.0548 | -23.1475 | -2.9398 | 214.284 | 3.5224 | 127.1639 | -41.8245 | 0 | 54.9694 | 125.0306 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -32.3182 | 0 | 0% | 12.77% | 0% | 80% | 0% | 0 | 14.9641 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8645 | 5 | -12.4 | 0 | 0 | 0 | 0 | 0 | 361 | 8645 | 300 | 356.0548 | -23.1475 | -2.9398 | 274.284 | 4.5224 | 112.1639 | -31.6017 | 0 | 54.9694 | 125.0306 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.251 | 0 | 0% | 12.78% | 0% | 80% | 0% | 0 | 15.0064 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8646 | 6 | -13 | 0 | 0 | 0 | 0 | 0 | 361 | 8646 | 360 | 356.0548 | -23.1475 | -2.9398 | 334.284 | 5.5224 | 97.1639 | -21.4065 | 0 | 54.9694 | 125.0306 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -17.6335 | 0 | 0% | 12.8% | 0% | 80% | 0% | 0 | 15.2621 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8647 | 7 | -12.7 | 0 | 0 | 0 | 0 | 0 | 361 | 8647 | 420 | 356.0548 | -23.1475 | -2.9398 | 394.284 | 6.5224 | 82.1639 | -11.5722 | 0 | 54.9694 | 125.0306 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 141.09 | 141.09 | 0% | 12.79% | 0% | 80% | 0% | 0 | 15.134 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8648 | 8 | -12.7 | 0 | 0 | 0 | 0 | 0 | 361 | 8648 | 480 | 356.0548 | -23.1475 | -2.9398 | 454.284 | 7.5224 | 67.1639 | -2.4113 | 0 | 54.9694 | 125.0306 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 146.7162 | 146.7162 | 0% | 12.79% | 0% | 80% | 0% | 0 | 15.134 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8649 | 9 | -12.5 | 0.19 | 3.42 | 3.61 | 3.42 | 1.71 | 361 | 8649 | 540 | 356.0548 | -23.1475 | -2.9398 | 514.284 | 8.5224 | 52.1639 | 5.7279 | 5.7279 | 46.8724 | 133.1276 | 56.5263 | 0 | 0 | 2.9192 | 2.9192 | -65.4368 | 0% | 1.32 | 0 | 0 | 127.1839 | 127.1839 | 0% | 12.78% | 0% | 80% | 0% | 0 | 15.0489 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8650 | 10 | -11.2 | 35.28 | 28.42 | 63.7 | 28.42 | 14.21 | 361 | 8650 | 600 | 356.0548 | -23.1475 | -2.9398 | 574.284 | 9.5224 | 37.1639 | 12.4365 | 12.4365 | 34.6674 | 145.3326 | 43.9285 | 117.985 | 117.985 | 24.258 | 142.243 | -0.5314 | 0% | 64.3223 | 0 | 0 | 133.4292 | 133.4292 | 0% | 12.48% | 0% | 80% | 0% | 0 | 14.5027 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8651 | 11 | -9 | 91.58 | 58.53 | 150.11 | 58.53 | 29.27 | 361 | 8651 | 660 | 356.0548 | -23.1475 | -2.9398 | 634.284 | 10.5224 | 22.1639 | 17.2602 | 17.2602 | 21.2996 | 158.7004 | 32.971 | 258.9401 | 258.9401 | 49.9585 | 308.8986 | 0.20762 | 20.76% | 139.6839 | 29.0011 | 20.3007 | 135.9532 | 135.9532 | 14.93% | 12.14% | 12.14% | 85% | 10.32% | 14.4084 | 13.6053 | 6 | 86.4505 | 31.8629 | 63.59% | 63.59%
12 | 361 | 27 | 8652 | 12 | -7.4 | 136.39 | 67.22 | 203.61 | 67.22 | 33.61 | 361 | 8652 | 720 | 356.0548 | -23.1475 | -2.9398 | 694.284 | 11.5224 | 7.1639 | 19.7749 | 19.7749 | 6.9992 | 173.0008 | 25.8837 | 362.6907 | 362.6907 | 57.3759 | 420.0666 | 0.37527 | 37.53% | 189.9541 | 71.2841 | 49.8989 | 112.0243 | 112.0243 | 44.54% | 11.92% | 11.92% | 85% | 10.14% | 19.2535 | 12.9739 | 6 | 115.5211 | 42.5774 | 103.1% | 103.1%
12 | 361 | 27 | 8653 | 13 | -6.8 | 132.5 | 96.19 | 228.69 | 96.19 | 48.1 | 361 | 8653 | 780 | 356.0548 | -23.1475 | -2.9398 | 754.284 | 12.5224 | -7.8361 | 19.7162 | 19.7162 | 7.6528 | 187.6528 | 26.0678 | 352.8007 | 352.8007 | 82.1033 | 434.904 | 0.39343 | 39.34% | 196.6636 | 77.3743 | 54.162 | 111.8386 | 111.8386 | 48.43% | 11.89% | 11.89% | 85% | 10.11% | 19.8761 | 12.7418 | 6 | 119.2563 | 43.9541 | 106.6% | 106.6%
12 | 361 | 27 | 8654 | 14 | -5.2 | 116.31 | 79.08 | 195.39 | 79.08 | 39.54 | 361 | 8654 | 840 | 356.0548 | -23.1475 | -2.9398 | 814.284 | 13.5224 | -22.8361 | 17.0907 | 17.0907 | 21.9217 | 201.9217 | 33.4029 | 330.3939 | 330.3939 | 67.499 | 397.8929 | 0.3655 | 36.55% | 179.9272 | 65.7627 | 46.0339 | 132.3837 | 132.3837 | 34.77% | 11.91% | 11.91% | 85% | 10.12% | 18.2139 | 12.1351 | 6 | 109.2833 | 40.2784 | 82.55% | 82.55%
12 | 361 | 27 | 8655 | 15 | -5.5 | 123.53 | 66.58 | 190.11 | 66.58 | 33.29 | 361 | 8655 | 900 | 356.0548 | -23.1475 | -2.9398 | 874.284 | 14.5224 | -37.8361 | 12.1728 | 12.1728 | 35.2395 | 215.2395 | 44.4679 | 418.0798 | 418.0798 | 56.8296 | 474.9094 | 0.435 | 43.5% | 214.754 | 93.4188 | 65.3932 | 108.2741 | 108.2741 | 60.4% | 11.81% | 0% | 85% | 0% | 0 | 12.2475 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8656 | 16 | -6.1 | 67.97 | 41.31 | 109.28 | 41.31 | 20.66 | 361 | 8656 | 960 | 356.0548 | -23.1475 | -2.9398 | 934.284 | 15.5224 | -52.8361 | 5.3905 | 5.3905 | 47.3927 | 227.3927 | 57.1118 | 0 | 0 | 35.2603 | 35.2603 | -4.2092 | 0% | 15.9447 | 0 | 0 | 144.0453 | 144.0453 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.4742 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8657 | 17 | -6.2 | 12.69 | 17.42 | 30.11 | 17.42 | 8.71 | 361 | 8657 | 1020 | 356.0548 | -23.1475 | -2.9398 | 994.284 | 16.5224 | -67.8361 | -2.8027 | 0 | 54.9694 | 234.9694 | 66.0532 | 0 | 0 | 14.8689 | 14.8689 | -11.1016 | 0% | 6.7237 | 0 | 0 | 136.7937 | 136.7937 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8658 | 18 | -7.1 | 0 | 0 | 0 | 0 | 0 | 361 | 8658 | 1080 | 356.0548 | -23.1475 | -2.9398 | 1054.284 | 17.5224 | -82.8361 | -12.0008 | 0 | 54.9694 | 234.9694 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.53 | 129.53 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.8576 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8659 | 19 | -7.2 | 0 | 0 | 0 | 0 | 0 | 361 | 8659 | 1140 | 356.0548 | -23.1475 | -2.9398 | 1114.284 | 18.5224 | -97.8361 | -21.8579 | 0 | 54.9694 | 234.9694 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.2397 | 126.2397 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8660 | 20 | -8.3 | 0 | 0 | 0 | 0 | 0 | 361 | 8660 | 1200 | 356.0548 | -23.1475 | -2.9398 | 1174.284 | 19.5224 | -112.8361 | -32.062 | 0 | 54.9694 | 234.9694 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 120.0942 | 120.0942 | 0% | 12.6% | 0% | 80% | 0% | 0 | 13.3269 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8661 | 21 | -9.1 | 0 | 0 | 0 | 0 | 0 | 361 | 8661 | 1260 | 356.0548 | -23.1475 | -2.9398 | 1234.284 | 20.5224 | -127.8361 | -42.2767 | 0 | 54.9694 | 234.9694 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.2163 | 0 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6454 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8662 | 22 | -10.1 | 0 | 0 | 0 | 0 | 0 | 361 | 8662 | 1320 | 356.0548 | -23.1475 | -2.9398 | 1294.284 | 21.5224 | -142.8361 | -52.0237 | 0 | 54.9694 | 234.9694 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.7581 | 0 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.0498 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8663 | 23 | -9.6 | 0 | 0 | 0 | 0 | 0 | 361 | 8663 | 1380 | 356.0548 | -23.1475 | -2.9398 | 1354.284 | 22.5224 | -157.8361 | -60.4145 | 0 | 54.9694 | 234.9694 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -29.6376 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.8467 | 6 | 0 | 0 | 0% | 0%
12 | 361 | 27 | 8664 | 24 | -10.1 | 0 | 0 | 0 | 0 | 0 | 361 | 8664 | 1440 | 356.0548 | -23.1475 | -2.9398 | 1414.284 | 23.5224 | -172.8361 | -65.6764 | 0 | 54.9694 | 234.9694 | 66.0532 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.041 | 0 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.0498 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8665 | 1 | -10.2 | 0 | 0 | 0 | 0 | 0 | 362 | 8665 | 60 | 357.0411 | -23.0994 | -3.1663 | 34.284 | 0.51863 | 172.2206 | -65.5074 | 0 | 55.0483 | 124.9517 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.7202 | 0 | 0% | 12.68% | 0% | 80% | 0% | 0 | 14.0906 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8666 | 2 | -10.5 | 0 | 0 | 0 | 0 | 0 | 362 | 8666 | 120 | 357.0411 | -23.0994 | -3.1663 | 94.284 | 1.5186 | 157.2206 | -60.0751 | 0 | 55.0483 | 124.9517 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.7834 | 0 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.2135 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8667 | 3 | -10.5 | 0 | 0 | 0 | 0 | 0 | 362 | 8667 | 180 | 357.0411 | -23.0994 | -3.1663 | 154.284 | 2.5186 | 142.2206 | -51.6066 | 0 | 55.0483 | 124.9517 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.3893 | 0 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.2135 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8668 | 4 | -11.1 | 0 | 0 | 0 | 0 | 0 | 362 | 8668 | 240 | 357.0411 | -23.0994 | -3.1663 | 214.284 | 3.5186 | 127.2206 | -41.8299 | 0 | 55.0483 | 124.9517 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.3037 | 0 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4612 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8669 | 5 | -11.1 | 0 | 0 | 0 | 0 | 0 | 362 | 8669 | 300 | 357.0411 | -23.0994 | -3.1663 | 274.284 | 4.5186 | 112.2206 | -31.6084 | 0 | 55.0483 | 124.9517 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.8787 | 0 | 0% | 12.72% | 0% | 80% | 0% | 0 | 14.4612 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8670 | 6 | -11.6 | 0 | 0 | 0 | 0 | 0 | 362 | 8670 | 360 | 357.0411 | -23.0994 | -3.1663 | 334.284 | 5.5186 | 97.2206 | -21.4116 | 0 | 55.0483 | 124.9517 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -14.2773 | 0 | 0% | 12.74% | 0% | 80% | 0% | 0 | 14.6695 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8671 | 7 | -11.8 | 0 | 0 | 0 | 0 | 0 | 362 | 8671 | 420 | 357.0411 | -23.0994 | -3.1663 | 394.284 | 6.5186 | 82.2206 | -11.5735 | 0 | 55.0483 | 124.9517 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 145.3822 | 145.3822 | 0% | 12.75% | 0% | 80% | 0% | 0 | 14.7533 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8672 | 8 | -11.6 | 0 | 0 | 0 | 0 | 0 | 362 | 8672 | 480 | 357.0411 | -23.0994 | -3.1663 | 454.284 | 7.5186 | 67.2206 | -2.4069 | 0 | 55.0483 | 124.9517 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 152.094 | 152.094 | 0% | 12.74% | 0% | 80% | 0% | 0 | 14.6695 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8673 | 9 | -11.4 | 0.28 | 2.31 | 2.59 | 2.31 | 1.16 | 362 | 8673 | 540 | 357.0411 | -23.0994 | -3.1663 | 514.284 | 8.5186 | 52.2206 | 5.7399 | 5.7399 | 46.9427 | 133.0573 | 56.5601 | 0 | 0 | 1.9717 | 1.9717 | -95.8 | 0% | 0.89161 | 0 | 0 | 132.7161 | 132.7161 | 0% | 12.73% | 0% | 80% | 0% | 0 | 14.5859 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8674 | 10 | -9.5 | 39.81 | 27.5 | 67.31 | 27.5 | 13.75 | 362 | 8674 | 600 | 357.0411 | -23.0994 | -3.1663 | 574.284 | 9.5186 | 37.2206 | 12.458 | 12.458 | 34.7366 | 145.2634 | 43.9502 | 132.8598 | 132.8598 | 23.4727 | 156.3326 | -0.38269 | 0% | 70.6936 | 0 | 0 | 140.4701 | 140.4701 | 0% | 12.4% | 0% | 80% | 0% | 0 | 13.8063 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8675 | 11 | -7.9 | 115.75 | 56.75 | 172.5 | 56.75 | 28.38 | 362 | 8675 | 660 | 357.0411 | -23.0994 | -3.1663 | 634.284 | 10.5186 | 22.2206 | 17.2924 | 17.2924 | 21.3658 | 158.6342 | 32.9725 | 326.6836 | 326.6836 | 48.4392 | 375.1228 | 0.32048 | 32.05% | 169.6305 | 54.3626 | 38.0538 | 142.6064 | 142.6064 | 26.68% | 12% | 12% | 85% | 10.2% | 17.308 | 13.1693 | 6 | 103.8483 | 38.2752 | 72.82% | 72.82%
12 | 362 | 28 | 8676 | 12 | -6.4 | 156.39 | 75.92 | 232.31 | 75.92 | 37.96 | 362 | 8676 | 720 | 357.0411 | -23.0994 | -3.1663 | 694.284 | 11.5186 | 7.2206 | 19.8181 | 19.8181 | 7.059 | 172.941 | 25.8526 | 415.1149 | 415.1149 | 64.8018 | 479.9166 | 0.43407 | 43.41% | 217.0183 | 94.202 | 65.9414 | 117.7057 | 117.7057 | 56.02% | 11.82% | 11.82% | 85% | 10.04% | 21.7979 | 12.5884 | 6 | 130.7871 | 48.204 | 111.1% | 111.1%
12 | 362 | 28 | 8677 | 13 | -4.6 | 176.03 | 87.58 | 263.61 | 87.58 | 43.79 | 362 | 8677 | 780 | 357.0411 | -23.0994 | -3.1663 | 754.284 | 12.5186 | -7.7794 | 19.7692 | 19.7692 | 7.6028 | 187.6028 | 26.0059 | 467.7451 | 467.7451 | 74.7542 | 542.4993 | 0.48519 | 48.52% | 245.3182 | 119.0248 | 83.3174 | 119.4487 | 119.4487 | 69.75% | 11.7% | 11.7% | 90% | 10.53% | 25.8329 | 11.9122 | 6 | 154.9973 | 57.1271 | 129.8% | 129.8%
12 | 362 | 28 | 8678 | 14 | -4 | 175.56 | 83.53 | 259.09 | 83.53 | 41.77 | 362 | 8678 | 840 | 357.0411 | -23.0994 | -3.1663 | 814.284 | 13.5186 | -22.7794 | 17.1514 | 17.1514 | 21.8833 | 201.8833 | 33.332 | 497.3942 | 497.3942 | 71.2973 | 568.6915 | 0.50253 | 50.25% | 257.1623 | 129.233 | 90.4631 | 118.7683 | 118.7683 | 76.17% | 11.66% | 11.66% | 90% | 10.49% | 26.9804 | 11.6918 | 6 | 161.8825 | 59.6648 | 136.3% | 136.3%
12 | 362 | 28 | 8679 | 15 | -3.7 | 165.08 | 72.31 | 237.39 | 72.31 | 36.16 | 362 | 8679 | 900 | 357.0411 | -23.0994 | -3.1663 | 874.284 | 14.5186 | -37.7794 | 12.2386 | 12.2386 | 35.2125 | 215.2125 | 44.399 | 556.3989 | 556.3989 | 61.7204 | 618.1193 | 0.52786 | 52.79% | 279.5136 | 147.5454 | 103.2818 | 115.7029 | 115.7029 | 89.26% | 11.59% | 0% | 90% | 0% | 0 | 11.5826 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8680 | 16 | -3.4 | 94.64 | 54.08 | 148.72 | 54.08 | 27.04 | 362 | 8680 | 960 | 357.0411 | -23.0994 | -3.1663 | 934.284 | 15.5186 | -52.7794 | 5.4593 | 5.4593 | 47.3754 | 227.3754 | 57.0472 | 0 | 0 | 46.1602 | 46.1602 | -2.8773 | 0% | 20.8736 | 0 | 0 | 152.5234 | 152.5234 | 0% | 12.32% | 0% | 80% | 0% | 0 | 11.4739 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8681 | 17 | -4.3 | 20.92 | 21.11 | 42.03 | 21.11 | 10.56 | 362 | 8681 | 1020 | 357.0411 | -23.0994 | -3.1663 | 994.284 | 16.5186 | -67.7794 | -2.7324 | 0 | 55.0483 | 235.0483 | 66.1032 | 0 | 0 | 18.0185 | 18.0185 | -8.7527 | 0% | 8.148 | 0 | 0 | 142.3267 | 142.3267 | 0% | 12.4% | 0% | 80% | 0% | 0 | 11.8017 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8682 | 18 | -5 | 0 | 0 | 0 | 0 | 0 | 362 | 8682 | 1080 | 357.0411 | -23.0994 | -3.1663 | 1054.284 | 17.5186 | -82.7794 | -11.93 | 0 | 55.0483 | 235.0483 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 133.5335 | 133.5335 | 0% | 12.45% | 0% | 80% | 0% | 0 | 12.0605 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8683 | 19 | -5.4 | 0 | 0 | 0 | 0 | 0 | 362 | 8683 | 1140 | 357.0411 | -23.0994 | -3.1663 | 1114.284 | 18.5186 | -97.7794 | -21.787 | 0 | 55.0483 | 235.0483 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.1453 | 129.1453 | 0% | 12.47% | 0% | 80% | 0% | 0 | 12.2099 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8684 | 20 | -6 | 0 | 0 | 0 | 0 | 0 | 362 | 8684 | 1200 | 357.0411 | -23.0994 | -3.1663 | 1174.284 | 19.5186 | -112.7794 | -31.9911 | 0 | 55.0483 | 235.0483 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 122.9888 | 122.9888 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.4362 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8685 | 21 | -6.8 | 0 | 0 | 0 | 0 | 0 | 362 | 8685 | 1260 | 357.0411 | -23.0994 | -3.1663 | 1234.284 | 20.5186 | -127.7794 | -42.2058 | 0 | 55.0483 | 235.0483 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -25.5212 | 0 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7418 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8686 | 22 | -7.5 | 0 | 0 | 0 | 0 | 0 | 362 | 8686 | 1320 | 357.0411 | -23.0994 | -3.1663 | 1294.284 | 21.5186 | -142.7794 | -51.953 | 0 | 55.0483 | 235.0483 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.7876 | 0 | 0% | 12.56% | 0% | 80% | 0% | 0 | 13.0129 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8687 | 23 | -7.9 | 0 | 0 | 0 | 0 | 0 | 362 | 8687 | 1380 | 357.0411 | -23.0994 | -3.1663 | 1354.284 | 22.5186 | -157.7794 | -60.3463 | 0 | 55.0483 | 235.0483 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -28.0031 | 0 | 0% | 12.58% | 0% | 80% | 0% | 0 | 13.1693 | 6 | 0 | 0 | 0% | 0%
12 | 362 | 28 | 8688 | 24 | -8.1 | 0 | 0 | 0 | 0 | 0 | 362 | 8688 | 1440 | 357.0411 | -23.0994 | -3.1663 | 1414.284 | 23.5186 | -172.7794 | -65.6185 | 0 | 55.0483 | 235.0483 | 66.1032 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.9139 | 0 | 0% | 12.59% | 0% | 80% | 0% | 0 | 13.248 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8689 | 1 | -8.7 | 0 | 0 | 0 | 0 | 0 | 363 | 8689 | 60 | 358.0274 | -23.044 | -3.3899 | 34.284 | 0.5149 | 172.2765 | -65.4649 | 0 | 55.139 | 124.861 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.7624 | 0 | 0% | 12.61% | 0% | 80% | 0% | 0 | 13.4856 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8690 | 2 | -9 | 0 | 0 | 0 | 0 | 0 | 363 | 8690 | 120 | 358.0274 | -23.044 | -3.3899 | 94.284 | 1.5149 | 157.2765 | -60.0555 | 0 | 55.139 | 124.861 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.0559 | 0 | 0% | 12.63% | 0% | 80% | 0% | 0 | 13.6053 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8691 | 3 | -9.4 | 0 | 0 | 0 | 0 | 0 | 363 | 8691 | 180 | 358.0274 | -23.044 | -3.3899 | 154.284 | 2.5149 | 142.2765 | -51.6005 | 0 | 55.139 | 124.861 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.5017 | 0 | 0% | 12.65% | 0% | 80% | 0% | 0 | 13.7659 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8692 | 4 | -8.9 | 0 | 0 | 0 | 0 | 0 | 363 | 8692 | 240 | 358.0274 | -23.044 | -3.3899 | 214.284 | 3.5149 | 127.2765 | -41.8298 | 0 | 55.139 | 124.861 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.7397 | 0 | 0% | 12.62% | 0% | 80% | 0% | 0 | 13.5653 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8693 | 5 | -9.8 | 0 | 0 | 0 | 0 | 0 | 363 | 8693 | 300 | 358.0274 | -23.044 | -3.3899 | 274.284 | 4.5149 | 112.2765 | -31.6097 | 0 | 55.139 | 124.861 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.5925 | 0 | 0% | 12.66% | 0% | 80% | 0% | 0 | 13.9277 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8694 | 6 | -10 | 0 | 0 | 0 | 0 | 0 | 363 | 8694 | 360 | 358.0274 | -23.044 | -3.3899 | 334.284 | 5.5149 | 97.2765 | -21.4113 | 0 | 55.139 | 124.861 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.6046 | 0 | 0% | 12.67% | 0% | 80% | 0% | 0 | 14.009 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8695 | 7 | -10.3 | 0 | 0 | 0 | 0 | 0 | 363 | 8695 | 420 | 358.0274 | -23.044 | -3.3899 | 394.284 | 6.5149 | 82.2765 | -11.5692 | 0 | 55.139 | 124.861 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.811 | 126.811 | 0% | 12.69% | 0% | 80% | 0% | 0 | 14.1315 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8696 | 8 | -9.9 | 0 | 0 | 0 | 0 | 0 | 363 | 8696 | 480 | 358.0274 | -23.044 | -3.3899 | 454.284 | 7.5149 | 67.2765 | -2.3965 | 0 | 55.139 | 124.861 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 130.3774 | 130.3774 | 0% | 12.67% | 0% | 80% | 0% | 0 | 13.9683 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8697 | 9 | -10 | 0 | 1.39 | 1.39 | 1.39 | 0.7 | 363 | 8697 | 540 | 358.0274 | -23.044 | -3.3899 | 514.284 | 8.5149 | 52.2765 | 5.7584 | 5.7584 | 47.0163 | 132.9837 | 56.5909 | 0 | 0 | 1.1864 | 1.1864 | -156.6567 | 0% | 0.53651 | 0 | 0 | 109.9086 | 109.9086 | 0% | 12.67% | 0% | 80% | 0% | 0 | 14.009 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8698 | 10 | -8.1 | 8.69 | 17.86 | 26.55 | 17.86 | 8.93 | 363 | 8698 | 600 | 358.0274 | -23.044 | -3.3899 | 574.284 | 9.5149 | 37.2765 | 12.4863 | 12.4863 | 34.8084 | 145.1916 | 43.9678 | 28.9282 | 28.9282 | 15.2445 | 44.1727 | -3.3138 | 0% | 19.9749 | 0 | 0 | 114.6504 | 114.6504 | 0% | 12.52% | 0% | 80% | 0% | 0 | 13.248 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8699 | 11 | -5.1 | 42.22 | 42.97 | 85.19 | 42.97 | 21.49 | 363 | 8699 | 660 | 358.0274 | -23.044 | -3.3899 | 634.284 | 10.5149 | 22.2765 | 17.3318 | 17.3318 | 21.4334 | 158.5666 | 32.9684 | 118.9016 | 118.9016 | 36.6772 | 155.5788 | -0.31584 | 0% | 70.3527 | 0 | 0 | 120.2497 | 120.2497 | 0% | 12.24% | 12.24% | 80% | 9.793% | 6.8899 | 12.0978 | 6 | 41.3391 | 15.2363 | 34.38% | 34.38%
12 | 363 | 29 | 8700 | 12 | -4.2 | 55 | 60.47 | 115.47 | 60.47 | 30.24 | 363 | 8700 | 720 | 358.0274 | -23.044 | -3.3899 | 694.284 | 11.5149 | 7.2765 | 19.8685 | 19.8685 | 7.1188 | 172.8812 | 25.8144 | 145.6809 | 145.6809 | 51.6144 | 197.2953 | -0.067513 | 0% | 89.2169 | 0 | 0 | 119.3992 | 119.3992 | 0% | 12.15% | 12.15% | 80% | 9.723% | 8.6749 | 11.765 | 6 | 52.0493 | 19.1837 | 43.59% | 43.59%
12 | 363 | 29 | 8701 | 13 | -3.8 | 88.53 | 68.61 | 157.14 | 68.61 | 34.31 | 363 | 8701 | 780 | 358.0274 | -23.044 | -3.3899 | 754.284 | 12.5149 | -7.7235 | 19.8294 | 19.8294 | 7.5542 | 187.5542 | 25.9374 | 234.6925 | 234.6925 | 58.5623 | 293.2548 | 0.22111 | 22.11% | 132.6098 | 29.3208 | 20.5246 | 120.9829 | 120.9829 | 16.96% | 12.02% | 12.02% | 80% | 9.612% | 12.7468 | 11.6189 | 6 | 76.4808 | 28.1884 | 63.22% | 63.22%
12 | 363 | 29 | 8702 | 14 | -2.1 | 87.5 | 70.92 | 158.42 | 70.92 | 35.46 | 363 | 8702 | 840 | 358.0274 | -23.044 | -3.3899 | 814.284 | 13.5149 | -22.7235 | 17.2189 | 17.2189 | 21.8477 | 201.8477 | 33.2565 | 247.1756 | 247.1756 | 60.534 | 307.7096 | 0.26235 | 26.23% | 139.1463 | 36.5046 | 25.5532 | 123.0148 | 123.0148 | 20.77% | 11.95% | 11.95% | 85% | 10.16% | 14.1342 | 11.0106 | 6 | 84.8054 | 31.2566 | 68.94% | 68.94%
12 | 363 | 29 | 8703 | 15 | -1.7 | 70.83 | 63.42 | 134.25 | 63.42 | 31.71 | 363 | 8703 | 900 | 358.0274 | -23.044 | -3.3899 | 874.284 | 14.5149 | -37.7235 | 12.3107 | 12.3107 | 35.1893 | 215.1893 | 44.3272 | 237.6456 | 237.6456 | 54.1324 | 291.778 | 0.23619 | 23.62% | 131.942 | 31.1635 | 21.8145 | 142.2091 | 142.2091 | 15.34% | 11.96% | 0% | 80% | 0% | 0 | 10.8704 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8704 | 16 | -1.8 | 38.81 | 55.92 | 94.73 | 55.92 | 27.96 | 363 | 8704 | 960 | 358.0274 | -23.044 | -3.3899 | 934.284 | 15.5149 | -52.7235 | 5.5338 | 5.5338 | 47.3627 | 227.3627 | 56.9809 | 0 | 0 | 47.7307 | 47.7307 | -2.6722 | 0% | 21.5838 | 0 | 0 | 139.4553 | 139.4553 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.9053 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8705 | 17 | -2.6 | 8.61 | 19.64 | 28.25 | 19.64 | 9.82 | 363 | 8705 | 1020 | 358.0274 | -23.044 | -3.3899 | 994.284 | 16.5149 | -67.7235 | -2.657 | 0 | 55.139 | 235.139 | 66.1607 | 0 | 0 | 16.7638 | 16.7638 | -9.213 | 0% | 7.5806 | 0 | 0 | 133.3369 | 133.3369 | 0% | 12.33% | 0% | 80% | 0% | 0 | 11.1874 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8706 | 18 | -3.5 | 0 | 0 | 0 | 0 | 0 | 363 | 8706 | 1080 | 358.0274 | -23.044 | -3.3899 | 1054.284 | 17.5149 | -82.7235 | -11.8544 | 0 | 55.139 | 235.139 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 128.1141 | 128.1141 | 0% | 12.39% | 0% | 80% | 0% | 0 | 11.5101 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8707 | 19 | -4.1 | 0 | 0 | 0 | 0 | 0 | 363 | 8707 | 1140 | 358.0274 | -23.044 | -3.3899 | 1114.284 | 18.5149 | -97.7235 | -21.7116 | 0 | 55.139 | 235.139 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.3988 | 125.3988 | 0% | 12.41% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8708 | 20 | -4.8 | 0 | 0 | 0 | 0 | 0 | 363 | 8708 | 1200 | 358.0274 | -23.044 | -3.3899 | 1174.284 | 19.5149 | -112.7235 | -31.9158 | 0 | 55.139 | 235.139 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 121.8701 | 121.8701 | 0% | 12.44% | 0% | 80% | 0% | 0 | 11.9862 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8709 | 21 | -5.7 | 0 | 0 | 0 | 0 | 0 | 363 | 8709 | 1260 | 358.0274 | -23.044 | -3.3899 | 1234.284 | 20.5149 | -127.7235 | -42.1304 | 0 | 55.139 | 235.139 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.114 | 0 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.3228 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8710 | 22 | -6.2 | 0 | 0 | 0 | 0 | 0 | 363 | 8710 | 1320 | 358.0274 | -23.044 | -3.3899 | 1294.284 | 21.5149 | -142.7235 | -51.8774 | 0 | 55.139 | 235.139 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.4435 | 0 | 0% | 12.5% | 0% | 80% | 0% | 0 | 12.5122 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8711 | 23 | -6.5 | 0 | 0 | 0 | 0 | 0 | 363 | 8711 | 1380 | 358.0274 | -23.044 | -3.3899 | 1354.284 | 22.5149 | -157.7235 | -60.2722 | 0 | 55.139 | 235.139 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.737 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
12 | 363 | 29 | 8712 | 24 | -6.5 | 0 | 0 | 0 | 0 | 0 | 363 | 8712 | 1440 | 358.0274 | -23.044 | -3.3899 | 1414.284 | 23.5149 | -172.7235 | -65.5536 | 0 | 55.139 | 235.139 | 66.1607 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -27.5733 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8713 | 1 | -6.6 | 0 | 0 | 0 | 0 | 0 | 364 | 8713 | 60 | 359.0137 | -22.9814 | -3.61 | 34.284 | 0.51123 | 172.3315 | -65.415 | 0 | 55.2415 | 124.7585 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.3889 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.665 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8714 | 2 | -6.5 | 0 | 0 | 0 | 0 | 0 | 364 | 8714 | 120 | 359.0137 | -22.9814 | -3.61 | 94.284 | 1.5112 | 157.3315 | -60.0291 | 0 | 55.2415 | 124.7585 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.1279 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8715 | 3 | -6.5 | 0 | 0 | 0 | 0 | 0 | 364 | 8715 | 180 | 359.0137 | -22.9814 | -3.61 | 154.284 | 2.5112 | 142.3315 | -51.5884 | 0 | 55.2415 | 124.7585 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -30.0194 | 0 | 0% | 12.52% | 0% | 80% | 0% | 0 | 12.6267 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8716 | 4 | -7.2 | 0 | 0 | 0 | 0 | 0 | 364 | 8716 | 240 | 359.0137 | -22.9814 | -3.61 | 214.284 | 3.5112 | 127.3315 | -41.8241 | 0 | 55.2415 | 124.7585 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -31.0862 | 0 | 0% | 12.55% | 0% | 80% | 0% | 0 | 12.8963 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8717 | 5 | -6.8 | 0 | 0 | 0 | 0 | 0 | 364 | 8717 | 300 | 359.0137 | -22.9814 | -3.61 | 274.284 | 4.5112 | 112.3315 | -31.6055 | 0 | 55.2415 | 124.7585 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -26.8378 | 0 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7418 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8718 | 6 | -6.9 | 0 | 0 | 0 | 0 | 0 | 364 | 8718 | 360 | 359.0137 | -22.9814 | -3.61 | 334.284 | 5.5112 | 97.3315 | -21.4054 | 0 | 55.2415 | 124.7585 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.2052 | 0 | 0% | 12.54% | 0% | 80% | 0% | 0 | 12.7803 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8719 | 7 | -6.7 | 0 | 0 | 0 | 0 | 0 | 364 | 8719 | 420 | 359.0137 | -22.9814 | -3.61 | 394.284 | 6.5112 | 82.3315 | -11.5591 | 0 | 55.2415 | 124.7585 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 126.6042 | 126.6042 | 0% | 12.53% | 0% | 80% | 0% | 0 | 12.7034 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8720 | 8 | -7.6 | 0 | 0 | 0 | 0 | 0 | 364 | 8720 | 480 | 359.0137 | -22.9814 | -3.61 | 454.284 | 7.5112 | 67.3315 | -2.38 | 0 | 55.2415 | 124.7585 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.8583 | 127.8583 | 0% | 12.57% | 0% | 80% | 0% | 0 | 13.0519 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8721 | 9 | -5.6 | 0 | 1.75 | 1.75 | 1.75 | 0.88 | 364 | 8721 | 540 | 359.0137 | -22.9814 | -3.61 | 514.284 | 8.5112 | 52.3315 | 5.7833 | 5.7833 | 47.0933 | 132.9067 | 56.6189 | 0 | 0 | 1.4937 | 1.4937 | -116.684 | 0% | 0.67546 | 0 | 0 | 110.636 | 110.636 | 0% | 12.48% | 0% | 80% | 0% | 0 | 12.2851 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8722 | 10 | -4.1 | 2.5 | 23.61 | 26.11 | 23.61 | 11.81 | 364 | 8722 | 600 | 359.0137 | -22.9814 | -3.61 | 574.284 | 9.5112 | 37.3315 | 12.5214 | 12.5214 | 34.8826 | 145.1174 | 43.9814 | 8.2974 | 8.2974 | 20.1524 | 28.4498 | -5.2309 | 0% | 12.865 | 0 | 0 | 114.8444 | 114.8444 | 0% | 12.37% | 0% | 80% | 0% | 0 | 11.7284 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8723 | 11 | -3.2 | 8.69 | 61.75 | 70.44 | 61.75 | 30.88 | 364 | 8723 | 660 | 359.0137 | -22.9814 | -3.61 | 634.284 | 10.5112 | 22.3315 | 17.3782 | 17.3782 | 21.5023 | 158.4977 | 32.9589 | 24.4124 | 24.4124 | 52.7069 | 77.1193 | -1.3929 | 0% | 34.8733 | 0 | 0 | 117.107 | 117.107 | 0% | 12.27% | 12.27% | 80% | 9.82% | 3.4244 | 11.4019 | 6 | 20.5464 | 7.5727 | 17.54% | 17.54%
12 | 364 | 30 | 8724 | 12 | 0.8 | 53.69 | 76.03 | 129.72 | 76.03 | 38.02 | 364 | 8724 | 720 | 359.0137 | -22.9814 | -3.61 | 694.284 | 11.5112 | 7.3315 | 19.9262 | 19.9262 | 7.1786 | 172.8214 | 25.7694 | 141.8702 | 141.8702 | 64.8957 | 206.7659 | 0.032661 | 3.266% | 93.4995 | 3.0538 | 2.1377 | 123.7664 | 123.7664 | 1.727% | 11.98% | 11.98% | 80% | 9.583% | 8.9598 | 10.0195 | 6 | 53.759 | 19.8139 | 43.44% | 43.44%
12 | 364 | 30 | 8725 | 13 | 0.3 | 84.53 | 85.83 | 170.36 | 85.83 | 42.92 | 364 | 8725 | 780 | 359.0137 | -22.9814 | -3.61 | 754.284 | 12.5112 | -7.6685 | 19.8967 | 19.8967 | 7.5071 | 187.5071 | 25.8623 | 223.5039 | 223.5039 | 73.2605 | 296.7644 | 0.26243 | 26.24% | 134.1969 | 35.2179 | 24.6525 | 124.3775 | 124.3775 | 19.82% | 11.9% | 11.9% | 80% | 9.518% | 12.7726 | 10.1862 | 6 | 76.6356 | 28.2455 | 61.62% | 61.62%
12 | 364 | 30 | 8726 | 14 | 0.7 | 85 | 95.19 | 180.19 | 95.19 | 47.6 | 364 | 8726 | 840 | 359.0137 | -22.9814 | -3.61 | 814.284 | 13.5112 | -22.6685 | 17.2931 | 17.2931 | 21.8148 | 201.8148 | 33.1764 | 239.3338 | 239.3338 | 81.2497 | 320.5835 | 0.30574 | 30.57% | 144.9679 | 44.3231 | 31.0262 | 125.1278 | 125.1278 | 24.8% | 11.86% | 11.86% | 85% | 10.08% | 14.6153 | 10.0527 | 6 | 87.6919 | 32.3205 | 70.08% | 70.08%
12 | 364 | 30 | 8727 | 15 | 2.4 | 75.83 | 77.22 | 153.05 | 77.22 | 38.61 | 364 | 8727 | 900 | 359.0137 | -22.9814 | -3.61 | 874.284 | 14.5112 | -37.6685 | 12.389 | 12.389 | 35.1699 | 215.1699 | 44.2526 | 253.1601 | 253.1601 | 65.9114 | 319.0715 | 0.31643 | 31.64% | 144.2842 | 45.6555 | 31.9588 | 104.4531 | 104.4531 | 30.6% | 11.82% | 0% | 85% | 0% | 0 | 9.4979 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8728 | 16 | 1.7 | 45.83 | 51.11 | 96.94 | 51.11 | 25.56 | 364 | 8728 | 960 | 359.0137 | -22.9814 | -3.61 | 934.284 | 15.5112 | -52.6685 | 5.6139 | 5.6139 | 47.3545 | 227.3545 | 56.913 | 0 | 0 | 43.6251 | 43.6251 | -2.8013 | 0% | 19.7273 | 0 | 0 | 142.3438 | 142.3438 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.7239 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8729 | 17 | 1.1 | 10.83 | 18.89 | 29.72 | 18.89 | 9.45 | 364 | 8729 | 1020 | 359.0137 | -22.9814 | -3.61 | 994.284 | 16.5112 | -67.6685 | -2.5765 | 0 | 55.2415 | 235.2415 | 66.2257 | 0 | 0 | 16.1236 | 16.1236 | -9.0418 | 0% | 7.2911 | 0 | 0 | 136.6272 | 136.6272 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8730 | 18 | 0.8 | 0 | 0 | 0 | 0 | 0 | 364 | 8730 | 1080 | 359.0137 | -22.9814 | -3.61 | 1054.284 | 17.5112 | -82.6685 | -11.7742 | 0 | 55.2415 | 235.2415 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 132.1922 | 132.1922 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8731 | 19 | 0.5 | 0 | 0 | 0 | 0 | 0 | 364 | 8731 | 1140 | 359.0137 | -22.9814 | -3.61 | 1114.284 | 18.5112 | -97.6685 | -21.6319 | 0 | 55.2415 | 235.2415 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.7967 | 129.7967 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8732 | 20 | 0.4 | 0 | 0 | 0 | 0 | 0 | 364 | 8732 | 1200 | 359.0137 | -22.9814 | -3.61 | 1174.284 | 19.5112 | -112.6685 | -31.8363 | 0 | 55.2415 | 235.2415 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.1623 | 127.1623 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8733 | 21 | 0.5 | 0 | 0 | 0 | 0 | 0 | 364 | 8733 | 1260 | 359.0137 | -22.9814 | -3.61 | 1234.284 | 20.5112 | -127.6685 | -42.0507 | 0 | 55.2415 | 235.2415 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.3174 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8734 | 22 | 1.1 | 0 | 0 | 0 | 0 | 0 | 364 | 8734 | 1320 | 359.0137 | -22.9814 | -3.61 | 1294.284 | 21.5112 | -142.6685 | -51.797 | 0 | 55.2415 | 235.2415 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -18.9799 | 0 | 0% | 12.18% | 0% | 80% | 0% | 0 | 9.9203 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8735 | 23 | 1 | 0 | 0 | 0 | 0 | 0 | 364 | 8735 | 1380 | 359.0137 | -22.9814 | -3.61 | 1354.284 | 22.5112 | -157.6685 | -60.1923 | 0 | 55.2415 | 235.2415 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.0237 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
12 | 364 | 30 | 8736 | 24 | 0.7 | 0 | 0 | 0 | 0 | 0 | 364 | 8736 | 1440 | 359.0137 | -22.9814 | -3.61 | 1414.284 | 23.5112 | -172.6685 | -65.4817 | 0 | 55.2415 | 235.2415 | 66.2257 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.3724 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0527 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8737 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 365 | 8737 | 60 | 360 | -22.9116 | -3.8263 | 34.284 | 0.50763 | 172.3856 | -65.3578 | 0 | 55.3557 | 124.6443 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.5135 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8738 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 365 | 8738 | 120 | 360 | -22.9116 | -3.8263 | 94.284 | 1.5076 | 157.3856 | -59.9961 | 0 | 55.3557 | 124.6443 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.6803 | 0 | 0% | 12.19% | 0% | 80% | 0% | 0 | 9.9533 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8739 | 3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 365 | 8739 | 180 | 360 | -22.9116 | -3.8263 | 154.284 | 2.5076 | 142.3856 | -51.5703 | 0 | 55.3557 | 124.6443 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.914 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0195 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8740 | 4 | 0.5 | 0 | 0 | 0 | 0 | 0 | 365 | 8740 | 240 | 360 | -22.9116 | -3.8263 | 214.284 | 3.5076 | 127.3856 | -41.8128 | 0 | 55.3557 | 124.6443 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -22.3712 | 0 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1193 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8741 | 5 | 0.1 | 0 | 0 | 0 | 0 | 0 | 365 | 8741 | 300 | 360 | -22.9116 | -3.8263 | 274.284 | 4.5076 | 112.3856 | -31.5959 | 0 | 55.3557 | 124.6443 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -20.9935 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.2533 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8742 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 8742 | 360 | 360 | -22.9116 | -3.8263 | 334.284 | 5.5076 | 97.3856 | -21.394 | 0 | 55.3557 | 124.6443 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -19.5496 | 0 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8743 | 7 | 0.4 | 0 | 0 | 0 | 0 | 0 | 365 | 8743 | 420 | 360 | -22.9116 | -3.8263 | 394.284 | 6.5076 | 82.3856 | -11.5433 | 0 | 55.3557 | 124.6443 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.2358 | 129.2358 | 0% | 12.21% | 0% | 80% | 0% | 0 | 10.1527 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8744 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 8744 | 480 | 360 | -22.9116 | -3.8263 | 454.284 | 7.5076 | 67.3856 | -2.3574 | 0 | 55.3557 | 124.6443 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.9348 | 129.9348 | 0% | 12.23% | 0% | 80% | 0% | 0 | 10.287 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8745 | 9 | 0.3 | 0 | 1.75 | 1.75 | 1.75 | 0.88 | 365 | 8745 | 540 | 360 | -22.9116 | -3.8263 | 514.284 | 8.5076 | 52.3856 | 5.8147 | 5.8147 | 47.1735 | 132.8265 | 56.6438 | 0 | 0 | 1.4937 | 1.4937 | -106.7915 | 0% | 0.67546 | 0 | 0 | 109.6722 | 109.6722 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.1862 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8746 | 10 | 1.4 | 0.19 | 17.22 | 17.41 | 17.22 | 8.61 | 365 | 8746 | 600 | 360 | -22.9116 | -3.8263 | 574.284 | 9.5076 | 37.3856 | 12.5634 | 12.5634 | 34.9592 | 145.0408 | 43.9909 | 0.62843 | 0.62843 | 14.6982 | 15.3266 | -9.5058 | 0% | 6.9307 | 0 | 0 | 111.9413 | 111.9413 | 0% | 12.15% | 0% | 80% | 0% | 0 | 9.8218 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8747 | 11 | 3.2 | 1.11 | 51.11 | 52.22 | 51.11 | 25.56 | 365 | 8747 | 660 | 360 | -22.9116 | -3.8263 | 634.284 | 10.5076 | 22.3856 | 17.4318 | 17.4318 | 21.5725 | 158.4275 | 32.9438 | 3.1095 | 3.1095 | 43.6251 | 46.7346 | -2.4832 | 0% | 21.1334 | 0 | 0 | 115.4276 | 115.4276 | 0% | 12.05% | 12.05% | 80% | 9.638% | 2.0369 | 9.2438 | 6 | 12.2215 | 4.5045 | 10.59% | 10.59%
12 | 365 | 31 | 8748 | 12 | 4.5 | 4.44 | 107.78 | 112.22 | 107.78 | 53.89 | 365 | 8748 | 720 | 360 | -22.9116 | -3.8263 | 694.284 | 11.5076 | 7.3856 | 19.991 | 19.991 | 7.2383 | 172.7617 | 25.7173 | 11.7009 | 11.7009 | 91.996 | 103.6968 | -0.64718 | 0% | 46.8917 | 0 | 0 | 118.8198 | 118.8198 | 0% | 11.95% | 11.95% | 80% | 9.556% | 4.4812 | 8.8405 | 6 | 26.8872 | 9.9098 | 22.63% | 22.63%
12 | 365 | 31 | 8749 | 13 | 4.9 | 1.67 | 111.39 | 113.06 | 111.39 | 55.7 | 365 | 8749 | 780 | 360 | -22.9116 | -3.8263 | 754.284 | 12.5076 | -7.6144 | 19.9709 | 19.9709 | 7.4616 | 187.4616 | 25.7806 | 4.4029 | 4.4029 | 95.0773 | 99.4802 | -0.69902 | 0% | 44.9849 | 0 | 0 | 119.2048 | 119.2048 | 0% | 11.93% | 11.93% | 80% | 9.547% | 4.2947 | 8.7188 | 6 | 25.7683 | 9.4974 | 21.62% | 21.62%
12 | 365 | 31 | 8750 | 14 | 6.3 | 1.53 | 97.5 | 99.03 | 97.5 | 48.75 | 365 | 8750 | 840 | 360 | -22.9116 | -3.8263 | 814.284 | 13.5076 | -22.6144 | 17.3739 | 17.3739 | 21.7849 | 201.7849 | 33.0917 | 4.2927 | 4.2927 | 83.2215 | 87.5142 | -0.86623 | 0% | 39.5739 | 0 | 0 | 120.4337 | 120.4337 | 0% | 11.89% | 11.89% | 80% | 9.511% | 3.7639 | 8.3016 | 6 | 22.5835 | 8.3235 | 18.75% | 18.75%
12 | 365 | 31 | 8751 | 15 | 5.5 | 0.56 | 69.25 | 69.81 | 69.25 | 34.63 | 365 | 8751 | 900 | 360 | -22.9116 | -3.8263 | 874.284 | 14.5076 | -37.6144 | 12.4734 | 12.4734 | 35.1545 | 215.1545 | 44.1753 | 1.8596 | 1.8596 | 59.1086 | 60.9681 | -1.6248 | 0% | 27.5698 | 0 | 0 | 138.2595 | 138.2595 | 0% | 11.94% | 0% | 80% | 0% | 0 | 8.5383 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8752 | 16 | 4.9 | 0.19 | 39.53 | 39.72 | 39.53 | 19.77 | 365 | 8752 | 960 | 360 | -22.9116 | -3.8263 | 934.284 | 15.5076 | -52.6144 | 5.6996 | 5.6996 | 47.351 | 227.351 | 56.8437 | 0 | 0 | 33.741 | 33.741 | -3.6274 | 0% | 15.2577 | 0 | 0 | 135.5036 | 135.5036 | 0% | 11.99% | 0% | 80% | 0% | 0 | 8.7188 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8753 | 17 | 3.69 | 0 | 13.97 | 13.97 | 13.97 | 6.99 | 365 | 8753 | 1020 | 360 | -22.9116 | -3.8263 | 994.284 | 16.5076 | -67.6144 | -2.4909 | 0 | 55.3557 | 235.3557 | 66.2982 | 0 | 0 | 11.9241 | 11.9241 | -11.98 | 0% | 5.3921 | 0 | 0 | 131.9424 | 131.9424 | 0% | 12.06% | 0% | 80% | 0% | 0 | 9.0904 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8754 | 18 | 2.88 | 0 | 0 | 0 | 0 | 0 | 365 | 8754 | 1080 | 360 | -22.9116 | -3.8263 | 1054.284 | 17.5076 | -82.6144 | -11.6894 | 0 | 55.3557 | 235.3557 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 129.4414 | 129.4414 | 0% | 12.11% | 0% | 80% | 0% | 0 | 9.3449 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8755 | 19 | 2.14 | 0 | 0 | 0 | 0 | 0 | 365 | 8755 | 1140 | 360 | -22.9116 | -3.8263 | 1114.284 | 18.5076 | -97.6144 | -21.5478 | 0 | 55.3557 | 235.3557 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 127.5107 | 127.5107 | 0% | 12.14% | 0% | 80% | 0% | 0 | 9.5814 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8756 | 20 | 1.46 | 0 | 0 | 0 | 0 | 0 | 365 | 8756 | 1200 | 360 | -22.9116 | -3.8263 | 1174.284 | 19.5076 | -112.6144 | -31.7526 | 0 | 55.3557 | 235.3557 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 125.2821 | 125.2821 | 0% | 12.17% | 0% | 80% | 0% | 0 | 9.8021 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8757 | 21 | 0.82 | 0 | 0 | 0 | 0 | 0 | 365 | 8757 | 1260 | 360 | -22.9116 | -3.8263 | 1234.284 | 20.5076 | -127.6144 | -41.9666 | 0 | 55.3557 | 235.3557 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -21.9788 | 0 | 0% | 12.2% | 0% | 80% | 0% | 0 | 10.0128 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8758 | 22 | 0.22 | 0 | 0 | 0 | 0 | 0 | 365 | 8758 | 1320 | 360 | -22.9116 | -3.8263 | 1294.284 | 21.5076 | -142.6144 | -51.7119 | 0 | 55.3557 | 235.3557 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.1537 | 0 | 0% | 12.22% | 0% | 80% | 0% | 0 | 10.213 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8759 | 23 | -0.35 | 0 | 0 | 0 | 0 | 0 | 365 | 8759 | 1380 | 360 | -22.9116 | -3.8263 | 1354.284 | 22.5076 | -157.6144 | -60.1068 | 0 | 55.3557 | 235.3557 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -23.9512 | 0 | 0% | 12.25% | 0% | 80% | 0% | 0 | 10.4054 | 6 | 0 | 0 | 0% | 0%
12 | 365 | 31 | 8760 | 24 | -0.89 | 0 | 0 | 0 | 0 | 0 | 365 | 8760 | 1440 | 360 | -22.9116 | -3.8263 | 1414.284 | 23.5076 | -172.6144 | -65.403 | 0 | 55.3557 | 235.3557 | 66.2982 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | -24.703 | 0 | 0% | 12.27% | 0% | 80% | 0% | 0 | 10.5899 | 6 | 0 | 0 | 0% | 0%
[15 empty] | 23.3157 | [8 empty] | 114.1215 | [5 empty] | 69.1%
[15 empty] | -23.2819 | [8 empty] | 4.1496 | [5 empty] | 0%

## Legend
Legend:
Symbol | Formula | U.M. | Significance
text |  | [°] | exterior temperature
tr |  | [°] | dew point
w |  | [m/s] | wind velocity
j |  | [%] | relative humidity of air
x |  | [g/m³] | absolute humidity of air
IDir oriz |  | [W/m²] | direct horizontal intensity
IDif oriz |  | [W/m²] | diffuse horizontal intensity
ITot oriz |  | [W/m²] | total horizontal intensity
ITot verticala |  | [W/m²] | total vertical intensity
IDif vert |  | [W/m²] | diffuse vertical intensity
LT |  | [min] | local time
y | 360°·(day of the year/number of the days of the year) | [°] | Day angle
δ(y) | 0.3948-23.25559·cos(y + 9.1°)-0.3915·cos(2y+5.4°)-0.1764·cos(3y+105.2°) | [°] | declination of the Sun
EQT(y) | 0.0066+7.3525·cos(y+85.9°)+9.9359·cos(2y+108.9°)+0.3387·cos(3y+105.2°) | [min] | the difference over the course of a year between the time as read from a sundial and a clock
MLT | LT-TZ+λ·4 min/° | [min] | mean local time
ST | MLT+EQT | [h] | solar time
ω | (12-ST)·15°/h | [°] | hour angle of the Sun
γs | arcsin(cos(ω)·cos(φ)·cos(δ) + sin(φ)·sin(δ)) | [°] | the angle of solar altitude
γs, interm | arcsin(cos(ω)·cos(φ)·cos(δ) + sin(φ)·sin(δ)) | [°] | intermediate value of angle of solar altitude
αs | 180°±arcos((sin(γS)·sin(φ)-sin(δ))/(cos(γS)·cos(φ))) | [°] | the angle of solar azimuth, ± = "+" if ST > 12:00 and "-" if ST < 12:00
αs, interm | 180°±arcos((sin(γS)·sin(φ)-sin(δ))/(cos(γS)·cos(φ))) | [°] | intermediate value of angle of solar azimuth
θ | arcos (- cos(γS)·sin(γt)·cos(αS - αt) + sin(γS)·cos(γt)) | [°] | solar angle of incidence on a tilted surface
Idirt | Idir·cos(θ)/sin(γS) | [W/m2] | direct normal radiation on a tilted surface
Idift | Idifti | [W/m2] | diffuse normal radiation on a tilted surface
Idifti | Idif·(1 +cos(γt))/2 | [W/m2] | diffuse radiation constant across the whole sky (isotropic assumption)
Igt | Idirt+Idift | [W/m2] | global solar radiation on a tilted surface
η | η0-(k1·(Δt/Igt)-k2·(Δt2/Igt)) | [%] | thermal efficiency of the thermal solar collectors
ηinterm | η0-(k1·(Δt/Igt)-k2·(Δt2/Igt)) | [%] | intermediate value of solar thermal efficiency of the thermal solar collectors
P | Igt·S/1000 | [kW] | thermal power | βref | 0.004
QS | P·η | [kW] | thermal power of the solar field | GNOCT | 800
Q0a | COPa·QS | [kW] | total cooling power of the absorption solar cooling system |  | 293
Q0,load |  | [kW] | total cooling load (need) of the building
SFa | Q0/Q0,load | [%] | solar fraction of absorption system
ηPV,interm | ηTref ·(1-βref ·(Text-Tref +(TNOCT-Tref)·(Igt/IgNOCT))) | [%] | intermediate value of electrical efficiency of the photovoltaic collectors
ηPV | ηTref ·(1-βref ·(Text-Tref +(TNOCT-Tref)·(Tgt/IgNOCT))) | [%] | electrical efficiency of the photovoltaic collectors
ηDCAC |  | [%] | conversion efficiency from the direct current provided by the photovoltaic collectors to the alternative current consumed by the electric chiller
ηgPV | ηPV·ηDCAC | [%] | global efficiency of the photovoltaic system
Pe | (Igt·ηgPV·S)/1000 | [kW] | electric power provided by the photovoltaic field
COPe,interm | 0.0035·text2-(0.3372·text2)+10.287 | [-] | intermediate value of coefficient of performance of the electric chiller
COPe | 0.0035·text2-(0.3372·text2)+10.287 | [-] | coefficient of performance of the electric chiller
Q0,PV | Pe·COPe | [kW] | cooling power of the photovoltaic cooling system
PPV1 | Pe·1000/S | [W/m2] | the ratio between electric power and the area of photovoltaic field
SFPV | Q0PV/Q0,load | [%] | solar fraction of photovoltaic system
SFPV,interm | Q0PV/Q0,load | [%] | intermediate value of solar fraction of photovoltaic system